## Contents
SHEPD Network Scenario Headroom Report 2023 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations up to 2050. SHEPD have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
May 2023
Version 1.1

## Key Information
SHEPD Network Scenario Headroom Report 2023 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. Where the capacity is shown as 0 MVA, this signifies that there may be no alternative supplies to restore power to these sites. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD.
`
May 2023
Version 1.1

## Primary Headroom Dem
Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | NO | 0.19179 | 0.1855 | 0.18071 | 0.15412 | 0.12592 | 0.10867 | 0.057268 | 0.042322 | -0.00031123 | -0.020938 | -0.057256 | -0.1541 | -0.28845 | -0.42362 | 0.18987 | 0.18744 | 0.1853 | 0.14649 | 0.11624 | 0.096626 | 0.032614 | 0.014239 | -0.035566 | -0.055628 | -0.098505 | -0.2098 | -0.37134 | -0.53615 | 0.17663 | 0.17128 | 0.16709 | 0.13131 | 0.098386 | 0.077749 | 0.013637 | -0.0048639 | -0.056511 | -0.0797 | -0.12423 | -0.24085 | -0.40569 | -0.57221
| ABERCHALDER | CT |  |  |  | 0.19374 | 0.1894 | 0.18669 | 0.17729 | 0.16658 | 0.11976 | 0.077779 | 0.066941 | 0.048154 | 0.023169 | -0.013937 | -0.1036 | -0.19431 | -0.28596 | 0.19057 | 0.18879 | 0.18744 | 0.17965 | 0.1684 | 0.1185 | 0.068092 | 0.054881 | 0.031492 | 0.0065363 | -0.038182 | -0.14731 | -0.25451 | -0.36837 | 0.17829 | 0.17456 | 0.17215 | 0.16227 | 0.14986 | 0.095274 | 0.043757 | 0.030455 | 0.0070583 | -0.021244 | -0.066388 | -0.17792 | -0.2884 | -0.40215
| ABERCHALDER | LW |  |  |  | 0.19179 | 0.1855 | 0.18071 | 0.17653 | 0.17371 | 0.17101 | 0.16372 | 0.16047 | 0.14975 | 0.14054 | 0.11941 | 0.085792 | -0.071912 | -0.29917 | 0.18987 | 0.18744 | 0.1853 | 0.18346 | 0.18203 | 0.18071 | 0.17742 | 0.17541 | 0.16357 | 0.15101 | 0.12714 | 0.091913 | -0.10176 | -0.38416 | 0.17663 | 0.17128 | 0.16709 | 0.16343 | 0.16088 | 0.15844 | 0.15189 | 0.14887 | 0.13653 | 0.12407 | 0.097478 | 0.059609 | -0.13606 | -0.41941
| ABERCHALDER | ST |  |  |  | 0.19377 | 0.19166 | 0.18752 | 0.15412 | 0.12592 | 0.10867 | 0.057268 | 0.042322 | -0.00031123 | -0.020938 | -0.057256 | -0.1541 | -0.28845 | -0.42362 | 0.19059 | 0.18972 | 0.18811 | 0.14649 | 0.11624 | 0.096626 | 0.032614 | 0.014239 | -0.035566 | -0.055628 | -0.098505 | -0.2098 | -0.37134 | -0.53615 | 0.17832 | 0.1765 | 0.17298 | 0.13131 | 0.098386 | 0.077749 | 0.013637 | -0.0048639 | -0.056511 | -0.0797 | -0.12423 | -0.24085 | -0.40569 | -0.57221
| ABERCHALDER | FS |  |  |  | 0.19379 | 0.19362 | 0.18956 | 0.18253 | 0.17347 | 0.16326 | 0.15491 | 0.14415 | 0.12773 | 0.11564 | 0.089215 | 0.059227 | 0.04457 | 0.024682 | 0.1906 | 0.19044 | 0.18886 | 0.18016 | 0.17071 | 0.15982 | 0.14954 | 0.13937 | 0.12082 | 0.10773 | 0.08059 | 0.057942 | 0.042961 | 0.021379 | 0.17834 | 0.17817 | 0.17471 | 0.16597 | 0.15553 | 0.14365 | 0.13332 | 0.12141 | 0.10182 | 0.08767 | 0.057427 | 0.026385 | 0.0097809 | -0.012851
TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 3.9457 | 3.8234 | 3.6043 | 3.2826 | 2.9508 | 2.6134 | 2.2038 | 1.8034 | 1.4481 | 1.0729 | 0.50745 | 0.47142 | 0.092292 | -0.10732 | 4.4326 | 4.3219 | 4.1786 | 4.0139 | 3.836 | 3.6384 | 3.3965 | 3.1623 | 2.9392 | 2.6985 | 2.3594 | 2.3598 | 2.1262 | 1.9215 | 3.5182 | 3.3616 | 3.1563 | 2.8906 | 2.5989 | 2.3007 | 1.9356 | 1.576 | 1.2534 | 0.91137 | 0.38892 | 0.37443 | 0.036817 | -0.14422
| ABERFELDY | CT |  |  |  | 3.9645 | 3.8461 | 3.68 | 3.4455 | 3.0796 | 2.7383 | 2.3752 | 2.0264 | 1.6873 | 1.3043 | 0.7255 | 0.47142 | 0.092292 | -0.10732 | 4.4608 | 4.3702 | 4.2463 | 4.0587 | 3.8496 | 3.6608 | 3.4422 | 3.2415 | 3.0316 | 2.7876 | 2.4461 | 2.3598 | 2.1262 | 1.9215 | 3.5776 | 3.4583 | 3.2959 | 3.0134 | 2.7001 | 2.3947 | 2.0715 | 1.7626 | 1.4581 | 1.1109 | 0.58209 | 0.37443 | 0.036817 | -0.14422
| ABERFELDY | LW |  |  |  | 3.9457 | 3.8234 | 3.6043 | 3.2826 | 2.9508 | 2.6134 | 2.2038 | 1.8034 | 1.4481 | 1.0729 | 0.50745 | 0.47354 | 0.27846 | 0.19686 | 4.4326 | 4.3219 | 4.1786 | 4.0139 | 3.836 | 3.6384 | 3.3965 | 3.1623 | 2.9392 | 2.6985 | 2.3594 | 2.432 | 2.328 | 2.265 | 3.5182 | 3.3616 | 3.1563 | 2.8906 | 2.5989 | 2.3007 | 1.9356 | 1.576 | 1.2534 | 0.91137 | 0.38892 | 0.38661 | 0.20815 | 0.12557
| ABERFELDY | ST |  |  |  | 3.9737 | 3.8857 | 3.7834 | 3.6645 | 3.5244 | 3.3763 | 3.2145 | 3.0674 | 2.8632 | 2.6266 | 2.2813 | 1.8494 | 1.5177 | 1.1708 | 4.4757 | 4.405 | 4.3196 | 4.2186 | 4.1015 | 3.9797 | 3.8431 | 3.7208 | 3.578 | 3.4126 | 3.1695 | 2.857 | 2.648 | 2.4276 | 3.6116 | 3.5247 | 3.4164 | 3.2903 | 3.1495 | 3.0013 | 2.8334 | 2.6788 | 2.4982 | 2.289 | 1.9725 | 1.5625 | 1.2742 | 0.97357
| ABERFELDY | FS |  |  |  | 3.9898 | 3.9222 | 3.8423 | 3.7481 | 3.6349 | 3.5191 | 3.3983 | 3.2526 | 3.0724 | 2.8745 | 2.572 | 2.0122 | 1.4428 | 1.1506 | 4.4869 | 4.4313 | 4.3634 | 4.2813 | 4.1843 | 4.0846 | 3.9801 | 3.8756 | 3.7569 | 3.6237 | 3.4222 | 3.0563 | 2.621 | 2.2974 | 3.6241 | 3.5562 | 3.4715 | 3.3642 | 3.2443 | 3.1181 | 2.9858 | 2.8523 | 2.6999 | 2.5293 | 2.2627 | 1.7657 | 1.2358 | 0.9794
STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | NO | 3.6283 | 3.6026 | 3.5527 | 3.4819 | 3.4058 | 3.3115 | 3.2108 | 3.1078 | 3.0411 | 2.9795 | 2.7417 | 2.7245 | 2.5563 | 2.4331 | 3.9836 | 3.9522 | 3.9054 | 3.858 | 3.7902 | 3.7315 | 3.6691 | 3.5939 | 3.5147 | 3.4285 | 3.2566 | 3.2997 | 3.1625 | 3.0322 | 3.6947 | 3.6421 | 3.5804 | 3.5093 | 3.4365 | 3.3595 | 3.2622 | 3.1677 | 3.1037 | 3.0205 | 2.8047 | 2.8055 | 2.6604 | 2.5488
| ABERFOYLE | CT |  |  |  | 3.6326 | 3.6026 | 3.5556 | 3.4985 | 3.4058 | 3.3115 | 3.2108 | 3.1078 | 3.0411 | 2.9795 | 2.8441 | 2.7951 | 2.566 | 2.4331 | 3.995 | 3.9706 | 3.9302 | 3.8629 | 3.7902 | 3.7315 | 3.6691 | 3.6058 | 3.544 | 3.4669 | 3.313 | 3.2997 | 3.1625 | 3.0322 | 3.7243 | 3.6895 | 3.6368 | 3.5464 | 3.453 | 3.3634 | 3.2687 | 3.1729 | 3.1176 | 3.0575 | 2.8911 | 2.866 | 2.6621 | 2.5488
| ABERFOYLE | LW |  |  |  | 3.6283 | 3.6054 | 3.5527 | 3.4819 | 3.4097 | 3.3323 | 3.2342 | 3.1362 | 3.0661 | 2.9868 | 2.7417 | 2.7245 | 2.5563 | 2.4372 | 3.9836 | 3.9522 | 3.9054 | 3.858 | 3.8057 | 3.7547 | 3.6775 | 3.5939 | 3.5147 | 3.4285 | 3.2566 | 3.3048 | 3.2318 | 3.1797 | 3.6947 | 3.6421 | 3.5804 | 3.5093 | 3.4365 | 3.3595 | 3.2622 | 3.1677 | 3.1037 | 3.0205 | 2.8047 | 2.8055 | 2.6604 | 2.5604
| ABERFOYLE | ST |  |  |  | 3.6366 | 3.6248 | 3.6104 | 3.5903 | 3.5657 | 3.5362 | 3.4884 | 3.4331 | 3.3714 | 3.3046 | 3.1507 | 3.0111 | 2.8396 | 2.72 | 4.0016 | 3.9871 | 3.9695 | 3.9444 | 3.9145 | 3.8816 | 3.8446 | 3.8023 | 3.7533 | 3.6971 | 3.5657 | 3.3931 | 3.2692 | 3.1485 | 3.7416 | 3.7192 | 3.6949 | 3.6579 | 3.6179 | 3.5754 | 3.5314 | 3.4829 | 3.4273 | 3.3694 | 3.2394 | 3.0689 | 2.9221 | 2.8207
| ABERFOYLE | FS |  |  |  | 3.6397 | 3.6307 | 3.6202 | 3.6048 | 3.5864 | 3.5649 | 3.5401 | 3.5102 | 3.461 | 3.4119 | 3.2958 | 3.1103 | 2.8285 | 2.7257 | 4.0072 | 3.995 | 3.9803 | 3.9608 | 3.9368 | 3.9109 | 3.8818 | 3.8492 | 3.8112 | 3.7703 | 3.6736 | 3.4702 | 3.2317 | 3.0614 | 3.7557 | 3.7379 | 3.7188 | 3.6921 | 3.6602 | 3.6268 | 3.5913 | 3.5527 | 3.5071 | 3.4634 | 3.3596 | 3.1486 | 2.9048 | 2.8172
KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | NO | 2.1018 | 2.0018 | 1.878 | 1.3241 | 0.73085 | -0.35574 | -1.5215 | -2.3281 | -2.5758 | -2.8395 | -3.3235 | -4.1155 | -4.4574 | -4.6517 | 2.3491 | 2.3242 | 2.2864 | 1.7179 | 1.0861 | -0.16401 | -1.5017 | -2.3753 | -2.6067 | -2.8509 | -3.301 | -4.0401 | -4.3909 | -4.6032 | 2.083 | 2.0488 | 2.0009 | 1.4205 | 0.77888 | -0.48124 | -1.8325 | -2.7196 | -2.9751 | -3.2463 | -3.747 | -4.4805 | -4.8697 | -5.0964
| ABERLOUR | CT |  |  |  | 2.1522 | 2.0831 | 1.9914 | 1.7925 | 1.5624 | 0.97658 | 0.35685 | 0.037109 | -0.13069 | -0.31456 | -0.66389 | -1.1152 | -1.4228 | -1.5752 | 2.35 | 2.3273 | 2.2864 | 2.1727 | 2.0138 | 1.3984 | 0.74166 | 0.47917 | 0.35399 | 0.22936 | -0.012265 | -0.33642 | -0.58072 | -0.7449 | 2.0896 | 2.0567 | 2.0043 | 1.8754 | 1.7033 | 1.0762 | 0.40724 | 0.13175 | -0.0046753 | -0.13864 | -0.42973 | -0.73986 | -1.0423 | -1.1978
| ABERLOUR | LW |  |  |  | 2.1018 | 2.0018 | 1.878 | 1.3241 | 0.73085 | -0.35574 | -1.5215 | -2.3281 | -2.5758 | -2.8395 | -3.3235 | -4.1155 | -4.4574 | -4.6517 | 2.3491 | 2.3242 | 2.288 | 1.7179 | 1.0861 | -0.16401 | -1.5017 | -2.3753 | -2.6067 | -2.8509 | -3.301 | -4.0401 | -4.3909 | -4.6032 | 2.083 | 2.0488 | 2.0009 | 1.4205 | 0.77888 | -0.48124 | -1.8325 | -2.7196 | -2.9751 | -3.2463 | -3.747 | -4.4805 | -4.8697 | -5.0964
| ABERLOUR | ST |  |  |  | 2.1615 | 2.1222 | 2.0597 | 1.5842 | 1.2571 | 1.0213 | 0.32161 | 0.010029 | -0.19849 | -0.32834 | -0.60902 | -1.2465 | -1.5977 | -1.8461 | 2.3509 | 2.3389 | 2.3221 | 1.7814 | 1.4122 | 1.1604 | 0.33176 | 0.013349 | -0.19853 | -0.30238 | -0.53709 | -0.83367 | -1.1408 | -1.3564 | 2.0936 | 2.0739 | 2.0503 | 1.5046 | 1.1309 | 0.87375 | 0.038845 | -0.28701 | -0.50684 | -0.62036 | -0.87774 | -1.1123 | -1.4291 | -1.6709
| ABERLOUR | FS |  |  |  | 2.1686 | 2.1466 | 2.1008 | 1.9689 | 1.8414 | 1.7011 | 1.5548 | 1.3761 | 1.2627 | 1.1582 | 0.94363 | 0.51006 | 0.17205 | 0.027841 | 2.353 | 2.3419 | 2.3289 | 2.2088 | 2.0906 | 1.9529 | 1.8133 | 1.6383 | 1.5529 | 1.4831 | 1.3376 | 1.3283 | 1.0916 | 0.94216 | 2.0982 | 2.0809 | 2.0608 | 1.936 | 1.814 | 1.6722 | 1.5279 | 1.3483 | 1.2567 | 1.1801 | 1.0193 | 1.0225 | 0.80581 | 0.68378
ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | NO | 1.231 | 1.1828 | 1.1166 | 1.053 | 0.94763 | 0.87092 | 0.75238 | 0.66847 | 0.59567 | 0.52001 | 0.36935 | 0.1417 | -0.32418 | -1.1315 | 1.5268 | 1.5073 | 1.4699 | 1.4298 | 1.3647 | 1.2867 | 1.1983 | 1.1529 | 1.0732 | 1.0135 | 0.87675 | 0.63993 | 0.088342 | -0.7951 | 1.5086 | 1.4762 | 1.4221 | 1.3656 | 1.2707 | 1.1808 | 1.0587 | 0.98006 | 0.89989 | 0.81667 | 0.65354 | 0.38194 | -0.19687 | -1.161
| ABERNETHY | CT |  |  |  | 1.2738 | 1.2265 | 1.1758 | 1.086 | 0.98744 | 0.87092 | 0.75238 | 0.66847 | 0.59567 | 0.52001 | 0.36935 | 0.1417 | -0.23669 | -0.58925 | 1.548 | 1.515 | 1.4797 | 1.43 | 1.3716 | 1.2867 | 1.1983 | 1.1529 | 1.0842 | 1.0177 | 0.88372 | 0.68971 | 0.31504 | -0.088586 | 1.5378 | 1.496 | 1.4507 | 1.3807 | 1.2997 | 1.1808 | 1.0587 | 0.98006 | 0.89989 | 0.81667 | 0.65354 | 0.38194 | -0.04911 | -0.47349
| ABERNETHY | LW |  |  |  | 1.231 | 1.1828 | 1.1166 | 1.053 | 0.94763 | 0.89044 | 0.82192 | 0.75347 | 0.68149 | 0.60625 | 0.46419 | 0.27723 | -0.32418 | -1.1315 | 1.5268 | 1.5073 | 1.4699 | 1.4397 | 1.3647 | 1.3404 | 1.3099 | 1.278 | 1.2132 | 1.145 | 1.0188 | 0.89535 | 0.19308 | -0.7951 | 1.5086 | 1.4762 | 1.4221 | 1.3656 | 1.2707 | 1.2203 | 1.159 | 1.0974 | 1.0198 | 0.93855 | 0.78704 | 0.5671 | -0.16204 | -1.161
| ABERNETHY | ST |  |  |  | 1.2954 | 1.2582 | 1.2211 | 1.1421 | 1.0723 | 1.0219 | 0.92946 | 0.87976 | 0.75739 | 0.68714 | 0.53371 | 0.19815 | -0.31213 | -0.82762 | 1.5558 | 1.5292 | 1.5023 | 1.4298 | 1.3664 | 1.3297 | 1.2389 | 1.2017 | 1.0732 | 1.0135 | 0.87675 | 0.63993 | 0.088342 | -0.49774 | 1.5506 | 1.5191 | 1.4873 | 1.4073 | 1.3371 | 1.2918 | 1.1917 | 1.1448 | 1.0064 | 0.93497 | 0.77277 | 0.40419 | -0.19687 | -0.8155
| ABERNETHY | FS |  |  |  | 1.3724 | 1.3425 | 1.3121 | 1.2663 | 1.225 | 1.1828 | 1.1404 | 1.0936 | 1.0202 | 0.95793 | 0.8181 | 0.57129 | 0.42761 | 0.32502 | 1.6325 | 1.6084 | 1.5841 | 1.5532 | 1.5235 | 1.4918 | 1.4598 | 1.4271 | 1.363 | 1.3115 | 1.1958 | 1.1112 | 1.0472 | 0.93481 | 1.6277 | 1.6006 | 1.573 | 1.5351 | 1.4991 | 1.461 | 1.4221 | 1.3812 | 1.3084 | 1.2463 | 1.105 | 0.87725 | 0.73992 | 0.63215
TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 7.5063 | 7.1468 | 6.735 | 6.2918 | 5.8233 | 5.3685 | 4.7423 | 4.0553 | 3.6886 | 3.356 | 2.6721 | 2.7932 | 2.0531 | 1.6627 | 9.3399 | 9.1903 | 9.0062 | 8.8154 | 8.6027 | 8.3087 | 7.9678 | 7.599 | 7.3353 | 7.1153 | 6.6747 | 6.7632 | 6.2388 | 5.7805 | 8.4224 | 8.1447 | 7.828 | 7.4981 | 7.1511 | 6.712 | 6.1783 | 5.6028 | 5.2546 | 4.9997 | 4.4468 | 4.6573 | 3.9081 | 3.5335
| ABOYNE | CT |  |  |  | 7.7377 | 7.4903 | 7.1908 | 6.5995 | 5.9867 | 5.3867 | 4.7423 | 4.0553 | 3.6886 | 3.356 | 2.6909 | 2.8726 | 2.0531 | 1.6627 | 9.4219 | 9.3083 | 9.1582 | 8.8871 | 8.6027 | 8.3087 | 7.9678 | 7.599 | 7.3353 | 7.1153 | 6.6747 | 6.7632 | 6.2388 | 5.7805 | 8.5916 | 8.3771 | 8.1176 | 7.6594 | 7.2004 | 6.712 | 6.1783 | 5.6028 | 5.2546 | 4.9997 | 4.4468 | 4.6573 | 3.9081 | 3.5335
| ABOYNE | LW |  |  |  | 7.5063 | 7.1468 | 6.735 | 6.2918 | 5.8233 | 5.3685 | 4.7948 | 4.1292 | 3.7199 | 3.3799 | 2.6721 | 2.7932 | 2.3132 | 1.9164 | 9.3399 | 9.1903 | 9.0062 | 8.8154 | 8.6101 | 8.4123 | 8.12 | 7.7456 | 7.4665 | 7.2539 | 6.8091 | 6.9981 | 6.6681 | 6.3151 | 8.4224 | 8.1447 | 7.828 | 7.4981 | 7.1511 | 6.8045 | 6.3616 | 5.8279 | 5.4734 | 5.1875 | 4.5192 | 4.6594 | 4.1856 | 3.7589
| ABOYNE | ST |  |  |  | 7.9109 | 7.7724 | 7.6187 | 7.3841 | 7.1414 | 6.8984 | 6.5737 | 6.2029 | 5.7923 | 5.4519 | 4.6962 | 3.7993 | 3.005 | 2.4103 | 9.4926 | 9.4307 | 9.3597 | 9.226 | 9.0936 | 8.9638 | 8.7409 | 8.4931 | 8.2102 | 8.0059 | 7.5426 | 7.0908 | 6.5116 | 5.963 | 8.725 | 8.6119 | 8.4882 | 8.2858 | 8.0822 | 7.8761 | 7.5785 | 7.2438 | 6.8678 | 6.5666 | 5.8839 | 5.4599 | 4.7112 | 4.1457
| ABOYNE | FS |  |  |  | 7.9755 | 7.8877 | 7.7798 | 7.6004 | 7.4093 | 7.2102 | 6.9842 | 6.7032 | 6.3734 | 6.0908 | 5.4822 | 4.0328 | 3.0079 | 2.5733 | 9.5213 | 9.4763 | 9.4246 | 9.3388 | 9.2451 | 9.1454 | 9.0174 | 8.8356 | 8.6324 | 8.4751 | 8.1282 | 7.468 | 6.7056 | 6.1194 | 8.7801 | 8.7 | 8.6135 | 8.4672 | 8.3128 | 8.1486 | 7.9586 | 7.7119 | 7.4266 | 7.1895 | 6.6744 | 5.7818 | 4.836 | 4.4516
GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0.29438 | 0.27909 | 0.25843 | 0.23847 | 0.2138 | 0.19218 | 0.16467 | 0.13433 | 0.11225 | 0.085364 | 0.036131 | 0.01341 | -0.0098445 | -0.022011 | 0.33743 | 0.33014 | 0.31862 | 0.3081 | 0.29308 | 0.28128 | 0.26765 | 0.24861 | 0.2308 | 0.21061 | 0.17238 | 0.1579 | 0.14176 | 0.12912 | 0.67839 | 0.66682 | 0.65252 | 0.63883 | 0.62221 | 0.60603 | 0.58834 | 0.56521 | 0.54611 | 0.51995 | 0.47064 | 0.44742 | 0.43095 | 0.42005
| ACHILTIBUIE | CT |  |  |  | 0.30223 | 0.29129 | 0.27655 | 0.24956 | 0.21816 | 0.19553 | 0.17156 | 0.14506 | 0.12348 | 0.10022 | 0.054388 | 0.024218 | -0.0098445 | -0.022011 | 0.34023 | 0.3345 | 0.32584 | 0.31048 | 0.29308 | 0.28128 | 0.26879 | 0.25547 | 0.24046 | 0.22137 | 0.18468 | 0.15935 | 0.14176 | 0.12912 | 0.68461 | 0.67558 | 0.66491 | 0.64675 | 0.62733 | 0.61109 | 0.59407 | 0.57433 | 0.55648 | 0.53549 | 0.48903 | 0.45646 | 0.43095 | 0.42005
| ACHILTIBUIE | LW |  |  |  | 0.29438 | 0.27909 | 0.25843 | 0.23847 | 0.2138 | 0.19218 | 0.16467 | 0.13433 | 0.11225 | 0.085364 | 0.036131 | 0.01341 | -0.0049462 | -0.0089407 | 0.33743 | 0.33014 | 0.31862 | 0.3081 | 0.29521 | 0.28437 | 0.26765 | 0.24861 | 0.2308 | 0.21061 | 0.17238 | 0.1579 | 0.15086 | 0.14952 | 0.67839 | 0.66682 | 0.65252 | 0.63883 | 0.62221 | 0.60603 | 0.58834 | 0.56521 | 0.54611 | 0.51995 | 0.47064 | 0.44742 | 0.43405 | 0.43135
| ACHILTIBUIE | ST |  |  |  | 0.30567 | 0.29998 | 0.29142 | 0.28264 | 0.2738 | 0.26274 | 0.24898 | 0.23505 | 0.2211 | 0.20301 | 0.1613 | 0.067134 | 0.033889 | 0.016193 | 0.3413 | 0.33839 | 0.33412 | 0.32927 | 0.32374 | 0.31717 | 0.30903 | 0.3001 | 0.29008 | 0.27752 | 0.24774 | 0.17872 | 0.15824 | 0.14571 | 0.68498 | 0.68333 | 0.67666 | 0.67047 | 0.66465 | 0.65681 | 0.64731 | 0.63787 | 0.62917 | 0.61779 | 0.58321 | 0.49029 | 0.46353 | 0.45158
| ACHILTIBUIE | FS |  |  |  | 0.30717 | 0.30522 | 0.29921 | 0.29043 | 0.28143 | 0.27182 | 0.26272 | 0.2483 | 0.23563 | 0.22488 | 0.19255 | 0.092216 | 0.017351 | 0.0052204 | 0.3419 | 0.34033 | 0.33708 | 0.33265 | 0.3276 | 0.32227 | 0.31666 | 0.30878 | 0.3009 | 0.29302 | 0.27196 | 0.20738 | 0.15152 | 0.13793 | 0.68514 | 0.68444 | 0.68295 | 0.67624 | 0.67016 | 0.66332 | 0.65694 | 0.64684 | 0.63858 | 0.63198 | 0.60945 | 0.5229 | 0.45126 | 0.44245
BROADFORD | ACHINTEE | MINIMUM HEADROOM | NG 93973 41406 | YES | NO | 0.94503 | 0.94439 | 0.94306 | 0.93924 | 0.93793 | 0.93686 | 0.93468 | 0.9322 | 0.92837 | 0.92309 | 0.91083 | 0.9189 | 0.91761 | 0.91517 | 0.96557 | 0.96508 | 0.96409 | 0.96192 | 0.96096 | 0.96012 | 0.95851 | 0.95666 | 0.95438 | 0.95022 | 0.94114 | 0.94798 | 0.94742 | 0.94599 | 0.95407 | 0.95347 | 0.95225 | 0.94801 | 0.94682 | 0.94582 | 0.9438 | 0.94153 | 0.93793 | 0.93261 | 0.92083 | 0.92936 | 0.92822 | 0.92576
| ACHINTEE | CT |  |  |  | 0.94511 | 0.9445 | 0.94344 | 0.94167 | 0.93848 | 0.93729 | 0.93468 | 0.93342 | 0.93128 | 0.927 | 0.9186 | 0.9189 | 0.91825 | 0.91517 | 0.96562 | 0.96512 | 0.96431 | 0.96299 | 0.96101 | 0.96012 | 0.95851 | 0.95754 | 0.95596 | 0.9531 | 0.94741 | 0.94798 | 0.94748 | 0.94599 | 0.95413 | 0.95352 | 0.95252 | 0.9509 | 0.94767 | 0.94658 | 0.9438 | 0.94262 | 0.94066 | 0.93652 | 0.92828 | 0.92936 | 0.92871 | 0.92576
| ACHINTEE | LW |  |  |  | 0.94503 | 0.94439 | 0.94306 | 0.93924 | 0.93793 | 0.93686 | 0.93473 | 0.9322 | 0.92837 | 0.92309 | 0.91083 | 0.91978 | 0.91833 | 0.91696 | 0.96557 | 0.96508 | 0.96409 | 0.96192 | 0.96096 | 0.96014 | 0.95855 | 0.95666 | 0.95438 | 0.95022 | 0.94114 | 0.94824 | 0.94756 | 0.94693 | 0.95407 | 0.95347 | 0.95225 | 0.94801 | 0.94682 | 0.94582 | 0.94386 | 0.94153 | 0.93793 | 0.93261 | 0.92083 | 0.93007 | 0.92877 | 0.92757
| ACHINTEE | ST |  |  |  | 0.94513 | 0.94486 | 0.94449 | 0.94399 | 0.9433 | 0.94252 | 0.94155 | 0.94038 | 0.94012 | 0.9373 | 0.92791 | 0.92193 | 0.91761 | 0.91758 | 0.96564 | 0.96544 | 0.96516 | 0.96478 | 0.96426 | 0.96368 | 0.96294 | 0.96205 | 0.9615 | 0.96013 | 0.95388 | 0.94989 | 0.94742 | 0.94739 | 0.95416 | 0.95391 | 0.95357 | 0.9531 | 0.95247 | 0.95174 | 0.95084 | 0.94974 | 0.9497 | 0.94773 | 0.93747 | 0.93218 | 0.92822 | 0.92818
| ACHINTEE | FS |  |  |  | 0.94515 | 0.94493 | 0.94463 | 0.94423 | 0.9437 | 0.94314 | 0.94246 | 0.94165 | 0.94067 | 0.93953 | 0.93542 | 0.92538 | 0.91763 | 0.91757 | 0.96566 | 0.96549 | 0.96526 | 0.96497 | 0.96458 | 0.96415 | 0.96364 | 0.96304 | 0.96231 | 0.96146 | 0.95873 | 0.95288 | 0.94743 | 0.94738 | 0.95419 | 0.95398 | 0.9537 | 0.95333 | 0.95285 | 0.95233 | 0.9517 | 0.95095 | 0.95005 | 0.949 | 0.94487 | 0.93573 | 0.92824 | 0.92817
BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0.46422 | 0.45662 | 0.44815 | 0.43675 | 0.42535 | 0.40529 | 0.38428 | 0.37053 | 0.35625 | 0.34556 | 0.31031 | 0.28002 | 0.24311 | 0.21022 | 0.52207 | 0.51832 | 0.51326 | 0.50744 | 0.4982 | 0.48183 | 0.46525 | 0.45625 | 0.44409 | 0.43138 | 0.40299 | 0.36628 | 0.32297 | 0.28188 | 0.50011 | 0.49317 | 0.48523 | 0.47482 | 0.46432 | 0.4423 | 0.42067 | 0.40734 | 0.39207 | 0.37872 | 0.34295 | 0.30848 | 0.26467 | 0.2251
| AIGAS | CT |  |  |  | 0.46826 | 0.46592 | 0.46053 | 0.44118 | 0.4275 | 0.40529 | 0.38428 | 0.37053 | 0.35625 | 0.34556 | 0.31031 | 0.28002 | 0.24311 | 0.21967 | 0.52354 | 0.52169 | 0.51803 | 0.50744 | 0.4982 | 0.48183 | 0.46525 | 0.45625 | 0.44409 | 0.43138 | 0.40299 | 0.36987 | 0.33738 | 0.30634 | 0.50364 | 0.50137 | 0.49624 | 0.47829 | 0.46464 | 0.4423 | 0.42067 | 0.40734 | 0.39207 | 0.37872 | 0.34295 | 0.30848 | 0.26982 | 0.24255
| AIGAS | LW |  |  |  | 0.46422 | 0.45662 | 0.44815 | 0.43675 | 0.42535 | 0.41259 | 0.39846 | 0.38568 | 0.37088 | 0.35792 | 0.32912 | 0.31052 | 0.27174 | 0.22422 | 0.52207 | 0.51832 | 0.51326 | 0.50746 | 0.50135 | 0.49513 | 0.48672 | 0.47759 | 0.46585 | 0.45448 | 0.43176 | 0.41697 | 0.37579 | 0.31956 | 0.50011 | 0.49317 | 0.48523 | 0.47482 | 0.46432 | 0.45273 | 0.43953 | 0.42666 | 0.41109 | 0.39729 | 0.36847 | 0.34892 | 0.30368 | 0.24568
| AIGAS | ST |  |  |  | 0.47383 | 0.46891 | 0.46774 | 0.45406 | 0.44336 | 0.43461 | 0.41782 | 0.41237 | 0.39308 | 0.38455 | 0.35173 | 0.28703 | 0.24465 | 0.21022 | 0.5256 | 0.52328 | 0.52216 | 0.51058 | 0.50165 | 0.49461 | 0.47815 | 0.47182 | 0.45566 | 0.44682 | 0.42196 | 0.36628 | 0.32297 | 0.28188 | 0.50852 | 0.50411 | 0.50295 | 0.48836 | 0.47709 | 0.46806 | 0.44924 | 0.44235 | 0.42199 | 0.41208 | 0.3789 | 0.31165 | 0.26467 | 0.2251
| AIGAS | FS |  |  |  | 0.47577 | 0.46947 | 0.46963 | 0.46511 | 0.45798 | 0.44756 | 0.44342 | 0.43568 | 0.42752 | 0.41826 | 0.39771 | 0.34337 | 0.30347 | 0.29516 | 0.52633 | 0.52354 | 0.52297 | 0.51943 | 0.51473 | 0.50856 | 0.5045 | 0.4991 | 0.49211 | 0.48509 | 0.46909 | 0.43234 | 0.40027 | 0.38599 | 0.50873 | 0.50463 | 0.50466 | 0.50005 | 0.49309 | 0.4832 | 0.47863 | 0.47097 | 0.46212 | 0.45259 | 0.43149 | 0.379 | 0.34028 | 0.33195
ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | NO | 4.8144 | 4.7631 | 4.7065 | 4.6335 | 4.5566 | 4.4729 | 4.3822 | 4.2679 | 4.1725 | 4.0654 | 3.8573 | 4.0908 | 4.0562 | 4.0314 | 5.7552 | 5.7177 | 5.6855 | 5.6422 | 5.5975 | 5.5514 | 5.49 | 5.429 | 5.3698 | 5.2917 | 5.1351 | 5.4708 | 5.4121 | 5.3075 | 4.473 | 4.4218 | 4.3746 | 4.3092 | 4.2437 | 4.1709 | 4.0837 | 4.0012 | 3.9335 | 3.856 | 3.6864 | 4.1647 | 4.1322 | 4.1131
| AIRD | CT |  |  |  | 4.8443 | 4.807 | 4.757 | 4.657 | 4.5572 | 4.4729 | 4.3822 | 4.3025 | 4.2363 | 4.1547 | 3.9864 | 4.1104 | 4.0562 | 4.0314 | 5.7814 | 5.7488 | 5.7099 | 5.6502 | 5.6028 | 5.5514 | 5.49 | 5.445 | 5.4051 | 5.3665 | 5.264 | 5.4708 | 5.4121 | 5.3456 | 4.5062 | 4.4644 | 4.4146 | 4.325 | 4.2498 | 4.1709 | 4.0837 | 4.0098 | 3.961 | 3.9198 | 3.82 | 4.1768 | 4.1322 | 4.1131
| AIRD | LW |  |  |  | 4.8144 | 4.7631 | 4.7065 | 4.6335 | 4.5566 | 4.4907 | 4.3824 | 4.2679 | 4.1725 | 4.0654 | 3.8573 | 4.0908 | 4.0628 | 4.0576 | 5.7552 | 5.7177 | 5.6855 | 5.6422 | 5.5975 | 5.5613 | 5.4909 | 5.429 | 5.3698 | 5.2917 | 5.1351 | 5.4863 | 5.4711 | 5.4682 | 4.473 | 4.4218 | 4.3746 | 4.3092 | 4.2437 | 4.1844 | 4.092 | 4.0012 | 3.9335 | 3.856 | 3.6864 | 4.1647 | 4.1379 | 4.1316
| AIRD | ST |  |  |  | 4.8552 | 4.8342 | 4.8071 | 4.7786 | 4.7414 | 4.701 | 4.6529 | 4.6062 | 4.5507 | 4.4833 | 4.3231 | 4.2243 | 4.1671 | 4.14 | 5.7874 | 5.7689 | 5.7475 | 5.7244 | 5.6998 | 5.6689 | 5.6275 | 5.597 | 5.5602 | 5.5148 | 5.3816 | 5.5313 | 5.4638 | 5.399 | 4.5177 | 4.4956 | 4.4687 | 4.4406 | 4.4067 | 4.3677 | 4.3206 | 4.2789 | 4.2297 | 4.1709 | 4.028 | 4.2593 | 4.2203 | 4.1876
| AIRD | FS |  |  |  | 4.889 | 4.8766 | 4.8518 | 4.8231 | 4.7971 | 4.7643 | 4.7222 | 4.6848 | 4.6385 | 4.5883 | 4.4753 | 4.3129 | 4.1272 | 4.1013 | 5.8256 | 5.8145 | 5.7949 | 5.7731 | 5.7551 | 5.7336 | 5.7 | 5.6746 | 5.6444 | 5.6114 | 5.5379 | 5.599 | 5.4173 | 5.3075 | 4.5563 | 4.5431 | 4.5183 | 4.4901 | 4.4659 | 4.4352 | 4.3939 | 4.3605 | 4.3196 | 4.2756 | 4.1789 | 4.2447 | 4.1886 | 4.1607
PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | NO | 0.32009 | 0.31782 | 0.31858 | 0.31544 | 0.30983 | 0.29914 | 0.29209 | 0.28939 | 0.28123 | 0.27794 | 0.27043 | 0.2499 | 0.2283 | 0.2041 | 0.33892 | 0.33792 | 0.33782 | 0.33233 | 0.32683 | 0.3226 | 0.31226 | 0.30737 | 0.29845 | 0.29484 | 0.28668 | 0.26409 | 0.23786 | 0.21078 | 0.31782 | 0.3158 | 0.31633 | 0.31175 | 0.30536 | 0.29607 | 0.28745 | 0.28274 | 0.27292 | 0.2691 | 0.26043 | 0.2361 | 0.20949 | 0.18053
| AIRIGH-NA-BRODAIG | CT |  |  |  | 0.32156 | 0.32213 | 0.32042 | 0.31553 | 0.31132 | 0.29914 | 0.29209 | 0.28939 | 0.28528 | 0.28067 | 0.27396 | 0.25177 | 0.23771 | 0.223 | 0.33964 | 0.33989 | 0.33871 | 0.33572 | 0.3326 | 0.3226 | 0.31413 | 0.31139 | 0.30685 | 0.30189 | 0.29291 | 0.27171 | 0.25458 | 0.23635 | 0.31931 | 0.31946 | 0.31805 | 0.3133 | 0.30902 | 0.29607 | 0.28745 | 0.28439 | 0.2796 | 0.27431 | 0.26572 | 0.24069 | 0.22328 | 0.20499
| AIRIGH-NA-BRODAIG | LW |  |  |  | 0.32009 | 0.31782 | 0.31858 | 0.31791 | 0.31525 | 0.30936 | 0.3029 | 0.30101 | 0.29811 | 0.29501 | 0.28919 | 0.28262 | 0.25741 | 0.21944 | 0.33892 | 0.33792 | 0.33782 | 0.33728 | 0.33595 | 0.3335 | 0.33054 | 0.32917 | 0.32635 | 0.32336 | 0.31752 | 0.30994 | 0.27884 | 0.23307 | 0.31782 | 0.3158 | 0.31633 | 0.31566 | 0.31324 | 0.308 | 0.30219 | 0.30036 | 0.2972 | 0.29384 | 0.28742 | 0.27911 | 0.24777 | 0.20107
| AIRIGH-NA-BRODAIG | ST |  |  |  | 0.32159 | 0.32148 | 0.32109 | 0.31544 | 0.30983 | 0.30546 | 0.29672 | 0.2897 | 0.28123 | 0.27794 | 0.27043 | 0.2499 | 0.2283 | 0.2041 | 0.33965 | 0.33952 | 0.33921 | 0.33233 | 0.32683 | 0.32292 | 0.31226 | 0.30737 | 0.29845 | 0.29484 | 0.28668 | 0.26409 | 0.23786 | 0.21078 | 0.31931 | 0.31913 | 0.31872 | 0.31175 | 0.30536 | 0.30059 | 0.28982 | 0.28274 | 0.27292 | 0.2691 | 0.26043 | 0.2361 | 0.20949 | 0.18053
| AIRIGH-NA-BRODAIG | FS |  |  |  | 0.32161 | 0.32151 | 0.32227 | 0.31982 | 0.31837 | 0.31549 | 0.31198 | 0.30855 | 0.30572 | 0.30319 | 0.29848 | 0.28746 | 0.28009 | 0.27469 | 0.33966 | 0.33955 | 0.33994 | 0.33773 | 0.33611 | 0.33369 | 0.33109 | 0.32865 | 0.32539 | 0.32283 | 0.3177 | 0.3098 | 0.30383 | 0.29987 | 0.31933 | 0.31918 | 0.3198 | 0.31718 | 0.31547 | 0.31237 | 0.30875 | 0.30527 | 0.3019 | 0.29904 | 0.2936 | 0.28239 | 0.27472 | 0.26912
COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | NO | 3.695 | 3.5115 | 3.2473 | 2.8949 | 2.5149 | 2.0991 | 1.5957 | 1.045 | 0.66465 | 0.3146 | -0.3323 | -0.87884 | -1.492 | -1.856 | 4.3164 | 4.2212 | 4.0688 | 3.8868 | 3.6974 | 3.4579 | 3.1751 | 2.9173 | 2.6817 | 2.4256 | 1.9499 | 1.5786 | 1.1293 | 0.6911 | 4.0826 | 3.9357 | 3.7168 | 3.4391 | 3.1352 | 2.8109 | 2.3993 | 1.9403 | 1.5942 | 1.2644 | 0.64729 | 0.11257 | -0.41873 | -0.78706
| ALYTH | CT |  |  |  | 3.7858 | 3.6517 | 3.452 | 3.0904 | 2.6927 | 2.2504 | 1.7722 | 1.3005 | 0.90671 | 0.49788 | -0.25299 | -0.87884 | -1.492 | -1.856 | 4.35 | 4.2737 | 4.1497 | 3.9432 | 3.7212 | 3.4579 | 3.1751 | 2.9173 | 2.6817 | 2.4256 | 1.9499 | 1.5786 | 1.1293 | 0.6911 | 4.1498 | 4.0403 | 3.8735 | 3.5709 | 3.234 | 2.8588 | 2.4542 | 2.0729 | 1.7276 | 1.3524 | 0.6593 | 0.11257 | -0.41873 | -0.78706
| ALYTH | LW |  |  |  | 3.695 | 3.5115 | 3.2473 | 2.8949 | 2.5149 | 2.0991 | 1.5957 | 1.045 | 0.66465 | 0.3146 | -0.3323 | -0.59711 | -1.068 | -1.4813 | 4.3164 | 4.2212 | 4.0688 | 3.8868 | 3.6974 | 3.4955 | 3.2357 | 2.9348 | 2.7055 | 2.4846 | 2.0695 | 2.0037 | 1.6209 | 1.1732 | 4.0826 | 3.9357 | 3.7168 | 3.4391 | 3.1352 | 2.8109 | 2.3993 | 1.9403 | 1.5942 | 1.2644 | 0.64729 | 0.44738 | -0.020358 | -0.49539
| ALYTH | ST |  |  |  | 3.811 | 3.705 | 3.5629 | 3.3492 | 3.1412 | 2.9199 | 2.6258 | 2.3579 | 2.1147 | 1.8927 | 1.4383 | 0.69715 | 0.081047 | -0.52054 | 4.36 | 4.3024 | 4.2179 | 4.0593 | 3.9179 | 3.7757 | 3.5547 | 3.3705 | 3.1784 | 3.0196 | 2.6779 | 2.1311 | 1.6018 | 1.0284 | 4.1681 | 4.0853 | 3.9751 | 3.7846 | 3.6012 | 3.4122 | 3.1383 | 2.9034 | 2.665 | 2.4536 | 2.0042 | 1.2475 | 0.65204 | 0.099041
| ALYTH | FS |  |  |  | 3.8296 | 3.746 | 3.6322 | 3.4762 | 3.3144 | 3.1327 | 2.9316 | 2.7185 | 2.524 | 2.3447 | 1.9878 | 1.2803 | 0.57304 | 0.19118 | 4.3683 | 4.3203 | 4.2504 | 4.1524 | 4.0515 | 3.9384 | 3.8126 | 3.6711 | 3.539 | 3.4142 | 3.1566 | 2.6741 | 2.0804 | 1.5466 | 4.1823 | 4.1168 | 4.0284 | 3.9022 | 3.768 | 3.6178 | 3.4509 | 3.2703 | 3.097 | 2.9349 | 2.6014 | 1.9379 | 1.2819 | 0.98493
FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 6.0823 | 5.9945 | 5.8915 | 5.7655 | 5.6324 | 5.4678 | 5.2879 | 5.1153 | 5.0463 | 4.9615 | 4.8006 | 4.7851 | 4.529 | 4.407 | 6.299 | 6.2602 | 6.2108 | 6.1541 | 6.079 | 5.9796 | 5.8794 | 5.7953 | 5.7421 | 5.6781 | 5.5547 | 5.5082 | 5.3184 | 5.1418 | 5.6305 | 5.5747 | 5.5071 | 5.4303 | 5.3264 | 5.1958 | 5.0643 | 4.9456 | 4.88 | 4.8212 | 4.694 | 4.7978 | 4.5866 | 4.4659
| ANNAT | CT |  |  |  | 6.1407 | 6.0807 | 6.0098 | 5.8336 | 5.6504 | 5.4678 | 5.2879 | 5.1153 | 5.0463 | 4.9615 | 4.8006 | 4.7851 | 4.529 | 4.407 | 6.3214 | 6.2928 | 6.255 | 6.1697 | 6.079 | 5.9796 | 5.8794 | 5.7953 | 5.7421 | 5.6781 | 5.5547 | 5.5082 | 5.3184 | 5.1418 | 5.663 | 5.6166 | 5.558 | 5.4412 | 5.3264 | 5.1958 | 5.0643 | 4.9456 | 4.88 | 4.8212 | 4.694 | 4.7978 | 4.5866 | 4.4659
| ANNAT | LW |  |  |  | 6.0823 | 5.9945 | 5.8915 | 5.7655 | 5.6324 | 5.5045 | 5.3501 | 5.186 | 5.105 | 5.0192 | 4.8465 | 4.8325 | 4.6297 | 4.4627 | 6.299 | 6.2602 | 6.2108 | 6.1541 | 6.0931 | 6.0353 | 5.9597 | 5.8772 | 5.8206 | 5.76 | 5.6395 | 5.6565 | 5.5013 | 5.3271 | 5.6305 | 5.5747 | 5.5071 | 5.4303 | 5.3492 | 5.268 | 5.1673 | 5.0584 | 4.9894 | 4.9147 | 4.7613 | 4.8854 | 4.6916 | 4.5047
| ANNAT | ST |  |  |  | 6.173 | 6.1384 | 6.1045 | 6.0372 | 5.9685 | 5.9053 | 5.8175 | 5.7413 | 5.6512 | 5.5671 | 5.3716 | 5.0635 | 4.8391 | 4.6579 | 6.3343 | 6.3183 | 6.3017 | 6.2551 | 6.2117 | 6.1731 | 6.1061 | 6.0593 | 5.9928 | 5.9377 | 5.8083 | 5.6011 | 5.3988 | 5.1831 | 5.6772 | 5.6565 | 5.6321 | 5.5752 | 5.5213 | 5.4706 | 5.39 | 5.3276 | 5.2461 | 5.1737 | 5.0022 | 4.98 | 4.7641 | 4.5917
| ANNAT | FS |  |  |  | 6.1917 | 6.1656 | 6.1409 | 6.0921 | 6.0409 | 5.9896 | 5.9336 | 5.8722 | 5.8078 | 5.7304 | 5.5734 | 5.1683 | 4.8988 | 4.7996 | 6.3417 | 6.3292 | 6.3166 | 6.2904 | 6.2621 | 6.2327 | 6.2003 | 6.1651 | 6.1229 | 6.076 | 5.9761 | 5.7475 | 5.5079 | 5.2769 | 5.6786 | 5.6735 | 5.6556 | 5.6208 | 5.5844 | 5.5459 | 5.5038 | 5.4585 | 5.4069 | 5.3492 | 5.2274 | 5.1552 | 4.9178 | 4.8433
NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | NO | 4.6669 | 4.5725 | 4.4478 | 4.2258 | 3.9873 | 3.6954 | 3.3602 | 3.0474 | 2.8566 | 2.6497 | 2.2258 | 1.7914 | 1.625 | 1.5027 | 5.1454 | 5.0846 | 5.0064 | 4.8666 | 4.7125 | 4.4974 | 4.243 | 4.0318 | 3.9 | 3.7604 | 3.4835 | 3.2956 | 3.1838 | 3.0745 | 4.5414 | 4.4809 | 4.3646 | 4.1711 | 3.9603 | 3.6873 | 3.357 | 3.0549 | 2.8676 | 2.6703 | 2.2744 | 1.9266 | 1.7642 | 1.6329
| ARDERSIER | CT |  |  |  | 4.6823 | 4.6351 | 4.5538 | 4.3576 | 4.1306 | 3.8537 | 3.5594 | 3.3108 | 3.1412 | 2.9511 | 2.5477 | 2.3188 | 2.0933 | 1.9823 | 5.1629 | 5.1133 | 5.0526 | 4.942 | 4.8166 | 4.6392 | 4.4514 | 4.3265 | 4.2189 | 4.0889 | 3.8298 | 3.6776 | 3.5351 | 3.4017 | 4.5603 | 4.506 | 4.4442 | 4.2811 | 4.0914 | 3.849 | 3.5843 | 3.3694 | 3.2105 | 3.0246 | 2.6501 | 2.442 | 2.2416 | 2.1337
| ARDERSIER | LW |  |  |  | 4.6669 | 4.5725 | 4.4478 | 4.2258 | 3.9873 | 3.6954 | 3.3602 | 3.0474 | 2.8566 | 2.6497 | 2.2258 | 1.7914 | 1.625 | 1.5027 | 5.1454 | 5.0846 | 5.0064 | 4.8666 | 4.7125 | 4.4974 | 4.243 | 4.0318 | 3.9 | 3.7604 | 3.4835 | 3.2956 | 3.1838 | 3.0745 | 4.5414 | 4.4809 | 4.3646 | 4.1711 | 3.9603 | 3.6873 | 3.357 | 3.0549 | 2.8676 | 2.6703 | 2.2744 | 1.9266 | 1.7642 | 1.6329
| ARDERSIER | ST |  |  |  | 4.6836 | 4.6498 | 4.6145 | 4.5037 | 4.3702 | 4.2442 | 4.0473 | 3.9105 | 3.7729 | 3.6245 | 3.2988 | 2.8616 | 2.6613 | 2.5152 | 5.1712 | 5.1348 | 5.0945 | 4.9748 | 4.874 | 4.7862 | 4.6119 | 4.5141 | 4.4221 | 4.3291 | 4.1199 | 3.7955 | 3.6333 | 3.4846 | 4.5698 | 4.5344 | 4.4961 | 4.3769 | 4.2518 | 4.1385 | 3.9373 | 3.8122 | 3.6899 | 3.5629 | 3.2829 | 2.8576 | 2.6665 | 2.5276
| ARDERSIER | FS |  |  |  | 4.6916 | 4.6584 | 4.6244 | 4.5761 | 4.5085 | 4.4074 | 4.2991 | 4.1882 | 4.075 | 3.9591 | 3.7055 | 3.1047 | 2.7583 | 2.6602 | 5.1814 | 5.1483 | 5.1146 | 5.056 | 4.9954 | 4.9304 | 4.8607 | 4.7893 | 4.7201 | 4.6482 | 4.4902 | 4.1265 | 3.8288 | 3.6599 | 4.58 | 4.5487 | 4.5177 | 4.4614 | 4.393 | 4.306 | 4.2124 | 4.1164 | 4.021 | 3.9224 | 3.7093 | 3.1969 | 2.8742 | 2.7927
FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 2.5383 | 2.5317 | 2.5212 | 2.5068 | 2.4776 | 2.445 | 2.4101 | 2.3722 | 2.3442 | 2.3157 | 2.2573 | 2.2421 | 2.2163 | 2.1987 | 2.6498 | 2.6412 | 2.6271 | 2.6124 | 2.5908 | 2.5738 | 2.5556 | 2.5339 | 2.5119 | 2.4888 | 2.4428 | 2.4329 | 2.4081 | 2.3858 | 2.5912 | 2.5764 | 2.5542 | 2.5284 | 2.4988 | 2.4689 | 2.437 | 2.4013 | 2.3736 | 2.3453 | 2.2875 | 2.2727 | 2.25 | 2.2342
| ARISAIG | CT |  |  |  | 2.5434 | 2.5344 | 2.5265 | 2.5068 | 2.4776 | 2.445 | 2.4101 | 2.3786 | 2.354 | 2.3261 | 2.271 | 2.2551 | 2.2163 | 2.1987 | 2.6542 | 2.6455 | 2.6352 | 2.6132 | 2.5908 | 2.5738 | 2.5556 | 2.5386 | 2.5205 | 2.4976 | 2.453 | 2.4329 | 2.4081 | 2.3858 | 2.6016 | 2.5866 | 2.5719 | 2.5352 | 2.4988 | 2.4689 | 2.437 | 2.4081 | 2.3842 | 2.3564 | 2.3019 | 2.2847 | 2.25 | 2.2342
| ARISAIG | LW |  |  |  | 2.5383 | 2.5317 | 2.5212 | 2.5078 | 2.4788 | 2.4513 | 2.4154 | 2.3722 | 2.3442 | 2.3157 | 2.2573 | 2.2421 | 2.2239 | 2.214 | 2.6498 | 2.6412 | 2.6271 | 2.6124 | 2.596 | 2.5817 | 2.5599 | 2.5339 | 2.5119 | 2.4888 | 2.4428 | 2.4334 | 2.4254 | 2.4216 | 2.5912 | 2.5764 | 2.5542 | 2.5284 | 2.5007 | 2.4755 | 2.4419 | 2.4013 | 2.3736 | 2.3453 | 2.2875 | 2.2727 | 2.2568 | 2.2483
| ARISAIG | ST |  |  |  | 2.5496 | 2.549 | 2.5463 | 2.544 | 2.5404 | 2.537 | 2.534 | 2.5278 | 2.5174 | 2.4936 | 2.4473 | 2.3517 | 2.3255 | 2.3066 | 2.6572 | 2.6547 | 2.65 | 2.6451 | 2.6378 | 2.6309 | 2.6229 | 2.6124 | 2.6009 | 2.5846 | 2.5492 | 2.4739 | 2.4508 | 2.4301 | 2.6085 | 2.6054 | 2.598 | 2.5912 | 2.5805 | 2.5713 | 2.5612 | 2.5468 | 2.5328 | 2.5101 | 2.4649 | 2.371 | 2.3464 | 2.33
| ARISAIG | FS |  |  |  | 2.5481 | 2.55 | 2.5473 | 2.5436 | 2.5407 | 2.5375 | 2.5349 | 2.5274 | 2.52 | 2.5048 | 2.4703 | 2.3681 | 2.2863 | 2.2706 | 2.6568 | 2.6558 | 2.6516 | 2.6461 | 2.6402 | 2.6339 | 2.6273 | 2.6174 | 2.6084 | 2.5977 | 2.5726 | 2.5 | 2.4298 | 2.4 | 2.6075 | 2.6075 | 2.601 | 2.5919 | 2.583 | 2.5735 | 2.5644 | 2.5488 | 2.5369 | 2.5224 | 2.4893 | 2.3914 | 2.312 | 2.2984
STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | NO | 12 | 12 | 12 | 11.9887 | 11.981 | 11.9759 | 11.9586 | 11.9537 | 11.8971 | 11.8771 | 11.833 | 11.7057 | 11.3357 | 10.7447 | 11.9999 | 11.9997 | 11.9994 | 11.9855 | 11.9758 | 11.9693 | 11.9473 | 11.9409 | 11.8699 | 11.8444 | 11.7882 | 11.6282 | 11.1642 | 10.4255 | 11.9999 | 11.9996 | 11.9992 | 11.9854 | 11.9757 | 11.9691 | 11.9471 | 11.9407 | 11.8696 | 11.844 | 11.7876 | 11.6277 | 11.162 | 10.4232
| ARNISH | CT |  |  |  | 12 | 12 | 12 | 11.9985 | 11.9959 | 11.9833 | 11.9699 | 11.9665 | 11.9408 | 11.9149 | 11.8681 | 11.7378 | 11.5393 | 11.3047 | 11.9999 | 11.9997 | 11.9994 | 11.9971 | 11.9936 | 11.9771 | 11.96 | 11.9554 | 11.9228 | 11.8899 | 11.8302 | 11.6666 | 11.4182 | 11.1254 | 11.9999 | 11.9996 | 11.9992 | 11.9969 | 11.9933 | 11.9758 | 11.9587 | 11.9542 | 11.9215 | 11.8881 | 11.8281 | 11.6637 | 11.4152 | 11.1231
| ARNISH | LW |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9719 | 11.9428 | 11.8918 | 11.7498 | 11.3357 | 10.7447 | 11.9999 | 11.9997 | 11.9994 | 11.9986 | 11.9984 | 11.9982 | 11.9977 | 11.9972 | 11.9617 | 11.9246 | 11.859 | 11.6815 | 11.1642 | 10.4255 | 11.9999 | 11.9997 | 11.9993 | 11.9976 | 11.9973 | 11.997 | 11.9965 | 11.9958 | 11.9607 | 11.9234 | 11.857 | 11.6785 | 11.162 | 10.4232
| ARNISH | ST |  |  |  | 12 | 12 | 12 | 11.9887 | 11.981 | 11.9759 | 11.9586 | 11.9537 | 11.8971 | 11.8771 | 11.833 | 11.7057 | 11.3995 | 11.0605 | 11.9999 | 11.9999 | 11.9998 | 11.9855 | 11.9758 | 11.9693 | 11.9473 | 11.9409 | 11.8699 | 11.8444 | 11.7882 | 11.6282 | 11.2447 | 10.8213 | 11.9999 | 11.9998 | 11.9997 | 11.9854 | 11.9757 | 11.9691 | 11.9471 | 11.9407 | 11.8696 | 11.844 | 11.7876 | 11.6277 | 11.2433 | 10.8206
| ARNISH | FS |  |  |  | 12 | 12 | 12 | 11.9977 | 11.9954 | 11.9927 | 11.99 | 11.9876 | 11.9672 | 11.9533 | 11.9255 | 11.9087 | 11.8916 | 11.8537 | 11.9999 | 11.9999 | 11.9998 | 11.9968 | 11.9938 | 11.9903 | 11.9868 | 11.9837 | 11.9579 | 11.9403 | 11.9048 | 11.8815 | 11.8592 | 11.8124 | 11.9999 | 11.9999 | 11.9998 | 11.9968 | 11.9937 | 11.9902 | 11.9866 | 11.9836 | 11.9577 | 11.94 | 11.9041 | 11.8788 | 11.857 | 11.811
ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | NO | 14.2316 | 13.2196 | 11.7982 | 10.1024 | 8.7411 | 7.3327 | 5.9057 | 4.0663 | 2.5564 | 0.8612 | -1.9344 | -5.1055 | -5.9681 | -6.4232 | 16.2733 | 15.5213 | 14.3643 | 13.0164 | 12.0341 | 10.9849 | 9.9353 | 8.5265 | 7.4795 | 6.2345 | 4.3965 | 2.6313 | 2.0442 | 1.1858 | 15.6829 | 14.7915 | 13.5046 | 11.9326 | 10.6663 | 9.3313 | 7.9708 | 6.2495 | 4.8802 | 3.3208 | 0.75808 | -1.7806 | -2.595 | -3.0852
| ASHGROVE | CT |  |  |  | 14.5028 | 13.6696 | 12.4706 | 10.9045 | 9.6058 | 8.2745 | 6.9503 | 5.2984 | 3.7985 | 2.0492 | -0.7664 | -3.5723 | -4.9441 | -5.7144 | 16.3664 | 15.6716 | 14.6067 | 13.4861 | 12.5883 | 11.6147 | 10.6483 | 9.3912 | 8.3235 | 7.0048 | 5.105 | 3.1966 | 2.1885 | 1.1858 | 15.9266 | 15.1891 | 14.1001 | 12.658 | 11.4599 | 10.2074 | 8.9638 | 7.4494 | 6.1026 | 4.5094 | 1.9479 | -0.46833 | -1.709 | -2.4256
| ASHGROVE | LW |  |  |  | 14.2316 | 13.2196 | 11.7982 | 10.1024 | 8.7411 | 7.3327 | 5.9057 | 4.0663 | 2.5564 | 0.8612 | -1.9344 | -5.1055 | -5.9681 | -6.4232 | 16.2733 | 15.5213 | 14.3643 | 13.0164 | 12.0341 | 10.9849 | 9.9353 | 8.5265 | 7.4795 | 6.2345 | 4.3965 | 2.6313 | 2.0442 | 1.6242 | 15.6829 | 14.7915 | 13.5046 | 11.9326 | 10.6663 | 9.3313 | 7.9708 | 6.2495 | 4.8802 | 3.3208 | 0.75808 | -1.7806 | -2.595 | -3.0852
| ASHGROVE | ST |  |  |  | 14.5928 | 13.8376 | 12.7542 | 11.5823 | 10.7304 | 9.9119 | 8.9939 | 7.7668 | 6.702 | 5.4542 | 3.5572 | 0.96436 | -0.29466 | -1.691 | 16.3691 | 15.6912 | 14.6665 | 13.4749 | 12.6734 | 11.9383 | 11.0634 | 9.8834 | 8.9756 | 7.8491 | 6.4324 | 4.7609 | 3.7155 | 2.4408 | 16.0051 | 15.3402 | 14.3607 | 13.2404 | 12.4292 | 11.6612 | 10.7623 | 9.6139 | 8.631 | 7.4852 | 5.7356 | 3.2971 | 2.1381 | 0.90617
| ASHGROVE | FS |  |  |  | 14.8686 | 14.2752 | 13.4295 | 12.5716 | 11.8595 | 11.2066 | 10.5433 | 9.5555 | 8.6022 | 7.4517 | 5.67 | 2.1062 | -0.33068 | -1.5107 | 16.666 | 16.1379 | 15.3387 | 14.5026 | 13.8596 | 13.2889 | 12.7106 | 11.7763 | 10.9769 | 9.9506 | 8.5338 | 5.9439 | 3.6779 | 1.8151 | 16.2556 | 15.742 | 14.9886 | 14.1947 | 13.5361 | 12.9336 | 12.317 | 11.395 | 10.536 | 9.4973 | 7.8883 | 4.7199 | 2.4548 | 1.4542
MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | NO | 2.9701 | 2.0851 | 1.1304 | -0.28538 | -1.9185 | -3.9133 | -5.8227 | -7.4152 | -8.6469 | -9.9958 | -12.7079 | -14.2891 | -15.4993 | -16.3353 | 4.8443 | 4.1926 | 3.4754 | 2.404 | 1.1221 | -0.5698 | -2.1762 | -3.4152 | -4.3589 | -5.4092 | -7.5195 | -8.6185 | -9.6031 | -10.518 | 3.452 | 2.6458 | 1.7617 | 0.3914 | -1.1935 | -3.1939 | -5.1283 | -6.7009 | -7.8847 | -9.1813 | -11.7804 | -13.304 | -14.5672 | -15.5486
| ASHLUDIE | CT |  |  |  | 3.3359 | 2.6407 | 1.8981 | 0.6798 | -0.76086 | -2.492 | -4.0024 | -5.1481 | -6.3397 | -7.7542 | -10.5259 | -12.8646 | -14.4143 | -15.3839 | 5.0187 | 4.4559 | 3.8387 | 2.973 | 1.8976 | 0.4792 | -0.74144 | -1.5655 | -2.4505 | -3.5304 | -5.6537 | -7.378 | -8.725 | -10.2485 | 3.7775 | 3.1398 | 2.4475 | 1.311 | -0.042415 | -1.7286 | -3.2107 | -4.2879 | -5.4115 | -6.7494 | -9.3684 | -11.5444 | -13.003 | -13.9575
| ASHLUDIE | LW |  |  |  | 2.9701 | 2.0851 | 1.1304 | -0.28538 | -1.9185 | -3.9133 | -5.8227 | -7.4152 | -8.6469 | -9.9958 | -12.7079 | -14.2891 | -15.4993 | -16.3353 | 4.8443 | 4.1926 | 3.4754 | 2.404 | 1.1221 | -0.5698 | -2.1762 | -3.4152 | -4.3589 | -5.4092 | -7.5195 | -8.6185 | -9.6031 | -10.518 | 3.452 | 2.6458 | 1.7617 | 0.3914 | -1.1935 | -3.1939 | -5.1283 | -6.7009 | -7.8847 | -9.1813 | -11.7804 | -13.304 | -14.5672 | -15.5486
| ASHLUDIE | ST |  |  |  | 3.4317 | 2.8259 | 2.2171 | 1.3423 | 0.34773 | -0.77688 | -1.9288 | -2.7058 | -3.5421 | -4.4707 | -6.4385 | -8.9354 | -10.5774 | -12.2944 | 5.0558 | 4.545 | 4.0146 | 3.168 | 2.2349 | 1.2011 | 0.059919 | -0.64744 | -1.413 | -2.2441 | -4.03 | -6.125 | -7.661 | -9.541 | 3.8619 | 3.3075 | 2.7424 | 1.8504 | 0.86808 | -0.22207 | -1.4153 | -2.1785 | -3.0013 | -3.8926 | -5.7861 | -8.1927 | -9.7912 | -11.4388
| ASHLUDIE | FS |  |  |  | 3.7095 | 3.2485 | 2.774 | 2.2019 | 1.4696 | 0.60337 | -0.099144 | -0.77135 | -1.5429 | -2.4033 | -4.1247 | -7.1234 | -9.7152 | -11.1053 | 5.2875 | 4.8921 | 4.4722 | 3.9648 | 3.3084 | 2.5298 | 1.895 | 1.2904 | 0.62197 | -0.12628 | -1.6341 | -4.1673 | -6.7489 | -9.1473 | 4.1175 | 3.698 | 3.2587 | 2.7109 | 2.0109 | 1.1813 | 0.50519 | -0.14106 | -0.87475 | -1.689 | -3.3217 | -6.1158 | -8.5283 | -9.7667
GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | -0.67507 | -0.72154 | -0.78662 | -0.85954 | -0.93982 | -1.0217 | -1.1108 | -1.2205 | -1.2994 | -1.3869 | -1.5542 | -1.6413 | -1.7128 | -1.7586 | -0.2147 | -0.24287 | -0.28408 | -0.32687 | -0.38318 | -0.43345 | -0.48487 | -0.55183 | -0.61249 | -0.67907 | -0.81779 | -0.87314 | -0.93081 | -0.98099 | -0.82547 | -0.86264 | -0.90778 | -0.95633 | -1.0087 | -1.0652 | -1.1268 | -1.2002 | -1.252 | -1.3343 | -1.4997 | -1.5837 | -1.647 | -1.6921
| AULTBEA | CT |  |  |  | -0.64827 | -0.6806 | -0.72675 | -0.82865 | -0.93562 | -1.0217 | -1.1089 | -1.1951 | -1.2599 | -1.3431 | -1.5066 | -1.606 | -1.7128 | -1.7586 | -0.20229 | -0.22447 | -0.25547 | -0.31792 | -0.38318 | -0.43345 | -0.48487 | -0.53601 | -0.58463 | -0.64841 | -0.77559 | -0.8685 | -0.93081 | -0.98099 | -0.80759 | -0.83979 | -0.87497 | -0.94412 | -1.0057 | -1.0652 | -1.1264 | -1.1882 | -1.2305 | -1.2897 | -1.4512 | -1.5511 | -1.647 | -1.6921
| AULTBEA | LW |  |  |  | -0.67507 | -0.72154 | -0.78662 | -0.85954 | -0.93982 | -1.011 | -1.1108 | -1.2205 | -1.2994 | -1.3869 | -1.5542 | -1.6413 | -1.6956 | -1.7123 | -0.2147 | -0.24287 | -0.28408 | -0.32687 | -0.37482 | -0.41652 | -0.48033 | -0.55183 | -0.61249 | -0.67907 | -0.81779 | -0.87314 | -0.89602 | -0.90198 | -0.82547 | -0.86264 | -0.90778 | -0.95633 | -1.0087 | -1.0596 | -1.1268 | -1.2002 | -1.252 | -1.3343 | -1.4997 | -1.5837 | -1.6321 | -1.6467
| AULTBEA | ST |  |  |  | -0.62984 | -0.64905 | -0.66682 | -0.69352 | -0.72536 | -0.75882 | -0.79725 | -0.84332 | -0.89461 | -0.95546 | -1.0969 | -1.4259 | -1.5229 | -1.5725 | -0.19285 | -0.20486 | -0.21706 | -0.23442 | -0.25579 | -0.27866 | -0.30549 | -0.33766 | -0.37462 | -0.41886 | -0.52312 | -0.78685 | -0.85907 | -0.90261 | -0.79203 | -0.80736 | -0.82133 | -0.84118 | -0.86409 | -0.88908 | -0.91801 | -0.95205 | -0.98925 | -1.033 | -1.1352 | -1.3883 | -1.4784 | -1.522
| AULTBEA | FS |  |  |  | -0.62211 | -0.639 | -0.65235 | -0.67852 | -0.70672 | -0.73515 | -0.77022 | -0.80694 | -0.84631 | -0.89561 | -1.0004 | -1.3403 | -1.5914 | -1.6363 | -0.18888 | -0.19943 | -0.20915 | -0.22536 | -0.24366 | -0.2625 | -0.28546 | -0.31033 | -0.33775 | -0.37114 | -0.44506 | -0.67187 | -0.88694 | -0.94056 | -0.78584 | -0.79921 | -0.80983 | -0.82944 | -0.84967 | -0.87088 | -0.89689 | -0.92356 | -0.95121 | -0.98502 | -1.057 | -1.2952 | -1.5385 | -1.578
BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | NO | 5.8896 | 5.787 | 5.6227 | 5.5042 | 5.3956 | 5.2726 | 5.0282 | 4.8511 | 4.668 | 4.4361 | 4.0031 | 4.6139 | 4.565 | 4.5311 | 9.9939 | 9.8895 | 9.7072 | 9.5158 | 9.3671 | 9.2214 | 9.0214 | 8.8584 | 8.666 | 8.4626 | 7.9748 | 9.183 | 9.0732 | 8.7371 | 7.9065 | 7.8017 | 7.6252 | 7.4862 | 7.3493 | 7.2104 | 6.9708 | 6.7998 | 6.5884 | 6.3789 | 5.9197 | 6.7091 | 6.6648 | 6.6348
| AVIEMORE | CT |  |  |  | 5.8917 | 5.7944 | 5.6449 | 5.5159 | 5.3972 | 5.2726 | 5.0394 | 4.8848 | 4.7135 | 4.4921 | 4.1129 | 4.6139 | 4.565 | 4.5311 | 9.9939 | 9.8895 | 9.7072 | 9.5158 | 9.3671 | 9.2214 | 9.0214 | 8.8584 | 8.666 | 8.4829 | 8.1362 | 9.183 | 9.0732 | 8.9053 | 7.9074 | 7.8026 | 7.6381 | 7.4862 | 7.3493 | 7.2104 | 6.9708 | 6.8033 | 6.613 | 6.4255 | 6.1089 | 6.7091 | 6.6648 | 6.6348
| AVIEMORE | LW |  |  |  | 5.8896 | 5.787 | 5.6227 | 5.5042 | 5.3956 | 5.2831 | 5.0282 | 4.8511 | 4.668 | 4.4361 | 4.0031 | 4.6388 | 4.5956 | 4.5589 | 9.9971 | 9.9095 | 9.7265 | 9.5833 | 9.4742 | 9.361 | 9.153 | 8.9429 | 8.711 | 8.4626 | 7.9748 | 9.2595 | 9.2358 | 9.2161 | 7.9065 | 7.8017 | 7.6252 | 7.4963 | 7.3795 | 7.2598 | 6.9999 | 6.7998 | 6.5884 | 6.3789 | 5.9197 | 6.7257 | 6.6869 | 6.6541
| AVIEMORE | ST |  |  |  | 5.8959 | 5.8186 | 5.7011 | 5.6142 | 5.5389 | 5.4526 | 5.2985 | 5.1848 | 5.0612 | 4.9254 | 4.5763 | 4.8953 | 4.842 | 4.8184 | 10.0066 | 9.9522 | 9.8466 | 9.741 | 9.6535 | 9.5463 | 9.3969 | 9.2393 | 9.0555 | 8.8379 | 8.315 | 9.273 | 9.1435 | 8.9775 | 7.9141 | 7.8386 | 7.7209 | 7.6273 | 7.544 | 7.4468 | 7.2846 | 7.1515 | 7.0028 | 6.8346 | 6.4175 | 6.922 | 6.8604 | 6.8368
| AVIEMORE | FS |  |  |  | 5.9097 | 5.8399 | 5.7445 | 5.6711 | 5.6065 | 5.5341 | 5.41 | 5.3249 | 5.2375 | 5.1454 | 4.9759 | 5.0606 | 4.9576 | 4.9212 | 10.0157 | 9.9696 | 9.8854 | 9.8049 | 9.7373 | 9.663 | 9.5551 | 9.4583 | 9.3479 | 9.2196 | 8.9388 | 9.3492 | 9.0915 | 8.7371 | 7.9274 | 7.8602 | 7.7651 | 7.6882 | 7.6193 | 7.5421 | 7.4156 | 7.3217 | 7.2223 | 7.1145 | 6.9021 | 7.0981 | 6.9732 | 6.9285
ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | NO | -2.237 | -2.3558 | -2.4979 | -2.6642 | -2.8339 | -3.0307 | -3.2444 | -3.4557 | -3.5891 | -3.7558 | -4.0989 | -3.7289 | -4.2291 | -4.8048 | -0.76807 | -0.83457 | -0.93302 | -1.0299 | -1.1778 | -1.2999 | -1.4294 | -1.5569 | -1.7363 | -1.94 | -2.3369 | -2.0951 | -2.6051 | -3.2722 | -1.3261 | -1.4213 | -1.5331 | -1.6639 | -1.7968 | -1.9844 | -2.1958 | -2.4052 | -2.6185 | -2.8554 | -3.3167 | -3.0178 | -3.5956 | -4.2914
| BALALDIE | CT |  |  |  | -2.1721 | -2.2625 | -2.3794 | -2.5957 | -2.8213 | -3.0307 | -3.2444 | -3.4557 | -3.5891 | -3.7296 | -3.9936 | -3.6057 | -4.0229 | -4.3207 | -0.7457 | -0.80222 | -0.88755 | -1.0276 | -1.1778 | -1.2999 | -1.4294 | -1.5569 | -1.7029 | -1.8743 | -2.199 | -2.0338 | -2.3964 | -2.7829 | -1.271 | -1.3442 | -1.4372 | -1.6088 | -1.7847 | -1.9844 | -2.1958 | -2.4052 | -2.5776 | -2.7757 | -3.1493 | -2.8857 | -3.3229 | -3.6718
| BALALDIE | LW |  |  |  | -2.237 | -2.3558 | -2.4979 | -2.6642 | -2.8339 | -2.9996 | -3.2008 | -3.4154 | -3.5801 | -3.7558 | -4.0989 | -3.7289 | -4.2291 | -4.8048 | -0.76807 | -0.83457 | -0.93302 | -1.0299 | -1.1358 | -1.2333 | -1.3804 | -1.5474 | -1.7363 | -1.94 | -2.3369 | -2.0951 | -2.6051 | -3.2722 | -1.3261 | -1.4213 | -1.5331 | -1.6639 | -1.7968 | -1.9354 | -2.1558 | -2.3975 | -2.6185 | -2.8554 | -3.3167 | -3.0178 | -3.5956 | -4.2914
| BALALDIE | ST |  |  |  | -2.1362 | -2.1871 | -2.2425 | -2.318 | -2.4031 | -2.4934 | -2.587 | -2.6992 | -2.8702 | -3.0352 | -3.4096 | -3.3524 | -3.8103 | -4.2418 | -0.73246 | -0.76341 | -0.80021 | -0.84872 | -0.90731 | -0.97224 | -1.0456 | -1.1347 | -1.2939 | -1.4394 | -1.7834 | -1.933 | -2.425 | -2.929 | -1.2418 | -1.282 | -1.3256 | -1.3855 | -1.4516 | -1.5231 | -1.5973 | -1.6862 | -1.8704 | -2.0579 | -2.5074 | -2.659 | -3.1689 | -3.6585
| BALALDIE | FS |  |  |  | -2.1124 | -2.1477 | -2.19 | -2.254 | -2.3266 | -2.3982 | -2.4717 | -2.5553 | -2.6628 | -2.7803 | -3.0286 | -3.2436 | -3.5395 | -3.7097 | -0.72344 | -0.74717 | -0.77656 | -0.8164 | -0.86399 | -0.91314 | -0.96703 | -1.0297 | -1.1214 | -1.2183 | -1.4367 | -1.6475 | -2.0317 | -2.2982 | -1.2231 | -1.2511 | -1.2845 | -1.3355 | -1.3931 | -1.4499 | -1.5093 | -1.5762 | -1.6684 | -1.7767 | -2.0517 | -2.3858 | -2.7798 | -2.9364
ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | NO | 3.214 | 3.081 | 2.8973 | 2.674 | 2.3986 | 2.0693 | 1.6519 | 1.3457 | 1.0455 | 0.70623 | -0.077402 | -0.30509 | -0.79954 | -1.162 | 4.5101 | 4.451 | 4.3428 | 4.2087 | 4.0611 | 3.8258 | 3.5671 | 3.3903 | 3.1723 | 2.9515 | 2.324 | 2.302 | 1.8466 | 1.2678 | 4.1372 | 4.0501 | 3.9216 | 3.7354 | 3.5285 | 3.2335 | 2.9065 | 2.6656 | 2.3844 | 2.0464 | 1.2856 | 0.99556 | 0.51525 | 0.12206
| BALBEGGIE | CT |  |  |  | 3.2756 | 3.1772 | 3.0284 | 2.76 | 2.4372 | 2.0693 | 1.6519 | 1.3457 | 1.0455 | 0.70623 | -0.077402 | -0.30509 | -0.79954 | -1.162 | 4.5101 | 4.451 | 4.3428 | 4.2087 | 4.0611 | 3.8258 | 3.5671 | 3.3903 | 3.1723 | 2.9515 | 2.324 | 2.302 | 1.8809 | 1.419 | 4.1453 | 4.0639 | 3.9252 | 3.7354 | 3.5285 | 3.2335 | 2.9065 | 2.6656 | 2.3844 | 2.0464 | 1.2856 | 0.99556 | 0.51525 | 0.12206
| BALBEGGIE | LW |  |  |  | 3.214 | 3.081 | 2.8973 | 2.674 | 2.3986 | 2.1329 | 1.7716 | 1.4533 | 1.1698 | 0.8675 | 0.13318 | 0.20529 | -0.34759 | -0.98711 | 4.5185 | 4.4609 | 4.3701 | 4.2874 | 4.1851 | 4.0806 | 3.9217 | 3.7524 | 3.5437 | 3.3119 | 2.6525 | 2.9835 | 2.422 | 1.6704 | 4.1372 | 4.0501 | 3.9216 | 3.7918 | 3.6337 | 3.4624 | 3.1569 | 2.8731 | 2.5934 | 2.2937 | 1.5833 | 1.615 | 0.99653 | 0.22509
| BALBEGGIE | ST |  |  |  | 3.3577 | 3.2966 | 3.2118 | 3.0195 | 2.83 | 2.6604 | 2.3695 | 2.1878 | 1.9321 | 1.7088 | 1.0631 | 0.50976 | -0.072693 | -0.63031 | 4.5881 | 4.5571 | 4.5164 | 4.3577 | 4.2169 | 4.0926 | 3.8321 | 3.6823 | 3.4336 | 3.2367 | 2.5962 | 2.4237 | 1.8466 | 1.2678 | 4.2426 | 4.1994 | 4.1433 | 3.9647 | 3.8009 | 3.652 | 3.3626 | 3.183 | 2.9026 | 2.6675 | 1.9464 | 1.5054 | 0.87806 | 0.30062
| BALBEGGIE | FS |  |  |  | 3.3769 | 3.329 | 3.2675 | 3.1601 | 3.0326 | 2.9055 | 2.7526 | 2.6259 | 2.4663 | 2.3089 | 1.8927 | 1.2889 | 0.74805 | 0.49184 | 4.601 | 4.5776 | 4.5474 | 4.4876 | 4.4167 | 4.3392 | 4.249 | 4.1647 | 4.0497 | 3.9387 | 3.5914 | 3.3547 | 2.877 | 2.5987 | 4.2601 | 4.2281 | 4.1882 | 4.1121 | 4.0238 | 3.9281 | 3.8164 | 3.7118 | 3.5727 | 3.4359 | 3.0359 | 2.495 | 1.9411 | 1.7364
MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | NO | 13.536 | 13.2742 | 12.9676 | 10.7454 | 8.3447 | 4.045 | -0.77777 | -3.9947 | -5.38 | -6.8656 | -9.0505 | -12.0489 | -13.3227 | -13.8757 | 16.144 | 16.0465 | 15.9495 | 13.7628 | 11.3287 | 6.4234 | 0.93926 | -2.5078 | -3.7454 | -5.0845 | -7.0966 | -10.2622 | -11.5372 | -12.1978 | 15.9909 | 15.898 | 15.7946 | 13.6524 | 10.9689 | 5.9091 | 0.32668 | -3.2146 | -4.5498 | -6.0376 | -8.2249 | -11.875 | -13.3323 | -14.0136
| BALDOVIE | CT |  |  |  | 13.7348 | 13.5845 | 13.3925 | 12.6133 | 11.6932 | 9.4644 | 6.9273 | 5.7101 | 4.6711 | 3.4719 | 1.8079 | -0.26652 | -1.5397 | -2.2229 | 16.1775 | 16.0938 | 16.0001 | 15.5836 | 14.9801 | 12.6781 | 9.9244 | 8.8201 | 8.0099 | 7.0484 | 5.7785 | 3.9798 | 2.717 | 1.4541 | 15.9967 | 15.9069 | 15.7946 | 15.4205 | 14.8647 | 12.4032 | 9.5673 | 8.3834 | 7.4714 | 6.4645 | 5.0025 | 2.8532 | 1.6254 | 0.96032
| BALDOVIE | LW |  |  |  | 13.536 | 13.2742 | 12.9676 | 10.7454 | 8.3447 | 4.045 | -0.77777 | -3.9947 | -5.38 | -6.8656 | -9.0505 | -12.0489 | -13.3227 | -13.8757 | 16.144 | 16.0465 | 15.9495 | 13.7628 | 11.3287 | 6.4234 | 0.93926 | -2.5078 | -3.7454 | -5.0845 | -7.0966 | -10.2622 | -11.5372 | -12.1978 | 15.9909 | 15.898 | 15.7997 | 13.6524 | 10.9689 | 5.9091 | 0.32668 | -3.2146 | -4.5498 | -6.0376 | -8.2249 | -11.875 | -13.3323 | -14.0136
| BALDOVIE | ST |  |  |  | 13.7992 | 13.7012 | 13.6186 | 12.0357 | 10.9601 | 10.1663 | 7.5274 | 6.5336 | 5.6451 | 4.9176 | 4.0591 | 2.2008 | 0.76928 | -0.53811 | 16.1936 | 16.1301 | 16.089 | 14.1667 | 12.8568 | 11.906 | 8.6306 | 7.4275 | 6.4516 | 5.7279 | 4.9692 | 3.2324 | 1.7489 | 0.20338 | 16.0007 | 15.9307 | 15.8797 | 13.9489 | 12.6335 | 11.6877 | 8.461 | 7.306 | 6.3536 | 5.6587 | 4.8735 | 3.6592 | 2.7104 | 1.3993
| BALDOVIE | FS |  |  |  | 13.814 | 13.7319 | 13.6628 | 13.268 | 12.8873 | 12.4151 | 11.8241 | 11.2218 | 10.6664 | 10.1281 | 9.3935 | 8.1755 | 6.4828 | 5.2413 | 16.2171 | 16.1623 | 16.1252 | 15.7011 | 15.2813 | 14.7433 | 14.0521 | 13.3443 | 12.8071 | 12.3116 | 11.7086 | 10.6919 | 8.7875 | 6.5339 | 16.0261 | 15.9657 | 15.9208 | 15.4945 | 15.079 | 14.5536 | 13.9018 | 13.246 | 12.7518 | 12.3021 | 11.7509 | 11.4035 | 10.2573 | 9.1637
TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 7.524 | 7.4876 | 7.3898 | 7.1785 | 6.9505 | 6.7379 | 6.4516 | 6.1424 | 5.9098 | 5.6615 | 5.1723 | 5.0664 | 4.8574 | 4.7048 | 8.6865 | 8.6089 | 8.4998 | 8.3927 | 8.2654 | 8.1342 | 8.0009 | 7.8331 | 7.6802 | 7.5164 | 7.1679 | 7.1477 | 6.9876 | 6.8427 | 8.3287 | 8.1799 | 7.9926 | 7.7985 | 7.59 | 7.3949 | 7.1345 | 6.8539 | 6.6477 | 6.4272 | 5.9697 | 5.8831 | 5.6996 | 5.5647
| BALLATER | CT |  |  |  | 7.5247 | 7.4876 | 7.4359 | 7.3025 | 7.0047 | 6.7465 | 6.4878 | 6.2254 | 6.0327 | 5.7929 | 5.3247 | 5.1973 | 4.8574 | 4.7048 | 8.7244 | 8.6625 | 8.578 | 8.4255 | 8.2654 | 8.1342 | 8.0009 | 7.8656 | 7.7399 | 7.5819 | 7.2622 | 7.1741 | 6.9876 | 6.8427 | 8.4177 | 8.3104 | 8.1752 | 7.9127 | 7.6404 | 7.4018 | 7.163 | 6.9205 | 6.7476 | 6.5354 | 6.1173 | 5.9994 | 5.6996 | 5.5647
| BALLATER | LW |  |  |  | 7.524 | 7.4995 | 7.3898 | 7.1785 | 6.9505 | 6.7379 | 6.4516 | 6.1424 | 5.9098 | 5.6615 | 5.1723 | 5.0664 | 4.9046 | 4.8198 | 8.6865 | 8.6089 | 8.4998 | 8.3927 | 8.2747 | 8.1675 | 8.0088 | 7.8331 | 7.6802 | 7.5164 | 7.1679 | 7.1477 | 7.0778 | 7.0435 | 8.3287 | 8.1799 | 7.9926 | 7.7985 | 7.59 | 7.3949 | 7.1345 | 6.8539 | 6.6477 | 6.4272 | 5.9697 | 5.8831 | 5.7433 | 5.6721
| BALLATER | ST |  |  |  | 7.5277 | 7.5151 | 7.498 | 7.4755 | 7.4464 | 7.4119 | 7.3256 | 7.1814 | 7.0189 | 6.8344 | 6.4164 | 5.6843 | 5.3497 | 5.1504 | 8.7476 | 8.7174 | 8.6785 | 8.6279 | 8.5681 | 8.5028 | 8.4279 | 8.3425 | 8.2437 | 8.129 | 7.8623 | 7.392 | 7.1855 | 7.0364 | 8.472 | 8.4187 | 8.3521 | 8.2648 | 8.1666 | 8.0608 | 7.9434 | 7.8127 | 7.6655 | 7.4981 | 7.1198 | 6.4368 | 6.1357 | 5.9634
| BALLATER | FS |  |  |  | 7.5297 | 7.5202 | 7.5078 | 7.4902 | 7.4682 | 7.4432 | 7.4134 | 7.3463 | 7.2097 | 7.0621 | 6.7378 | 5.8747 | 5.2138 | 5.0437 | 8.7593 | 8.7355 | 8.7062 | 8.6614 | 8.6111 | 8.5599 | 8.501 | 8.4362 | 8.3576 | 8.2709 | 8.0745 | 7.5905 | 7.0933 | 6.8889 | 8.4985 | 8.458 | 8.4104 | 8.3307 | 8.2456 | 8.1614 | 8.0664 | 7.9643 | 7.8403 | 7.7061 | 7.4117 | 6.6412 | 6.0145 | 5.8674
CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.48775 | 0.48699 | 0.48559 | 0.47203 | 0.4613 | 0.45082 | 0.4098 | 0.38318 | 0.36133 | 0.33562 | 0.29202 | 0.25122 | 0.1913 | 0.1394 | 0.60142 | 0.60041 | 0.59854 | 0.58157 | 0.56812 | 0.55879 | 0.52906 | 0.51951 | 0.49615 | 0.48608 | 0.45226 | 0.39526 | 0.33398 | 0.25435 | 0.47632 | 0.47331 | 0.46777 | 0.45387 | 0.43945 | 0.40232 | 0.36396 | 0.34156 | 0.32473 | 0.30662 | 0.27538 | 0.22694 | 0.16024 | 0.099369
| BALLIEKINE | CT |  |  |  | 0.48785 | 0.48729 | 0.48614 | 0.4823 | 0.47678 | 0.45082 | 0.4098 | 0.38318 | 0.36133 | 0.33562 | 0.29202 | 0.25122 | 0.1913 | 0.1394 | 0.60158 | 0.60062 | 0.59905 | 0.59412 | 0.58741 | 0.56508 | 0.54049 | 0.53211 | 0.51584 | 0.49483 | 0.45226 | 0.39526 | 0.33702 | 0.27768 | 0.47643 | 0.47556 | 0.47395 | 0.45714 | 0.43945 | 0.40232 | 0.36396 | 0.34156 | 0.32473 | 0.30662 | 0.27538 | 0.22694 | 0.16024 | 0.099995
| BALLIEKINE | LW |  |  |  | 0.48775 | 0.48699 | 0.48559 | 0.48429 | 0.48281 | 0.47074 | 0.44783 | 0.41965 | 0.40242 | 0.38385 | 0.34486 | 0.32854 | 0.24612 | 0.14138 | 0.60142 | 0.60041 | 0.59854 | 0.59693 | 0.59505 | 0.59339 | 0.59034 | 0.58468 | 0.57111 | 0.55493 | 0.51879 | 0.50008 | 0.40858 | 0.28131 | 0.47632 | 0.47331 | 0.46777 | 0.45387 | 0.44066 | 0.42685 | 0.41311 | 0.39365 | 0.38449 | 0.37465 | 0.34544 | 0.3269 | 0.22891 | 0.099369
| BALLIEKINE | ST |  |  |  | 0.48796 | 0.48767 | 0.4873 | 0.47203 | 0.4613 | 0.45395 | 0.43029 | 0.42275 | 0.40417 | 0.39624 | 0.37836 | 0.31526 | 0.25402 | 0.19407 | 0.60172 | 0.60131 | 0.60076 | 0.58157 | 0.56812 | 0.55879 | 0.52906 | 0.51951 | 0.49615 | 0.48608 | 0.46332 | 0.41216 | 0.33398 | 0.25435 | 0.47646 | 0.47604 | 0.47545 | 0.4562 | 0.44263 | 0.43316 | 0.40284 | 0.39182 | 0.3666 | 0.35425 | 0.326 | 0.25441 | 0.17987 | 0.10756
| BALLIEKINE | FS |  |  |  | 0.48796 | 0.48776 | 0.48746 | 0.48401 | 0.48044 | 0.47629 | 0.47205 | 0.46818 | 0.46095 | 0.4556 | 0.44432 | 0.41525 | 0.37095 | 0.35643 | 0.60174 | 0.6014 | 0.60094 | 0.59653 | 0.59198 | 0.58674 | 0.58133 | 0.57636 | 0.56726 | 0.56046 | 0.54618 | 0.53587 | 0.49965 | 0.48323 | 0.47649 | 0.47615 | 0.47566 | 0.47126 | 0.46664 | 0.46135 | 0.45586 | 0.45036 | 0.43998 | 0.43165 | 0.41375 | 0.38799 | 0.36478 | 0.3516
BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | NO | 7.8948 | 7.822 | 7.725 | 6.9914 | 6.1802 | 4.6578 | 3.0179 | 2.0194 | 1.712 | 1.3905 | 0.80521 | -0.20983 | -0.69235 | -1.0181 | 8.0888 | 8.0538 | 8.0038 | 7.1664 | 6.2326 | 4.4061 | 2.4484 | 1.2875 | 0.95307 | 0.60322 | -0.024519 | -1.2883 | -1.8328 | -2.221 | 7.3835 | 7.3108 | 7.2281 | 6.3508 | 5.3797 | 3.5143 | 1.5205 | 0.3312 | -0.00068558 | -0.34696 | -0.96332 | -2.1781 | -2.7507 | -3.148
| BALLINDALLOCH | CT |  |  |  | 7.9373 | 7.8828 | 7.813 | 7.6008 | 7.3116 | 6.4982 | 5.6279 | 5.3158 | 5.1352 | 4.9343 | 4.5639 | 4.0992 | 3.7569 | 3.5791 | 8.1048 | 8.0758 | 8.0329 | 7.8595 | 7.6026 | 6.6796 | 5.6947 | 5.3996 | 5.2159 | 5.0142 | 4.6406 | 4.0317 | 3.7243 | 3.5178 | 7.4289 | 7.3728 | 7.3075 | 7.0889 | 6.7878 | 5.8168 | 4.7779 | 4.4339 | 4.2473 | 4.0526 | 3.6688 | 3.1849 | 2.8276 | 2.6291
| BALLINDALLOCH | LW |  |  |  | 7.8948 | 7.822 | 7.725 | 6.9914 | 6.1802 | 4.6578 | 3.0179 | 2.0194 | 1.712 | 1.3905 | 0.80521 | -0.20983 | -0.69235 | -1.0181 | 8.0888 | 8.0538 | 8.0038 | 7.1664 | 6.2326 | 4.4061 | 2.4484 | 1.2875 | 0.95307 | 0.60322 | -0.024519 | -1.2883 | -1.8328 | -2.221 | 7.3835 | 7.3108 | 7.2281 | 6.3508 | 5.3797 | 3.5143 | 1.5205 | 0.3312 | -0.00068558 | -0.34696 | -0.96332 | -2.1781 | -2.7507 | -3.148
| BALLINDALLOCH | ST |  |  |  | 7.9596 | 7.9269 | 7.8916 | 7.2243 | 6.7535 | 6.4207 | 5.4045 | 5.0661 | 4.7727 | 4.6034 | 4.2375 | 3.4694 | 3.0415 | 2.7746 | 8.1132 | 8.097 | 8.0784 | 7.2766 | 6.7224 | 6.3436 | 5.1138 | 4.7398 | 4.4197 | 4.2652 | 3.9201 | 3.1262 | 2.7073 | 2.4281 | 7.4548 | 7.4214 | 7.3872 | 6.5656 | 5.9929 | 5.594 | 4.3457 | 3.9517 | 3.6147 | 3.44 | 3.0197 | 2.3336 | 1.8675 | 1.5772
| BALLINDALLOCH | FS |  |  |  | 7.9724 | 7.9516 | 7.928 | 7.762 | 7.591 | 7.4022 | 7.2066 | 7.0299 | 6.888 | 6.766 | 6.4971 | 6.0574 | 5.7408 | 5.6427 | 8.1183 | 8.1071 | 8.0937 | 7.9146 | 7.732 | 7.5236 | 7.311 | 7.1222 | 6.9874 | 6.8807 | 6.652 | 6.3617 | 6.1281 | 6.0343 | 7.4693 | 7.449 | 7.4273 | 7.2305 | 7.0301 | 6.807 | 6.578 | 6.3745 | 6.2212 | 6.0967 | 5.8277 | 5.5082 | 5.2685 | 5.1783
CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 1.7456 | 1.7226 | 1.694 | 1.6594 | 1.6232 | 1.5523 | 1.4711 | 1.4208 | 1.3847 | 1.3515 | 1.2723 | 1.2122 | 1.0721 | 0.95335 | 1.8354 | 1.8258 | 1.8108 | 1.7867 | 1.751 | 1.7013 | 1.6348 | 1.6053 | 1.5612 | 1.5197 | 1.4315 | 1.2745 | 1.0963 | 0.92337 | 1.7274 | 1.711 | 1.6871 | 1.6619 | 1.6227 | 1.5505 | 1.4715 | 1.4299 | 1.3834 | 1.3323 | 1.2284 | 1.0957 | 0.90669 | 0.7263
| BALLURE | CT |  |  |  | 1.7598 | 1.7424 | 1.7231 | 1.6777 | 1.6232 | 1.5523 | 1.4711 | 1.4208 | 1.3847 | 1.3515 | 1.2723 | 1.2122 | 1.0721 | 0.96794 | 1.8393 | 1.8317 | 1.8209 | 1.7953 | 1.7628 | 1.7013 | 1.6348 | 1.6053 | 1.5651 | 1.5197 | 1.4315 | 1.308 | 1.1847 | 1.0616 | 1.7363 | 1.7241 | 1.7076 | 1.6696 | 1.6227 | 1.5505 | 1.4715 | 1.4299 | 1.3834 | 1.3323 | 1.2284 | 1.1009 | 0.96094 | 0.83431
| BALLURE | LW |  |  |  | 1.7456 | 1.7226 | 1.694 | 1.6594 | 1.6272 | 1.5941 | 1.5525 | 1.5099 | 1.4829 | 1.4502 | 1.3926 | 1.3842 | 1.2038 | 0.97105 | 1.8354 | 1.8258 | 1.8108 | 1.7962 | 1.7804 | 1.7661 | 1.7431 | 1.7171 | 1.6846 | 1.6492 | 1.5827 | 1.5422 | 1.341 | 1.0564 | 1.7274 | 1.711 | 1.6871 | 1.6619 | 1.6362 | 1.6118 | 1.5763 | 1.5375 | 1.4985 | 1.4552 | 1.3744 | 1.3269 | 1.1164 | 0.82926
| BALLURE | ST |  |  |  | 1.7734 | 1.7705 | 1.7597 | 1.715 | 1.6796 | 1.655 | 1.5875 | 1.5572 | 1.5008 | 1.4634 | 1.3919 | 1.26 | 1.1095 | 0.95335 | 1.842 | 1.8392 | 1.8341 | 1.7867 | 1.751 | 1.725 | 1.6514 | 1.6225 | 1.5612 | 1.5278 | 1.4538 | 1.2745 | 1.0963 | 0.92337 | 1.7418 | 1.7378 | 1.7292 | 1.678 | 1.6379 | 1.6086 | 1.5298 | 1.496 | 1.4292 | 1.3889 | 1.3029 | 1.0957 | 0.90669 | 0.7263
| BALLURE | FS |  |  |  | 1.7779 | 1.7757 | 1.7713 | 1.7515 | 1.7329 | 1.7109 | 1.6901 | 1.6715 | 1.6392 | 1.6159 | 1.5568 | 1.4587 | 1.3885 | 1.3481 | 1.8432 | 1.8408 | 1.8376 | 1.8233 | 1.8084 | 1.7914 | 1.7739 | 1.7572 | 1.7293 | 1.7068 | 1.6563 | 1.5735 | 1.5026 | 1.4743 | 1.7443 | 1.7408 | 1.736 | 1.7173 | 1.6985 | 1.6767 | 1.655 | 1.6343 | 1.6007 | 1.5736 | 1.5106 | 1.3933 | 1.3018 | 1.2696
DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 2.7274 | 2.5875 | 2.3988 | 2.0539 | 1.6607 | 1.1541 | 0.36145 | -0.50456 | -0.90545 | -1.2503 | -1.9634 | -2.2889 | -2.704 | -3.0491 | 4.0612 | 4.0246 | 3.9609 | 3.8185 | 3.6273 | 3.302 | 2.6579 | 1.9767 | 1.7764 | 1.648 | 1.1921 | 1.1156 | 0.88327 | 0.47328 | 3.2596 | 3.202 | 3.0243 | 2.698 | 2.3228 | 1.8262 | 1.0547 | 0.22681 | -0.16453 | -0.50709 | -1.2122 | -1.4735 | -1.8543 | -2.0837
| BALMEDIE | CT |  |  |  | 2.8562 | 2.763 | 2.6288 | 2.3118 | 1.9687 | 1.5195 | 0.85193 | 0.16057 | -0.25777 | -0.64437 | -1.3852 | -1.9872 | -2.6791 | -3.0491 | 4.0903 | 4.0471 | 3.9778 | 3.8628 | 3.7293 | 3.4481 | 2.8899 | 2.3384 | 2.1225 | 1.9686 | 1.6239 | 1.3401 | 0.89721 | 0.47328 | 3.2931 | 3.2465 | 3.1662 | 2.9239 | 2.5982 | 2.1631 | 1.5271 | 0.88798 | 0.49447 | 0.12044 | -0.59454 | -1.1142 | -1.717 | -2.0494
| BALMEDIE | LW |  |  |  | 2.7274 | 2.5875 | 2.3988 | 2.0539 | 1.6607 | 1.1541 | 0.36145 | -0.50456 | -0.90545 | -1.2503 | -1.9634 | -2.2889 | -2.704 | -2.9287 | 4.0612 | 4.0246 | 3.9609 | 3.8185 | 3.6273 | 3.302 | 2.6579 | 1.9767 | 1.7764 | 1.648 | 1.1921 | 1.1156 | 0.88327 | 0.70198 | 3.2596 | 3.202 | 3.0243 | 2.698 | 2.3228 | 1.8262 | 1.0547 | 0.22681 | -0.16453 | -0.50709 | -1.2122 | -1.4735 | -1.8543 | -2.0837
| BALMEDIE | ST |  |  |  | 2.894 | 2.8346 | 2.7663 | 2.6119 | 2.4634 | 2.2514 | 1.7368 | 1.2097 | 0.96997 | 0.77845 | 0.37907 | -0.32965 | -0.97174 | -1.6481 | 4.0989 | 4.0691 | 4.0357 | 3.9125 | 3.8072 | 3.6342 | 3.0891 | 2.5698 | 2.3833 | 2.269 | 2.0413 | 1.8676 | 1.4088 | 0.8823 | 3.3039 | 3.2746 | 3.2407 | 3.1146 | 3.0061 | 2.8209 | 2.3082 | 1.806 | 1.5683 | 1.376 | 0.96732 | 0.29561 | -0.2948 | -0.90704
| BALMEDIE | FS |  |  |  | 2.9662 | 2.9196 | 2.8669 | 2.7834 | 2.6892 | 2.5242 | 2.2372 | 1.8299 | 1.6086 | 1.4173 | 1.0368 | 0.17298 | -0.77884 | -1.3266 | 4.1634 | 4.1367 | 4.1076 | 4.0621 | 4.0126 | 3.8854 | 3.6087 | 3.2061 | 3.0534 | 2.9389 | 2.7197 | 2.4165 | 1.6443 | 0.99326 | 3.3607 | 3.3357 | 3.3079 | 3.2609 | 3.2091 | 3.085 | 2.8313 | 2.4542 | 2.2449 | 2.0623 | 1.6934 | 0.87419 | -0.0065001 | -0.48704
CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 9.7627 | 9.7174 | 9.5936 | 9.3955 | 9.1753 | 8.9446 | 8.6815 | 8.3724 | 8.0815 | 7.7692 | 7.1334 | 7.4111 | 6.7903 | 6.2227 | 9.1426 | 9.0991 | 9.03 | 8.8921 | 8.7193 | 8.5349 | 8.3421 | 8.1844 | 7.9952 | 7.7898 | 7.3737 | 7.1446 | 6.2265 | 4.7985 | 9.1994 | 9.1755 | 9.1021 | 8.9925 | 8.8082 | 8.5691 | 8.321 | 8.0994 | 7.8107 | 7.4997 | 6.8714 | 7.1076 | 6.4703 | 5.6312
| BALNAGASK | CT |  |  |  | 9.7675 | 9.7405 | 9.6464 | 9.4754 | 9.2015 | 8.9446 | 8.6815 | 8.4447 | 8.198 | 7.9259 | 7.385 | 7.4111 | 6.7903 | 6.3438 | 9.1629 | 9.1241 | 9.0449 | 8.8921 | 8.7193 | 8.5349 | 8.3421 | 8.1844 | 7.9952 | 7.7898 | 7.3737 | 7.1446 | 6.2265 | 5.0267 | 9.2028 | 9.1797 | 9.1021 | 8.9925 | 8.8082 | 8.5691 | 8.321 | 8.1083 | 7.8672 | 7.6002 | 7.07 | 7.1076 | 6.4703 | 5.9575
| BALNAGASK | LW |  |  |  | 9.7627 | 9.7174 | 9.5936 | 9.3955 | 9.1753 | 8.9631 | 8.6839 | 8.3724 | 8.0815 | 7.7692 | 7.1334 | 7.6603 | 7.0309 | 6.2227 | 9.1426 | 9.0991 | 9.03 | 8.9321 | 8.8218 | 8.7144 | 8.5658 | 8.3967 | 8.2022 | 7.9924 | 7.5702 | 7.8771 | 7.156 | 6.1632 | 9.1994 | 9.1755 | 9.1358 | 9.0071 | 8.8166 | 8.6332 | 8.3825 | 8.0994 | 7.8107 | 7.4997 | 6.8714 | 7.3789 | 6.6298 | 5.6312
| BALNAGASK | ST |  |  |  | 9.7708 | 9.7576 | 9.7414 | 9.6817 | 9.6279 | 9.5769 | 9.4753 | 9.4078 | 9.2559 | 9.1183 | 8.7679 | 8.5297 | 7.8027 | 6.9929 | 9.1742 | 9.1521 | 9.1249 | 9.0426 | 8.9679 | 8.8971 | 8.7627 | 8.6725 | 8.4783 | 8.3395 | 8.0075 | 7.5588 | 6.4721 | 5.0081 | 9.2053 | 9.1937 | 9.1794 | 9.1124 | 9.0551 | 9.004 | 8.8926 | 8.8277 | 8.6622 | 8.5477 | 8.2114 | 7.9422 | 7.1555 | 6.304
| BALNAGASK | FS |  |  |  | 9.7794 | 9.7684 | 9.7557 | 9.7317 | 9.7067 | 9.6775 | 9.644 | 9.5949 | 9.4817 | 9.3728 | 9.1181 | 8.9153 | 8.3671 | 7.9553 | 9.1798 | 9.1547 | 9.1279 | 9.0781 | 9.0231 | 8.9617 | 8.8899 | 8.8131 | 8.6893 | 8.5685 | 8.2848 | 7.785 | 6.66 | 4.7985 | 9.2127 | 9.2029 | 9.1915 | 9.1673 | 9.1422 | 9.1129 | 9.0799 | 9.0445 | 8.9743 | 8.9116 | 8.6553 | 8.4795 | 7.9862 | 7.642
KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | NO | 3.1323 | 2.7463 | 2.2781 | 1.5928 | 0.86735 | 0.15038 | -0.73761 | -1.9665 | -2.8336 | -3.5978 | -5.2373 | -5.4113 | -6.9228 | -7.755 | 6.4727 | 6.2808 | 6.0062 | 5.6715 | 5.3033 | 4.9029 | 4.4319 | 3.5992 | 2.9494 | 2.4104 | 1.2903 | 1.1929 | 0.13294 | -0.94938 | 5.0271 | 4.6768 | 4.2116 | 3.5958 | 2.9308 | 2.2883 | 1.4279 | 0.23646 | -0.6859 | -1.515 | -3.2198 | -3.1449 | -4.4059 | -5.1097
| BANCHORY | CT |  |  |  | 3.4421 | 3.2059 | 2.883 | 2.1239 | 1.3308 | 0.59547 | -0.20031 | -1.2547 | -2.1131 | -2.8865 | -4.5331 | -5.3319 | -6.9228 | -7.755 | 6.5766 | 6.4335 | 6.2076 | 5.7745 | 5.309 | 4.9029 | 4.4462 | 3.7623 | 3.1569 | 2.6001 | 1.4859 | 1.1929 | 0.13294 | -0.94938 | 5.2737 | 5.0488 | 4.7157 | 3.9894 | 3.217 | 2.5395 | 1.8073 | 0.84876 | -0.0044635 | -0.84328 | -2.5148 | -3.1069 | -4.4059 | -5.1097
| BANCHORY | LW |  |  |  | 3.1323 | 2.7463 | 2.2781 | 1.5928 | 0.86735 | 0.15038 | -0.73761 | -1.9665 | -2.8336 | -3.5978 | -5.2373 | -5.4113 | -6.3251 | -6.7876 | 6.4727 | 6.2808 | 6.0062 | 5.6715 | 5.3033 | 4.9508 | 4.4319 | 3.5992 | 2.9494 | 2.4104 | 1.2903 | 1.5984 | 1.1534 | 0.84811 | 5.0271 | 4.6768 | 4.2116 | 3.5958 | 2.9308 | 2.2883 | 1.4279 | 0.23646 | -0.6859 | -1.515 | -3.2198 | -3.1449 | -3.9147 | -4.338
| BANCHORY | ST |  |  |  | 3.5974 | 3.477 | 3.334 | 3.1226 | 2.8934 | 2.6468 | 2.3217 | 1.7263 | 1.2124 | 0.79943 | -0.12795 | -1.4931 | -2.8366 | -4.2659 | 6.6409 | 6.5641 | 6.4679 | 6.318 | 6.151 | 5.9715 | 5.7066 | 5.2045 | 4.7661 | 4.4216 | 3.623 | 2.6468 | 1.5782 | 0.27118 | 5.3966 | 5.2809 | 5.1391 | 4.9248 | 4.6859 | 4.429 | 4.0838 | 3.494 | 2.9589 | 2.4951 | 1.429 | 0.032671 | -1.1877 | -2.3835
| BANCHORY | FS |  |  |  | 3.6496 | 3.565 | 3.4616 | 3.2821 | 3.0876 | 2.8806 | 2.6377 | 2.178 | 1.7394 | 1.3811 | 0.60146 | -1.1174 | -3.0942 | -4.2651 | 6.6614 | 6.5999 | 6.522 | 6.4074 | 6.2752 | 6.132 | 5.9525 | 5.5721 | 5.234 | 4.9624 | 4.3449 | 3.0688 | 1.2588 | -0.52011 | 5.4394 | 5.3552 | 5.2497 | 5.0758 | 4.8805 | 4.6722 | 4.426 | 3.9787 | 3.5486 | 3.1773 | 2.3511 | 0.5909 | -1.3052 | -2.2609
TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | -2.3865 | -2.4344 | -2.4994 | -2.5822 | -2.6786 | -2.7786 | -2.8907 | -2.9922 | -3.0404 | -3.1112 | -3.2503 | -3.2696 | -3.3763 | -3.4357 | -2.3446 | -2.3549 | -2.3811 | -2.4302 | -2.5039 | -2.5692 | -2.641 | -2.7029 | -2.7498 | -2.8139 | -2.9342 | -2.9618 | -3.0484 | -3.1274 | -2.7726 | -2.8188 | -2.8828 | -2.9625 | -3.0638 | -3.1642 | -3.279 | -3.3865 | -3.4388 | -3.5138 | -3.6514 | -3.6663 | -3.7742 | -3.8406
| BARCALDINE | CT |  |  |  | -2.3609 | -2.3943 | -2.4462 | -2.563 | -2.6786 | -2.7786 | -2.8907 | -2.9922 | -3.0404 | -3.1112 | -3.2503 | -3.2696 | -3.3763 | -3.4357 | -2.344 | -2.3549 | -2.3774 | -2.4302 | -2.5039 | -2.5692 | -2.641 | -2.7029 | -2.7498 | -2.8139 | -2.9342 | -2.9618 | -3.0484 | -3.1274 | -2.7484 | -2.7808 | -2.8339 | -2.9485 | -3.0638 | -3.1642 | -3.279 | -3.3865 | -3.4388 | -3.5138 | -3.6514 | -3.6663 | -3.7742 | -3.8406
| BARCALDINE | LW |  |  |  | -2.3865 | -2.4344 | -2.4994 | -2.5822 | -2.6588 | -2.735 | -2.8296 | -2.9418 | -3.0114 | -3.0854 | -3.2437 | -3.2464 | -3.3249 | -3.3953 | -2.3446 | -2.3549 | -2.3811 | -2.4288 | -2.4751 | -2.5192 | -2.5816 | -2.6555 | -2.7168 | -2.7826 | -2.9127 | -2.8984 | -2.9681 | -3.0463 | -2.7726 | -2.8188 | -2.8828 | -2.9625 | -3.0378 | -3.1121 | -3.2072 | -3.3228 | -3.3976 | -3.477 | -3.6363 | -3.632 | -3.7194 | -3.8035
| BARCALDINE | ST |  |  |  | -2.348 | -2.3742 | -2.3961 | -2.4342 | -2.4747 | -2.5075 | -2.5598 | -2.6047 | -2.6662 | -2.7256 | -2.8663 | -3.1367 | -3.2485 | -3.3304 | -2.343 | -2.3486 | -2.3551 | -2.3738 | -2.3891 | -2.4105 | -2.4548 | -2.4903 | -2.5409 | -2.5887 | -2.7031 | -2.9049 | -3.0117 | -3.1037 | -2.7368 | -2.7618 | -2.7834 | -2.8234 | -2.8654 | -2.9004 | -2.9572 | -3.0043 | -3.0705 | -3.1338 | -3.2844 | -3.553 | -3.6748 | -3.7609
| BARCALDINE | FS |  |  |  | -2.3396 | -2.358 | -2.3753 | -2.4054 | -2.4332 | -2.4667 | -2.4986 | -2.535 | -2.5761 | -2.6189 | -2.7206 | -3.0041 | -3.2162 | -3.2561 | -2.342 | -2.3467 | -2.352 | -2.3606 | -2.3685 | -2.3777 | -2.3993 | -2.4256 | -2.457 | -2.49 | -2.5679 | -2.7566 | -2.9313 | -2.9935 | -2.729 | -2.7465 | -2.7631 | -2.793 | -2.8214 | -2.8552 | -2.8882 | -2.9254 | -2.9685 | -3.0132 | -3.1193 | -3.3952 | -3.6117 | -3.6515
STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | NO | 0.80921 | 0.6207 | 0.47863 | 0.31536 | 0.13855 | -0.02485 | -0.21325 | -0.41277 | -0.51613 | -0.62404 | -0.83619 | -0.97377 | -1.1762 | -1.2668 | 1.466 | 1.3737 | 1.3337 | 1.2966 | 1.2526 | 1.2141 | 1.1651 | 1.1059 | 1.0072 | 0.90197 | 0.69726 | 0.5951 | 0.46904 | 0.38111 | 0.45538 | 0.3542 | 0.31101 | 0.26735 | 0.16907 | 0.045269 | -0.13686 | -0.33193 | -0.44722 | -0.56828 | -0.83883 | -1.0327 | -1.1964 | -1.2834
| BARVAS | CT |  |  |  | 0.8966 | 0.7574 | 0.65856 | 0.44327 | 0.22087 | 0.020777 | -0.17823 | -0.36993 | -0.4536 | -0.55907 | -0.76724 | -0.88738 | -1.1762 | -1.2668 | 1.4785 | 1.3957 | 1.365 | 1.3141 | 1.2637 | 1.2169 | 1.1715 | 1.1296 | 1.0667 | 0.9611 | 0.75846 | 0.61137 | 0.46904 | 0.38111 | 0.47316 | 0.38348 | 0.34453 | 0.28422 | 0.21509 | 0.077849 | -0.10672 | -0.28474 | -0.37655 | -0.4962 | -0.74047 | -0.95304 | -1.1964 | -1.2834
| BARVAS | LW |  |  |  | 0.80921 | 0.6207 | 0.47863 | 0.31536 | 0.13855 | -0.02485 | -0.21325 | -0.41277 | -0.51613 | -0.62404 | -0.83619 | -0.97377 | -1.1137 | -1.1556 | 1.466 | 1.3737 | 1.3337 | 1.2966 | 1.2526 | 1.2141 | 1.1651 | 1.1059 | 1.0072 | 0.90197 | 0.69726 | 0.5951 | 0.53919 | 0.52427 | 0.45538 | 0.3542 | 0.31101 | 0.26735 | 0.16907 | 0.045269 | -0.13686 | -0.33193 | -0.44722 | -0.56828 | -0.83883 | -1.0327 | -1.15 | -1.183
| BARVAS | ST |  |  |  | 0.93128 | 0.81707 | 0.7586 | 0.67752 | 0.5944 | 0.5058 | 0.4196 | 0.33159 | 0.22854 | 0.11989 | -0.1192 | -0.62597 | -0.86926 | -1.0242 | 1.4818 | 1.4095 | 1.3928 | 1.3733 | 1.3526 | 1.3248 | 1.2969 | 1.2697 | 1.238 | 1.2014 | 1.1151 | 0.73147 | 0.59123 | 0.49186 | 0.4786 | 0.40245 | 0.38156 | 0.35635 | 0.3296 | 0.3003 | 0.26982 | 0.23909 | 0.19595 | 0.13144 | -0.088079 | -0.71288 | -0.94749 | -1.0726
| BARVAS | FS |  |  |  | 0.9706 | 0.89064 | 0.84551 | 0.77411 | 0.7031 | 0.63309 | 0.55801 | 0.48295 | 0.38626 | 0.2869 | 0.073163 | -0.60278 | -1.0098 | -1.1356 | 1.4981 | 1.4441 | 1.4311 | 1.4135 | 1.3965 | 1.3804 | 1.3585 | 1.3343 | 1.306 | 1.2754 | 1.2072 | 0.86498 | 0.52962 | 0.41777 | 0.49627 | 0.43933 | 0.42302 | 0.40024 | 0.37781 | 0.35603 | 0.33195 | 0.3056 | 0.27497 | 0.23819 | 0.10597 | -0.56268 | -1.0499 | -1.1481
STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | NO | 4.7735 | 4.1389 | 3.1348 | 1.9577 | 0.63817 | -0.74337 | -2.2577 | -3.5969 | -4.6247 | -5.6987 | -8.3866 | -7.4346 | -8.3098 | -8.9374 | 8.6077 | 8.1746 | 7.3271 | 6.3649 | 5.2622 | 3.9996 | 2.6213 | 1.4769 | 0.48078 | -0.51877 | -3.1974 | -2.0932 | -2.8227 | -3.5108 | 6.2596 | 5.646 | 4.573 | 3.3207 | 1.9082 | 0.39155 | -1.2622 | -2.6976 | -3.8528 | -5.0334 | -7.6621 | -6.8277 | -7.7303 | -8.4666
| BATTERY POINT | CT |  |  |  | 4.9719 | 4.4666 | 3.6403 | 2.3972 | 0.95082 | -0.44391 | -1.8668 | -3.0733 | -4.0239 | -5.0519 | -7.5779 | -6.7896 | -7.8362 | -8.3801 | 8.6781 | 8.3041 | 7.5717 | 6.6266 | 5.4561 | 4.2822 | 3.0529 | 2.08 | 1.136 | 0.12354 | -2.3741 | -1.5723 | -2.3861 | -3.155 | 6.4335 | 5.9377 | 5.0439 | 3.761 | 2.2273 | 0.73305 | -0.77491 | -2.023 | -3.095 | -4.2617 | -6.7158 | -6.0455 | -7.0208 | -7.5827
| BATTERY POINT | LW |  |  |  | 4.7735 | 4.1389 | 3.1348 | 1.9577 | 0.63817 | -0.74337 | -2.2577 | -3.5969 | -4.6247 | -5.6987 | -8.3866 | -7.4346 | -8.3098 | -8.9374 | 8.6077 | 8.1746 | 7.3271 | 6.3649 | 5.2622 | 3.9996 | 2.6213 | 1.4769 | 0.48078 | -0.51877 | -3.1974 | -2.0932 | -2.8227 | -3.5108 | 6.2596 | 5.646 | 4.573 | 3.3207 | 1.9082 | 0.39155 | -1.2622 | -2.6976 | -3.8528 | -5.0334 | -7.6621 | -6.8277 | -7.7303 | -8.4666
| BATTERY POINT | ST |  |  |  | 5.1232 | 4.7548 | 4.1404 | 3.3929 | 2.4658 | 1.5642 | 0.56512 | -0.25134 | -1.1722 | -2.1434 | -4.7287 | -5.2256 | -6.1914 | -7.0199 | 8.7457 | 8.4538 | 7.8633 | 7.1343 | 6.2118 | 5.2497 | 4.1134 | 3.2425 | 2.2812 | 1.2126 | -1.6406 | -1.0227 | -1.9207 | -2.8651 | 6.4823 | 6.2006 | 5.5082 | 4.6582 | 3.5892 | 2.5461 | 1.3964 | 0.47626 | -0.55665 | -1.6334 | -4.132 | -4.7854 | -5.7791 | -6.5964
| BATTERY POINT | FS |  |  |  | 5.1778 | 4.8928 | 4.4258 | 3.8647 | 3.1315 | 2.4255 | 1.7353 | 1.0699 | 0.33117 | -0.45555 | -2.3311 | -4.1342 | -5.9859 | -6.5417 | 8.7699 | 8.5418 | 8.0913 | 7.579 | 6.8691 | 6.1798 | 5.4941 | 4.8238 | 4.0667 | 3.2664 | 1.4728 | 0.2523 | -1.5005 | -2.5425 | 6.497 | 6.2874 | 5.8116 | 5.1925 | 4.3582 | 3.5477 | 2.7638 | 2.0149 | 1.1867 | 0.30679 | -1.5501 | -3.3542 | -5.2995 | -5.8083
DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0.18217 | 0.15969 | 0.12709 | 0.092767 | 0.055667 | -0.014382 | -0.088311 | -0.13902 | -0.17745 | -0.22419 | -0.31142 | -0.4219 | -0.56231 | -0.6947 | 0.40153 | 0.38866 | 0.36807 | 0.34787 | 0.3118 | 0.25208 | 0.18883 | 0.15416 | 0.11554 | 0.06908 | -0.018053 | -0.15282 | -0.31384 | -0.46445 | 0.21121 | 0.19027 | 0.1591 | 0.1267 | 0.084843 | 0.010548 | -0.067974 | -0.1179 | -0.16128 | -0.21416 | -0.31256 | -0.4416 | -0.611 | -0.76297
| BETTYHILL | CT |  |  |  | 0.19625 | 0.18142 | 0.16056 | 0.1089 | 0.055667 | -0.014382 | -0.088311 | -0.13902 | -0.17745 | -0.22419 | -0.31142 | -0.4219 | -0.54175 | -0.63299 | 0.40757 | 0.39787 | 0.38329 | 0.34911 | 0.3118 | 0.25208 | 0.18883 | 0.15416 | 0.11554 | 0.06908 | -0.018053 | -0.13481 | -0.24888 | -0.35883 | 0.22286 | 0.20875 | 0.18823 | 0.13772 | 0.084843 | 0.010548 | -0.067974 | -0.1179 | -0.16128 | -0.21416 | -0.31256 | -0.4416 | -0.57126 | -0.67715
| BETTYHILL | LW |  |  |  | 0.18217 | 0.15969 | 0.12709 | 0.092767 | 0.056189 | 0.020955 | -0.02301 | -0.070118 | -0.10733 | -0.14891 | -0.22321 | -0.28817 | -0.43677 | -0.62183 | 0.40153 | 0.38866 | 0.36807 | 0.34787 | 0.32566 | 0.30537 | 0.27581 | 0.24307 | 0.20817 | 0.17015 | 0.10007 | 0.049817 | -0.11356 | -0.33737 | 0.21121 | 0.19027 | 0.1591 | 0.1267 | 0.09204 | 0.059261 | 0.015888 | -0.03084 | -0.072175 | -0.11767 | -0.19985 | -0.2689 | -0.44337 | -0.67119
| BETTYHILL | ST |  |  |  | 0.20116 | 0.19119 | 0.18075 | 0.14118 | 0.10215 | 0.074842 | 0.01814 | -0.017407 | -0.071275 | -0.11121 | -0.19738 | -0.40587 | -0.56231 | -0.6947 | 0.40987 | 0.40408 | 0.3976 | 0.35673 | 0.32203 | 0.29686 | 0.23502 | 0.20457 | 0.14945 | 0.11429 | 0.03571 | -0.15282 | -0.31384 | -0.46445 | 0.22772 | 0.21864 | 0.20919 | 0.16395 | 0.12212 | 0.092885 | 0.026683 | -0.011062 | -0.072381 | -0.11542 | -0.20928 | -0.43659 | -0.611 | -0.76297
| BETTYHILL | FS |  |  |  | 0.20836 | 0.19989 | 0.19201 | 0.17347 | 0.15322 | 0.13076 | 0.10817 | 0.08566 | 0.053003 | 0.022716 | -0.040261 | -0.20689 | -0.32543 | -0.35862 | 0.41308 | 0.40813 | 0.40295 | 0.38854 | 0.37272 | 0.35502 | 0.3367 | 0.31837 | 0.29036 | 0.26529 | 0.21181 | 0.09502 | -0.0029086 | -0.042483 | 0.2341 | 0.22646 | 0.21913 | 0.20052 | 0.18012 | 0.15736 | 0.13448 | 0.11141 | 0.076969 | 0.045232 | -0.020882 | -0.18694 | -0.30931 | -0.34229
ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | NO | 10.0688 | 19.1178 | 19.0221 | 18.3961 | 17.6746 | 16.3907 | 15.0031 | 14.1012 | 13.7489 | 13.3754 | 12.7038 | 11.7418 | 11.3179 | 11.1084 | 9.5402 | 18.5049 | 18.4526 | 17.767 | 16.989 | 15.5063 | 13.9144 | 12.9434 | 12.6312 | 12.3026 | 11.7141 | 10.6736 | 10.2647 | 10.0373 | 8.9178 | 17.905 | 17.8823 | 17.2398 | 16.5121 | 15.0761 | 13.5416 | 12.6339 | 12.3727 | 12.0991 | 11.6108 | 10.4925 | 10.0097 | 9.7621
| BILBOHALL | CT |  |  |  | 10.1261 | 19.2041 | 19.143 | 18.9384 | 18.6548 | 17.9702 | 17.2456 | 16.9401 | 16.6896 | 16.4034 | 15.8734 | 15.174 | 14.7577 | 14.5577 | 9.5629 | 18.5388 | 18.5015 | 18.3458 | 18.1137 | 17.3685 | 16.5765 | 16.3126 | 16.1216 | 15.9077 | 15.5095 | 14.878 | 14.519 | 14.2248 | 8.9194 | 17.9055 | 17.8828 | 17.772 | 17.5953 | 16.8956 | 16.1508 | 15.9354 | 15.7997 | 15.6603 | 15.3984 | 14.7759 | 14.3499 | 14.1434
| BILBOHALL | LW |  |  |  | 10.0688 | 19.1178 | 19.0221 | 18.3961 | 17.6746 | 16.3907 | 15.0031 | 14.1012 | 13.7489 | 13.3754 | 12.7038 | 11.7418 | 11.3179 | 11.1084 | 9.5402 | 18.5049 | 18.4526 | 17.767 | 16.989 | 15.5063 | 13.9144 | 12.9434 | 12.6312 | 12.3026 | 11.7141 | 10.6736 | 10.2647 | 10.0373 | 8.9178 | 17.905 | 17.8823 | 17.2398 | 16.5121 | 15.0761 | 13.5416 | 12.6339 | 12.3727 | 12.0991 | 11.6108 | 10.4925 | 10.0097 | 9.7621
| BILBOHALL | ST |  |  |  | 10.1372 | 19.2348 | 19.2092 | 18.6874 | 18.3014 | 18.0213 | 17.2129 | 16.9296 | 16.6784 | 16.5168 | 16.1716 | 15.3948 | 14.9518 | 14.5934 | 9.5676 | 18.5549 | 18.5396 | 17.9155 | 17.4735 | 17.1664 | 16.2013 | 15.8962 | 15.6376 | 15.4982 | 15.1922 | 14.4646 | 14.0503 | 13.675 | 8.9209 | 17.9153 | 17.9083 | 17.2984 | 16.8719 | 16.5809 | 15.6337 | 15.348 | 15.1128 | 14.9993 | 14.7492 | 14.3599 | 14.1304 | 13.9703
| BILBOHALL | FS |  |  |  | 10.1494 | 19.252 | 19.2304 | 19.1005 | 18.9497 | 18.7805 | 18.6088 | 18.4435 | 18.3016 | 18.1727 | 17.9105 | 17.4019 | 16.9621 | 16.7325 | 9.5727 | 18.5623 | 18.5491 | 18.407 | 18.2527 | 18.0765 | 17.8973 | 17.7326 | 17.6071 | 17.4998 | 17.2768 | 16.9018 | 16.4794 | 16.0379 | 8.9219 | 17.9173 | 17.9116 | 17.7816 | 17.6422 | 17.4811 | 17.3179 | 17.1723 | 17.0739 | 16.9959 | 16.8383 | 16.7933 | 16.7193 | 16.646
RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | NO | 0.034348 | 0.033813 | 0.030931 | 0.028191 | 0.023903 | 0.022873 | 0.020427 | 0.012564 | 0.011279 | 0.007665 | -0.003196 | 0.012475 | 0.010665 | 0.01138 | 0.012743 | 0.01229 | 0.01082 | 0.0094141 | 0.0067782 | 0.0059026 | 0.0046082 | 0.0011525 | -0.00054384 | -0.0043588 | -0.012307 | -0.0013037 | -0.0026916 | -0.0034432 | 0.0066955 | 0.0061714 | 0.0035404 | 0.0010831 | -0.0029329 | -0.0039937 | -0.0053986 | -0.013068 | -0.013111 | -0.015134 | -0.02354 | -0.01425 | -0.015849 | -0.015182
| BLACKMOUNT | CT |  |  |  | 0.034384 | 0.033813 | 0.032718 | 0.029256 | 0.023903 | 0.022873 | 0.020427 | 0.012564 | 0.011279 | 0.0087074 | 0.0029028 | 0.012815 | 0.010665 | 0.011686 | 0.012764 | 0.01229 | 0.01138 | 0.0094141 | 0.0067782 | 0.0059026 | 0.0046082 | 0.0011525 | -0.00054384 | -0.0025468 | -0.007278 | -0.0013037 | -0.0026916 | -0.0031781 | 0.0067391 | 0.0061714 | 0.0050626 | 0.0018684 | -0.0029329 | -0.0039937 | -0.0053986 | -0.013068 | -0.013111 | -0.015134 | -0.018926 | -0.013912 | -0.015849 | -0.014993
| BLACKMOUNT | LW |  |  |  | 0.034348 | 0.033842 | 0.030931 | 0.028191 | 0.02724 | 0.024437 | 0.02346 | 0.018321 | 0.012669 | 0.007665 | -0.003196 | 0.012475 | 0.011949 | 0.011949 | 0.012743 | 0.012321 | 0.01082 | 0.0094629 | 0.0086548 | 0.0072584 | 0.0064708 | 0.0031799 | -0.00052292 | -0.0043588 | -0.012307 | -0.001121 | -0.0013875 | -0.0013879 | 0.0066955 | 0.0061741 | 0.0035404 | 0.0010831 | 8.3984e-05 | -0.0024215 | -0.0027528 | -0.0063561 | -0.010265 | -0.013132 | -0.02354 | -0.01425 | -0.014731 | -0.014731
| BLACKMOUNT | ST |  |  |  | 0.034427 | 0.034214 | 0.033932 | 0.033545 | 0.03303 | 0.032426 | 0.031709 | 0.02851 | 0.026082 | 0.022253 | 0.014466 | 0.013738 | 0.012774 | 0.012748 | 0.012793 | 0.012602 | 0.012348 | 0.012009 | 0.011557 | 0.011032 | 0.010942 | 0.008784 | 0.0078019 | 0.0053523 | -0.00060954 | -0.00057326 | -0.0017533 | -0.0024925 | 0.0067753 | 0.0065577 | 0.0062647 | 0.0058638 | 0.0053264 | 0.0047024 | 0.0052591 | 0.0010634 | -0.00012533 | -0.0028463 | -0.0069364 | -0.012996 | -0.013956 | -0.013982
| BLACKMOUNT | FS |  |  |  | 0.034458 | 0.03429 | 0.034068 | 0.033778 | 0.033405 | 0.03299 | 0.032488 | 0.02995 | 0.030729 | 0.028105 | 0.022805 | 0.01709 | 0.011444 | 0.01138 | 0.012816 | 0.012658 | 0.012449 | 0.01219 | 0.011855 | 0.011486 | 0.011041 | 0.009832 | 0.0097663 | 0.0083536 | 0.0058996 | 0.0020854 | -0.0023798 | -0.0034432 | 0.0068062 | 0.0066335 | 0.0064029 | 0.0061002 | 0.0057078 | 0.0052753 | 0.0047532 | 0.0025108 | 0.003099 | 0.00060465 | -0.0031316 | -0.0096566 | -0.015119 | -0.015182
BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 4.8063 | 4.7016 | 4.5578 | 4.4111 | 4.2543 | 4.0822 | 3.8632 | 3.6504 | 3.5152 | 3.3495 | 3.0292 | 2.7496 | 2.1591 | 1.3666 | 5.9725 | 5.9234 | 5.8492 | 5.7781 | 5.6892 | 5.5587 | 5.4221 | 5.3115 | 5.1981 | 5.0579 | 4.7828 | 4.4599 | 3.8511 | 3.0082 | 5.3402 | 5.2576 | 5.1416 | 5.0245 | 4.8982 | 4.7314 | 4.5395 | 4.3689 | 4.2337 | 4.0718 | 3.766 | 3.4378 | 2.8038 | 1.8425
| BLACKSTAND | CT |  |  |  | 4.8711 | 4.8023 | 4.7014 | 4.5009 | 4.2937 | 4.0822 | 3.8632 | 3.6504 | 3.5152 | 3.3495 | 3.0344 | 2.7496 | 2.2399 | 1.8387 | 5.9974 | 5.9618 | 5.9066 | 5.8015 | 5.6892 | 5.5587 | 5.4221 | 5.3115 | 5.1981 | 5.0579 | 4.7828 | 4.4599 | 3.9825 | 3.4679 | 5.3891 | 5.3343 | 5.2528 | 5.0886 | 4.9161 | 4.7314 | 4.5395 | 4.3689 | 4.2337 | 4.0718 | 3.766 | 3.4378 | 2.9239 | 2.4754
| BLACKSTAND | LW |  |  |  | 4.8063 | 4.7016 | 4.5578 | 4.4111 | 4.2543 | 4.1049 | 3.9197 | 3.6908 | 3.5295 | 3.3594 | 3.0292 | 2.8043 | 2.1591 | 1.3666 | 5.9725 | 5.9234 | 5.8492 | 5.7781 | 5.7005 | 5.6296 | 5.5297 | 5.4071 | 5.276 | 5.131 | 4.8546 | 4.644 | 3.949 | 3.0082 | 5.3402 | 5.2576 | 5.1416 | 5.0245 | 4.8982 | 4.7812 | 4.6261 | 4.4379 | 4.2821 | 4.1175 | 3.8012 | 3.5445 | 2.8038 | 1.8425
| BLACKSTAND | ST |  |  |  | 4.8975 | 4.8529 | 4.7901 | 4.6915 | 4.5969 | 4.5107 | 4.3744 | 4.257 | 4.0764 | 3.9339 | 3.618 | 2.9443 | 2.3325 | 1.7724 | 6.0083 | 5.9859 | 5.9532 | 5.8791 | 5.8132 | 5.7558 | 5.6459 | 5.5699 | 5.41 | 5.3057 | 5.0617 | 4.4978 | 3.8511 | 3.1711 | 5.4099 | 5.3752 | 5.3263 | 5.2339 | 5.1483 | 5.0725 | 4.9401 | 4.8389 | 4.6552 | 4.5242 | 4.2314 | 3.5755 | 2.9169 | 2.2876
| BLACKSTAND | FS |  |  |  | 4.92 | 4.8868 | 4.8389 | 4.7772 | 4.7068 | 4.6342 | 4.5602 | 4.468 | 4.3508 | 4.2351 | 3.9907 | 3.3764 | 2.9403 | 2.7767 | 6.0173 | 5.9996 | 5.9732 | 5.9367 | 5.8951 | 5.851 | 5.8045 | 5.7486 | 5.6622 | 5.5822 | 5.4099 | 5.0198 | 4.6412 | 4.3551 | 5.4266 | 5.4007 | 5.3632 | 5.3118 | 5.2529 | 5.1917 | 5.1288 | 5.0518 | 4.9438 | 4.8405 | 4.6215 | 4.0986 | 3.7164 | 3.5713
COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | NO | 14.7539 | 14.3266 | 13.7798 | 12.9186 | 12.0054 | 10.9539 | 9.756 | 8.5733 | 7.2939 | 5.9162 | 3.6466 | 2.4454 | 1.4373 | 0.72377 | 17.5716 | 17.3185 | 16.9692 | 16.4735 | 15.9302 | 15.2729 | 14.4983 | 13.7772 | 12.9044 | 11.9422 | 10.3824 | 10.0138 | 9.322 | 8.4652 | 16.71 | 16.3348 | 15.8388 | 15.0614 | 14.2281 | 13.2578 | 12.1316 | 11.0347 | 9.8479 | 8.5638 | 6.4258 | 5.4947 | 4.5883 | 4.0466
| BLAIRGOWRIE | CT |  |  |  | 14.9883 | 14.702 | 14.3116 | 13.5156 | 12.6514 | 11.7061 | 10.7102 | 9.7863 | 8.5361 | 7.0952 | 4.6816 | 2.9608 | 1.5159 | 0.72377 | 17.6538 | 17.4573 | 17.177 | 16.7093 | 16.1799 | 15.5811 | 14.9534 | 14.437 | 13.6264 | 12.6401 | 11.0305 | 10.2145 | 9.322 | 8.4652 | 16.9081 | 16.6534 | 16.2954 | 15.5721 | 14.7772 | 13.9054 | 12.9879 | 12.1679 | 11.0328 | 9.7036 | 7.4674 | 6.0081 | 4.7551 | 4.0466
| BLAIRGOWRIE | LW |  |  |  | 14.7539 | 14.3266 | 13.7798 | 12.9186 | 12.0054 | 10.9539 | 9.756 | 8.5733 | 7.2939 | 5.9162 | 3.6466 | 2.4454 | 1.4373 | 1.0217 | 17.5716 | 17.3185 | 16.9692 | 16.4735 | 15.9302 | 15.2729 | 14.4983 | 13.7772 | 12.9044 | 11.9422 | 10.3824 | 10.0138 | 9.4562 | 9.1145 | 16.71 | 16.3348 | 15.8388 | 15.0614 | 14.2281 | 13.2578 | 12.1316 | 11.0347 | 9.8479 | 8.5638 | 6.4258 | 5.4947 | 4.5883 | 4.1608
| BLAIRGOWRIE | ST |  |  |  | 15.1017 | 14.9036 | 14.6499 | 14.297 | 13.9237 | 13.5312 | 13.0043 | 12.5791 | 11.8483 | 10.9682 | 9.5255 | 8.1458 | 6.9315 | 5.4773 | 17.6984 | 17.5521 | 17.3658 | 17.0543 | 16.7352 | 16.418 | 15.9469 | 15.6085 | 15.0042 | 14.2784 | 13.0789 | 11.9918 | 11.103 | 10.0038 | 17.0038 | 16.831 | 16.6081 | 16.2584 | 15.8954 | 15.5264 | 14.9971 | 14.5943 | 13.9071 | 13.0836 | 11.7018 | 10.3213 | 9.2165 | 7.951
| BLAIRGOWRIE | FS |  |  |  | 15.1124 | 14.9535 | 14.7489 | 14.488 | 14.1852 | 13.8551 | 13.5017 | 13.1464 | 12.5227 | 11.855 | 10.6771 | 8.7861 | 6.8658 | 5.6044 | 17.7056 | 17.5858 | 17.434 | 17.2415 | 17.0097 | 16.7592 | 16.4937 | 16.2252 | 15.7396 | 15.216 | 14.2703 | 12.8244 | 11.1289 | 9.6009 | 17.013 | 16.8758 | 16.6984 | 16.4629 | 16.1851 | 15.8854 | 15.5649 | 15.2413 | 14.6735 | 14.0638 | 12.9669 | 11.2069 | 9.4017 | 8.3389
STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | NO | 0.46053 | 0.45418 | 0.44685 | 0.43746 | 0.43134 | 0.42516 | 0.4187 | 0.41265 | 0.40143 | 0.37312 | 0.31759 | 0.44644 | 0.44663 | 0.44614 | 0.60505 | 0.59568 | 0.58485 | 0.57046 | 0.56159 | 0.55217 | 0.54231 | 0.53235 | 0.51375 | 0.49277 | 0.45182 | 0.55132 | 0.54588 | 0.54289 | 0.53768 | 0.52906 | 0.51913 | 0.50627 | 0.49838 | 0.49023 | 0.48162 | 0.47316 | 0.45855 | 0.44041 | 0.40521 | 0.51789 | 0.50975 | 0.50601
| BLAIRLINNANS | CT |  |  |  | 0.46053 | 0.45418 | 0.44685 | 0.43746 | 0.43134 | 0.42516 | 0.4187 | 0.41265 | 0.40311 | 0.39533 | 0.35565 | 0.44717 | 0.44669 | 0.44629 | 0.60505 | 0.59568 | 0.58485 | 0.57046 | 0.56159 | 0.55217 | 0.54231 | 0.53235 | 0.51783 | 0.50673 | 0.47708 | 0.55407 | 0.54588 | 0.54289 | 0.53768 | 0.52906 | 0.51913 | 0.50627 | 0.49838 | 0.49023 | 0.48162 | 0.47316 | 0.4603 | 0.45038 | 0.42392 | 0.52367 | 0.50975 | 0.50601
| BLAIRLINNANS | LW |  |  |  | 0.46064 | 0.45681 | 0.45067 | 0.44565 | 0.44054 | 0.43519 | 0.42543 | 0.41398 | 0.40143 | 0.37312 | 0.31759 | 0.44644 | 0.44663 | 0.44646 | 0.60519 | 0.59953 | 0.58964 | 0.58198 | 0.57376 | 0.56533 | 0.5506 | 0.53299 | 0.51375 | 0.49277 | 0.45182 | 0.55132 | 0.54866 | 0.54755 | 0.53792 | 0.53298 | 0.52426 | 0.51769 | 0.5105 | 0.50343 | 0.49052 | 0.4753 | 0.45855 | 0.44041 | 0.40521 | 0.51789 | 0.51335 | 0.5111
| BLAIRLINNANS | ST |  |  |  | 0.46146 | 0.45988 | 0.45793 | 0.45627 | 0.45307 | 0.44901 | 0.44417 | 0.4383 | 0.43105 | 0.42234 | 0.40109 | 0.44799 | 0.44697 | 0.44655 | 0.6065 | 0.60402 | 0.6012 | 0.59734 | 0.59243 | 0.58636 | 0.57888 | 0.56978 | 0.55872 | 0.54543 | 0.51268 | 0.55745 | 0.54952 | 0.54445 | 0.53892 | 0.53686 | 0.53442 | 0.53113 | 0.52689 | 0.52164 | 0.51518 | 0.50732 | 0.49776 | 0.48618 | 0.45794 | 0.52744 | 0.51551 | 0.50715
| BLAIRLINNANS | FS |  |  |  | 0.46168 | 0.46036 | 0.45889 | 0.45746 | 0.45552 | 0.45261 | 0.44927 | 0.44544 | 0.441 | 0.43566 | 0.42346 | 0.45128 | 0.44674 | 0.44614 | 0.60685 | 0.60478 | 0.60252 | 0.59971 | 0.5961 | 0.59183 | 0.58669 | 0.58085 | 0.57408 | 0.56609 | 0.54739 | 0.56573 | 0.54834 | 0.54412 | 0.53918 | 0.53749 | 0.53555 | 0.53307 | 0.52999 | 0.52628 | 0.52188 | 0.51678 | 0.51086 | 0.50395 | 0.48774 | 0.53058 | 0.51335 | 0.50726
BOAT OF GARTEN | BOAT OF GARTEN 11 kV | MINIMUM HEADROOM | NH 95609 19427 | NO | NO | 7.0775 | 7.0615 | 7.0431 | 7.0205 | 6.9957 | 6.9433 | 6.8209 | 6.7086 | 6.66 | 6.5894 | 6.3482 | 6.2709 | 6.074 | 5.9636 | 8.0695 | 8.0394 | 8.0083 | 7.9696 | 7.9308 | 7.8719 | 7.8059 | 7.7531 | 7.7235 | 7.6947 | 7.593 | 7.4613 | 7.3275 | 7.1946 | 6.9546 | 6.8966 | 6.8349 | 6.7569 | 6.6788 | 6.5902 | 6.4758 | 6.3741 | 6.3264 | 6.28 | 6.1797 | 6.2898 | 6.128 | 6.0304
| BOAT OF GARTEN 11 kV | CT |  |  |  | 7.0787 | 7.0623 | 7.0462 | 7.0205 | 6.9957 | 6.9433 | 6.8209 | 6.7086 | 6.66 | 6.6129 | 6.3843 | 6.2709 | 6.074 | 5.9636 | 8.0862 | 8.0641 | 8.0401 | 7.9874 | 7.9353 | 7.8719 | 7.8059 | 7.7531 | 7.7235 | 7.6947 | 7.593 | 7.4613 | 7.3275 | 7.1946 | 6.9915 | 6.9513 | 6.9053 | 6.8023 | 6.7008 | 6.5902 | 6.4758 | 6.3741 | 6.3264 | 6.28 | 6.1797 | 6.2898 | 6.128 | 6.0304
| BOAT OF GARTEN 11 kV | LW |  |  |  | 7.0775 | 7.0615 | 7.0431 | 7.0283 | 7.0111 | 6.9455 | 6.844 | 6.736 | 6.6808 | 6.5894 | 6.3482 | 6.2847 | 6.1432 | 6.0296 | 8.0695 | 8.0394 | 8.0083 | 7.9696 | 7.9308 | 7.8918 | 7.8446 | 7.7939 | 7.7626 | 7.7239 | 7.5955 | 7.5576 | 7.4566 | 7.3427 | 6.9546 | 6.8966 | 6.8349 | 6.7569 | 6.6788 | 6.6003 | 6.5085 | 6.4104 | 6.3573 | 6.2992 | 6.1841 | 6.3415 | 6.2031 | 6.074
| BOAT OF GARTEN 11 kV | ST |  |  |  | 7.0798 | 7.0702 | 7.0646 | 7.0453 | 7.0275 | 7.0107 | 6.9779 | 6.9563 | 6.9219 | 6.8925 | 6.8223 | 6.5696 | 6.3916 | 6.2561 | 8.0996 | 8.0877 | 8.0777 | 8.0499 | 8.025 | 8.001 | 7.9603 | 7.9342 | 7.8937 | 7.8616 | 7.7766 | 7.5602 | 7.403 | 7.2585 | 7.0176 | 6.9955 | 6.9749 | 6.9333 | 6.893 | 6.8522 | 6.7949 | 6.7502 | 6.6898 | 6.6359 | 6.5147 | 6.4851 | 6.3412 | 6.2025
| BOAT OF GARTEN 11 kV | FS |  |  |  | 7.0815 | 7.0727 | 7.0677 | 7.059 | 7.049 | 7.0379 | 7.0254 | 7.0116 | 6.9932 | 6.9745 | 6.9318 | 6.7112 | 6.3808 | 6.3061 | 8.1036 | 8.0937 | 8.0867 | 8.0695 | 8.0501 | 8.0304 | 8.0117 | 7.9915 | 7.9653 | 7.9394 | 7.8878 | 7.7713 | 7.4858 | 7.3525 | 7.0253 | 7.0078 | 6.9933 | 6.9602 | 6.923 | 6.886 | 6.8512 | 6.8133 | 6.7673 | 6.7203 | 6.6277 | 6.5076 | 6.3972 | 6.3332
PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 1.9089 | 1.768 | 1.6992 | 1.5659 | 1.4432 | 1.3317 | 0.7412 | 0.16015 | -0.4198 | -1.1285 | -2.0414 | -2.1947 | -2.7302 | -3.3833 | 1.9367 | 1.757 | 1.7055 | 1.6032 | 1.5107 | 1.4283 | 0.82477 | 0.24344 | -0.33246 | -1.0589 | -1.9145 | -2.3371 | -2.8436 | -3.6274 | 1.0629 | 0.90813 | 0.86448 | 0.77403 | 0.69013 | 0.61505 | 0.052365 | -0.48964 | -1.0287 | -1.7122 | -2.5127 | -3 | -3.5174 | -4.309
| BODDAM | CT |  |  |  | 1.9351 | 1.8043 | 1.7042 | 1.5659 | 1.4432 | 1.3317 | 0.7412 | 0.16015 | -0.41806 | -1.1285 | -2.008 | -2.1947 | -2.5879 | -2.9148 | 1.9597 | 1.7905 | 1.707 | 1.6032 | 1.5107 | 1.4283 | 0.82477 | 0.24344 | -0.33246 | -1.0589 | -1.9145 | -2.2967 | -2.6091 | -2.9419 | 1.0834 | 0.9389 | 0.86611 | 0.77403 | 0.69013 | 0.61505 | 0.052365 | -0.48964 | -1.0287 | -1.7122 | -2.5127 | -2.9667 | -3.3228 | -3.7193
| BODDAM | LW |  |  |  | 1.9089 | 1.768 | 1.6992 | 1.6169 | 1.5197 | 1.4383 | 0.83017 | 0.18374 | -0.4198 | -1.1155 | -2.0414 | -2.1235 | -2.7302 | -3.3833 | 1.9367 | 1.757 | 1.7055 | 1.6509 | 1.5742 | 1.5276 | 0.92134 | 0.28222 | -0.31389 | -1.0035 | -1.8744 | -2.1939 | -2.8436 | -3.6274 | 1.0629 | 0.90813 | 0.86448 | 0.81549 | 0.74872 | 0.70805 | 0.14539 | -0.4477 | -1.0034 | -1.6464 | -2.4521 | -2.8697 | -3.5174 | -4.309
| BODDAM | ST |  |  |  | 1.9419 | 1.8325 | 1.7958 | 1.7296 | 1.6724 | 1.6187 | 1.0652 | 0.52569 | -0.053094 | -0.75443 | -1.6413 | -2.0176 | -2.4332 | -2.8598 | 1.9622 | 1.8058 | 1.7684 | 1.6995 | 1.6445 | 1.5982 | 1.0097 | 0.44844 | -0.15787 | -0.88218 | -1.7628 | -2.3371 | -2.7925 | -3.2598 | 1.0854 | 0.95054 | 0.91817 | 0.85493 | 0.80571 | 0.76482 | 0.21557 | -0.30768 | -0.87793 | -1.5554 | -2.3723 | -3 | -3.4551 | -3.9205
| BODDAM | FS |  |  |  | 1.9898 | 1.9072 | 1.8787 | 1.8338 | 1.7966 | 1.7596 | 1.439 | 1.0195 | 0.59796 | 0.14908 | -0.52048 | -1.2275 | -1.8654 | -2.049 | 2.0315 | 1.9133 | 1.8834 | 1.8375 | 1.802 | 1.7695 | 1.4305 | 0.98657 | 0.54458 | 0.077323 | -0.60588 | -1.4319 | -2.0647 | -2.2235 | 1.1453 | 1.0435 | 1.0176 | 0.97652 | 0.94519 | 0.91659 | 0.60151 | 0.18811 | -0.22579 | -0.66254 | -1.2971 | -2.1215 | -2.726 | -2.8711
TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | -2.3682 | -2.4256 | -2.514 | -2.6323 | -2.7641 | -2.9451 | -3.136 | -3.3046 | -3.4794 | -3.6614 | -3.996 | -3.8918 | -4.1471 | -4.3207 | -1.3868 | -1.4164 | -1.4653 | -1.5402 | -1.6308 | -1.7555 | -1.889 | -1.9856 | -2.1096 | -2.2488 | -2.5226 | -2.4932 | -2.6979 | -2.9288 | -2.3163 | -2.3709 | -2.4603 | -2.5695 | -2.712 | -2.8901 | -3.0776 | -3.2318 | -3.4051 | -3.5964 | -3.9487 | -3.9312 | -4.1831 | -4.3736
| BONSKEID | CT |  |  |  | -2.3503 | -2.3933 | -2.4663 | -2.6067 | -2.7641 | -2.9451 | -3.136 | -3.3046 | -3.4794 | -3.6614 | -3.996 | -3.8918 | -4.1471 | -4.3207 | -1.374 | -1.4052 | -1.4572 | -1.5402 | -1.6308 | -1.7555 | -1.889 | -1.9856 | -2.1096 | -2.2488 | -2.5226 | -2.4932 | -2.6979 | -2.8974 | -2.286 | -2.3303 | -2.4092 | -2.554 | -2.712 | -2.8901 | -3.0776 | -3.2318 | -3.4051 | -3.5964 | -3.9487 | -3.9312 | -4.1831 | -4.3736
| BONSKEID | LW |  |  |  | -2.3682 | -2.4256 | -2.514 | -2.6323 | -2.7564 | -2.8878 | -3.052 | -3.2335 | -3.3953 | -3.5738 | -3.8998 | -3.6943 | -3.9487 | -4.2354 | -1.3868 | -1.4164 | -1.4653 | -1.5223 | -1.5832 | -1.6451 | -1.7336 | -1.8466 | -1.9704 | -2.1057 | -2.3597 | -2.2147 | -2.4641 | -2.7942 | -2.3163 | -2.3709 | -2.4603 | -2.5695 | -2.687 | -2.8034 | -2.9595 | -3.1346 | -3.3038 | -3.4895 | -3.8346 | -3.6808 | -3.9642 | -4.3072
| BONSKEID | ST |  |  |  | -2.3384 | -2.3528 | -2.38 | -2.4579 | -2.5375 | -2.6186 | -2.7452 | -2.8428 | -2.9853 | -3.1173 | -3.4027 | -3.4384 | -3.7308 | -4.0143 | -1.3641 | -1.3778 | -1.3978 | -1.4736 | -1.5381 | -1.5975 | -1.7125 | -1.7844 | -1.9002 | -1.9961 | -2.3243 | -2.3914 | -2.6646 | -2.9288 | -2.268 | -2.2903 | -2.3233 | -2.4194 | -2.5066 | -2.59 | -2.7307 | -2.8327 | -2.9842 | -3.1184 | -3.4103 | -3.5909 | -3.9064 | -4.196
| BONSKEID | FS |  |  |  | -2.3358 | -2.3457 | -2.365 | -2.4043 | -2.4484 | -2.5079 | -2.5748 | -2.6441 | -2.7318 | -2.8263 | -3.0155 | -3.1446 | -3.3884 | -3.5288 | -1.3612 | -1.3697 | -1.3859 | -1.4192 | -1.454 | -1.4941 | -1.5387 | -1.5851 | -1.647 | -1.7089 | -1.8556 | -1.9878 | -2.2171 | -2.3496 | -2.2631 | -2.2767 | -2.3045 | -2.3555 | -2.4086 | -2.4686 | -2.5357 | -2.6061 | -2.696 | -2.7896 | -2.9835 | -3.1787 | -3.4617 | -3.5803
PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | NO | 1.868 | 1.7946 | 1.6863 | 0.89184 | 0.17394 | -0.57936 | -0.76487 | -0.96481 | -1.0639 | -1.1653 | -1.3738 | -1.4183 | -1.8809 | -2.4234 | 2.3686 | 2.3143 | 2.2582 | 1.4763 | 0.72193 | -0.076369 | -0.16912 | -0.27934 | -0.35026 | -0.4241 | -0.57091 | -0.64133 | -1.13 | -1.7827 | 1.1058 | 1.0096 | 0.91134 | 0.10679 | -0.65712 | -1.4598 | -1.6253 | -1.8057 | -1.9019 | -2.0209 | -2.2605 | -2.3396 | -2.8788 | -3.5452
| BOWMORE | CT |  |  |  | 1.889 | 1.8399 | 1.7947 | 1.0315 | 0.26087 | -0.49125 | -0.71809 | -0.9483 | -1.0563 | -1.1431 | -1.3037 | -1.3032 | -1.6733 | -1.9487 | 2.389 | 2.3467 | 2.3014 | 1.5802 | 0.80238 | 0.033718 | -0.088456 | -0.22366 | -0.32275 | -0.38346 | -0.49787 | -0.5564 | -0.87771 | -1.1972 | 1.1544 | 1.085 | 1.0114 | 0.23926 | -0.57054 | -1.3642 | -1.5695 | -1.7806 | -1.8886 | -1.9742 | -2.1641 | -2.2134 | -2.602 | -2.9215
| BOWMORE | LW |  |  |  | 1.868 | 1.7946 | 1.6863 | 0.89184 | 0.17394 | -0.57936 | -0.76487 | -0.96481 | -1.0639 | -1.1653 | -1.3738 | -1.4183 | -1.8809 | -2.4234 | 2.3686 | 2.3143 | 2.2582 | 1.4763 | 0.72193 | -0.076369 | -0.16912 | -0.27934 | -0.35026 | -0.4241 | -0.57091 | -0.64133 | -1.13 | -1.7827 | 1.1058 | 1.0096 | 0.91134 | 0.10679 | -0.65712 | -1.4598 | -1.6253 | -1.8057 | -1.9019 | -2.0209 | -2.2605 | -2.3396 | -2.8788 | -3.5452
| BOWMORE | ST |  |  |  | 1.9245 | 1.8984 | 1.8827 | 1.2734 | 0.64022 | 0.0043265 | -0.055064 | -0.12658 | -0.27771 | -0.36882 | -0.57558 | -0.92368 | -1.3383 | -1.7331 | 2.4105 | 2.3846 | 2.3644 | 1.7012 | 0.9684 | 0.2336 | 0.16933 | 0.089492 | -0.037671 | -0.084952 | -0.21596 | -0.42445 | -0.84193 | -1.2874 | 1.1991 | 1.1576 | 1.125 | 0.48929 | -0.18624 | -0.86451 | -0.95534 | -1.0545 | -1.2126 | -1.2985 | -1.507 | -1.8793 | -2.3462 | -2.8067
| BOWMORE | FS |  |  |  | 1.9303 | 1.912 | 1.8986 | 1.4314 | 0.91722 | 0.43716 | 0.28323 | 0.17429 | 0.03422 | -0.18542 | -0.42998 | -0.81369 | -1.1299 | -1.2492 | 2.4158 | 2.3956 | 2.3777 | 1.8738 | 1.2818 | 0.72504 | 0.54934 | 0.44351 | 0.32833 | 0.11686 | -0.078862 | -0.2492 | -0.46438 | -0.61602 | 1.2088 | 1.179 | 1.1512 | 0.65904 | 0.10143 | -0.42071 | -0.60908 | -0.73202 | -0.87381 | -1.0983 | -1.3367 | -1.7075 | -2.0291 | -2.1462
WOODHILL | BRAE | MINIMUM HEADROOM | HU 3604068816 | YES | NO | -2.5375 | -2.8475 | -3.2224 | -3.6564 | -4.2154 | -4.7354 | -5.5334 | -6.1762 | -6.8587 | -7.6841 | -8.7253 | -8.972 | -9.4799 | -10.2593 | -1.0739 | -1.4769 | -1.9024 | -2.3589 | -2.967 | -3.5331 | -4.4208 | -5.1197 | -5.8541 | -6.7736 | -7.9323 | -8.4205 | -9.0101 | -9.906 | -2.3721 | -2.7621 | -3.176 | -3.6152 | -4.1845 | -4.7142 | -5.5328 | -6.1854 | -6.847 | -7.6699 | -8.6643 | -9.0193 | -9.6112 | -10.5815
| BRAE | CT |  |  |  | -2.4932 | -2.7532 | -3.0904 | -3.521 | -4.0818 | -4.6539 | -5.4892 | -6.1137 | -6.7701 | -7.6712 | -8.7253 | -8.972 | -9.3525 | -9.7133 | -1.0145 | -1.3833 | -1.7774 | -2.2259 | -2.8233 | -3.4382 | -4.3578 | -5.0324 | -5.7866 | -6.7736 | -7.9323 | -8.3892 | -8.8099 | -9.2456 | -2.3086 | -2.6626 | -3.0428 | -3.4833 | -4.0526 | -4.6413 | -5.5019 | -6.1387 | -6.8193 | -7.6699 | -8.6643 | -9.0193 | -9.4571 | -9.8884
| BRAE | LW |  |  |  | -2.5375 | -2.8475 | -3.2224 | -3.6564 | -4.2154 | -4.7354 | -5.5334 | -6.1762 | -6.8587 | -7.6841 | -8.6731 | -8.84 | -9.4799 | -10.2593 | -1.0739 | -1.4769 | -1.9024 | -2.3589 | -2.967 | -3.5331 | -4.4208 | -5.1197 | -5.8541 | -6.739 | -7.7931 | -8.182 | -8.9431 | -9.906 | -2.3721 | -2.7621 | -3.176 | -3.6152 | -4.1845 | -4.7142 | -5.5328 | -6.1854 | -6.847 | -7.624 | -8.5731 | -8.842 | -9.6112 | -10.5815
| BRAE | ST |  |  |  | -2.4699 | -2.7142 | -3.0251 | -3.4194 | -3.9321 | -4.4216 | -5.2605 | -5.8966 | -6.6531 | -7.552 | -8.6166 | -8.8857 | -9.3802 | -9.8655 | -1.0043 | -1.3632 | -1.7437 | -2.1992 | -2.795 | -3.3601 | -4.279 | -4.9455 | -5.757 | -6.7626 | -7.9174 | -8.4205 | -9.0101 | -9.613 | -2.2893 | -2.6259 | -2.9819 | -3.4052 | -3.9424 | -4.4528 | -5.2835 | -5.8848 | -6.6193 | -7.4875 | -8.5304 | -8.877 | -9.4706 | -10.0689
| BRAE | FS |  |  |  | -2.3621 | -2.5467 | -2.7496 | -3.0265 | -3.4197 | -3.8002 | -4.334 | -4.8472 | -5.4594 | -6.1557 | -7.1402 | -7.9245 | -8.5544 | -8.7324 | -0.8437 | -1.1156 | -1.4092 | -1.7304 | -2.1784 | -2.6159 | -3.2229 | -3.805 | -4.4611 | -5.1922 | -6.2601 | -7.2688 | -8.0033 | -8.2458 | -2.1463 | -2.3965 | -2.6712 | -2.981 | -3.3969 | -3.7932 | -4.3451 | -4.8723 | -5.468 | -6.1291 | -7.0658 | -7.845 | -8.5377 | -8.733
BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | NO | 4.9483 | 4.6729 | 4.3098 | 3.6862 | 3.0192 | 2.3194 | 1.4588 | 0.20089 | -0.58903 | -1.421 | -3.0924 | -3.3175 | -4.3729 | -5.2888 | 6.5171 | 6.371 | 6.161 | 5.8041 | 5.4154 | 4.9542 | 4.3474 | 3.4159 | 2.8502 | 2.2508 | 0.98983 | 0.98119 | -0.0060074 | -1.0882 | 6.0137 | 5.7779 | 5.4596 | 4.8897 | 4.2761 | 3.5996 | 2.7598 | 1.5692 | 0.82169 | 0.032963 | -1.6096 | -1.7266 | -2.8702 | -3.9737
| BRECHIN | CT |  |  |  | 4.9909 | 4.8754 | 4.6948 | 4.1119 | 3.4931 | 2.8442 | 2.1195 | 1.1171 | 0.33039 | -0.52266 | -2.1858 | -3.1424 | -4.3313 | -5.1128 | 6.5765 | 6.46 | 6.303 | 5.9784 | 5.6244 | 5.1924 | 4.6862 | 3.9703 | 3.4251 | 2.8217 | 1.635 | 0.98669 | -0.0060074 | -1.0882 | 6.1639 | 6.0045 | 5.7953 | 5.2722 | 4.7112 | 4.0865 | 3.3854 | 2.4595 | 1.727 | 0.93028 | -0.62687 | -1.4842 | -2.6346 | -3.441
| BRECHIN | LW |  |  |  | 4.9483 | 4.6729 | 4.3098 | 3.6862 | 3.0192 | 2.3194 | 1.4588 | 0.20089 | -0.58903 | -1.421 | -3.0924 | -3.3175 | -4.3729 | -5.2888 | 6.5171 | 6.371 | 6.161 | 5.8041 | 5.4154 | 4.9542 | 4.3474 | 3.4159 | 2.8502 | 2.2508 | 0.98983 | 0.98119 | 0.038041 | -1.0244 | 6.0137 | 5.7779 | 5.4596 | 4.8897 | 4.2761 | 3.5996 | 2.7598 | 1.5692 | 0.82169 | 0.032963 | -1.6096 | -1.7266 | -2.8702 | -3.9737
| BRECHIN | ST |  |  |  | 5.002 | 4.934 | 4.85 | 4.6371 | 4.449 | 4.2886 | 3.9258 | 3.293 | 2.7815 | 2.2564 | 1.1376 | 0.26526 | -0.872 | -2.2591 | 6.6202 | 6.559 | 6.4796 | 6.2389 | 6.0298 | 5.8577 | 5.4558 | 4.86 | 4.3963 | 3.9449 | 2.9737 | 2.1039 | 0.95997 | -0.46585 | 6.2594 | 6.1903 | 6.0974 | 5.8399 | 5.6098 | 5.4224 | 4.9994 | 4.3695 | 3.8659 | 3.3668 | 2.265 | 1.3761 | 0.21025 | -1.1466
| BRECHIN | FS |  |  |  | 5.006 | 4.9482 | 4.8764 | 4.7721 | 4.6574 | 4.5195 | 4.3116 | 3.7975 | 3.4252 | 3.0385 | 2.1986 | 1.071 | -0.34018 | -1.2408 | 6.6185 | 6.5631 | 6.4936 | 6.3714 | 6.2368 | 6.0999 | 5.9271 | 5.4796 | 5.1654 | 4.8417 | 4.1252 | 3.1191 | 1.635 | 0.08509 | 6.2527 | 6.1903 | 6.1119 | 5.9655 | 5.8058 | 5.6451 | 5.4495 | 4.9687 | 4.6182 | 4.2567 | 3.4664 | 2.4443 | 1.0992 | 0.31806
PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 8.7309 | 7.6282 | 6.3142 | 4.0657 | 1.7339 | -0.45862 | -2.0566 | -3.688 | -4.6769 | -5.7742 | -8.0658 | -5.5469 | -6.4599 | -7.2938 | 12.8517 | 11.7021 | 10.3615 | 8.1893 | 5.9842 | 3.858 | 2.5027 | 1.0662 | 0.19385 | -0.75928 | -2.7099 | 1.1164 | 0.32371 | -1.1333 | 11.4839 | 10.3936 | 9.1 | 6.6408 | 4.2586 | 1.9613 | 0.35745 | -1.1947 | -2.0577 | -2.9802 | -4.8531 | -2.7569 | -3.7408 | -4.7129
| BRIDGE OF DON | CT |  |  |  | 8.7585 | 7.7219 | 6.5217 | 4.638 | 2.5978 | 0.65408 | -0.73704 | -2.0418 | -3.1037 | -4.001 | -5.8331 | -4.5546 | -5.8808 | -6.7134 | 12.8776 | 11.8072 | 10.591 | 8.6238 | 6.4354 | 4.4992 | 3.3007 | 2.2132 | 1.3905 | 0.71861 | -0.6508 | 1.8377 | 0.57556 | -0.99828 | 11.5106 | 10.4899 | 9.3134 | 7.4335 | 5.285 | 3.2441 | 1.8574 | 0.61912 | -0.28065 | -1.0773 | -2.6441 | -1.489 | -2.7118 | -3.5174
| BRIDGE OF DON | LW |  |  |  | 8.7309 | 7.6282 | 6.3142 | 4.0657 | 1.7339 | -0.45862 | -2.0566 | -3.688 | -4.6769 | -5.7742 | -8.0658 | -5.5469 | -6.4599 | -7.2938 | 12.8517 | 11.7021 | 10.3615 | 8.1893 | 5.9842 | 3.858 | 2.5027 | 1.0662 | 0.19385 | -0.75928 | -2.7099 | 1.1164 | 0.32371 | -0.58921 | 11.4839 | 10.3936 | 9.1 | 6.6408 | 4.2586 | 1.9613 | 0.35745 | -1.1947 | -2.0577 | -2.9802 | -4.8531 | -2.7569 | -3.7408 | -4.7129
| BRIDGE OF DON | ST |  |  |  | 8.7905 | 7.882 | 6.8896 | 5.0903 | 3.2314 | 1.7854 | 0.78246 | -0.22354 | -1.137 | -2.1021 | -4.4558 | -1.1542 | -2.6166 | -4.0299 | 12.9034 | 11.9357 | 10.886 | 8.9096 | 6.7986 | 5.1291 | 4.077 | 3.1567 | 2.4728 | 1.777 | 0.093937 | 2.4178 | 1.3401 | -0.51201 | 11.5404 | 10.6387 | 9.6553 | 7.8241 | 5.9015 | 4.4048 | 3.3382 | 2.386 | 1.726 | 0.94483 | -1.3433 | 1.3426 | -0.14302 | -1.6076
| BRIDGE OF DON | FS |  |  |  | 8.9065 | 8.1963 | 7.4254 | 6.1412 | 4.7093 | 3.6187 | 2.8965 | 2.1629 | 1.6585 | 0.86491 | -0.69608 | 0.16662 | -1.6776 | -2.955 | 13.0147 | 12.2693 | 11.4688 | 10.0931 | 8.4726 | 7.2253 | 6.4544 | 5.6996 | 5.1969 | 4.4473 | 3.2517 | 3.721 | 2.0178 | -1.1333 | 11.6511 | 10.9488 | 10.1882 | 8.9118 | 7.4617 | 6.3386 | 5.6065 | 4.8696 | 4.3646 | 3.6362 | 2.4671 | 2.7312 | 1.2313 | 0.072943
BRIDGE OF DUN | BRIDGE OF DUN 11kV | MINIMUM HEADROOM | NO 66018 58883 | YES | NO | -0.20534 | -0.22991 | -0.25409 | -0.28199 | -0.30945 | -0.34733 | -0.39484 | -0.43439 | -0.47754 | -0.52836 | -0.61672 | -0.75184 | -1.1955 | -1.8135 | -0.0050043 | -0.015078 | -0.02727 | -0.039776 | -0.058641 | -0.091636 | -0.12622 | -0.14725 | -0.20242 | -0.2449 | -0.3384 | -0.54579 | -1.0273 | -1.7888 | -0.33204 | -0.35059 | -0.37072 | -0.39272 | -0.41514 | -0.45733 | -0.50207 | -0.53469 | -0.58523 | -0.64425 | -0.7498 | -0.9506 | -1.4707 | -2.2377
| BRIDGE OF DUN 11kV | CT |  |  |  | -0.1915 | -0.20869 | -0.22589 | -0.26142 | -0.30128 | -0.34733 | -0.39484 | -0.43439 | -0.47754 | -0.52836 | -0.61672 | -0.75184 | -1.0132 | -1.277 | -0.00045496 | -0.0081829 | -0.017426 | -0.036568 | -0.058641 | -0.091636 | -0.12622 | -0.14725 | -0.19344 | -0.2449 | -0.3384 | -0.51832 | -0.80086 | -1.1224 | -0.32227 | -0.33532 | -0.34967 | -0.37975 | -0.41414 | -0.45733 | -0.50207 | -0.53469 | -0.58523 | -0.64425 | -0.7498 | -0.93558 | -1.2369 | -1.5572
| BRIDGE OF DUN 11kV | LW |  |  |  | -0.20534 | -0.22991 | -0.25409 | -0.28199 | -0.30945 | -0.33951 | -0.37313 | -0.40848 | -0.4553 | -0.50811 | -0.60631 | -0.74311 | -1.1955 | -1.8135 | -0.0050043 | -0.015078 | -0.02727 | -0.039776 | -0.052949 | -0.066029 | -0.08385 | -0.10342 | -0.15455 | -0.20931 | -0.30911 | -0.48682 | -1.0273 | -1.7888 | -0.33204 | -0.35059 | -0.37072 | -0.39272 | -0.41514 | -0.43835 | -0.46705 | -0.4978 | -0.55379 | -0.61526 | -0.72933 | -0.91788 | -1.4707 | -2.2377
| BRIDGE OF DUN 11kV | ST |  |  |  | -0.18541 | -0.19284 | -0.20605 | -0.23559 | -0.25943 | -0.28094 | -0.31813 | -0.3412 | -0.41894 | -0.46163 | -0.55579 | -0.75085 | -1.1231 | -1.512 | 0.0015411 | -0.0020124 | -0.0077279 | -0.031726 | -0.05039 | -0.065777 | -0.10053 | -0.11746 | -0.20242 | -0.2417 | -0.32973 | -0.54579 | -0.96924 | -1.4289 | -0.31817 | -0.32402 | -0.33402 | -0.3633 | -0.38661 | -0.40682 | -0.44657 | -0.46857 | -0.55903 | -0.60465 | -0.70628 | -0.9506 | -1.3888 | -1.8555
| BRIDGE OF DUN 11kV | FS |  |  |  | -0.17782 | -0.185 | -0.1943 | -0.20668 | -0.22363 | -0.23925 | -0.25381 | -0.27189 | -0.31154 | -0.34119 | -0.41611 | -0.53421 | -0.625 | -0.69818 | 0.0040167 | 0.00062728 | -0.0037147 | -0.011838 | -0.021872 | -0.032065 | -0.042379 | -0.053764 | -0.089961 | -0.11711 | -0.17807 | -0.25838 | -0.33404 | -0.41008 | -0.31292 | -0.31849 | -0.32565 | -0.33685 | -0.35143 | -0.36552 | -0.37919 | -0.39522 | -0.43715 | -0.46876 | -0.54375 | -0.66234 | -0.75843 | -0.83338
ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | NO | 10.535 | 10.0207 | 9.4088 | 8.6456 | 7.7525 | 6.8108 | 5.8164 | 4.9352 | 4.2139 | 3.4287 | 1.915 | 0.37361 | -0.30926 | -0.74062 | 12.2171 | 11.8476 | 11.3959 | 10.8484 | 10.1818 | 9.4597 | 8.7064 | 8.0929 | 7.588 | 7.0222 | 5.9097 | 4.9107 | 4.3885 | 3.9255 | 11.0455 | 10.5903 | 10.033 | 9.3328 | 8.5034 | 7.6133 | 6.6632 | 5.8379 | 5.1699 | 4.4402 | 3.0257 | 1.6737 | 1.0008 | 0.503
| BRIDGE OF EARN | CT |  |  |  | 10.6916 | 10.2663 | 9.7636 | 9.059 | 8.2302 | 7.322 | 6.4054 | 5.6474 | 4.9176 | 4.0671 | 2.4581 | 0.80985 | 0.13684 | -0.25536 | 12.2968 | 11.9711 | 11.5781 | 11.0949 | 10.4975 | 9.8034 | 9.112 | 8.6158 | 8.1143 | 7.5046 | 6.3323 | 5.1091 | 4.6197 | 4.1551 | 11.1821 | 10.8019 | 10.342 | 9.7024 | 8.9399 | 8.0829 | 7.2183 | 6.5382 | 5.8722 | 5.0857 | 3.5928 | 2.0747 | 1.4513 | 1.0606
| BRIDGE OF EARN | LW |  |  |  | 10.535 | 10.0207 | 9.4088 | 8.6456 | 7.7525 | 6.8108 | 5.8164 | 4.9352 | 4.2139 | 3.4287 | 1.915 | 0.37361 | -0.30926 | -0.74062 | 12.2171 | 11.8476 | 11.3959 | 10.8484 | 10.1818 | 9.4597 | 8.7064 | 8.0929 | 7.588 | 7.0222 | 5.9097 | 4.9107 | 4.3885 | 3.9255 | 11.0455 | 10.5903 | 10.033 | 9.3328 | 8.5034 | 7.6133 | 6.6632 | 5.8379 | 5.1699 | 4.4402 | 3.0257 | 1.6737 | 1.0008 | 0.503
| BRIDGE OF EARN | ST |  |  |  | 10.7582 | 10.3753 | 9.9351 | 9.3763 | 8.7451 | 8.1548 | 7.4437 | 6.9365 | 6.3868 | 5.7821 | 4.5746 | 2.866 | 2.2203 | 1.5831 | 12.3204 | 12.0181 | 11.6621 | 11.1669 | 10.621 | 10.1236 | 9.4774 | 9.0629 | 8.6153 | 8.134 | 7.1483 | 5.7404 | 5.181 | 4.5844 | 11.2375 | 10.8965 | 10.4982 | 9.9559 | 9.3556 | 8.8038 | 8.098 | 7.6227 | 7.1054 | 6.5464 | 5.4141 | 3.7738 | 3.1328 | 2.5051
| BRIDGE OF EARN | FS |  |  |  | 10.9108 | 10.6147 | 10.2681 | 9.8762 | 9.3941 | 8.9188 | 8.4527 | 8.001 | 7.518 | 6.9784 | 5.9444 | 3.9357 | 2.6456 | 2.1711 | 12.4529 | 12.2178 | 11.9384 | 11.6261 | 11.2322 | 10.843 | 10.4654 | 10.1054 | 9.7227 | 9.2953 | 8.4662 | 6.8982 | 5.8112 | 5.2139 | 11.3831 | 11.1206 | 10.8086 | 10.453 | 10.0116 | 9.5758 | 9.1493 | 8.7369 | 8.2962 | 7.8045 | 6.8507 | 4.9963 | 3.804 | 3.3815
RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | NO | 0.36959 | 0.36227 | 0.34883 | 0.34335 | 0.32745 | 0.30961 | 0.28522 | 0.26862 | 0.25476 | 0.23878 | 0.21218 | 0.2 | 0.16488 | 0.12718 | 0.19629 | 0.19271 | 0.186 | 0.17992 | 0.16874 | 0.15344 | 0.13526 | 0.12491 | 0.1134 | 0.099941 | 0.07644 | 0.055836 | 0.013722 | -0.025817 | 0.13877 | 0.13217 | 0.11998 | 0.11451 | 0.097934 | 0.078932 | 0.054204 | 0.038366 | 0.023688 | 0.0064916 | -0.021527 | -0.038 | -0.082297 | -0.12485
| BRIDGE OF GAUR | CT |  |  |  | 0.374 | 0.37032 | 0.36313 | 0.3444 | 0.32745 | 0.30961 | 0.28522 | 0.26862 | 0.25476 | 0.23878 | 0.21218 | 0.2 | 0.16951 | 0.14255 | 0.19794 | 0.19571 | 0.1907 | 0.17992 | 0.16874 | 0.15344 | 0.13526 | 0.12491 | 0.1134 | 0.099941 | 0.07644 | 0.059905 | 0.031512 | 0.0021848 | 0.14257 | 0.1391 | 0.13205 | 0.11451 | 0.097934 | 0.078932 | 0.054204 | 0.038366 | 0.023688 | 0.0064916 | -0.021527 | -0.038 | -0.07117 | -0.10169
| BRIDGE OF GAUR | LW |  |  |  | 0.36959 | 0.36227 | 0.34883 | 0.34335 | 0.33013 | 0.31685 | 0.30663 | 0.28918 | 0.27876 | 0.26329 | 0.23256 | 0.23387 | 0.19423 | 0.14497 | 0.19629 | 0.19271 | 0.186 | 0.18234 | 0.17561 | 0.16913 | 0.16212 | 0.15193 | 0.14229 | 0.13042 | 0.1074 | 0.10752 | 0.065317 | 0.0071707 | 0.13877 | 0.13217 | 0.11998 | 0.11454 | 0.10249 | 0.090571 | 0.080367 | 0.063856 | 0.052317 | 0.036473 | 0.0061968 | 0.0059703 | -0.040422 | -0.10056
| BRIDGE OF GAUR | ST |  |  |  | 0.37599 | 0.37486 | 0.36999 | 0.35982 | 0.34739 | 0.33854 | 0.32303 | 0.3087 | 0.29484 | 0.28292 | 0.25341 | 0.20831 | 0.16488 | 0.12718 | 0.19864 | 0.19775 | 0.19535 | 0.18492 | 0.17533 | 0.16821 | 0.1519 | 0.14229 | 0.12801 | 0.11831 | 0.094919 | 0.055836 | 0.013722 | -0.025817 | 0.14422 | 0.14304 | 0.13865 | 0.12702 | 0.11424 | 0.10502 | 0.087062 | 0.073019 | 0.057121 | 0.044644 | 0.014044 | -0.034233 | -0.082297 | -0.12485
| BRIDGE OF GAUR | FS |  |  |  | 0.37808 | 0.37716 | 0.37435 | 0.37156 | 0.36482 | 0.35428 | 0.34849 | 0.34478 | 0.33527 | 0.32078 | 0.30268 | 0.2592 | 0.22314 | 0.21449 | 0.19944 | 0.1987 | 0.19717 | 0.19428 | 0.18983 | 0.18376 | 0.17916 | 0.17529 | 0.16785 | 0.1592 | 0.14486 | 0.11887 | 0.093831 | 0.083874 | 0.146 | 0.14503 | 0.14247 | 0.13924 | 0.13266 | 0.12278 | 0.11675 | 0.1125 | 0.10267 | 0.088923 | 0.070129 | 0.028331 | -0.0060639 | -0.014752
BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | NO | 4.2351 | 4.2089 | 4.1706 | 4.1184 | 4.0496 | 3.8793 | 3.7843 | 3.7081 | 3.6772 | 3.6352 | 3.5469 | 3.5046 | 3.3948 | 3.3077 | 4.2431 | 4.2289 | 4.2067 | 4.1796 | 4.1313 | 4.0225 | 3.9515 | 3.905 | 3.8717 | 3.8303 | 3.7471 | 3.6682 | 3.5526 | 3.4308 | 3.7837 | 3.7572 | 3.7189 | 3.6673 | 3.5992 | 3.435 | 3.3341 | 3.2572 | 3.2224 | 3.1775 | 3.0843 | 3.0271 | 2.9031 | 2.799
| BROADFORD | CT |  |  |  | 4.2509 | 4.2326 | 4.208 | 4.1293 | 4.0496 | 3.8793 | 3.7843 | 3.7081 | 3.6772 | 3.6352 | 3.5469 | 3.5046 | 3.3948 | 3.3077 | 4.2501 | 4.239 | 4.2232 | 4.1796 | 4.1313 | 4.0225 | 3.9515 | 3.905 | 3.8717 | 3.8303 | 3.7471 | 3.6682 | 3.5526 | 3.4308 | 3.8001 | 3.7818 | 3.7576 | 3.6792 | 3.5992 | 3.435 | 3.3341 | 3.2572 | 3.2224 | 3.1775 | 3.0843 | 3.0271 | 2.9031 | 2.799
| BROADFORD | LW |  |  |  | 4.2351 | 4.2089 | 4.1706 | 4.1184 | 4.0633 | 3.9267 | 3.8607 | 3.7892 | 3.7524 | 3.7141 | 3.6437 | 3.622 | 3.488 | 3.3198 | 4.2431 | 4.2289 | 4.2067 | 4.1798 | 4.1491 | 4.0767 | 4.0375 | 3.9946 | 3.9624 | 3.9284 | 3.8649 | 3.8409 | 3.6932 | 3.4931 | 3.7837 | 3.7572 | 3.7189 | 3.6673 | 3.6127 | 3.4898 | 3.4247 | 3.3546 | 3.3163 | 3.2765 | 3.2031 | 3.1762 | 3.015 | 2.8087
| BROADFORD | ST |  |  |  | 4.2744 | 4.2708 | 4.266 | 4.2358 | 4.2089 | 4.1324 | 4.0848 | 4.0585 | 4.0101 | 3.9711 | 3.8811 | 3.7149 | 3.6011 | 3.4818 | 4.2594 | 4.2558 | 4.2511 | 4.2164 | 4.1882 | 4.1373 | 4.083 | 4.0576 | 4.0081 | 3.9747 | 3.8976 | 3.7345 | 3.5897 | 3.4358 | 3.8221 | 3.8178 | 3.8124 | 3.7756 | 3.7441 | 3.6751 | 3.618 | 3.5887 | 3.5334 | 3.4925 | 3.3988 | 3.217 | 3.0767 | 2.9329
| BROADFORD | FS |  |  |  | 4.2757 | 4.2719 | 4.2661 | 4.2473 | 4.2276 | 4.1631 | 4.1396 | 4.1155 | 4.086 | 4.0555 | 3.9955 | 3.8512 | 3.7391 | 3.7028 | 4.2605 | 4.2567 | 4.2517 | 4.2371 | 4.2216 | 4.1812 | 4.1624 | 4.1434 | 4.1171 | 4.0923 | 4.0408 | 3.9336 | 3.8294 | 3.7569 | 3.8233 | 3.8191 | 3.8127 | 3.7921 | 3.7704 | 3.7136 | 3.6883 | 3.6627 | 3.6308 | 3.5989 | 3.5353 | 3.3915 | 3.2796 | 3.241
CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 2.7015 | 2.5836 | 2.4535 | 2.2947 | 2.071 | 1.8763 | 1.6719 | 1.4694 | 1.3055 | 1.1028 | 0.7016 | 0.77702 | 0.68569 | 0.60654 | 4.3174 | 4.2476 | 4.1662 | 4.0713 | 3.9178 | 3.8008 | 3.6776 | 3.554 | 3.454 | 3.3135 | 3.0323 | 3.131 | 3.0184 | 2.9106 | 2.6919 | 2.6185 | 2.5371 | 2.4012 | 2.2473 | 2.1163 | 1.977 | 1.8308 | 1.718 | 1.6174 | 1.3946 | 1.6666 | 1.5853 | 1.5121
| BRODICK | CT |  |  |  | 2.748 | 2.6572 | 2.5522 | 2.3197 | 2.071 | 1.8763 | 1.6719 | 1.4694 | 1.3291 | 1.1419 | 0.77838 | 0.84031 | 0.68569 | 0.60654 | 4.342 | 4.2859 | 4.2138 | 4.0713 | 3.9178 | 3.8008 | 3.6776 | 3.554 | 3.454 | 3.3238 | 3.0694 | 3.1377 | 3.0184 | 2.9106 | 2.7226 | 2.6527 | 2.5513 | 2.4012 | 2.2473 | 2.1163 | 1.977 | 1.8308 | 1.718 | 1.6174 | 1.3946 | 1.7258 | 1.5853 | 1.5121
| BRODICK | LW |  |  |  | 2.7015 | 2.5836 | 2.4535 | 2.2947 | 2.1234 | 1.9624 | 1.7403 | 1.4901 | 1.3055 | 1.1028 | 0.7016 | 0.77702 | 0.70229 | 0.68297 | 4.3174 | 4.2476 | 4.1662 | 4.0733 | 3.9717 | 3.877 | 3.7397 | 3.5837 | 3.4548 | 3.3135 | 3.0323 | 3.131 | 3.0882 | 3.0781 | 2.6919 | 2.6185 | 2.5371 | 2.4491 | 2.3548 | 2.2584 | 2.1296 | 1.9837 | 1.8603 | 1.7237 | 1.4404 | 1.6666 | 1.5992 | 1.5823
| BRODICK | ST |  |  |  | 2.8238 | 2.7906 | 2.7725 | 2.7467 | 2.7093 | 2.6612 | 2.6025 | 2.5324 | 2.432 | 2.3108 | 2.0168 | 1.5984 | 1.5291 | 1.4614 | 4.3512 | 4.333 | 4.3175 | 4.2961 | 4.2687 | 4.2346 | 4.192 | 4.1408 | 4.0782 | 3.9984 | 3.7892 | 3.5241 | 3.4334 | 3.3347 | 2.7496 | 2.7182 | 2.6929 | 2.66 | 2.6201 | 2.5704 | 2.5112 | 2.4418 | 2.357 | 2.255 | 2.0044 | 2.3653 | 2.2879 | 2.2211
| BRODICK | FS |  |  |  | 2.8146 | 2.7826 | 2.7638 | 2.722 | 2.6674 | 2.6146 | 2.555 | 2.4847 | 2.4142 | 2.3323 | 2.1442 | 1.648 | 1.1977 | 1.1366 | 4.3534 | 4.3388 | 4.3284 | 4.3097 | 4.2736 | 4.2376 | 4.1966 | 4.1486 | 4.098 | 4.0396 | 3.9032 | 3.5858 | 3.2374 | 3.0888 | 2.7501 | 2.7233 | 2.7029 | 2.6654 | 2.6217 | 2.5756 | 2.5246 | 2.4669 | 2.4088 | 2.343 | 2.1897 | 2.3212 | 2.0386 | 1.9845
BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | NO | 4.7687 | 4.7664 | 4.7623 | 4.7582 | 2.9082 | 2.8221 | 2.7311 | 2.6213 | 2.5852 | 2.5031 | 2.3532 | 2.2613 | 2.161 | 2.1019 | 5.1482 | 5.1158 | 5.0708 | 5.0214 | 3.6682 | 3.6086 | 3.5492 | 3.4754 | 3.4205 | 3.3598 | 3.2461 | 3.2053 | 3.1029 | 2.995 | 4.9391 | 4.8816 | 4.8057 | 4.7189 | 3.3267 | 3.2365 | 3.1257 | 3.0012 | 2.9207 | 2.831 | 2.6649 | 2.5809 | 2.4932 | 2.4357
| BRORA | CT |  |  |  | 4.7694 | 4.7673 | 4.7642 | 4.7583 | 2.9455 | 2.8353 | 2.7311 | 2.6213 | 2.5926 | 2.5412 | 2.392 | 2.3054 | 2.161 | 2.1019 | 5.1661 | 5.1418 | 5.1101 | 5.0417 | 3.6694 | 3.6086 | 3.5492 | 3.4877 | 3.4442 | 3.3851 | 3.2711 | 3.2053 | 3.1029 | 3.0166 | 4.9744 | 4.9336 | 4.8824 | 4.7661 | 3.343 | 3.2365 | 3.1337 | 3.0272 | 2.9646 | 2.879 | 2.7153 | 2.6268 | 2.4932 | 2.4357
| BRORA | LW |  |  |  | 4.7687 | 4.7664 | 4.7623 | 4.7582 | 2.9082 | 2.8221 | 2.7315 | 2.623 | 2.5852 | 2.5031 | 2.3532 | 2.2613 | 2.1811 | 2.1516 | 5.1482 | 5.1158 | 5.0708 | 5.0214 | 3.6682 | 3.6191 | 3.5508 | 3.4754 | 3.4205 | 3.3598 | 3.2461 | 3.2076 | 3.1672 | 3.1525 | 4.9391 | 4.8816 | 4.8057 | 4.7189 | 3.3267 | 3.24 | 3.1257 | 3.0012 | 2.9207 | 2.831 | 2.6649 | 2.5809 | 2.5066 | 2.4803
| BRORA | ST |  |  |  | 4.7702 | 4.7694 | 4.7683 | 4.7669 | 2.9649 | 2.9628 | 2.9604 | 2.9572 | 2.9531 | 2.9482 | 2.8695 | 2.5538 | 2.4363 | 2.3631 | 5.177 | 5.1647 | 5.1498 | 5.1303 | 3.8069 | 3.7826 | 3.7569 | 3.7249 | 3.6867 | 3.6428 | 3.5411 | 3.3246 | 3.2272 | 3.1376 | 4.9954 | 4.9745 | 4.9496 | 4.9173 | 3.579 | 3.5401 | 3.5003 | 3.4502 | 3.3913 | 3.3243 | 3.1716 | 2.842 | 2.7241 | 2.6556
| BRORA | FS |  |  |  | 4.7705 | 4.7699 | 4.7692 | 4.768 | 2.9665 | 2.9651 | 2.9632 | 2.961 | 2.9583 | 2.9551 | 2.9306 | 2.5891 | 2.3379 | 2.2754 | 5.1807 | 5.1711 | 5.1598 | 5.1418 | 3.8199 | 3.7992 | 3.7749 | 3.7476 | 3.7161 | 3.6809 | 3.6019 | 3.3636 | 3.1415 | 2.995 | 5.0026 | 4.9871 | 4.9691 | 4.9391 | 3.6028 | 3.5695 | 3.5308 | 3.4877 | 3.4391 | 3.3854 | 3.2678 | 2.9052 | 2.6423 | 2.5834
MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | NO | 6.7308 | 6.6166 | 6.4624 | 6.16 | 5.8484 | 5.5296 | 5.1172 | 4.6714 | 4.2448 | 3.7879 | 2.8842 | 2.763 | 2.161 | 1.596 | 7.9589 | 7.8889 | 7.7704 | 7.621 | 7.4143 | 7.2461 | 7.059 | 6.7842 | 6.4697 | 6.1292 | 5.4613 | 5.2632 | 4.3702 | 2.6467 | 7.5328 | 7.4235 | 7.2664 | 6.9902 | 6.7046 | 6.4157 | 6.0355 | 5.6214 | 5.2119 | 4.774 | 3.9102 | 3.8344 | 3.178 | 2.4945
| BROUGHTY FERRY | CT |  |  |  | 6.832 | 6.7767 | 6.6757 | 6.3548 | 6.0206 | 5.7275 | 5.4423 | 5.1508 | 4.7855 | 4.3561 | 3.4946 | 2.9302 | 2.2502 | 1.7626 | 7.9812 | 7.9224 | 7.8249 | 7.6274 | 7.4143 | 7.2461 | 7.0743 | 6.8976 | 6.6373 | 6.3194 | 5.6781 | 5.2632 | 4.3702 | 3.1477 | 7.6185 | 7.5551 | 7.4414 | 7.1581 | 6.8476 | 6.5797 | 6.3171 | 6.0488 | 5.7017 | 5.295 | 4.4819 | 3.9925 | 3.3347 | 2.8306
| BROUGHTY FERRY | LW |  |  |  | 6.7308 | 6.6166 | 6.4624 | 6.16 | 5.8484 | 5.5296 | 5.1172 | 4.6714 | 4.2448 | 3.7879 | 2.8842 | 2.763 | 2.161 | 1.596 | 7.9589 | 7.8889 | 7.7704 | 7.621 | 7.4587 | 7.3015 | 7.059 | 6.7842 | 6.4697 | 6.1292 | 5.4613 | 5.5885 | 5.0413 | 4.3771 | 7.5328 | 7.4235 | 7.2664 | 6.9902 | 6.7046 | 6.4157 | 6.0355 | 5.6214 | 5.2119 | 4.774 | 3.9102 | 3.8344 | 3.178 | 2.4945
| BROUGHTY FERRY | ST |  |  |  | 6.8632 | 6.8448 | 6.8159 | 6.7775 | 6.7152 | 6.6478 | 6.569 | 6.4685 | 6.3041 | 6.1197 | 5.6772 | 5.0228 | 4.2348 | 3.429 | 7.9924 | 7.9616 | 7.9198 | 7.8684 | 7.8007 | 7.7242 | 7.6331 | 7.5226 | 7.3348 | 7.1453 | 6.6911 | 5.944 | 4.921 | 3.5671 | 7.6402 | 7.6146 | 7.5767 | 7.5277 | 7.4585 | 7.3819 | 7.29 | 7.175 | 6.981 | 6.7753 | 6.2816 | 5.5731 | 4.8211 | 4.0996
| BROUGHTY FERRY | FS |  |  |  | 6.8644 | 6.8442 | 6.8231 | 6.7799 | 6.7298 | 6.6677 | 6.6024 | 6.5218 | 6.3825 | 6.2341 | 5.8962 | 5.2697 | 4.3348 | 3.7239 | 7.9932 | 7.9621 | 7.9238 | 7.8738 | 7.8144 | 7.7473 | 7.6699 | 7.5782 | 7.435 | 7.2796 | 6.9147 | 6.1126 | 4.6717 | 2.6467 | 7.6422 | 7.618 | 7.5886 | 7.5414 | 7.4856 | 7.4216 | 7.3505 | 7.2637 | 7.1223 | 6.9707 | 6.6214 | 6.0222 | 5.1662 | 4.7147
DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | NO | 10.7483 | 10.6758 | 10.5682 | 10.4423 | 10.2842 | 10.1056 | 9.914 | 9.7334 | 9.5256 | 9.2993 | 8.8354 | 9.5882 | 9.4116 | 9.269 | 11.4503 | 11.4034 | 11.3289 | 11.2497 | 11.1298 | 10.994 | 10.8483 | 10.7357 | 10.6133 | 10.4371 | 10.0796 | 10.5105 | 10.3193 | 10.1072 | 11.1885 | 11.173 | 11.0694 | 10.9511 | 10.7949 | 10.616 | 10.4242 | 10.2656 | 10.0647 | 9.8379 | 9.3745 | 10.0672 | 9.8801 | 9.7209
| BRUCHAG | CT |  |  |  | 10.7745 | 10.7156 | 10.6435 | 10.4746 | 10.2842 | 10.1056 | 9.914 | 9.7488 | 9.6012 | 9.4417 | 9.0963 | 9.5882 | 9.4116 | 9.269 | 11.4625 | 11.4226 | 11.3709 | 11.2586 | 11.1298 | 10.994 | 10.8483 | 10.7357 | 10.6135 | 10.482 | 10.2005 | 10.5105 | 10.3193 | 10.1072 | 11.1889 | 11.1852 | 11.1384 | 10.9775 | 10.7949 | 10.616 | 10.4242 | 10.2656 | 10.1153 | 9.9528 | 9.6028 | 10.0672 | 9.8801 | 9.7209
| BRUCHAG | LW |  |  |  | 10.7483 | 10.6758 | 10.5682 | 10.4423 | 10.3023 | 10.1688 | 9.9638 | 9.7334 | 9.5256 | 9.2993 | 8.8354 | 9.745 | 9.5393 | 9.2966 | 11.4503 | 11.4034 | 11.3289 | 11.2497 | 11.1598 | 11.0736 | 10.9347 | 10.7744 | 10.6133 | 10.4371 | 10.0796 | 10.7579 | 10.5391 | 10.2523 | 11.1885 | 11.173 | 11.0694 | 10.9511 | 10.8188 | 10.6924 | 10.4956 | 10.2726 | 10.0647 | 9.8379 | 9.3745 | 10.2726 | 10.0355 | 9.7404
| BRUCHAG | ST |  |  |  | 10.8351 | 10.8257 | 10.8144 | 10.7619 | 10.7095 | 10.659 | 10.5581 | 10.4849 | 10.3651 | 10.251 | 9.9803 | 10.1498 | 10.0563 | 9.8853 | 11.4911 | 11.4797 | 11.4654 | 11.4047 | 11.3494 | 11.2983 | 11.1927 | 11.1237 | 11.0113 | 10.9147 | 10.6861 | 10.7346 | 10.5355 | 10.2819 | 11.1935 | 11.1936 | 11.1934 | 11.1526 | 11.1239 | 11.1042 | 11.0061 | 10.9283 | 10.7997 | 10.6828 | 10.4057 | 10.5455 | 10.4131 | 10.2158
| BRUCHAG | FS |  |  |  | 10.8267 | 10.8193 | 10.807 | 10.7671 | 10.7233 | 10.6765 | 10.6184 | 10.553 | 10.4854 | 10.412 | 10.2414 | 10.2966 | 10.1009 | 10.0401 | 11.488 | 11.4784 | 11.4649 | 11.432 | 11.3951 | 11.3544 | 11.3062 | 11.2528 | 11.1897 | 11.1243 | 10.9735 | 10.9864 | 10.7613 | 10.5697 | 11.1928 | 11.1929 | 11.1927 | 11.1833 | 11.1736 | 11.1571 | 11.0984 | 11.0328 | 10.9619 | 10.8865 | 10.712 | 10.7679 | 10.5729 | 10.5141
KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | NO | 7.8451 | 7.2841 | 6.6652 | 5.584 | 4.3715 | 3.0796 | 1.861 | 0.55151 | -0.53209 | -1.646 | -3.5243 | -4.7634 | -6.2189 | -7.2913 | 10.7846 | 10.4351 | 10.0389 | 9.3893 | 8.6349 | 7.7786 | 7.0039 | 6.1491 | 5.4515 | 4.7133 | 3.4869 | 2.932 | 1.959 | 0.95334 | 9.523 | 9.0262 | 8.471 | 7.4769 | 6.3609 | 5.1392 | 3.9761 | 2.7437 | 1.7392 | 0.69871 | -1.0762 | -2.2318 | -3.615 | -4.6025
| BUCKIE | CT |  |  |  | 8.1956 | 7.8272 | 7.3555 | 6.3805 | 5.2723 | 4.1464 | 3.1998 | 2.1954 | 1.0874 | -0.13653 | -2.1949 | -4.2383 | -6.2189 | -7.2913 | 10.907 | 10.646 | 10.2854 | 9.7459 | 9.0649 | 8.3317 | 7.7649 | 7.1511 | 6.4804 | 5.7083 | 4.4371 | 3.428 | 2.147 | 0.95334 | 9.833 | 9.5048 | 9.0766 | 8.1938 | 7.1878 | 6.1414 | 5.2595 | 4.3438 | 3.3336 | 2.2083 | 0.3016 | -1.5407 | -3.366 | -4.4044
| BUCKIE | LW |  |  |  | 7.8451 | 7.2841 | 6.6652 | 5.584 | 4.3715 | 3.0796 | 1.861 | 0.55151 | -0.53209 | -1.646 | -3.5243 | -4.7634 | -6.1361 | -6.9882 | 10.7846 | 10.4351 | 10.0389 | 9.3893 | 8.6349 | 7.7786 | 7.0039 | 6.1491 | 5.4515 | 4.7133 | 3.4869 | 2.932 | 1.959 | 1.0535 | 9.523 | 9.0262 | 8.471 | 7.4769 | 6.3609 | 5.1392 | 3.9761 | 2.7437 | 1.7392 | 0.69871 | -1.0762 | -2.2318 | -3.615 | -4.6025
| BUCKIE | ST |  |  |  | 8.2855 | 7.9904 | 7.6703 | 7.2114 | 6.6824 | 6.174 | 5.7366 | 5.2578 | 4.6894 | 4.101 | 3.1101 | 1.4868 | -0.40023 | -2.5709 | 10.9232 | 10.7003 | 10.4606 | 10.0678 | 9.6384 | 9.2322 | 8.857 | 8.4413 | 7.9554 | 7.4727 | 6.643 | 5.4563 | 4.0676 | 2.3851 | 9.9125 | 9.6524 | 9.3686 | 8.9205 | 8.4221 | 7.9509 | 7.5065 | 7.0503 | 6.5022 | 5.9505 | 4.9943 | 3.3015 | 1.5854 | -0.40317
| BUCKIE | FS |  |  |  | 8.4243 | 8.196 | 7.948 | 7.6196 | 7.2112 | 6.8023 | 6.5011 | 6.0995 | 5.5785 | 5.0357 | 4.0894 | 2.1445 | 0.096676 | -1.4833 | 11.0444 | 10.8749 | 10.6856 | 10.4549 | 10.144 | 9.8232 | 9.5978 | 9.259 | 8.8639 | 8.4449 | 7.7018 | 6.3129 | 4.5602 | 2.6418 | 10.0393 | 9.8405 | 9.6227 | 9.3253 | 8.9567 | 8.587 | 8.3172 | 7.9455 | 7.4686 | 6.9703 | 6.0844 | 4.3035 | 2.4197 | 1.0197
FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | NO | 1.7648 | 1.7566 | 1.7353 | 1.7148 | 1.6899 | 1.6714 | 1.6479 | 1.3234 | 1.2987 | 1.2822 | 1.2439 | 1.2179 | 1.1774 | 1.1622 | 1.8472 | 1.8431 | 1.8333 | 1.8242 | 1.8133 | 1.8026 | 1.7889 | 1.6356 | 1.6208 | 1.6079 | 1.5786 | 1.5626 | 1.5425 | 1.5273 | 1.824 | 1.8217 | 1.8094 | 1.793 | 1.7729 | 1.7572 | 1.7338 | 1.4603 | 1.437 | 1.4201 | 1.3817 | 1.3584 | 1.3237 | 1.3104
| BUNOICH | CT |  |  |  | 1.7786 | 1.7684 | 1.7571 | 1.7324 | 1.7061 | 1.6793 | 1.6488 | 1.3762 | 1.3598 | 1.3349 | 1.2698 | 1.2179 | 1.1774 | 1.1622 | 1.8512 | 1.8466 | 1.8399 | 1.8272 | 1.8137 | 1.8026 | 1.7889 | 1.6608 | 1.6501 | 1.6343 | 1.5934 | 1.5626 | 1.5425 | 1.5273 | 1.8268 | 1.8231 | 1.8186 | 1.804 | 1.7811 | 1.7601 | 1.7339 | 1.5015 | 1.4869 | 1.4631 | 1.4039 | 1.3584 | 1.3237 | 1.3104
| BUNOICH | LW |  |  |  | 1.7648 | 1.7566 | 1.7353 | 1.7148 | 1.6899 | 1.6714 | 1.6479 | 1.3234 | 1.2987 | 1.2822 | 1.2439 | 1.2191 | 1.1987 | 1.1881 | 1.8472 | 1.8431 | 1.8333 | 1.8242 | 1.8133 | 1.8047 | 1.7905 | 1.6356 | 1.6208 | 1.6079 | 1.5786 | 1.5664 | 1.5587 | 1.555 | 1.824 | 1.8217 | 1.8094 | 1.793 | 1.7729 | 1.7572 | 1.7338 | 1.4603 | 1.437 | 1.4201 | 1.3817 | 1.3588 | 1.3414 | 1.3327
| BUNOICH | ST |  |  |  | 1.7825 | 1.7757 | 1.7724 | 1.7629 | 1.7493 | 1.743 | 1.7342 | 1.5887 | 1.5712 | 1.5489 | 1.4967 | 1.4043 | 1.3743 | 1.353 | 1.8524 | 1.8495 | 1.8473 | 1.843 | 1.8369 | 1.8325 | 1.8268 | 1.7461 | 1.7356 | 1.7228 | 1.6911 | 1.6337 | 1.6146 | 1.598 | 1.8282 | 1.8265 | 1.8254 | 1.8231 | 1.8192 | 1.8132 | 1.8047 | 1.6783 | 1.6634 | 1.6447 | 1.6 | 1.518 | 1.4952 | 1.4806
| BUNOICH | FS |  |  |  | 1.7883 | 1.7816 | 1.7804 | 1.7677 | 1.762 | 1.7544 | 1.7444 | 1.6269 | 1.6064 | 1.5931 | 1.545 | 1.438 | 1.3806 | 1.365 | 1.8539 | 1.8512 | 1.8497 | 1.8448 | 1.8414 | 1.8373 | 1.8322 | 1.7621 | 1.7521 | 1.7437 | 1.7168 | 1.6565 | 1.6141 | 1.5945 | 1.8296 | 1.828 | 1.8276 | 1.824 | 1.8226 | 1.8202 | 1.8137 | 1.7065 | 1.6904 | 1.6791 | 1.6399 | 1.5501 | 1.4978 | 1.4864
THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | NO | 2.8664 | 2.8264 | 2.7738 | 2.6979 | 2.596 | 2.4769 | 2.3557 | 2.251 | 2.2012 | 2.1424 | 2.0211 | 1.9655 | 1.8257 | 1.7274 | 3.3154 | 3.295 | 3.2641 | 3.2233 | 3.1575 | 3.0804 | 3.0006 | 2.9435 | 2.8951 | 2.8362 | 2.7112 | 2.6064 | 2.461 | 2.303 | 3.0892 | 3.0528 | 3.0038 | 2.9348 | 2.8373 | 2.7212 | 2.6023 | 2.5052 | 2.4525 | 2.3837 | 2.2408 | 2.1557 | 2.0113 | 1.902
| BURGARHILL | CT |  |  |  | 2.8897 | 2.8635 | 2.82 | 2.7139 | 2.596 | 2.4769 | 2.3557 | 2.251 | 2.2012 | 2.1424 | 2.0211 | 1.9655 | 1.8257 | 1.7274 | 3.3241 | 3.3085 | 3.2817 | 3.2233 | 3.1575 | 3.0804 | 3.0006 | 2.9435 | 2.8951 | 2.8362 | 2.7112 | 2.6064 | 2.4799 | 2.3513 | 3.1048 | 3.0857 | 3.045 | 2.9469 | 2.8373 | 2.7212 | 2.6023 | 2.5052 | 2.4525 | 2.3837 | 2.2408 | 2.1557 | 2.0113 | 1.902
| BURGARHILL | LW |  |  |  | 2.8664 | 2.8264 | 2.7738 | 2.6979 | 2.6185 | 2.5461 | 2.4523 | 2.3454 | 2.2848 | 2.2212 | 2.0906 | 2.0623 | 1.9158 | 1.7471 | 3.3154 | 3.295 | 3.2641 | 3.2265 | 3.1857 | 3.1495 | 3.0963 | 3.0348 | 2.9827 | 2.9252 | 2.804 | 2.7707 | 2.6238 | 2.4293 | 3.0892 | 3.0528 | 3.0038 | 2.9348 | 2.8624 | 2.7966 | 2.7096 | 2.6102 | 2.5437 | 2.4712 | 2.3253 | 2.2869 | 2.1202 | 1.9171
| BURGARHILL | ST |  |  |  | 2.907 | 2.888 | 2.87 | 2.8238 | 2.7826 | 2.7409 | 2.6756 | 2.6266 | 2.5579 | 2.496 | 2.3593 | 2.0751 | 1.9063 | 1.7787 | 3.3305 | 3.3205 | 3.3097 | 3.2681 | 3.2329 | 3.2011 | 3.1378 | 3.1001 | 3.0385 | 2.9908 | 2.8817 | 2.6314 | 2.461 | 2.303 | 3.1059 | 3.1022 | 3.0913 | 3.0416 | 2.9985 | 2.9566 | 2.8837 | 2.833 | 2.7576 | 2.693 | 2.5479 | 2.2432 | 2.0605 | 1.9169
| BURGARHILL | FS |  |  |  | 2.9113 | 2.8968 | 2.8817 | 2.8549 | 2.8252 | 2.7977 | 2.7626 | 2.729 | 2.6823 | 2.6386 | 2.5371 | 2.2847 | 2.0747 | 2.0339 | 3.3322 | 3.3241 | 3.3148 | 3.2967 | 3.2763 | 3.2557 | 3.2311 | 3.2065 | 3.1715 | 3.1388 | 3.0634 | 2.8837 | 2.7099 | 2.6368 | 3.1065 | 3.1035 | 3.0997 | 3.0759 | 3.0471 | 3.0199 | 2.9857 | 2.9518 | 2.9041 | 2.8591 | 2.7548 | 2.4951 | 2.2897 | 2.2508
ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | NO | 7.481 | 7.2626 | 6.9708 | 5.6866 | 4.2669 | 1.7343 | -0.96832 | -2.69 | -3.2754 | -3.8894 | -5.0358 | -6.3151 | -6.9968 | -7.3569 | 8.1469 | 8.0423 | 7.8861 | 6.5053 | 4.967 | 2.0386 | -1.0976 | -3.0032 | -3.5948 | -4.216 | -5.3538 | -7.0506 | -7.7648 | -8.1487 | 6.9355 | 6.7413 | 6.4803 | 4.9843 | 3.3252 | 0.2745 | -2.9872 | -5.0203 | -5.6761 | -6.3636 | -7.6359 | -9.3118 | -10.1001 | -10.5185
| BURGHEAD | CT |  |  |  | 7.602 | 7.4442 | 7.2224 | 6.703 | 6.0761 | 4.6572 | 3.1961 | 2.5682 | 2.2127 | 1.8075 | 1.05 | 0.574 | -0.016085 | -0.28056 | 8.191 | 8.1073 | 7.9795 | 7.6138 | 7.1199 | 5.6244 | 4.0512 | 3.518 | 3.1866 | 2.8157 | 2.1199 | 1.3655 | 0.81682 | 0.38489 | 7.0418 | 6.9005 | 6.7016 | 6.1905 | 5.5485 | 3.9087 | 2.2015 | 1.5348 | 1.1542 | 0.72433 | -0.079102 | -0.7388 | -1.3387 | -1.6137
| BURGHEAD | LW |  |  |  | 7.481 | 7.2626 | 6.9708 | 5.6866 | 4.2669 | 1.7343 | -0.96832 | -2.69 | -3.2754 | -3.8894 | -5.0358 | -6.3151 | -6.9968 | -7.3569 | 8.1469 | 8.0423 | 7.8861 | 6.5053 | 4.967 | 2.0386 | -1.0976 | -3.0032 | -3.5948 | -4.216 | -5.3538 | -7.0506 | -7.7648 | -8.1487 | 6.9355 | 6.7413 | 6.4803 | 4.9843 | 3.3252 | 0.2745 | -2.9872 | -5.0203 | -5.6761 | -6.3636 | -7.6359 | -9.3118 | -10.1001 | -10.5185
| BURGHEAD | ST |  |  |  | 7.6789 | 7.5854 | 7.4622 | 6.3689 | 5.5689 | 4.9719 | 3.3648 | 2.7824 | 2.268 | 1.9258 | 1.1568 | -0.058657 | -0.74341 | -1.1301 | 8.2207 | 8.1724 | 8.1064 | 6.8498 | 5.9633 | 5.3375 | 3.4337 | 2.8184 | 2.3005 | 2.0082 | 1.3438 | 0.13797 | -0.54474 | -1.0544 | 7.1095 | 7.0275 | 6.9215 | 5.6127 | 4.6731 | 3.9913 | 2.0367 | 1.3669 | 0.78976 | 0.43466 | -0.36625 | -1.73 | -2.4503 | -2.838
| BURGHEAD | FS |  |  |  | 7.7168 | 7.649 | 7.5542 | 7.2335 | 6.9017 | 6.5304 | 6.1718 | 5.8406 | 5.5596 | 5.3051 | 4.7584 | 3.8404 | 3.134 | 2.9199 | 8.2358 | 8.1984 | 8.1453 | 7.8364 | 7.5189 | 7.1563 | 6.7969 | 6.4716 | 6.2272 | 6.0176 | 5.5646 | 4.937 | 4.2448 | 3.6772 | 7.1427 | 7.0837 | 7.0028 | 6.6516 | 6.2895 | 5.8809 | 5.4791 | 5.1112 | 4.8162 | 4.5565 | 3.9992 | 3.13 | 2.4524 | 2.2583
BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | NO | 1.8671 | 1.2229 | 0.47695 | -0.80199 | -2.3247 | -3.7543 | -5.474 | -7.1518 | -8.5294 | -9.9597 | -13.1525 | -12.5805 | -13.9263 | -14.382 | 4.3496 | 3.9096 | 3.3777 | 2.4929 | 1.4303 | 0.40638 | -0.8252 | -1.9319 | -2.7984 | -3.718 | -5.8253 | -4.5636 | -5.2876 | -6.2655 | 2.6966 | 2.1489 | 1.4802 | 0.35106 | -1.0334 | -2.4224 | -4.1023 | -5.6941 | -6.9819 | -8.3399 | -11.3457 | -10.3798 | -11.594 | -12.0574
| BURGHMUIR | CT |  |  |  | 2.092 | 1.6095 | 1.0305 | -0.09349 | -1.4547 | -2.671 | -3.982 | -5.2115 | -6.5591 | -8.0003 | -11.1892 | -10.8676 | -12.6897 | -13.6508 | 4.4145 | 4.042 | 3.5803 | 2.8316 | 1.9031 | 1.0549 | 0.14544 | -0.60452 | -1.4325 | -2.3352 | -4.4034 | -3.5766 | -4.9016 | -6.2655 | 2.8512 | 2.4293 | 1.8993 | 0.9198 | -0.26866 | -1.4048 | -2.6471 | -3.7574 | -4.9874 | -6.3286 | -9.2726 | -8.6479 | -10.2732 | -11.1429
| BURGHMUIR | LW |  |  |  | 1.8671 | 1.2229 | 0.47695 | -0.80199 | -2.3247 | -3.7543 | -5.474 | -7.1518 | -8.5294 | -9.9597 | -13.1525 | -12.5805 | -13.9263 | -14.382 | 4.3496 | 3.9096 | 3.3777 | 2.4929 | 1.4303 | 0.40638 | -0.8252 | -1.9319 | -2.7984 | -3.718 | -5.8253 | -4.5636 | -5.2876 | -5.6434 | 2.6966 | 2.1489 | 1.4802 | 0.35106 | -1.0334 | -2.4224 | -4.1023 | -5.6941 | -6.9819 | -8.3399 | -11.3457 | -10.3798 | -11.594 | -12.0574
| BURGHMUIR | ST |  |  |  | 2.5945 | 2.2418 | 1.8828 | 1.1875 | 0.34509 | -0.19409 | -1.0215 | -1.6872 | -2.3811 | -3.1445 | -5.1856 | -5.3625 | -6.9454 | -8.6709 | 4.7711 | 4.486 | 4.1845 | 3.5321 | 2.8012 | 2.3676 | 1.614 | 1.0897 | 0.56288 | -0.0099212 | -2.0325 | -1.6717 | -2.985 | -4.6379 | 3.2984 | 2.9942 | 2.6754 | 1.9913 | 1.208 | 0.69714 | -0.15178 | -0.78553 | -1.4361 | -2.1537 | -4.057 | -4.3221 | -5.6578 | -7.0309
| BURGHMUIR | FS |  |  |  | 2.7497 | 2.4858 | 2.2195 | 1.7777 | 1.1769 | 0.772 | 0.29003 | -0.19402 | -0.74298 | -1.3524 | -2.7583 | -4.3918 | -6.8772 | -8.4616 | 4.8911 | 4.6741 | 4.446 | 4.0757 | 3.5808 | 3.2659 | 2.8934 | 2.5234 | 2.1261 | 1.6679 | 0.58529 | -0.64423 | -3.0449 | -5.6735 | 3.4331 | 3.2057 | 2.9692 | 2.5723 | 2.0405 | 1.672 | 1.2363 | 0.79585 | 0.31138 | -0.23239 | -1.4951 | -2.8914 | -5.1105 | -6.4185
CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | NO | 0.099726 | 0.094185 | 0.086121 | 0.081977 | 0.068265 | 0.049906 | 0.028442 | 0.014558 | 0.0058542 | -0.0095621 | -0.03622 | -0.066054 | -0.11703 | -0.16387 | 0.10839 | 0.10573 | 0.1015 | 0.092305 | 0.081376 | 0.068519 | 0.048101 | 0.03863 | 0.022627 | 0.01175 | -0.013356 | -0.059319 | -0.11737 | -0.17535 | 0.10154 | 0.09654 | 0.089182 | 0.084651 | 0.071041 | 0.050252 | 0.026436 | 0.012838 | 0.0025129 | -0.013962 | -0.042884 | -0.085092 | -0.14517 | -0.20166
| BUTTERBRIDGE | CT |  |  |  | 0.10566 | 0.098349 | 0.093611 | 0.084291 | 0.068265 | 0.049906 | 0.028442 | 0.014558 | 0.0058542 | -0.0095621 | -0.03622 | -0.060696 | -0.10059 | -0.12925 | 0.11047 | 0.10709 | 0.1039 | 0.096547 | 0.087063 | 0.068519 | 0.048101 | 0.03863 | 0.026987 | 0.014191 | -0.010754 | -0.044512 | -0.08559 | -0.12611 | 0.10677 | 0.1002 | 0.095757 | 0.086518 | 0.071041 | 0.050252 | 0.026436 | 0.012838 | 0.0025129 | -0.013962 | -0.042884 | -0.074764 | -0.11979 | -0.15571
| BUTTERBRIDGE | LW |  |  |  | 0.099726 | 0.094185 | 0.086121 | 0.081977 | 0.073526 | 0.065138 | 0.05704 | 0.045852 | 0.037144 | 0.024079 | 0.0030459 | -0.0040408 | -0.057462 | -0.13111 | 0.10839 | 0.10573 | 0.1015 | 0.098882 | 0.094529 | 0.090408 | 0.085028 | 0.078234 | 0.068888 | 0.057543 | 0.036725 | 0.032527 | -0.030674 | -0.12122 | 0.10154 | 0.09654 | 0.089182 | 0.08531 | 0.077615 | 0.070021 | 0.062203 | 0.051758 | 0.042585 | 0.029138 | 0.0068291 | -0.0023968 | -0.067622 | -0.15904
| BUTTERBRIDGE | ST |  |  |  | 0.10769 | 0.10296 | 0.10025 | 0.085215 | 0.074733 | 0.069918 | 0.045655 | 0.035183 | 0.019658 | 0.0079414 | -0.019416 | -0.066054 | -0.11703 | -0.16387 | 0.11121 | 0.10915 | 0.1077 | 0.092305 | 0.081376 | 0.074459 | 0.050178 | 0.040984 | 0.022627 | 0.01175 | -0.013356 | -0.059319 | -0.11737 | -0.17535 | 0.10847 | 0.10434 | 0.10188 | 0.084651 | 0.072647 | 0.066356 | 0.038802 | 0.02765 | 0.0091282 | -0.0034267 | -0.033052 | -0.085092 | -0.14517 | -0.20166
| BUTTERBRIDGE | FS |  |  |  | 0.10777 | 0.10344 | 0.10254 | 0.097641 | 0.0944 | 0.086614 | 0.079283 | 0.073517 | 0.066624 | 0.058941 | 0.039899 | 0.007536 | -0.014403 | -0.027351 | 0.11126 | 0.10939 | 0.10861 | 0.10445 | 0.10073 | 0.095 | 0.089314 | 0.084311 | 0.076664 | 0.06983 | 0.054339 | 0.032358 | 0.012745 | -0.0022405 | 0.10855 | 0.10478 | 0.10388 | 0.098698 | 0.094868 | 0.086969 | 0.079463 | 0.073382 | 0.065454 | 0.057306 | 0.037638 | 0.0061372 | -0.015748 | -0.028838
BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 2.9607 | 2.6375 | 2.5332 | 2.387 | 2.0596 | 1.7265 | 1.3606 | 0.97679 | 0.67889 | 0.3549 | -0.30656 | -0.53714 | -1.4143 | -2.082 | 3.6828 | 3.3903 | 3.324 | 3.2258 | 3.0993 | 2.9892 | 2.8159 | 2.6085 | 2.4223 | 2.2178 | 1.7997 | 1.8777 | 1.3577 | 0.89208 | 3.0795 | 2.7534 | 2.6344 | 2.4705 | 2.2776 | 2.0758 | 1.8558 | 1.5907 | 1.3075 | 0.95687 | 0.15797 | 0.21676 | -0.54992 | -1.1362
| CALLANDER | CT |  |  |  | 3.0137 | 2.7387 | 2.6027 | 2.4077 | 2.2038 | 1.884 | 1.5309 | 1.1916 | 0.90335 | 0.602 | -0.0060015 | -0.4122 | -1.4143 | -2.082 | 3.7141 | 3.4563 | 3.349 | 3.2258 | 3.0993 | 2.9892 | 2.8179 | 2.642 | 2.4753 | 2.2951 | 1.9292 | 1.8777 | 1.3577 | 0.89208 | 3.1106 | 2.8469 | 2.7158 | 2.5258 | 2.2919 | 2.0758 | 1.8558 | 1.6516 | 1.4716 | 1.2216 | 0.54959 | 0.2955 | -0.54992 | -1.1362
| CALLANDER | LW |  |  |  | 2.9607 | 2.6375 | 2.5332 | 2.387 | 2.0596 | 1.7265 | 1.3606 | 0.97679 | 0.67889 | 0.3549 | -0.30656 | -0.53714 | -1.3149 | -1.8671 | 3.6828 | 3.3903 | 3.324 | 3.2646 | 3.1727 | 3.0073 | 2.8159 | 2.6085 | 2.4223 | 2.2178 | 1.7997 | 1.9407 | 1.5759 | 1.2817 | 3.0795 | 2.7534 | 2.6344 | 2.4705 | 2.2776 | 2.0872 | 1.8726 | 1.5907 | 1.3075 | 0.95687 | 0.15797 | 0.21676 | -0.43855 | -0.93029
| CALLANDER | ST |  |  |  | 3.0311 | 2.7806 | 2.7201 | 2.6363 | 2.5501 | 2.4538 | 2.3476 | 2.2552 | 2.1452 | 2.0216 | 1.7102 | 1.3099 | 0.60072 | -0.16449 | 3.7188 | 3.477 | 3.4281 | 3.3606 | 3.2955 | 3.2251 | 3.1441 | 3.0829 | 3.003 | 2.9167 | 2.7067 | 2.5219 | 2.0935 | 1.5909 | 3.1173 | 2.8747 | 2.8217 | 2.7474 | 2.6729 | 2.5897 | 2.4791 | 2.3824 | 2.2693 | 2.145 | 1.8561 | 1.5532 | 0.99517 | 0.44291
| CALLANDER | FS |  |  |  | 3.0882 | 2.9032 | 2.859 | 2.7901 | 2.7232 | 2.6532 | 2.58 | 2.5033 | 2.413 | 2.314 | 2.0626 | 1.4115 | 0.70376 | 0.061526 | 3.7758 | 3.5967 | 3.5596 | 3.5073 | 3.458 | 3.411 | 3.3593 | 3.305 | 3.2428 | 3.1746 | 3.0202 | 2.6364 | 2.1029 | 1.5085 | 3.1709 | 2.9912 | 2.9519 | 2.8951 | 2.8394 | 2.7844 | 2.721 | 2.6404 | 2.5422 | 2.4365 | 2.2064 | 1.8117 | 1.0794 | 0.61068
STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | NO | 2.6184 | 2.5434 | 2.45 | 2.3481 | 2.238 | 2.1369 | 2.0109 | 1.8807 | 1.81 | 1.736 | 1.5675 | 1.4557 | 1.3563 | 1.3027 | 2.8509 | 2.841 | 2.8229 | 2.8079 | 2.7537 | 2.6996 | 2.6409 | 2.5699 | 2.5172 | 2.4611 | 2.3302 | 2.266 | 2.1829 | 2.122 | 2.6131 | 2.6022 | 2.5538 | 2.4741 | 2.3868 | 2.3092 | 2.2045 | 2.0931 | 2.0169 | 1.9362 | 1.7683 | 1.6626 | 1.5632 | 1.5103
| CALLANISH | CT |  |  |  | 2.6631 | 2.621 | 2.556 | 2.4173 | 2.2751 | 2.1492 | 2.0253 | 1.8976 | 1.8405 | 1.7665 | 1.6262 | 1.5048 | 1.3563 | 1.3027 | 2.8561 | 2.846 | 2.8275 | 2.8084 | 2.7594 | 2.6996 | 2.6417 | 2.5821 | 2.5404 | 2.4842 | 2.368 | 2.2708 | 2.1829 | 2.122 | 2.6175 | 2.6062 | 2.5847 | 2.5221 | 2.407 | 2.3109 | 2.2162 | 2.1191 | 2.0593 | 1.9769 | 1.823 | 1.7079 | 1.5632 | 1.5103
| CALLANISH | LW |  |  |  | 2.6184 | 2.5434 | 2.45 | 2.3481 | 2.238 | 2.1369 | 2.0109 | 1.8807 | 1.81 | 1.736 | 1.5675 | 1.4557 | 1.3827 | 1.3648 | 2.8509 | 2.841 | 2.8229 | 2.8079 | 2.7537 | 2.7068 | 2.6409 | 2.5699 | 2.5172 | 2.4611 | 2.3302 | 2.266 | 2.2327 | 2.2253 | 2.6131 | 2.6022 | 2.5538 | 2.4741 | 2.3868 | 2.3092 | 2.2045 | 2.0931 | 2.0169 | 1.9362 | 1.7683 | 1.6626 | 1.5905 | 1.5727
| CALLANISH | ST |  |  |  | 2.6762 | 2.6505 | 2.6167 | 2.5728 | 2.5219 | 2.4707 | 2.4138 | 2.3538 | 2.2941 | 2.2215 | 2.0585 | 1.6584 | 1.5158 | 1.4409 | 2.8568 | 2.8516 | 2.8403 | 2.8326 | 2.8244 | 2.8141 | 2.8045 | 2.7889 | 2.7527 | 2.7085 | 2.6079 | 2.3446 | 2.2577 | 2.1933 | 2.6185 | 2.6133 | 2.6008 | 2.5924 | 2.5828 | 2.5593 | 2.5118 | 2.4603 | 2.4065 | 2.341 | 2.1943 | 1.8415 | 1.7152 | 1.6489
| CALLANISH | FS |  |  |  | 2.6921 | 2.6751 | 2.6467 | 2.614 | 2.5738 | 2.5309 | 2.4874 | 2.4414 | 2.3827 | 2.3187 | 2.1866 | 1.7584 | 1.4536 | 1.3896 | 2.8652 | 2.8618 | 2.8524 | 2.8461 | 2.8396 | 2.8327 | 2.8248 | 2.8158 | 2.8054 | 2.7697 | 2.6915 | 2.4499 | 2.2252 | 2.1524 | 2.6248 | 2.6212 | 2.6112 | 2.6044 | 2.597 | 2.5889 | 2.5709 | 2.5312 | 2.4817 | 2.427 | 2.3104 | 1.9261 | 1.6627 | 1.6006
TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | -0.85016 | -0.86385 | -0.88531 | -0.90658 | -0.93354 | -0.96441 | -0.99686 | -1.0264 | -1.0508 | -1.0748 | -1.1365 | -1.0091 | -1.0483 | -1.0893 | 0.15684 | 0.14641 | 0.12978 | 0.1146 | 0.095958 | 0.068974 | 0.040491 | 0.017304 | -0.000807 | -0.025022 | -0.067817 | -0.088944 | -0.13801 | -0.19109 | 0.020667 | -0.00010888 | -0.031673 | -0.06114 | -0.092404 | -0.1264 | -0.17236 | -0.21497 | -0.23875 | -0.27304 | -0.3297 | -0.35727 | -0.43241 | -0.47266
| CALVINE | CT |  |  |  | -0.84301 | -0.85607 | -0.87565 | -0.90658 | -0.93354 | -0.96441 | -0.99686 | -1.0264 | -1.0508 | -1.0748 | -1.125 | -1.0091 | -1.0482 | -1.074 | 0.16402 | 0.15611 | 0.14355 | 0.11972 | 0.095958 | 0.068974 | 0.040491 | 0.017304 | -0.000807 | -0.025022 | -0.067817 | -0.088944 | -0.13762 | -0.17522 | 0.037639 | 0.023219 | 0.0016755 | -0.041386 | -0.08276 | -0.1264 | -0.17236 | -0.21497 | -0.23875 | -0.27304 | -0.3297 | -0.35727 | -0.43241 | -0.47266
| CALVINE | LW |  |  |  | -0.85016 | -0.86385 | -0.88531 | -0.90366 | -0.92388 | -0.94414 | -0.97207 | -1.0053 | -1.0352 | -1.0691 | -1.1365 | -0.97862 | -1.0202 | -1.0693 | 0.15684 | 0.14641 | 0.12978 | 0.1146 | 0.0981 | 0.082788 | 0.062553 | 0.038284 | 0.018685 | -0.0037479 | -0.046308 | -0.046175 | -0.095021 | -0.15466 | 0.020667 | -0.00010888 | -0.031673 | -0.06114 | -0.092404 | -0.12202 | -0.15709 | -0.19935 | -0.22582 | -0.25736 | -0.31595 | -0.32634 | -0.39011 | -0.45747
| CALVINE | ST |  |  |  | -0.83902 | -0.84575 | -0.85305 | -0.86825 | -0.88424 | -0.89947 | -0.92393 | -0.94224 | -0.9694 | -0.9948 | -1.0539 | -0.99814 | -1.0483 | -1.0893 | 0.16745 | 0.16234 | 0.15661 | 0.14175 | 0.12711 | 0.11439 | 0.091919 | 0.078391 | 0.05526 | 0.036329 | -0.0051263 | -0.075967 | -0.13801 | -0.19109 | 0.045634 | 0.035501 | 0.024595 | 0.0036251 | -0.019157 | -0.039241 | -0.069449 | -0.089087 | -0.12192 | -0.15074 | -0.21072 | -0.31713 | -0.40562 | -0.47208
| CALVINE | FS |  |  |  | -0.83624 | -0.84179 | -0.84675 | -0.85545 | -0.86683 | -0.87667 | -0.88951 | -0.90159 | -0.91914 | -0.9367 | -0.97488 | -0.96156 | -0.98989 | -1.006 | 0.17019 | 0.16542 | 0.16198 | 0.15459 | 0.14445 | 0.13653 | 0.12595 | 0.11682 | 0.10148 | 0.087418 | 0.057459 | -0.012031 | -0.068262 | -0.09518 | 0.051993 | 0.042421 | 0.036598 | 0.024029 | 0.0057051 | -0.0066241 | -0.024553 | -0.038548 | -0.064051 | -0.086946 | -0.13395 | -0.26167 | -0.34571 | -0.38066
CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 7.0996 | 6.9204 | 6.7135 | 6.4251 | 6.1446 | 5.8209 | 5.4324 | 5.1142 | 4.8065 | 4.4643 | 3.8111 | 3.4505 | 2.5181 | 1.607 | 8.9939 | 8.907 | 8.7964 | 8.662 | 8.4774 | 8.2201 | 7.9483 | 7.7714 | 7.5429 | 7.2844 | 6.7908 | 6.3613 | 5.5499 | 4.5113 | 7.5953 | 7.438 | 7.2611 | 6.9868 | 6.7182 | 6.3814 | 5.973 | 5.6547 | 5.3654 | 5.0599 | 4.4766 | 4.077 | 3.0065 | 1.8641
| CAMPBELTOWN | CT |  |  |  | 7.1923 | 7.0678 | 6.9053 | 6.5533 | 6.1934 | 5.8209 | 5.4324 | 5.1142 | 4.8065 | 4.4643 | 3.8111 | 3.4505 | 2.5181 | 1.8067 | 9.0257 | 8.9589 | 8.8665 | 8.6791 | 8.4774 | 8.2201 | 7.9483 | 7.7714 | 7.5429 | 7.2844 | 6.7908 | 6.3613 | 5.5499 | 4.685 | 7.6916 | 7.586 | 7.4468 | 7.1147 | 6.7737 | 6.3814 | 5.973 | 5.6547 | 5.3654 | 5.0599 | 4.4766 | 4.077 | 3.0065 | 2.176
| CAMPBELTOWN | LW |  |  |  | 7.0996 | 6.9204 | 6.7135 | 6.4251 | 6.1446 | 5.8956 | 5.5714 | 5.2181 | 4.9023 | 4.5596 | 3.8898 | 3.868 | 2.7997 | 1.607 | 8.9939 | 8.907 | 8.7964 | 8.662 | 8.5278 | 8.4111 | 8.2405 | 8.0483 | 7.8198 | 7.573 | 7.0963 | 7.0274 | 5.9466 | 4.5113 | 7.5953 | 7.438 | 7.2611 | 6.9868 | 6.7182 | 6.4731 | 6.1733 | 5.8526 | 5.5799 | 5.2842 | 4.7092 | 4.6269 | 3.3447 | 1.8641
| CAMPBELTOWN | ST |  |  |  | 7.2648 | 7.1942 | 7.1286 | 6.9613 | 6.8316 | 6.7198 | 6.499 | 6.3605 | 6.084 | 5.8878 | 5.4256 | 4.7799 | 3.8453 | 2.7657 | 9.0542 | 9.0157 | 8.9778 | 8.8195 | 8.6986 | 8.6009 | 8.3707 | 8.2538 | 7.9814 | 7.8145 | 7.4248 | 6.7418 | 5.7355 | 4.5768 | 7.7753 | 7.7251 | 7.6788 | 7.5097 | 7.3843 | 7.2795 | 7.0461 | 6.9232 | 6.6376 | 6.4546 | 5.9718 | 5.2574 | 4.2017 | 3.0127
| CAMPBELTOWN | FS |  |  |  | 7.2735 | 7.2103 | 7.15 | 7.047 | 6.9475 | 6.8528 | 6.7515 | 6.6434 | 6.4808 | 6.3256 | 5.989 | 5.4393 | 4.7892 | 4.3925 | 9.0589 | 9.0239 | 8.9889 | 8.9195 | 8.8504 | 8.7799 | 8.7035 | 8.6236 | 8.4856 | 8.3606 | 8.0851 | 7.6496 | 7.0231 | 6.3642 | 7.7785 | 7.7354 | 7.6926 | 7.6043 | 7.5152 | 7.4282 | 7.3369 | 7.2415 | 7.0838 | 6.9402 | 6.6351 | 6.1339 | 5.5099 | 5.1345
COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | NO | 6.5793 | 6.3641 | 6.1124 | 5.7623 | 5.3974 | 4.9839 | 4.4812 | 4.0437 | 3.7905 | 3.5243 | 2.6788 | 2.7189 | 1.9852 | 1.5379 | 8.7283 | 8.6605 | 8.5645 | 8.4009 | 8.2288 | 7.9424 | 7.5909 | 7.4015 | 7.2079 | 6.987 | 6.311 | 6.2336 | 5.7338 | 5.207 | 7.0191 | 6.8187 | 6.5674 | 6.2245 | 5.8596 | 5.4422 | 4.9135 | 4.4437 | 4.1284 | 3.7934 | 2.9514 | 2.9346 | 2.1957 | 1.6348
| CAPUTH | CT |  |  |  | 6.7453 | 6.6013 | 6.42 | 6.0235 | 5.6165 | 5.1268 | 4.5845 | 4.1784 | 3.9248 | 3.66 | 2.9122 | 2.72 | 1.9852 | 1.5526 | 8.7522 | 8.6805 | 8.568 | 8.4009 | 8.2288 | 7.9424 | 7.5909 | 7.4015 | 7.2079 | 7.0286 | 6.4044 | 6.2336 | 5.7338 | 5.2672 | 7.161 | 7.025 | 6.8426 | 6.4511 | 6.0374 | 5.5384 | 4.9899 | 4.596 | 4.3009 | 3.9685 | 3.1361 | 2.9346 | 2.1957 | 1.7377
| CAPUTH | LW |  |  |  | 6.5793 | 6.3641 | 6.1124 | 5.7623 | 5.3974 | 4.9839 | 4.4812 | 4.0437 | 3.7905 | 3.5243 | 2.6788 | 2.7189 | 2.1167 | 1.5379 | 8.7283 | 8.6605 | 8.5645 | 8.4207 | 8.2612 | 8.0412 | 7.7164 | 7.4738 | 7.2485 | 6.987 | 6.311 | 6.4252 | 5.9081 | 5.2817 | 7.0191 | 6.8187 | 6.5674 | 6.2245 | 5.8596 | 5.4422 | 4.9135 | 4.4437 | 4.1284 | 3.7934 | 2.9514 | 2.9831 | 2.3216 | 1.6348
| CAPUTH | ST |  |  |  | 6.854 | 6.7742 | 6.693 | 6.4665 | 6.2728 | 6.0919 | 5.7434 | 5.5474 | 5.2958 | 5.0803 | 4.3933 | 3.6814 | 2.9055 | 2.2215 | 8.7801 | 8.7489 | 8.7129 | 8.5238 | 8.3723 | 8.2416 | 7.8968 | 7.7428 | 7.5308 | 7.3604 | 6.7143 | 6.442 | 5.8199 | 5.207 | 7.2521 | 7.1767 | 7.0966 | 6.8451 | 6.6306 | 6.4353 | 6.0426 | 5.8237 | 5.5408 | 5.2992 | 4.575 | 3.7961 | 2.9991 | 2.276
| CAPUTH | FS |  |  |  | 6.8804 | 6.8435 | 6.7851 | 6.659 | 6.5319 | 6.3918 | 6.2283 | 6.0781 | 5.893 | 5.7138 | 5.1831 | 4.3138 | 3.4669 | 3.0794 | 8.7947 | 8.7724 | 8.7461 | 8.6793 | 8.6081 | 8.526 | 8.4096 | 8.3168 | 8.2049 | 8.0958 | 7.6855 | 7.3434 | 6.7105 | 6.3144 | 7.2875 | 7.2357 | 7.1761 | 7.0481 | 6.9151 | 6.7688 | 6.5991 | 6.4384 | 6.2421 | 6.0497 | 5.5056 | 4.5582 | 3.7725 | 3.4
ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | NO | 4.3227 | 3.6889 | 2.9631 | 1.8783 | 0.63315 | -0.31162 | -1.3271 | -2.124 | -2.7836 | -3.4642 | -4.8119 | -5.8443 | -7.2871 | -8.0815 | 6.6179 | 6.1752 | 5.6662 | 5.0256 | 4.2204 | 3.6501 | 3.0109 | 2.5642 | 2.153 | 1.7189 | 0.86297 | 0.13128 | -0.94548 | -2.154 | 5.6569 | 5.11 | 4.4596 | 3.5395 | 2.4643 | 1.6469 | 0.71906 | -0.040979 | -0.71565 | -1.421 | -2.8145 | -3.5304 | -4.7176 | -5.3982
| CARNOUSTIE | CT |  |  |  | 4.732 | 4.2372 | 3.6528 | 2.6308 | 1.5519 | 0.62777 | -0.25236 | -0.88923 | -1.6403 | -2.4268 | -3.9551 | -5.8443 | -7.2871 | -8.0815 | 6.838 | 6.4421 | 5.9766 | 5.3174 | 4.5851 | 3.9524 | 3.3649 | 3.0136 | 2.5768 | 2.0928 | 1.1407 | 0.13128 | -0.94548 | -2.154 | 5.9893 | 5.5543 | 5.0283 | 4.123 | 3.1513 | 2.3264 | 1.5374 | 0.96884 | 0.26674 | -0.50368 | -2.0021 | -3.5304 | -4.7176 | -5.3982
| CARNOUSTIE | LW |  |  |  | 4.3227 | 3.6889 | 2.9631 | 1.8783 | 0.63315 | -0.31162 | -1.3271 | -2.124 | -2.7836 | -3.4642 | -4.8119 | -5.6326 | -6.4194 | -6.771 | 6.6179 | 6.1752 | 5.6662 | 5.0256 | 4.2204 | 3.6501 | 3.0109 | 2.5642 | 2.153 | 1.7189 | 0.86297 | 0.761 | 0.33986 | 0.022559 | 5.6569 | 5.11 | 4.4596 | 3.5395 | 2.4643 | 1.6469 | 0.71906 | -0.040979 | -0.71565 | -1.421 | -2.8145 | -3.3082 | -3.998 | -4.37
| CARNOUSTIE | ST |  |  |  | 4.7938 | 4.368 | 3.8742 | 3.3438 | 2.768 | 2.2898 | 1.8215 | 1.5959 | 1.3451 | 1.1098 | 0.58431 | -0.81035 | -2.1686 | -3.7904 | 6.8613 | 6.5077 | 6.1091 | 5.668 | 5.1693 | 4.7362 | 4.3015 | 4.0987 | 3.8602 | 3.6356 | 3.1156 | 1.9247 | 0.79951 | -0.70985 | 6.0376 | 5.6706 | 5.2456 | 4.7716 | 4.2484 | 3.8008 | 3.3414 | 3.0958 | 2.8088 | 2.5288 | 1.8855 | 0.40096 | -0.78357 | -2.0985
| CARNOUSTIE | FS |  |  |  | 5.2494 | 4.9173 | 4.5112 | 4.068 | 3.6025 | 3.1886 | 2.7854 | 2.5178 | 2.1758 | 1.8032 | 1.0732 | -0.62849 | -2.4145 | -3.8112 | 7.2604 | 6.9823 | 6.646 | 6.2916 | 5.9 | 5.5373 | 5.1794 | 4.9401 | 4.6536 | 4.3316 | 3.6824 | 2.1925 | 0.28602 | -2.0197 | 6.4286 | 6.1431 | 5.794 | 5.4099 | 4.9956 | 4.6174 | 4.2429 | 3.9793 | 3.6479 | 3.284 | 2.5497 | 0.89904 | -0.82002 | -1.9088
KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | NO | 0.82293 | 0.81131 | 0.79316 | 0.77692 | 0.76027 | 0.7458 | 0.7249 | 0.70366 | 0.69237 | 0.67834 | 0.65114 | 0.65326 | 0.62632 | 0.61675 | 0.88769 | 0.88277 | 0.8748 | 0.86774 | 0.85868 | 0.8504 | 0.84017 | 0.83206 | 0.82468 | 0.81597 | 0.79787 | 0.80552 | 0.79479 | 0.78974 | 0.8559 | 0.84577 | 0.82986 | 0.81565 | 0.80092 | 0.78814 | 0.7684 | 0.75013 | 0.73894 | 0.7253 | 0.69865 | 0.70119 | 0.67865 | 0.67025
| CASHLIE | CT |  |  |  | 0.83265 | 0.82337 | 0.81296 | 0.78962 | 0.76598 | 0.74809 | 0.7249 | 0.70831 | 0.6952 | 0.68257 | 0.65944 | 0.66472 | 0.62632 | 0.61675 | 0.89119 | 0.88709 | 0.88125 | 0.87016 | 0.85868 | 0.8504 | 0.84017 | 0.83206 | 0.82468 | 0.81666 | 0.80159 | 0.80933 | 0.79479 | 0.78974 | 0.86411 | 0.85598 | 0.84641 | 0.82566 | 0.80447 | 0.78865 | 0.7684 | 0.75357 | 0.74133 | 0.72897 | 0.70621 | 0.71115 | 0.67865 | 0.67025
| CASHLIE | LW |  |  |  | 0.82293 | 0.81131 | 0.79316 | 0.77692 | 0.76027 | 0.7458 | 0.72734 | 0.70366 | 0.69237 | 0.67834 | 0.65114 | 0.65326 | 0.63525 | 0.62714 | 0.88769 | 0.88277 | 0.8748 | 0.86774 | 0.86021 | 0.85363 | 0.84443 | 0.83284 | 0.82508 | 0.81597 | 0.79787 | 0.80552 | 0.7991 | 0.79623 | 0.8559 | 0.84577 | 0.82986 | 0.81565 | 0.80092 | 0.78814 | 0.77145 | 0.75013 | 0.73894 | 0.7253 | 0.69865 | 0.70119 | 0.686 | 0.6792
| CASHLIE | ST |  |  |  | 0.83871 | 0.83219 | 0.82514 | 0.81653 | 0.80869 | 0.79907 | 0.78923 | 0.77808 | 0.76734 | 0.75346 | 0.72894 | 0.69015 | 0.65379 | 0.63024 | 0.89333 | 0.89067 | 0.88768 | 0.88398 | 0.8803 | 0.87586 | 0.8711 | 0.86558 | 0.85983 | 0.8525 | 0.83779 | 0.81928 | 0.80475 | 0.79542 | 0.86912 | 0.86353 | 0.85738 | 0.84989 | 0.8429 | 0.83435 | 0.82556 | 0.81551 | 0.80564 | 0.79291 | 0.7697 | 0.733 | 0.70161 | 0.68184
| CASHLIE | FS |  |  |  | 0.84035 | 0.83789 | 0.83138 | 0.82628 | 0.81582 | 0.81033 | 0.8065 | 0.79503 | 0.78691 | 0.77464 | 0.75064 | 0.68775 | 0.64062 | 0.62196 | 0.89397 | 0.89281 | 0.89014 | 0.88783 | 0.88351 | 0.88085 | 0.87863 | 0.87357 | 0.86949 | 0.86372 | 0.85175 | 0.82434 | 0.80015 | 0.79189 | 0.87053 | 0.86836 | 0.86275 | 0.85822 | 0.84919 | 0.84424 | 0.84061 | 0.83054 | 0.82319 | 0.81224 | 0.79055 | 0.7341 | 0.69078 | 0.6751
KILLIN | CHAORACH | MINIMUM HEADROOM | NN 4540027553 | YES | NO | 0.72035 | 0.71794 | 0.70925 | 0.71015 | 0.70388 | 0.70117 | 0.6958 | 0.69094 | 0.68947 | 0.68575 | 0.68182 | 0.68185 | 0.67552 | 0.67497 | 0.8072 | 0.80613 | 0.80262 | 0.80254 | 0.79989 | 0.79856 | 0.79593 | 0.79375 | 0.79202 | 0.78946 | 0.78622 | 0.7871 | 0.78483 | 0.78447 | 0.75679 | 0.75468 | 0.74723 | 0.74778 | 0.74234 | 0.73992 | 0.73512 | 0.73086 | 0.72932 | 0.72558 | 0.72153 | 0.72078 | 0.71546 | 0.71488
| CHAORACH | CT |  |  |  | 0.72232 | 0.72182 | 0.71327 | 0.71204 | 0.70701 | 0.70229 | 0.69797 | 0.69094 | 0.68947 | 0.68575 | 0.68182 | 0.68556 | 0.67552 | 0.67497 | 0.80792 | 0.80751 | 0.80413 | 0.80308 | 0.80071 | 0.79864 | 0.79668 | 0.79375 | 0.79249 | 0.79023 | 0.78693 | 0.78856 | 0.78483 | 0.78447 | 0.75846 | 0.75795 | 0.75066 | 0.74937 | 0.74487 | 0.74076 | 0.73696 | 0.73086 | 0.72932 | 0.72573 | 0.72153 | 0.72397 | 0.71546 | 0.71488
| CHAORACH | LW |  |  |  | 0.72035 | 0.71794 | 0.70925 | 0.71015 | 0.70388 | 0.70117 | 0.6958 | 0.69403 | 0.69007 | 0.68592 | 0.68293 | 0.68185 | 0.6759 | 0.6759 | 0.8072 | 0.80613 | 0.80262 | 0.80254 | 0.79989 | 0.79856 | 0.79593 | 0.79443 | 0.79202 | 0.78946 | 0.78622 | 0.7871 | 0.78494 | 0.78494 | 0.75679 | 0.75468 | 0.74723 | 0.74778 | 0.74234 | 0.73992 | 0.73512 | 0.73327 | 0.72952 | 0.72558 | 0.72209 | 0.72078 | 0.71577 | 0.71577
| CHAORACH | ST |  |  |  | 0.72236 | 0.72216 | 0.71996 | 0.71572 | 0.71345 | 0.71289 | 0.70832 | 0.70747 | 0.70642 | 0.70362 | 0.69599 | 0.69115 | 0.68428 | 0.68174 | 0.80794 | 0.80778 | 0.80688 | 0.80521 | 0.80415 | 0.80369 | 0.80174 | 0.80103 | 0.80014 | 0.79852 | 0.79426 | 0.79091 | 0.78804 | 0.7871 | 0.75848 | 0.75828 | 0.75639 | 0.75277 | 0.75072 | 0.75015 | 0.74619 | 0.74531 | 0.74421 | 0.74161 | 0.73452 | 0.72882 | 0.7228 | 0.72058
| CHAORACH | FS |  |  |  | 0.72432 | 0.72222 | 0.722 | 0.71784 | 0.71719 | 0.71485 | 0.71438 | 0.71187 | 0.70775 | 0.70695 | 0.70282 | 0.69137 | 0.68222 | 0.67844 | 0.80864 | 0.80782 | 0.80764 | 0.80604 | 0.80562 | 0.8046 | 0.80419 | 0.80303 | 0.80124 | 0.80057 | 0.79814 | 0.79255 | 0.78734 | 0.78597 | 0.76012 | 0.75834 | 0.75811 | 0.75458 | 0.75391 | 0.75188 | 0.75138 | 0.74916 | 0.74557 | 0.74474 | 0.74083 | 0.7299 | 0.72112 | 0.7179
ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | NO | 4.2128 | 3.991 | 3.6927 | 3.025 | 2.3247 | 1.5852 | 0.5961 | -0.52265 | -1.4789 | -2.3532 | -3.8284 | -3.9602 | -5.0189 | -5.7381 | 5.5601 | 5.4395 | 5.251 | 4.9008 | 4.5206 | 4.0812 | 3.4183 | 2.6589 | 1.9791 | 1.3429 | 0.37415 | 0.80303 | -0.26019 | -1.9227 | 5.285 | 5.0783 | 4.7872 | 4.1729 | 3.5216 | 2.8176 | 1.8573 | 0.78454 | -0.14023 | -0.99364 | -2.4492 | -2.3214 | -3.0723 | -3.6863
| CHARLES AVENUE | CT |  |  |  | 4.4521 | 4.3511 | 4.1986 | 3.6008 | 2.9789 | 2.3728 | 1.6287 | 0.82514 | -0.12428 | -1.0413 | -2.5643 | -3.5905 | -5.0189 | -5.7381 | 5.6387 | 5.5554 | 5.425 | 5.0893 | 4.7282 | 4.363 | 3.8744 | 3.3461 | 2.7127 | 2.0693 | 1.1067 | 0.80303 | -0.26019 | -1.4715 | 5.4868 | 5.3835 | 5.2241 | 4.6679 | 4.0826 | 3.5102 | 2.8069 | 2.0636 | 1.1791 | 0.31285 | -1.1349 | -1.8613 | -3.0723 | -3.6863
| CHARLES AVENUE | LW |  |  |  | 4.2128 | 3.991 | 3.6927 | 3.025 | 2.3247 | 1.5852 | 0.5961 | -0.52265 | -1.4789 | -2.3532 | -3.8284 | -3.9602 | -4.6143 | -4.7437 | 5.5601 | 5.4395 | 5.251 | 4.9008 | 4.5206 | 4.0812 | 3.4183 | 2.6589 | 1.9791 | 1.3429 | 0.37415 | 0.85338 | 0.59642 | 0.54511 | 5.285 | 5.0783 | 4.7872 | 4.1729 | 3.5216 | 2.8176 | 1.8573 | 0.78454 | -0.14023 | -0.99364 | -2.4492 | -2.3214 | -2.8793 | -2.987
| CHARLES AVENUE | ST |  |  |  | 4.5519 | 4.5398 | 4.5106 | 4.42 | 4.3201 | 4.2194 | 3.9232 | 3.5465 | 3.1069 | 2.7074 | 2.1091 | 1.709 | 0.56725 | -0.95046 | 5.6776 | 5.6472 | 5.6025 | 5.4755 | 5.3489 | 5.2237 | 4.9008 | 4.5272 | 4.1087 | 3.6902 | 3.0855 | 2.647 | 1.6442 | 0.16767 | 5.5711 | 5.5516 | 5.5144 | 5.3989 | 5.2775 | 5.157 | 4.8317 | 4.4475 | 4.009 | 3.6018 | 2.9548 | 2.5585 | 1.5605 | 0.2864
| CHARLES AVENUE | FS |  |  |  | 4.5345 | 4.5171 | 4.4872 | 4.4084 | 4.3135 | 4.2102 | 4.0244 | 3.7221 | 3.3268 | 2.999 | 2.4529 | 1.6044 | -0.063378 | -1.4687 | 5.6729 | 5.6425 | 5.6007 | 5.5196 | 5.4231 | 5.3154 | 5.1325 | 4.84 | 4.4887 | 4.1712 | 3.6408 | 2.7156 | 0.72094 | -1.9227 | 5.5577 | 5.5356 | 5.5004 | 5.4165 | 5.3153 | 5.2046 | 5.015 | 4.7149 | 4.3351 | 4.0151 | 3.4646 | 2.6742 | 1.1179 | -0.062864
CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | NO | 8.2733 | 8.1987 | 8.0527 | 7.8378 | 7.5964 | 7.2554 | 6.8124 | 6.4025 | 6.0599 | 5.5714 | 4.4608 | 5.879 | 5.3965 | 4.829 | 2.6786 | 2.6102 | 2.4965 | 2.3506 | 2.1937 | 1.9437 | 1.6086 | 1.3199 | 1.0205 | 0.60397 | -0.38047 | 1.2272 | 0.68534 | -0.020853 | 4.356 | 4.2768 | 4.1499 | 3.8945 | 3.6066 | 3.2419 | 2.7894 | 2.3873 | 2.0764 | 1.7354 | 0.78533 | 1.8511 | 1.2781 | 0.57152
| CHARLESTON | CT |  |  |  | 8.3079 | 8.2254 | 8.0527 | 7.8378 | 7.6153 | 7.3533 | 7.0085 | 6.7281 | 6.3824 | 6.042 | 5.2383 | 6.2748 | 5.8498 | 5.5291 | 2.6786 | 2.6102 | 2.4965 | 2.3506 | 2.1937 | 1.9744 | 1.7199 | 1.5512 | 1.3087 | 1.0322 | 0.34297 | 1.4855 | 0.93683 | 0.22756 | 4.4015 | 4.3213 | 4.154 | 3.9435 | 3.7233 | 3.4229 | 3.0818 | 2.831 | 2.5785 | 2.3117 | 1.5929 | 2.3466 | 1.9071 | 1.5455
| CHARLESTON | LW |  |  |  | 8.2733 | 8.1987 | 8.0756 | 7.851 | 7.5964 | 7.2554 | 6.8124 | 6.4025 | 6.0599 | 5.5714 | 4.4608 | 5.879 | 5.3965 | 4.829 | 2.6812 | 2.6297 | 2.5337 | 2.3824 | 2.2026 | 1.9437 | 1.6086 | 1.3199 | 1.0205 | 0.60397 | -0.38047 | 1.2272 | 0.68534 | -0.020853 | 4.356 | 4.2768 | 4.1499 | 3.8945 | 3.6066 | 3.2419 | 2.7894 | 2.3873 | 2.0764 | 1.7354 | 0.78533 | 1.8511 | 1.2781 | 0.57152
| CHARLESTON | ST |  |  |  | 8.3436 | 8.2994 | 8.2439 | 8.0988 | 7.955 | 7.8062 | 7.5472 | 7.3328 | 7.0577 | 6.6964 | 5.6611 | 7.2739 | 6.788 | 6.1988 | 2.6884 | 2.6567 | 2.6174 | 2.4766 | 2.3501 | 2.2319 | 1.9943 | 1.8343 | 1.6228 | 1.4165 | 0.59138 | 1.4933 | 1 | 0.15082 | 4.4358 | 4.3928 | 4.3388 | 4.1777 | 4.0243 | 3.8712 | 3.5891 | 3.3728 | 3.0923 | 2.8001 | 1.9403 | 3.2092 | 2.6304 | 1.9871
| CHARLESTON | FS |  |  |  | 8.3565 | 8.3322 | 8.2915 | 8.2276 | 8.1529 | 8.0631 | 7.9578 | 7.8375 | 7.6958 | 7.5382 | 7.0568 | 7.6789 | 7.2411 | 6.8798 | 2.709 | 2.6832 | 2.6527 | 2.5985 | 2.5368 | 2.4634 | 2.3794 | 2.2866 | 2.1767 | 2.0591 | 1.6884 | 2.0416 | 1.4478 | 0.37951 | 4.4483 | 4.426 | 4.3863 | 4.3202 | 4.2435 | 4.1515 | 4.0446 | 3.9239 | 3.7816 | 3.6257 | 3.1746 | 3.6831 | 3.2918 | 2.9595
ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | NO | 1.0678 | 1.0206 | 0.92672 | 0.84222 | 0.73952 | -1.3979 | -3.4991 | -5.2454 | -6.953 | -9.0979 | -14.3329 | -17.1624 | -17.333 | -17.4112 | 1.6902 | 1.6598 | 1.5942 | 1.5477 | 1.4775 | -1.2114 | -4.3779 | -6.952 | -9.5303 | -12.6115 | -19.3692 | -23.1623 | -23.3633 | -23.4742 | 1.1041 | 1.0588 | 0.97794 | 0.88632 | 0.79 | -1.6629 | -4.3572 | -6.5753 | -8.8168 | -11.4986 | -17.3599 | -20.656 | -20.9074 | -21.0207
| CLACHAN | CT |  |  |  | 1.0962 | 1.0615 | 0.98622 | 0.86752 | 0.73952 | -1.3979 | -3.4369 | -5.0149 | -6.7023 | -9.0979 | -14.3329 | -17.1624 | -17.333 | -17.4112 | 1.7072 | 1.6827 | 1.6211 | 1.5511 | 1.4775 | -1.2114 | -4.2561 | -6.5889 | -9.1636 | -12.6115 | -19.3692 | -23.1623 | -23.3633 | -23.4721 | 1.1269 | 1.0764 | 0.98499 | 0.88632 | 0.79 | -1.6629 | -4.2612 | -6.2734 | -8.5041 | -11.4986 | -17.3599 | -20.656 | -20.9074 | -21.0207
| CLACHAN | LW |  |  |  | 1.0678 | 1.0206 | 0.92672 | 0.84222 | 0.7546 | -1.3592 | -3.4991 | -5.2454 | -6.953 | -9.0621 | -14.06 | -16.7882 | -17.2864 | -17.3759 | 1.6902 | 1.6598 | 1.5942 | 1.5477 | 1.4987 | -1.1709 | -4.3779 | -6.952 | -9.5303 | -12.5891 | -19.0259 | -22.6657 | -23.3029 | -23.4141 | 1.1041 | 1.0588 | 0.97794 | 0.91595 | 0.85238 | -1.6254 | -4.3572 | -6.5753 | -8.8168 | -11.479 | -17.067 | -20.2586 | -20.8455 | -20.9569
| CLACHAN | ST |  |  |  | 1.1102 | 1.091 | 1.0475 | 1.0162 | 0.9781 | -1.0961 | -3.0694 | -4.5952 | -6.2794 | -8.8968 | -14.1544 | -17.1076 | -17.266 | -17.3453 | 1.7131 | 1.699 | 1.6603 | 1.6376 | 1.6111 | -1.1336 | -4.17 | -6.4958 | -9.0622 | -12.508 | -19.2711 | -23.1548 | -23.3603 | -23.4666 | 1.1396 | 1.1173 | 1.07 | 1.0368 | 0.99814 | -1.3839 | -3.9234 | -5.8979 | -8.1339 | -11.1316 | -17.0192 | -20.5142 | -20.7465 | -20.8745
| CLACHAN | FS |  |  |  | 1.1298 | 1.1183 | 1.082 | 1.0545 | 1.0242 | -0.47934 | -1.7364 | -3.0459 | -4.4671 | -5.9569 | -9.686 | -14.1339 | -17.0026 | -17.3808 | 1.7299 | 1.7207 | 1.6889 | 1.6696 | 1.6484 | -0.21172 | -2.1329 | -4.1354 | -6.2991 | -8.5606 | -13.5359 | -19.2962 | -22.9808 | -23.4742 | 1.1603 | 1.1466 | 1.1093 | 1.0812 | 1.051 | -0.59999 | -2.2142 | -3.896 | -5.7283 | -7.7052 | -12.0421 | -17.2009 | -20.4857 | -20.9351
CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0.2109 | 0.2059 | 0.198 | 0.18616 | 0.17973 | 0.16001 | 0.14058 | 0.12963 | 0.11628 | 0.10123 | 0.076495 | 0.040843 | -0.00092955 | -0.046713 | 0.2572 | 0.25476 | 0.25065 | 0.2436 | 0.23441 | 0.22015 | 0.20208 | 0.19434 | 0.18072 | 0.17044 | 0.14701 | 0.1003 | 0.047897 | -0.0053457 | 0.22377 | 0.21919 | 0.21196 | 0.20132 | 0.19431 | 0.17251 | 0.15108 | 0.14015 | 0.12612 | 0.11038 | 0.0834 | 0.040973 | -0.011603 | -0.067803
| CLAONAIG | CT |  |  |  | 0.21317 | 0.21014 | 0.2061 | 0.19018 | 0.18017 | 0.16001 | 0.14058 | 0.12963 | 0.11628 | 0.10123 | 0.076495 | 0.040843 | -0.00092955 | -0.033271 | 0.25807 | 0.2563 | 0.25376 | 0.24515 | 0.23781 | 0.22015 | 0.20208 | 0.19434 | 0.18309 | 0.17044 | 0.14701 | 0.10818 | 0.069867 | 0.031782 | 0.22584 | 0.22297 | 0.21916 | 0.20433 | 0.19431 | 0.17251 | 0.15108 | 0.14015 | 0.12612 | 0.11038 | 0.0834 | 0.040973 | -0.0038211 | -0.041522
| CLAONAIG | LW |  |  |  | 0.2109 | 0.2059 | 0.198 | 0.18616 | 0.17973 | 0.17207 | 0.16209 | 0.14768 | 0.136 | 0.12897 | 0.11014 | 0.08997 | 0.038386 | -0.028834 | 0.2572 | 0.25476 | 0.25065 | 0.24531 | 0.24176 | 0.23798 | 0.23238 | 0.2248 | 0.21618 | 0.20866 | 0.19205 | 0.17539 | 0.11822 | 0.037831 | 0.22377 | 0.21919 | 0.21196 | 0.20132 | 0.19537 | 0.18841 | 0.17915 | 0.16592 | 0.15427 | 0.14663 | 0.12639 | 0.10395 | 0.042824 | -0.039484
| CLAONAIG | ST |  |  |  | 0.21856 | 0.21276 | 0.2136 | 0.19959 | 0.19156 | 0.18026 | 0.16075 | 0.15404 | 0.13668 | 0.12512 | 0.10448 | 0.051123 | 0.0019441 | -0.046713 | 0.26013 | 0.25757 | 0.25746 | 0.2436 | 0.23441 | 0.2258 | 0.2051 | 0.19796 | 0.18072 | 0.17138 | 0.15179 | 0.1003 | 0.047897 | -0.0053457 | 0.23073 | 0.22532 | 0.22597 | 0.21011 | 0.20057 | 0.18894 | 0.1663 | 0.15866 | 0.1391 | 0.12713 | 0.10452 | 0.045119 | -0.011603 | -0.067803
| CLAONAIG | FS |  |  |  | 0.21999 | 0.21661 | 0.21227 | 0.2126 | 0.20405 | 0.20035 | 0.18974 | 0.18431 | 0.1796 | 0.16905 | 0.15416 | 0.11343 | 0.083844 | 0.073225 | 0.26084 | 0.25902 | 0.25704 | 0.25506 | 0.24968 | 0.24576 | 0.23918 | 0.23466 | 0.22851 | 0.22115 | 0.20826 | 0.18208 | 0.15947 | 0.14686 | 0.2321 | 0.22871 | 0.22484 | 0.22432 | 0.216 | 0.21179 | 0.20151 | 0.19585 | 0.19004 | 0.17954 | 0.16387 | 0.1242 | 0.094859 | 0.084023
CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 9.4758 | 9.0884 | 8.4791 | 7.3861 | 6.1878 | 4.8104 | 2.9089 | 0.87512 | -0.89177 | -2.8323 | -6.7918 | 2.0191 | 0.88769 | -0.057433 | 14.5084 | 14.2699 | 13.8796 | 13.2516 | 12.5287 | 11.6378 | 10.3601 | 8.8634 | 7.512 | 6.0207 | 2.9854 | 8.4413 | 4.8453 | -3.6833 | 12.9555 | 12.5071 | 11.7788 | 10.699 | 9.499 | 8.111 | 6.2048 | 4.1991 | 2.457 | 0.54179 | -3.3601 | 5.6151 | 4.7399 | 3.8604
| CLAYHILLS | CT |  |  |  | 9.678 | 9.4413 | 9.0842 | 7.964 | 6.6904 | 5.4982 | 4.2183 | 3.0324 | 1.7969 | 0.57023 | -2.1544 | 2.5318 | 0.88769 | -0.057433 | 14.5279 | 14.2719 | 13.9342 | 13.2684 | 12.5287 | 11.6826 | 10.7617 | 9.9126 | 8.9156 | 7.9121 | 5.638 | 8.4413 | 5.4783 | 1.1244 | 13.1253 | 12.7859 | 12.3222 | 11.2138 | 9.9835 | 8.8131 | 7.5536 | 6.4184 | 5.2191 | 4.0282 | 1.3772 | 6.407 | 4.947 | 4.0546
| CLAYHILLS | LW |  |  |  | 9.4758 | 9.0884 | 8.4791 | 7.3861 | 6.1878 | 4.8104 | 2.9089 | 0.87512 | -0.89177 | -2.8323 | -6.7918 | 2.0191 | 1.1721 | 0.39377 | 14.5084 | 14.2699 | 13.8796 | 13.2516 | 12.5531 | 11.6378 | 10.3601 | 8.8634 | 7.512 | 6.0207 | 2.9854 | 10.0322 | 9.3296 | 8.5255 | 12.9555 | 12.5071 | 11.7788 | 10.699 | 9.499 | 8.111 | 6.2048 | 4.1991 | 2.457 | 0.54179 | -3.3601 | 5.6151 | 4.7399 | 3.8604
| CLAYHILLS | ST |  |  |  | 9.7233 | 9.6456 | 9.5507 | 9.2926 | 9.0439 | 8.7748 | 8.1201 | 7.5107 | 6.8091 | 5.9964 | 4.0111 | 7.2893 | 6.0477 | 4.3698 | 14.6062 | 14.4919 | 14.3324 | 13.9767 | 13.6291 | 13.2695 | 12.6544 | 12.1489 | 11.5515 | 10.8098 | 8.8808 | 10.1939 | 7.2423 | 2.4839 | 13.2005 | 13.1264 | 13.0238 | 12.6509 | 12.2646 | 11.8477 | 11.1423 | 10.5211 | 9.8115 | 9.0001 | 7.0207 | 10.3028 | 9.0983 | 7.5142
| CLAYHILLS | FS |  |  |  | 9.7316 | 9.6736 | 9.6013 | 9.484 | 9.3461 | 9.0434 | 8.6637 | 8.2111 | 7.7033 | 7.1301 | 5.7905 | 7.5726 | 5.867 | 4.297 | 14.6112 | 14.4776 | 14.3156 | 14.0805 | 13.8079 | 13.4918 | 13.1229 | 12.7062 | 12.238 | 11.6812 | 10.276 | 9.638 | 4.8453 | -3.6833 | 13.2116 | 13.1528 | 13.0576 | 12.8191 | 12.5364 | 12.2043 | 11.8124 | 11.361 | 10.8603 | 10.2963 | 8.9763 | 10.8135 | 9.2457 | 7.9453
DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0.23511 | 0.19286 | 0.14863 | 0.10143 | 0.053354 | 0.0034722 | -0.05018 | -0.10372 | -0.12854 | -0.15093 | -0.20375 | -0.21321 | -0.28284 | -0.31098 | 0.33924 | 0.32307 | 0.30271 | 0.28263 | 0.26089 | 0.24003 | 0.2131 | 0.18174 | 0.15517 | 0.12769 | 0.07199 | 0.050921 | 0.018266 | -0.0028726 | 0.13872 | 0.10975 | 0.076127 | 0.038489 | -0.0021888 | -0.044675 | -0.091753 | -0.14643 | -0.18039 | -0.21102 | -0.28473 | -0.31292 | -0.36416 | -0.38726
| COLDBACKIE | CT |  |  |  | 0.26269 | 0.23217 | 0.20158 | 0.14028 | 0.083091 | 0.023452 | -0.030442 | -0.09023 | -0.12089 | -0.1461 | -0.20071 | -0.18311 | -0.28284 | -0.31098 | 0.3482 | 0.3361 | 0.3209 | 0.29258 | 0.26419 | 0.24003 | 0.21735 | 0.19139 | 0.16763 | 0.13887 | 0.082479 | 0.057647 | 0.018266 | -0.0028726 | 0.15407 | 0.12384 | 0.091705 | 0.045344 | 0.0021586 | -0.044178 | -0.091125 | -0.14643 | -0.18039 | -0.21102 | -0.28473 | -0.2912 | -0.36416 | -0.38726
| COLDBACKIE | LW |  |  |  | 0.23511 | 0.19286 | 0.14863 | 0.10143 | 0.053354 | 0.0034722 | -0.05018 | -0.10372 | -0.12854 | -0.15093 | -0.20375 | -0.21321 | -0.26155 | -0.27531 | 0.33924 | 0.32307 | 0.30271 | 0.28263 | 0.26089 | 0.24095 | 0.2131 | 0.18174 | 0.15517 | 0.12769 | 0.07199 | 0.050921 | 0.034555 | 0.030406 | 0.13872 | 0.10975 | 0.076127 | 0.038489 | -0.0021888 | -0.044675 | -0.091753 | -0.13876 | -0.16288 | -0.19541 | -0.26419 | -0.31292 | -0.34784 | -0.3573
| COLDBACKIE | ST |  |  |  | 0.27425 | 0.2555 | 0.2305 | 0.20441 | 0.17959 | 0.15167 | 0.12301 | 0.093201 | 0.056239 | 0.024228 | -0.054541 | -0.13112 | -0.21062 | -0.2661 | 0.35144 | 0.34421 | 0.33451 | 0.32384 | 0.31238 | 0.29959 | 0.28588 | 0.27061 | 0.25186 | 0.23117 | 0.17932 | 0.084533 | 0.044543 | 0.019006 | 0.16061 | 0.14616 | 0.12782 | 0.1072 | 0.085794 | 0.060839 | 0.032742 | 0.00198 | -0.03435 | -0.07298 | -0.16713 | -0.23603 | -0.30121 | -0.33942
| COLDBACKIE | FS |  |  |  | 0.27878 | 0.27565 | 0.25907 | 0.23943 | 0.21377 | 0.19168 | 0.16677 | 0.14276 | 0.11021 | 0.082257 | 0.011885 | -0.14696 | -0.25048 | -0.29891 | 0.35602 | 0.35154 | 0.34444 | 0.33609 | 0.32539 | 0.31553 | 0.30425 | 0.29232 | 0.27694 | 0.26194 | 0.22351 | 0.11761 | 0.031754 | 0.0052482 | 0.16852 | 0.15969 | 0.14737 | 0.13127 | 0.11123 | 0.092201 | 0.070249 | 0.046884 | 0.017922 | -0.010566 | -0.080012 | -0.21365 | -0.32918 | -0.3601
DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | NO | 0.45906 | 0.45739 | 0.45068 | 0.44089 | 0.43237 | 0.42601 | 0.41608 | 0.40487 | 0.39612 | 0.38868 | 0.37276 | 0.36055 | 0.35279 | 0.34585 | 0.50858 | 0.5073 | 0.50352 | 0.49884 | 0.49396 | 0.49039 | 0.4853 | 0.47832 | 0.47155 | 0.4649 | 0.45194 | 0.44515 | 0.43948 | 0.43387 | 0.49029 | 0.48856 | 0.48234 | 0.47346 | 0.46564 | 0.4598 | 0.45053 | 0.43999 | 0.43074 | 0.42241 | 0.40662 | 0.39524 | 0.38837 | 0.38212
| COLINTRAIVE | CT |  |  |  | 0.46524 | 0.45984 | 0.45558 | 0.44596 | 0.43432 | 0.42796 | 0.4193 | 0.41098 | 0.40578 | 0.39666 | 0.37985 | 0.36399 | 0.35279 | 0.34585 | 0.51085 | 0.50823 | 0.50556 | 0.50019 | 0.49396 | 0.49039 | 0.48592 | 0.48144 | 0.47678 | 0.46951 | 0.45619 | 0.44546 | 0.43948 | 0.43387 | 0.49564 | 0.49075 | 0.48674 | 0.47783 | 0.46712 | 0.46123 | 0.45332 | 0.4457 | 0.44003 | 0.4303 | 0.41347 | 0.39842 | 0.38837 | 0.38212
| COLINTRAIVE | LW |  |  |  | 0.45906 | 0.45739 | 0.45068 | 0.44089 | 0.43237 | 0.42601 | 0.41608 | 0.40487 | 0.39612 | 0.38868 | 0.37276 | 0.36055 | 0.35435 | 0.35264 | 0.50858 | 0.5073 | 0.50352 | 0.49884 | 0.4944 | 0.49105 | 0.4853 | 0.47832 | 0.47155 | 0.4649 | 0.45194 | 0.44515 | 0.44278 | 0.44222 | 0.49029 | 0.48856 | 0.48234 | 0.47346 | 0.46564 | 0.4598 | 0.45053 | 0.43999 | 0.43074 | 0.42241 | 0.40662 | 0.39524 | 0.38972 | 0.38822
| COLINTRAIVE | ST |  |  |  | 0.46788 | 0.46582 | 0.46133 | 0.45691 | 0.45502 | 0.4533 | 0.44898 | 0.44236 | 0.43767 | 0.43191 | 0.41827 | 0.38211 | 0.3731 | 0.36542 | 0.5121 | 0.5109 | 0.50869 | 0.50652 | 0.50508 | 0.50363 | 0.50096 | 0.49723 | 0.49365 | 0.48927 | 0.4789 | 0.45327 | 0.44689 | 0.44191 | 0.49835 | 0.4964 | 0.49205 | 0.48804 | 0.48621 | 0.48449 | 0.48046 | 0.47428 | 0.46945 | 0.46347 | 0.44958 | 0.41478 | 0.40638 | 0.39964
| COLINTRAIVE | FS |  |  |  | 0.46795 | 0.46737 | 0.46196 | 0.46073 | 0.45735 | 0.45423 | 0.44909 | 0.44879 | 0.44103 | 0.43628 | 0.42608 | 0.3894 | 0.36524 | 0.35998 | 0.51214 | 0.51169 | 0.50902 | 0.50812 | 0.50629 | 0.50453 | 0.50189 | 0.50085 | 0.497 | 0.49386 | 0.48665 | 0.46294 | 0.44384 | 0.4386 | 0.49841 | 0.49784 | 0.49263 | 0.49145 | 0.48835 | 0.48547 | 0.48078 | 0.48031 | 0.47324 | 0.46862 | 0.45833 | 0.42291 | 0.39949 | 0.39487
STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | NO | 2.1354 | 2.053 | 1.942 | 1.8053 | 1.6623 | 1.5084 | 1.3347 | 1.1659 | 1.0259 | 0.86856 | 0.55365 | 0.35604 | -0.094318 | -0.63411 | 2.9132 | 2.8723 | 2.8104 | 2.7425 | 2.6497 | 2.5669 | 2.4797 | 2.3767 | 2.2435 | 2.1039 | 1.8342 | 1.6371 | 1.1478 | 0.49586 | 2.9529 | 2.8971 | 2.8077 | 2.6836 | 2.5518 | 2.4045 | 2.2487 | 2.0809 | 1.9211 | 1.7568 | 1.4329 | 1.207 | 0.67598 | 0.010941
| COLL | CT |  |  |  | 2.1894 | 2.1341 | 2.0571 | 1.8714 | 1.6738 | 1.5084 | 1.3347 | 1.1681 | 1.0698 | 0.93667 | 0.65418 | 0.47011 | 0.119 | -0.15784 | 2.9331 | 2.9028 | 2.857 | 2.7589 | 2.6497 | 2.5669 | 2.4797 | 2.3948 | 2.2966 | 2.1674 | 1.9229 | 1.7055 | 1.3855 | 1.0447 | 2.9934 | 2.9559 | 2.9077 | 2.7363 | 2.5529 | 2.4045 | 2.2487 | 2.0985 | 1.9845 | 1.832 | 1.5424 | 1.3297 | 0.9548 | 0.63332
| COLL | LW |  |  |  | 2.1354 | 2.053 | 1.942 | 1.8053 | 1.6623 | 1.5272 | 1.3521 | 1.1659 | 1.0259 | 0.86856 | 0.55365 | 0.35604 | -0.094318 | -0.63411 | 2.9132 | 2.8723 | 2.8104 | 2.7425 | 2.6668 | 2.5986 | 2.4937 | 2.3767 | 2.2435 | 2.1039 | 1.8342 | 1.6371 | 1.1478 | 0.49586 | 2.9529 | 2.8971 | 2.8077 | 2.6836 | 2.5518 | 2.4296 | 2.2621 | 2.0809 | 1.9211 | 1.7568 | 1.4329 | 1.207 | 0.67598 | 0.010941
| COLL | ST |  |  |  | 2.2192 | 2.1838 | 2.1477 | 2.0947 | 2.038 | 1.9751 | 1.9063 | 1.8324 | 1.7027 | 1.5818 | 1.3019 | 0.71254 | 0.27125 | -0.11472 | 2.9442 | 2.9259 | 2.9054 | 2.8768 | 2.8436 | 2.8059 | 2.7606 | 2.7091 | 2.5932 | 2.4997 | 2.2838 | 1.8074 | 1.3568 | 0.90465 | 3.0115 | 2.9905 | 2.967 | 2.9327 | 2.8874 | 2.8271 | 2.7597 | 2.6857 | 2.5441 | 2.4207 | 2.1413 | 1.5437 | 1.0509 | 0.60228
| COLL | FS |  |  |  | 2.2325 | 2.2076 | 2.1798 | 2.1315 | 2.0801 | 2.0276 | 1.9707 | 1.9109 | 1.8203 | 1.7295 | 1.5302 | 0.9686 | 0.55264 | 0.44235 | 2.9494 | 2.9354 | 2.9188 | 2.8936 | 2.8651 | 2.8354 | 2.8007 | 2.7615 | 2.6939 | 2.6274 | 2.4788 | 2.112 | 1.7828 | 1.6387 | 3.0162 | 3.0049 | 2.9902 | 2.9576 | 2.9251 | 2.8767 | 2.8222 | 2.7638 | 2.6714 | 2.5793 | 2.3777 | 1.8439 | 1.4391 | 1.3297
CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 9.9753 | 9.8325 | 9.5209 | 9.1806 | 8.8347 | 8.5607 | 8.248 | 7.8998 | 7.3358 | 6.8519 | 5.4604 | 9.5292 | 9.1511 | 8.6246 | 12.9983 | 12.8873 | 12.6505 | 12.3925 | 12.1313 | 11.9209 | 11.6453 | 11.1826 | 10.6706 | 10.2344 | 9.1269 | 12.3497 | 11.9305 | 11.3464 | 11.5426 | 11.4227 | 11.1609 | 10.8487 | 10.5334 | 10.2787 | 9.8404 | 9.2602 | 8.6295 | 8.092 | 6.7304 | 10.9882 | 10.5424 | 9.892
| COMMERCE STREET | CT |  |  |  | 9.9753 | 9.8325 | 9.5209 | 9.1806 | 8.8347 | 8.5607 | 8.248 | 7.8998 | 7.3358 | 6.8519 | 5.6433 | 9.593 | 9.408 | 9.1947 | 12.9983 | 12.8873 | 12.6505 | 12.3925 | 12.1313 | 11.9209 | 11.6453 | 11.1826 | 10.6706 | 10.2344 | 9.277 | 12.3497 | 11.9305 | 11.3464 | 11.543 | 11.4227 | 11.1609 | 10.8487 | 10.5334 | 10.2787 | 9.8404 | 9.2602 | 8.6295 | 8.092 | 6.913 | 11.0413 | 10.805 | 10.5449
| COMMERCE STREET | LW |  |  |  | 9.979 | 9.8736 | 9.6922 | 9.5437 | 9.3702 | 9.1848 | 8.8752 | 8.5026 | 8.0537 | 7.2989 | 5.4604 | 9.5292 | 9.1511 | 8.6246 | 13.0067 | 12.9292 | 12.7932 | 12.6822 | 12.5522 | 12.4129 | 12.1746 | 11.8879 | 11.2959 | 10.592 | 9.1269 | 12.4853 | 12.0246 | 11.3734 | 11.5426 | 11.4516 | 11.2939 | 11.1465 | 10.9788 | 10.7993 | 10.5157 | 10.1752 | 9.4093 | 8.5412 | 6.7304 | 10.9882 | 10.5424 | 9.892
| COMMERCE STREET | ST |  |  |  | 9.9935 | 9.9408 | 9.8746 | 9.7854 | 9.6703 | 9.5241 | 9.3388 | 9.1082 | 8.7822 | 8.4173 | 7.2023 | 9.5372 | 9.218 | 8.9053 | 13.015 | 12.9749 | 12.9241 | 12.856 | 12.7678 | 12.6555 | 12.5088 | 12.3269 | 12.0505 | 11.7572 | 10.5026 | 12.4914 | 12.0324 | 11.4181 | 11.5966 | 11.5709 | 11.5339 | 11.48 | 11.4025 | 11.3015 | 11.1646 | 10.9419 | 10.6147 | 10.1044 | 8.4858 | 11.3013 | 10.9194 | 10.5348
| COMMERCE STREET | FS |  |  |  | 10.0056 | 9.9686 | 9.9241 | 9.8643 | 9.7909 | 9.7018 | 9.5934 | 9.4633 | 9.2956 | 9.1057 | 8.6401 | 9.7857 | 9.6687 | 9.5799 | 13.0226 | 12.9932 | 12.9575 | 12.9106 | 12.8525 | 12.782 | 12.6954 | 12.5896 | 12.4452 | 12.285 | 11.8944 | 12.6834 | 12.2528 | 11.4952 | 11.5953 | 11.5769 | 11.553 | 11.5114 | 11.4587 | 11.3925 | 11.311 | 11.2088 | 11.077 | 10.9284 | 10.443 | 11.5732 | 11.4605 | 11.3633
ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | NO | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035
| COMRIE | CT |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035
| COMRIE | LW |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035
| COMRIE | ST |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035
| COMRIE | FS |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.045129 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035 | 0.043035
TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | -0.7673 | -0.81847 | -0.87959 | -0.95316 | -1.047 | -1.1616 | -1.2797 | -1.3796 | -1.444 | -1.5289 | -1.6901 | -1.7113 | -1.8493 | -1.9452 | -0.10878 | -0.13948 | -0.17616 | -0.21801 | -0.28545 | -0.36976 | -0.45761 | -0.52025 | -0.57246 | -0.6375 | -0.76181 | -0.81579 | -0.96388 | -1.134 | -0.43081 | -0.47278 | -0.51177 | -0.56597 | -0.6307 | -0.74246 | -0.8704 | -0.9752 | -1.0405 | -1.1249 | -1.2851 | -1.3166 | -1.4763 | -1.5919
| CONNEL | CT |  |  |  | -0.74671 | -0.78713 | -0.83368 | -0.93516 | -1.047 | -1.1616 | -1.2797 | -1.3796 | -1.444 | -1.5289 | -1.6901 | -1.7113 | -1.8493 | -1.9452 | -0.099033 | -0.12489 | -0.15415 | -0.21596 | -0.28545 | -0.36976 | -0.45761 | -0.52025 | -0.57246 | -0.6375 | -0.76181 | -0.81579 | -0.95343 | -1.0894 | -0.40995 | -0.44407 | -0.47577 | -0.5514 | -0.6307 | -0.74246 | -0.8704 | -0.9752 | -1.0405 | -1.1249 | -1.2851 | -1.3166 | -1.4763 | -1.5919
| CONNEL | LW |  |  |  | -0.7673 | -0.81847 | -0.87959 | -0.95316 | -1.0322 | -1.1092 | -1.2116 | -1.3228 | -1.4023 | -1.4887 | -1.6606 | -1.5942 | -1.7416 | -1.9211 | -0.10878 | -0.13948 | -0.17616 | -0.21801 | -0.26348 | -0.30724 | -0.36828 | -0.4354 | -0.49208 | -0.55367 | -0.67766 | -0.63169 | -0.79219 | -1.0072 | -0.43081 | -0.47278 | -0.51177 | -0.56597 | -0.62131 | -0.68104 | -0.78327 | -0.89424 | -0.97143 | -1.0555 | -1.2225 | -1.1647 | -1.3448 | -1.5674
| CONNEL | ST |  |  |  | -0.73192 | -0.75016 | -0.77509 | -0.82605 | -0.87908 | -0.92624 | -1.0033 | -1.0585 | -1.1352 | -1.2017 | -1.3541 | -1.6027 | -1.7619 | -1.8929 | -0.089811 | -0.10166 | -0.11688 | -0.16391 | -0.20686 | -0.24322 | -0.31545 | -0.35734 | -0.42394 | -0.47331 | -0.587 | -0.79126 | -0.96388 | -1.134 | -0.39346 | -0.40729 | -0.4246 | -0.47275 | -0.51802 | -0.55486 | -0.62534 | -0.66549 | -0.72772 | -0.79437 | -0.94885 | -1.208 | -1.3962 | -1.5571
| CONNEL | FS |  |  |  | -0.7232 | -0.7378 | -0.75839 | -0.78904 | -0.8242 | -0.8615 | -0.90183 | -0.94167 | -0.99086 | -1.0378 | -1.1462 | -1.375 | -1.5684 | -1.6105 | -0.085188 | -0.094815 | -0.1078 | -0.12967 | -0.1544 | -0.18114 | -0.21004 | -0.23861 | -0.27634 | -0.31137 | -0.39107 | -0.54019 | -0.6935 | -0.78303 | -0.3852 | -0.39502 | -0.40922 | -0.43382 | -0.46067 | -0.48934 | -0.51905 | -0.54688 | -0.58446 | -0.61639 | -0.7218 | -0.95241 | -1.1424 | -1.1899
BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 1.6742 | 1.4227 | 0.96199 | 0.66956 | 0.29154 | 0.02347 | -0.31338 | -0.80126 | -1.0927 | -1.4072 | -2.008 | -2.2788 | -2.8363 | -3.0924 | 3.1188 | 2.9918 | 2.7435 | 2.5974 | 2.4049 | 2.2712 | 2.0728 | 1.7967 | 1.5826 | 1.3508 | 0.90301 | 0.70686 | 0.3472 | -0.0030627 | 2.9412 | 2.7335 | 2.3555 | 2.0977 | 1.7703 | 1.531 | 1.213 | 0.77017 | 0.47193 | 0.14979 | -0.46942 | -0.70664 | -1.1623 | -1.3811
| CONON BRIDGE | CT |  |  |  | 1.7875 | 1.6091 | 1.2404 | 0.91637 | 0.50955 | 0.22726 | -0.080688 | -0.5133 | -0.80374 | -1.1446 | -1.7772 | -2.2623 | -2.8363 | -3.0924 | 3.1581 | 3.0583 | 2.8498 | 2.6629 | 2.4314 | 2.2812 | 2.1166 | 1.8975 | 1.707 | 1.465 | 1.01 | 0.70686 | 0.3472 | -0.0030627 | 3.0348 | 2.8873 | 2.5866 | 2.2874 | 1.921 | 1.6674 | 1.3931 | 1.0229 | 0.74371 | 0.40377 | -0.23108 | -0.6824 | -1.1623 | -1.3811
| CONON BRIDGE | LW |  |  |  | 1.6742 | 1.4227 | 0.96199 | 0.66956 | 0.29154 | 0.02347 | -0.31338 | -0.80126 | -1.0927 | -1.4072 | -2.008 | -2.2788 | -2.5861 | -2.6779 | 3.1188 | 2.9918 | 2.7435 | 2.5974 | 2.4049 | 2.2712 | 2.0728 | 1.7967 | 1.5826 | 1.3508 | 0.90301 | 0.82144 | 0.70266 | 0.66802 | 2.9412 | 2.7335 | 2.3555 | 2.0977 | 1.7703 | 1.531 | 1.213 | 0.77017 | 0.47193 | 0.14979 | -0.46942 | -0.70664 | -0.95989 | -1.0328
| CONON BRIDGE | ST |  |  |  | 1.8197 | 1.6755 | 1.3806 | 1.2806 | 1.1121 | 0.99866 | 0.85753 | 0.6375 | 0.46848 | 0.27751 | -0.12694 | -0.96532 | -1.4473 | -1.8887 | 3.1691 | 3.0917 | 2.9361 | 2.876 | 2.7767 | 2.7018 | 2.607 | 2.4668 | 2.3443 | 2.2011 | 1.8781 | 1.2029 | 0.843 | 0.44809 | 3.0606 | 2.9462 | 2.7196 | 2.6292 | 2.484 | 2.3766 | 2.2445 | 2.0495 | 1.8839 | 1.6936 | 1.2767 | 0.39952 | -0.024922 | -0.3833
| CONON BRIDGE | FS |  |  |  | 1.8633 | 1.74 | 1.5031 | 1.3998 | 1.2496 | 1.1401 | 1.0255 | 0.85474 | 0.70326 | 0.54492 | 0.19899 | -0.74445 | -1.5584 | -1.9335 | 3.1871 | 3.1178 | 2.9858 | 2.9258 | 2.8373 | 2.7687 | 2.6931 | 2.5845 | 2.4831 | 2.3724 | 2.1185 | 1.4174 | 0.64314 | 0.041358 | 3.0952 | 2.9987 | 2.8196 | 2.73 | 2.6035 | 2.5049 | 2.3996 | 2.2507 | 2.1089 | 1.9578 | 1.6224 | 0.69567 | -0.11373 | -0.41822
GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | NO | 0.22346 | 0.21603 | 0.20083 | 0.19195 | 0.17489 | 0.16085 | 0.14681 | 0.13083 | 0.12371 | 0.10872 | 0.087893 | 0.077945 | 0.065447 | 0.057334 | 0.3126 | 0.309 | 0.30166 | 0.29672 | 0.2888 | 0.28225 | 0.27389 | 0.26416 | 0.25673 | 0.24643 | 0.22921 | 0.22451 | 0.21734 | 0.21144 | 0.24767 | 0.24095 | 0.22727 | 0.21895 | 0.20371 | 0.19122 | 0.17784 | 0.16262 | 0.15501 | 0.1408 | 0.12045 | 0.11163 | 0.10062 | 0.093342
| CONON FALLS | CT |  |  |  | 0.22524 | 0.22366 | 0.21359 | 0.1988 | 0.18232 | 0.16691 | 0.15043 | 0.13707 | 0.12718 | 0.11823 | 0.094989 | 0.088216 | 0.065447 | 0.057334 | 0.31418 | 0.31187 | 0.30646 | 0.29835 | 0.28951 | 0.28225 | 0.27462 | 0.26794 | 0.26074 | 0.25252 | 0.23483 | 0.22753 | 0.21734 | 0.21144 | 0.25143 | 0.24793 | 0.23832 | 0.22461 | 0.20939 | 0.19557 | 0.18089 | 0.16878 | 0.15888 | 0.14984 | 0.1275 | 0.1208 | 0.10062 | 0.093342
| CONON FALLS | LW |  |  |  | 0.22346 | 0.21603 | 0.20083 | 0.19195 | 0.17489 | 0.16085 | 0.14681 | 0.13083 | 0.12371 | 0.10872 | 0.087893 | 0.077945 | 0.068724 | 0.064936 | 0.3126 | 0.309 | 0.30166 | 0.29672 | 0.2888 | 0.28237 | 0.27389 | 0.26416 | 0.25673 | 0.24643 | 0.22921 | 0.22451 | 0.22084 | 0.21953 | 0.24767 | 0.24095 | 0.22727 | 0.21895 | 0.20371 | 0.19122 | 0.17784 | 0.16262 | 0.15501 | 0.1408 | 0.12045 | 0.11163 | 0.10348 | 0.10018
| CONON FALLS | ST |  |  |  | 0.22542 | 0.22486 | 0.22408 | 0.21661 | 0.21297 | 0.20701 | 0.19996 | 0.19144 | 0.18168 | 0.17454 | 0.15272 | 0.1158 | 0.093158 | 0.079364 | 0.31533 | 0.3141 | 0.31166 | 0.30825 | 0.30573 | 0.30235 | 0.29821 | 0.29328 | 0.28746 | 0.282 | 0.26725 | 0.23927 | 0.22763 | 0.22065 | 0.25443 | 0.25238 | 0.24775 | 0.2411 | 0.2375 | 0.23196 | 0.22529 | 0.21732 | 0.20819 | 0.20132 | 0.18071 | 0.14547 | 0.12512 | 0.11303
| CONON FALLS | FS |  |  |  | 0.22549 | 0.22505 | 0.2245 | 0.22265 | 0.21901 | 0.21017 | 0.20805 | 0.20142 | 0.19148 | 0.18601 | 0.16832 | 0.11755 | 0.081834 | 0.07251 | 0.31666 | 0.31476 | 0.31325 | 0.31061 | 0.30838 | 0.30444 | 0.30242 | 0.29866 | 0.2936 | 0.28971 | 0.27895 | 0.24877 | 0.22349 | 0.21712 | 0.25775 | 0.25385 | 0.25132 | 0.24632 | 0.24284 | 0.23504 | 0.23273 | 0.22651 | 0.21747 | 0.21218 | 0.19574 | 0.14883 | 0.11519 | 0.10701
DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 7.653 | 7.3041 | 6.8085 | 5.8477 | 4.8701 | 3.6511 | 2.1734 | 0.80401 | -0.12618 | -1.1384 | -3.1725 | -0.3966 | -1.0585 | -1.6602 | 10.3913 | 10.2464 | 10.0404 | 9.4091 | 8.7259 | 7.7388 | 6.5534 | 5.5637 | 4.9274 | 4.1775 | 2.6645 | 4.6151 | 2.0343 | -4.8854 | 9.1021 | 8.8928 | 8.3793 | 7.4114 | 6.4343 | 5.1545 | 3.636 | 2.2931 | 1.4433 | 0.52103 | -1.3284 | 1.0463 | 0.3177 | -0.40107
| CONSTABLE STREET | CT |  |  |  | 7.7528 | 7.5317 | 7.2358 | 6.4939 | 5.6139 | 4.6335 | 3.5808 | 2.7194 | 2.004 | 1.2525 | -0.30553 | 0.88634 | -0.30166 | -0.9946 | 10.3913 | 10.2464 | 10.0404 | 9.5936 | 9.005 | 8.2311 | 7.3927 | 6.7905 | 6.2565 | 5.6881 | 4.444 | 4.6151 | 2.2722 | -1.1729 | 9.1031 | 8.9275 | 8.6764 | 8.053 | 7.2309 | 6.2467 | 5.1934 | 4.3835 | 3.7331 | 3.0528 | 1.6443 | 2.6658 | 1.5058 | 0.80292
| CONSTABLE STREET | LW |  |  |  | 7.653 | 7.3041 | 6.8085 | 5.8477 | 4.8701 | 3.6511 | 2.1734 | 0.80401 | -0.12618 | -1.1384 | -3.1725 | -0.3966 | -1.0585 | -1.6602 | 10.3971 | 10.2642 | 10.0702 | 9.4091 | 8.7259 | 7.7388 | 6.5534 | 5.5637 | 4.9274 | 4.1775 | 2.6645 | 4.8722 | 4.2634 | 3.5815 | 9.1021 | 8.8928 | 8.3793 | 7.4114 | 6.4343 | 5.1545 | 3.636 | 2.2931 | 1.4433 | 0.52103 | -1.3284 | 1.0463 | 0.3177 | -0.40107
| CONSTABLE STREET | ST |  |  |  | 7.8804 | 7.7663 | 7.6371 | 7.3546 | 7.1722 | 7.0219 | 6.5162 | 6.1652 | 5.8219 | 5.4359 | 4.4936 | 5.1863 | 4.3274 | 2.9846 | 10.426 | 10.3322 | 10.2263 | 9.8613 | 9.5913 | 9.3636 | 8.6869 | 8.2853 | 7.9171 | 7.522 | 6.5464 | 6.1228 | 3.8135 | 0.041725 | 9.1181 | 8.9931 | 8.8582 | 8.4803 | 8.2082 | 7.9779 | 7.4025 | 7.117 | 6.8739 | 6.624 | 6.0139 | 6.6636 | 5.8035 | 4.4567
| CONSTABLE STREET | FS |  |  |  | 7.8761 | 7.7752 | 7.6658 | 7.5418 | 7.4447 | 7.3284 | 7.1305 | 6.8643 | 6.5963 | 6.2969 | 5.6088 | 5.6582 | 4.3034 | 3.1519 | 10.4323 | 10.3414 | 10.2398 | 10.0978 | 9.9608 | 9.7201 | 9.41 | 9.0762 | 8.7447 | 8.3726 | 7.4853 | 6.0157 | 2.0343 | -4.8854 | 9.1362 | 9.0243 | 8.9036 | 8.7646 | 8.6453 | 8.5034 | 8.35 | 8.1938 | 8.0614 | 7.8673 | 7.2556 | 7.3153 | 6.0828 | 4.9892
ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | NO | 0.094789 | 0.094789 | 0.094789 | 0.082968 | 0.074977 | 0.069697 | 0.051551 | 0.046504 | 0.032856 | 0.028016 | 0.017369 | -0.013334 | -0.058397 | -0.10465 | 0.10193 | 0.10193 | 0.10193 | 0.087159 | 0.077169 | 0.070569 | 0.047888 | 0.041579 | 0.024518 | 0.018468 | 0.0051602 | -0.033218 | -0.089548 | -0.14736 | 0.098613 | 0.098613 | 0.098613 | 0.083838 | 0.073848 | 0.067248 | 0.044566 | 0.038257 | 0.021197 | 0.015147 | 0.0018388 | -0.03654 | -0.092869 | -0.15068
| CONTULLICH | CT |  |  |  | 0.094789 | 0.094789 | 0.094789 | 0.093249 | 0.090516 | 0.077376 | 0.063363 | 0.059809 | 0.053604 | 0.047378 | 0.036074 | 0.0046508 | -0.024991 | -0.056989 | 0.10193 | 0.10193 | 0.10193 | 0.10001 | 0.096594 | 0.080168 | 0.062652 | 0.05821 | 0.050454 | 0.042671 | 0.028542 | -0.010738 | -0.04779 | -0.087787 | 0.098613 | 0.098613 | 0.098613 | 0.096689 | 0.093272 | 0.076847 | 0.059331 | 0.054889 | 0.047133 | 0.03935 | 0.02522 | -0.014059 | -0.051111 | -0.091109
| CONTULLICH | LW |  |  |  | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.092362 | 0.089845 | 0.085443 | 0.073185 | 0.018166 | -0.062452 | 0.10193 | 0.10193 | 0.10193 | 0.10193 | 0.10193 | 0.10193 | 0.10193 | 0.10193 | 0.098901 | 0.095755 | 0.090252 | 0.07493 | 0.0061566 | -0.094617 | 0.098613 | 0.098613 | 0.098613 | 0.098613 | 0.098613 | 0.098613 | 0.098613 | 0.098613 | 0.09558 | 0.092434 | 0.086931 | 0.071608 | 0.0028352 | -0.097938
| CONTULLICH | ST |  |  |  | 0.094789 | 0.094789 | 0.094789 | 0.082968 | 0.074977 | 0.069697 | 0.051551 | 0.046504 | 0.032856 | 0.028016 | 0.017369 | -0.013334 | -0.058397 | -0.10465 | 0.10193 | 0.10193 | 0.10193 | 0.087159 | 0.077169 | 0.070569 | 0.047888 | 0.041579 | 0.024518 | 0.018468 | 0.0051602 | -0.033218 | -0.089548 | -0.14736 | 0.098613 | 0.098613 | 0.098613 | 0.083838 | 0.073848 | 0.067248 | 0.044566 | 0.038257 | 0.021197 | 0.015147 | 0.0018388 | -0.03654 | -0.092869 | -0.15068
| CONTULLICH | FS |  |  |  | 0.094789 | 0.094789 | 0.094789 | 0.092372 | 0.089954 | 0.087137 | 0.08432 | 0.081903 | 0.076963 | 0.073613 | 0.066912 | 0.062852 | 0.060036 | 0.054868 | 0.10193 | 0.10193 | 0.10193 | 0.098913 | 0.095892 | 0.09237 | 0.088849 | 0.085828 | 0.079653 | 0.075465 | 0.067089 | 0.062013 | 0.058494 | 0.052034 | 0.098613 | 0.098613 | 0.098613 | 0.095592 | 0.09257 | 0.089049 | 0.085528 | 0.082506 | 0.076332 | 0.072144 | 0.063767 | 0.058692 | 0.055172 | 0.048713
FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | -0.38583 | -0.42222 | -0.46868 | -0.5188 | -0.59189 | -0.70034 | -0.81527 | -0.90206 | -0.95928 | -1.0233 | -1.1416 | -1.0749 | -1.276 | -1.4663 | -0.012787 | -0.030725 | -0.059285 | -0.099617 | -0.15816 | -0.24807 | -0.34361 | -0.40134 | -0.46362 | -0.53627 | -0.67335 | -0.73911 | -0.96758 | -1.1838 | -0.17494 | -0.2063 | -0.25086 | -0.29663 | -0.37871 | -0.48954 | -0.6069 | -0.68715 | -0.75963 | -0.84624 | -1.0072 | -1.0329 | -1.2806 | -1.4961
| CORRAN | CT |  |  |  | -0.36326 | -0.38968 | -0.43164 | -0.50976 | -0.59189 | -0.70034 | -0.81527 | -0.90206 | -0.95928 | -1.0233 | -1.1416 | -1.0749 | -1.2551 | -1.3853 | -0.0061023 | -0.020446 | -0.048558 | -0.099617 | -0.15816 | -0.24807 | -0.34361 | -0.40134 | -0.46362 | -0.53627 | -0.67335 | -0.7052 | -0.86832 | -1.0268 | -0.1585 | -0.18166 | -0.22214 | -0.29663 | -0.37871 | -0.48954 | -0.6069 | -0.68715 | -0.75963 | -0.84624 | -1.0072 | -1.0268 | -1.2117 | -1.3642
| CORRAN | LW |  |  |  | -0.38583 | -0.42222 | -0.46868 | -0.5188 | -0.56977 | -0.62717 | -0.69119 | -0.76458 | -0.81513 | -0.86918 | -0.99288 | -0.88229 | -1.1044 | -1.3718 | -0.012787 | -0.030725 | -0.059285 | -0.087178 | -0.11779 | -0.14883 | -0.19248 | -0.24346 | -0.29911 | -0.3594 | -0.48511 | -0.43384 | -0.67234 | -0.99713 | -0.17494 | -0.2063 | -0.25086 | -0.29595 | -0.34388 | -0.39379 | -0.45833 | -0.53297 | -0.60081 | -0.67372 | -0.82873 | -0.77595 | -1.0312 | -1.3599
| CORRAN | ST |  |  |  | -0.34394 | -0.36584 | -0.38315 | -0.44577 | -0.49661 | -0.54464 | -0.63316 | -0.68513 | -0.77122 | -0.83084 | -0.97505 | -1.0566 | -1.276 | -1.4663 | 0.0024466 | -0.0074711 | -0.017288 | -0.07788 | -0.12547 | -0.16577 | -0.25975 | -0.30568 | -0.39139 | -0.44658 | -0.57867 | -0.73911 | -0.96758 | -1.1838 | -0.14409 | -0.16189 | -0.1776 | -0.24695 | -0.30317 | -0.35326 | -0.45632 | -0.5125 | -0.61049 | -0.67771 | -0.83927 | -1.0329 | -1.2806 | -1.4961
| CORRAN | FS |  |  |  | -0.33315 | -0.34794 | -0.36131 | -0.38932 | -0.41849 | -0.45008 | -0.48119 | -0.51446 | -0.5599 | -0.60432 | -0.70021 | -0.81225 | -0.93255 | -0.98977 | 0.0061297 | -0.0010406 | -0.0086674 | -0.028791 | -0.050624 | -0.074939 | -0.10062 | -0.12764 | -0.16787 | -0.20486 | -0.28686 | -0.38947 | -0.5078 | -0.56845 | -0.13638 | -0.14885 | -0.16104 | -0.18854 | -0.21811 | -0.25044 | -0.28354 | -0.31853 | -0.36825 | -0.41587 | -0.52048 | -0.68042 | -0.83 | -0.88054
KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | NO | 1.8598 | 1.8162 | 1.7463 | 1.6705 | 1.5779 | 1.4873 | 1.3815 | 1.26 | 1.1766 | 1.0863 | 0.92427 | 0.89495 | 0.82102 | 0.77669 | 2.1319 | 2.1053 | 2.0671 | 2.0295 | 1.9741 | 1.9219 | 1.8702 | 1.8117 | 1.754 | 1.6916 | 1.5762 | 1.5684 | 1.508 | 1.4606 | 1.9749 | 1.9329 | 1.8744 | 1.8154 | 1.7425 | 1.6634 | 1.5844 | 1.4825 | 1.4008 | 1.3126 | 1.1506 | 1.1035 | 1.0547 | 1.022
| COSHIEVILLE | CT |  |  |  | 1.8606 | 1.8472 | 1.8165 | 1.7115 | 1.5941 | 1.4873 | 1.3831 | 1.2796 | 1.2093 | 1.1238 | 0.97093 | 0.93183 | 0.82102 | 0.77669 | 2.1458 | 2.1248 | 2.0931 | 2.037 | 1.9741 | 1.9219 | 1.8702 | 1.8184 | 1.7717 | 1.7119 | 1.6019 | 1.57 | 1.508 | 1.4606 | 1.9995 | 1.9684 | 1.9231 | 1.8389 | 1.7439 | 1.6634 | 1.5844 | 1.5058 | 1.4399 | 1.3547 | 1.1999 | 1.1325 | 1.0547 | 1.022
| COSHIEVILLE | LW |  |  |  | 1.8598 | 1.8162 | 1.7463 | 1.6705 | 1.5779 | 1.4935 | 1.3815 | 1.26 | 1.1766 | 1.0863 | 0.92427 | 0.89495 | 0.85043 | 0.83378 | 2.1319 | 2.1053 | 2.0671 | 2.0295 | 1.9827 | 1.941 | 1.8798 | 1.8117 | 1.754 | 1.6916 | 1.5762 | 1.5684 | 1.5495 | 1.5432 | 1.9749 | 1.9329 | 1.8744 | 1.8154 | 1.7425 | 1.6778 | 1.5851 | 1.4825 | 1.4008 | 1.3126 | 1.1506 | 1.1035 | 1.0733 | 1.0629
| COSHIEVILLE | ST |  |  |  | 1.8624 | 1.858 | 1.8526 | 1.8451 | 1.8173 | 1.7688 | 1.7222 | 1.6711 | 1.6116 | 1.5461 | 1.3994 | 1.1435 | 1.0355 | 0.96406 | 2.1552 | 2.1428 | 2.1308 | 2.1149 | 2.0913 | 2.065 | 2.0376 | 2.0067 | 1.9701 | 1.9282 | 1.8322 | 1.6539 | 1.5869 | 1.5391 | 2.0163 | 1.9973 | 1.9804 | 1.9571 | 1.9225 | 1.8839 | 1.8448 | 1.801 | 1.7487 | 1.6892 | 1.5536 | 1.2862 | 1.2042 | 1.1601
| COSHIEVILLE | FS |  |  |  | 1.8633 | 1.8599 | 1.8558 | 1.8502 | 1.8406 | 1.8122 | 1.7729 | 1.7305 | 1.6777 | 1.6229 | 1.5079 | 1.2016 | 0.97974 | 0.92264 | 2.1597 | 2.1505 | 2.1414 | 2.126 | 2.108 | 2.0865 | 2.0644 | 2.0398 | 2.0099 | 1.9778 | 1.9081 | 1.7263 | 1.5659 | 1.5077 | 2.0238 | 2.0105 | 1.9985 | 1.9752 | 1.9493 | 1.9177 | 1.8859 | 1.8509 | 1.8072 | 1.7609 | 1.6611 | 1.3797 | 1.1643 | 1.1271
COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | NO | 1.5 | 1.3779 | 1.1799 | 0.86071 | 0.51325 | 0.10796 | -0.39471 | -0.96034 | -1.325 | -1.7044 | -3.2313 | -3.403 | -4.1092 | -4.5818 | 1.1601 | 1.0979 | 0.99351 | 0.80767 | 0.60002 | 0.32049 | -0.031084 | -0.41608 | -0.64693 | -0.89147 | -2.0484 | -2.2759 | -2.7681 | -3.3374 | 0.98575 | 0.87054 | 0.69739 | 0.41206 | 0.089863 | -0.31558 | -0.81386 | -1.3578 | -1.7007 | -2.059 | -3.5108 | -3.6968 | -4.3877 | -5.0215
| COUPAR ANGUS | CT |  |  |  | 1.5703 | 1.497 | 1.358 | 1.0731 | 0.73688 | 0.30751 | -0.16107 | -0.60692 | -0.95927 | -1.3526 | -2.8997 | -3.403 | -4.1092 | -4.5501 | 1.1876 | 1.1438 | 1.061 | 0.89361 | 0.69852 | 0.38335 | 0.042351 | -0.23047 | -0.45241 | -0.71099 | -1.8862 | -2.2759 | -2.7681 | -3.2503 | 1.0545 | 0.98377 | 0.85186 | 0.57931 | 0.27485 | -0.14349 | -0.60935 | -1.0269 | -1.3604 | -1.7339 | -3.207 | -3.6968 | -4.3877 | -4.8518
| COUPAR ANGUS | LW |  |  |  | 1.5 | 1.3779 | 1.1799 | 0.86071 | 0.51325 | 0.10796 | -0.39471 | -0.96034 | -1.325 | -1.7044 | -3.2313 | -3.3314 | -3.9918 | -4.5818 | 1.1601 | 1.0979 | 0.99351 | 0.80767 | 0.60002 | 0.32049 | -0.031084 | -0.41608 | -0.64693 | -0.89147 | -2.0484 | -2.0905 | -2.6653 | -3.3374 | 0.98575 | 0.87054 | 0.69739 | 0.41206 | 0.089863 | -0.31558 | -0.81386 | -1.3578 | -1.7007 | -2.059 | -3.5108 | -3.5977 | -4.3131 | -5.0215
| COUPAR ANGUS | ST |  |  |  | 1.6081 | 1.5611 | 1.49 | 1.273 | 1.0885 | 0.92702 | 0.59149 | 0.30689 | 0.049014 | -0.17252 | -1.4627 | -2.2076 | -2.9394 | -3.662 | 1.2044 | 1.1779 | 1.137 | 0.92012 | 0.74923 | 0.61166 | 0.2731 | 0.032743 | -0.1855 | -0.34991 | -1.4046 | -2.0511 | -2.6706 | -3.3305 | 1.0914 | 1.0465 | 0.98137 | 0.73582 | 0.53379 | 0.36317 | -0.016001 | -0.30149 | -0.56916 | -0.78831 | -1.9664 | -2.7274 | -3.4613 | -4.2073
| COUPAR ANGUS | FS |  |  |  | 1.6204 | 1.5859 | 1.5317 | 1.4355 | 1.3303 | 1.2074 | 1.0778 | 0.87969 | 0.70132 | 0.51944 | -0.36233 | -1.2636 | -2.101 | -2.5169 | 1.2096 | 1.1888 | 1.156 | 1.0812 | 0.99958 | 0.9056 | 0.80427 | 0.64045 | 0.51339 | 0.38851 | -0.3096 | -0.9622 | -1.6322 | -2.1448 | 1.1033 | 1.0705 | 1.0219 | 0.92334 | 0.81643 | 0.69157 | 0.56206 | 0.3639 | 0.19281 | 0.023157 | -0.7658 | -1.5964 | -2.3747 | -2.7559
CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | NO | 16.6703 | 16.4516 | 16.1623 | 15.6616 | 15.062 | 14.6016 | 14.0341 | 13.4163 | 12.8198 | 12.1995 | 10.9406 | 11.0144 | 10.2078 | 9.4992 | 18.8544 | 18.7303 | 18.5435 | 18.295 | 17.9901 | 17.7588 | 17.4269 | 17.0525 | 16.6534 | 16.217 | 15.2962 | 15.4442 | 14.552 | 13.4178 | 17.8193 | 17.6214 | 17.3434 | 16.8952 | 16.3623 | 15.9415 | 15.3967 | 14.7984 | 14.2173 | 13.5779 | 12.2905 | 12.5525 | 11.7812 | 11.0402
| CRAIGIEBUCKLER | CT |  |  |  | 16.8234 | 16.6904 | 16.5155 | 16.0194 | 15.4359 | 15.0202 | 14.5895 | 14.1531 | 13.6036 | 12.9891 | 11.7906 | 11.1187 | 10.2078 | 9.4992 | 18.9023 | 18.8056 | 18.6709 | 18.3838 | 18.0453 | 17.8148 | 17.5707 | 17.3219 | 16.9768 | 16.5777 | 15.7595 | 15.4442 | 14.552 | 13.4178 | 17.948 | 17.8236 | 17.6521 | 17.1897 | 16.6518 | 16.267 | 15.867 | 15.4616 | 14.9466 | 14.3479 | 13.1617 | 12.6679 | 11.8132 | 11.122
| CRAIGIEBUCKLER | LW |  |  |  | 16.6703 | 16.4516 | 16.1623 | 15.6616 | 15.062 | 14.6016 | 14.0341 | 13.4163 | 12.8198 | 12.1995 | 10.9406 | 11.0144 | 10.2751 | 9.6343 | 18.8544 | 18.7303 | 18.5435 | 18.295 | 17.9901 | 17.7588 | 17.4269 | 17.0525 | 16.6534 | 16.217 | 15.2962 | 15.6918 | 15.0773 | 14.3743 | 17.8193 | 17.6214 | 17.3434 | 16.8952 | 16.3623 | 15.9415 | 15.3967 | 14.7984 | 14.2173 | 13.5779 | 12.2905 | 12.5525 | 11.7812 | 11.0402
| CRAIGIEBUCKLER | ST |  |  |  | 16.8617 | 16.7818 | 16.6856 | 16.5756 | 16.4073 | 16.309 | 16.1877 | 16.037 | 15.8009 | 15.5512 | 14.9817 | 14.141 | 13.0963 | 12.0297 | 18.9189 | 18.8589 | 18.7856 | 18.7011 | 18.5767 | 18.4833 | 18.3683 | 18.2299 | 18.0118 | 17.7947 | 17.2855 | 16.5637 | 15.5148 | 14.2064 | 17.9814 | 17.9104 | 17.8223 | 17.7189 | 17.5657 | 17.46 | 17.3293 | 17.1661 | 16.9043 | 16.6321 | 16.0003 | 15.1967 | 14.1792 | 13.1834
| CRAIGIEBUCKLER | FS |  |  |  | 16.8808 | 16.8113 | 16.7339 | 16.6332 | 16.4797 | 16.3893 | 16.2832 | 16.1627 | 15.9779 | 15.7774 | 15.3109 | 14.5465 | 13.1902 | 12.2333 | 18.9274 | 18.872 | 18.8073 | 18.7309 | 18.6201 | 18.5393 | 18.4437 | 18.333 | 18.1697 | 17.9974 | 17.595 | 16.8809 | 15.4596 | 13.74 | 17.9976 | 17.9367 | 17.8665 | 17.7742 | 17.6382 | 17.546 | 17.4369 | 17.3117 | 17.1219 | 16.9155 | 16.4306 | 15.6936 | 14.4047 | 13.6162
CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 16.9939 | 16.9004 | 16.6896 | 16.4184 | 16.1126 | 15.5335 | 14.675 | 13.8281 | 13.1396 | 12.3799 | 10.818 | 13.8267 | 13.1809 | 12.5783 | 17.4558 | 17.3411 | 17.0969 | 16.7796 | 16.4012 | 15.7003 | 14.8199 | 14.0934 | 13.5336 | 12.9156 | 11.6532 | 14.3629 | 13.7716 | 11.6485 | 16.0234 | 15.867 | 15.6495 | 15.0956 | 14.4841 | 13.5982 | 12.603 | 11.8019 | 11.2481 | 10.4932 | 8.949 | 10.6916 | 9.9585 | 9.2237
| CRAIGINCHES | CT |  |  |  | 16.9939 | 16.9004 | 16.6896 | 16.4184 | 16.1157 | 15.7125 | 15.1284 | 14.6136 | 14.1111 | 13.6568 | 12.6825 | 15.1167 | 14.2611 | 13.8063 | 17.4558 | 17.3411 | 17.0969 | 16.7796 | 16.4489 | 15.97 | 15.4093 | 15.0266 | 14.642 | 14.2921 | 13.5488 | 15.6999 | 14.4948 | 12.7742 | 16.0863 | 15.9919 | 15.6495 | 15.1945 | 14.735 | 14.1424 | 13.4651 | 12.9607 | 12.4679 | 12.0212 | 11.0672 | 12.3271 | 11.5018 | 11.0221
| CRAIGINCHES | LW |  |  |  | 16.9948 | 16.913 | 16.7713 | 16.4655 | 16.1126 | 15.5335 | 14.675 | 13.8281 | 13.1396 | 12.3799 | 10.818 | 13.8267 | 13.1809 | 12.5783 | 17.4585 | 17.3628 | 17.196 | 16.8242 | 16.4012 | 15.7003 | 14.8199 | 14.0934 | 13.5336 | 12.9156 | 11.6532 | 14.3629 | 13.7716 | 13.0523 | 16.0234 | 15.867 | 15.6629 | 15.0956 | 14.4841 | 13.5982 | 12.603 | 11.8019 | 11.2481 | 10.4932 | 8.949 | 10.6916 | 9.9585 | 9.2237
| CRAIGINCHES | ST |  |  |  | 17.0072 | 16.9678 | 16.9185 | 16.6746 | 16.4696 | 16.2833 | 15.8745 | 15.6303 | 15.3184 | 15.0206 | 14.0008 | 15.5184 | 15.1212 | 14.7607 | 17.4721 | 17.4253 | 17.367 | 17.0661 | 16.8152 | 16.5888 | 16.0864 | 15.792 | 15.4219 | 15.0665 | 14.1062 | 15.6856 | 14.8356 | 12.8286 | 16.0989 | 16.0619 | 16.0157 | 15.7019 | 15.4102 | 15.1321 | 14.5653 | 14.1909 | 13.7233 | 13.2574 | 12.0938 | 13.7958 | 12.8129 | 11.7858
| CRAIGINCHES | FS |  |  |  | 17.0157 | 16.9866 | 16.9511 | 16.87 | 16.7789 | 16.6705 | 16.5481 | 16.4159 | 16.2677 | 16.1117 | 15.7268 | 16.4879 | 16.3497 | 16.1231 | 17.4813 | 17.446 | 17.4029 | 17.3029 | 17.1908 | 17.0575 | 16.9072 | 16.7454 | 16.5642 | 16.3737 | 15.9183 | 16.8012 | 14.9172 | 11.6485 | 16.1069 | 16.0796 | 16.0463 | 15.9587 | 15.8265 | 15.6603 | 15.4715 | 15.2639 | 15.027 | 14.7719 | 14.161 | 14.7386 | 14.068 | 13.4093
CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | NO | 8.1835 | 7.5052 | 6.7486 | 5.0616 | 4.0006 | 2.9076 | 1.7409 | 0.20445 | -0.95241 | -2.1802 | -4.2824 | -4.4456 | -5.4765 | -6.2688 | 9.2216 | 8.8071 | 8.3245 | 7.3054 | 6.6693 | 6.0222 | 5.3239 | 4.296 | 3.5549 | 2.746 | 1.2875 | 0.85748 | -0.19617 | -1.4242 | 8.2778 | 7.7114 | 7.0524 | 5.6825 | 4.7675 | 3.8367 | 2.8024 | 1.4206 | 0.3704 | -0.73421 | -2.6714 | -2.8924 | -3.9181 | -4.8803
| CRAIGTON | CT |  |  |  | 8.3581 | 7.812 | 7.207 | 5.6165 | 4.5598 | 3.4755 | 2.3663 | 0.99542 | -0.18493 | -1.4456 | -3.5966 | -4.4456 | -5.4765 | -6.2688 | 9.29 | 8.9318 | 8.5224 | 7.5295 | 6.849 | 6.1473 | 5.4287 | 4.5075 | 3.7471 | 2.9222 | 1.437 | 0.85748 | -0.19617 | -1.4242 | 8.4248 | 7.9675 | 7.443 | 6.1182 | 5.1766 | 4.2135 | 3.2255 | 2.0238 | 0.96304 | -0.17283 | -2.1368 | -2.8924 | -3.9181 | -4.7569
| CRAIGTON | LW |  |  |  | 8.1835 | 7.5052 | 6.7486 | 5.0616 | 4.0006 | 2.9076 | 1.7409 | 0.20445 | -0.95241 | -2.1802 | -4.2824 | -4.1211 | -5.0875 | -6.1674 | 9.2216 | 8.8071 | 8.3245 | 7.3054 | 6.6693 | 6.0222 | 5.3239 | 4.296 | 3.5549 | 2.746 | 1.2875 | 1.5519 | 0.56582 | -0.70348 | 8.2778 | 7.7114 | 7.0524 | 5.6825 | 4.7675 | 3.8367 | 2.8024 | 1.4206 | 0.3704 | -0.73421 | -2.6714 | -2.4809 | -3.5765 | -4.8803
| CRAIGTON | ST |  |  |  | 8.4089 | 7.9285 | 7.426 | 6.1664 | 5.5019 | 4.8404 | 4.1085 | 3.1406 | 2.3217 | 1.5185 | 0.028932 | -1.2216 | -2.4782 | -3.6408 | 9.3111 | 8.9979 | 8.6685 | 7.8022 | 7.3052 | 6.8171 | 6.2345 | 5.4634 | 4.8121 | 4.216 | 3.0608 | 1.9949 | 0.66146 | -0.83634 | 8.4685 | 8.0763 | 7.6587 | 6.6277 | 6.0446 | 5.4692 | 4.7989 | 3.936 | 3.1795 | 2.4696 | 1.1029 | -0.10725 | -1.3985 | -2.6196
| CRAIGTON | FS |  |  |  | 8.5478 | 8.1638 | 7.7779 | 6.8158 | 6.2268 | 5.6857 | 5.0712 | 4.2886 | 3.6297 | 2.8297 | 1.5492 | 0.20208 | -1.3418 | -2.1521 | 9.3992 | 9.1384 | 8.8694 | 8.2386 | 7.814 | 7.423 | 6.9813 | 6.3658 | 5.8786 | 5.2972 | 4.3237 | 3.2636 | 1.769 | 0.40163 | 8.5855 | 8.2775 | 7.962 | 7.1845 | 6.7032 | 6.2436 | 5.7254 | 5.0407 | 4.4629 | 3.781 | 2.6422 | 1.4296 | -0.014299 | -0.74581
BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 5.5154 | 5.1538 | 4.7135 | 4.119 | 3.4715 | 2.85 | 2.1628 | 1.4327 | 0.73892 | -0.0078638 | -1.7788 | -2.0816 | -3.1352 | -3.7721 | 8.7651 | 8.548 | 8.2506 | 7.9233 | 7.5521 | 7.1473 | 6.7231 | 6.2793 | 5.7888 | 5.2588 | 3.9641 | 3.7196 | 2.9021 | 2.0187 | 6.2989 | 5.984 | 5.565 | 5.057 | 4.4928 | 3.9627 | 3.2903 | 2.5493 | 1.8635 | 1.1288 | -0.57797 | -0.7325 | -1.6879 | -2.2781
| CRIEFF | CT |  |  |  | 5.7 | 5.4422 | 5.1188 | 4.4911 | 3.8165 | 3.1552 | 2.502 | 1.8804 | 1.2481 | 0.49601 | -1.2761 | -2.0464 | -3.1352 | -3.7721 | 8.8283 | 8.6503 | 8.4091 | 8.0121 | 7.5691 | 7.1473 | 6.7231 | 6.3493 | 5.8984 | 5.3736 | 4.0917 | 3.7196 | 2.9021 | 2.0187 | 6.4331 | 6.2005 | 5.8882 | 5.311 | 4.678 | 4.0855 | 3.4934 | 2.9281 | 2.2875 | 1.5608 | -0.12093 | -0.7325 | -1.6879 | -2.2781
| CRIEFF | LW |  |  |  | 5.5154 | 5.1538 | 4.7135 | 4.119 | 3.4715 | 2.85 | 2.1628 | 1.4327 | 0.73892 | -0.0078638 | -1.7788 | -2.0816 | -2.9207 | -3.4265 | 8.7651 | 8.548 | 8.2506 | 7.9233 | 7.5521 | 7.2082 | 6.7649 | 6.2793 | 5.7888 | 5.2588 | 3.9641 | 4.1811 | 3.6407 | 3.1552 | 6.2989 | 5.984 | 5.565 | 5.057 | 4.4928 | 3.9627 | 3.2903 | 2.5493 | 1.8635 | 1.1288 | -0.57797 | -0.63458 | -1.4173 | -1.9705
| CRIEFF | ST |  |  |  | 5.814 | 5.6427 | 5.4468 | 5.2023 | 4.9342 | 4.677 | 4.366 | 4.0975 | 3.7555 | 3.3835 | 2.206 | 1.1718 | 0.20343 | -0.8507 | 8.8714 | 8.7467 | 8.6017 | 8.3886 | 8.1583 | 7.9356 | 7.6356 | 7.3874 | 7.058 | 6.7257 | 5.7295 | 4.8227 | 3.9431 | 2.8894 | 6.5136 | 6.3596 | 6.1795 | 5.9308 | 5.6589 | 5.395 | 5.0526 | 4.7562 | 4.3701 | 3.9729 | 2.8377 | 1.7463 | 0.86154 | -0.018096
| CRIEFF | FS |  |  |  | 5.852 | 5.7121 | 5.5501 | 5.3535 | 5.1246 | 4.897 | 4.6813 | 4.4575 | 4.1772 | 3.88 | 3.0363 | 1.6567 | 0.18733 | -0.60259 | 8.8975 | 8.7922 | 8.6691 | 8.5202 | 8.3421 | 8.1605 | 7.9774 | 7.7829 | 7.5401 | 7.2788 | 6.5501 | 5.4519 | 3.9734 | 2.6033 | 6.546 | 6.4195 | 6.2705 | 6.0857 | 5.8673 | 5.6465 | 5.4274 | 5.1946 | 4.9059 | 4.5968 | 3.7754 | 2.5194 | 1.1508 | 0.54029
PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | NO | 0.19561 | 0.19214 | 0.18488 | 0.17669 | 0.16431 | 0.14372 | 0.10176 | 0.068815 | 0.043441 | 0.0055162 | -0.0627 | -0.1137 | -0.16749 | -0.19888 | 0.38364 | 0.376 | 0.36351 | 0.35001 | 0.32114 | 0.29164 | 0.26155 | 0.23974 | 0.21489 | 0.18022 | 0.11595 | 0.062327 | 0.014584 | -0.031718 | 0.18523 | 0.17848 | 0.16705 | 0.14638 | 0.12718 | 0.09423 | 0.059253 | 0.030622 | 0.014726 | -0.0081429 | -0.071935 | -0.1218 | -0.18172 | -0.21938
| CRINAN | CT |  |  |  | 0.19615 | 0.19317 | 0.18742 | 0.17669 | 0.16431 | 0.14372 | 0.10176 | 0.068815 | 0.043441 | 0.0055162 | -0.0627 | -0.1137 | -0.16749 | -0.19888 | 0.3872 | 0.38103 | 0.37131 | 0.3503 | 0.32114 | 0.29164 | 0.26155 | 0.23974 | 0.21489 | 0.18022 | 0.11595 | 0.062327 | 0.014584 | -0.031718 | 0.18561 | 0.18344 | 0.17925 | 0.15759 | 0.12941 | 0.09423 | 0.059253 | 0.030622 | 0.014726 | -0.0081429 | -0.071935 | -0.1218 | -0.18172 | -0.21938
| CRINAN | LW |  |  |  | 0.19561 | 0.19214 | 0.18488 | 0.17884 | 0.17153 | 0.16322 | 0.1244 | 0.083466 | 0.050058 | 0.016787 | -0.054457 | -0.0906 | -0.1361 | -0.18653 | 0.38364 | 0.376 | 0.36351 | 0.35001 | 0.33143 | 0.31587 | 0.2892 | 0.25993 | 0.23013 | 0.19895 | 0.13652 | 0.11115 | 0.065079 | 0.006018 | 0.18523 | 0.17848 | 0.16705 | 0.14638 | 0.12718 | 0.10953 | 0.087279 | 0.057784 | 0.037106 | 0.017889 | -0.058732 | -0.090399 | -0.14537 | -0.20786
| CRINAN | ST |  |  |  | 0.19611 | 0.1947 | 0.19267 | 0.18322 | 0.17489 | 0.1677 | 0.15221 | 0.14302 | 0.12733 | 0.11481 | 0.07776 | -0.042225 | -0.099672 | -0.1436 | 0.38833 | 0.38539 | 0.38204 | 0.36867 | 0.35578 | 0.34512 | 0.32386 | 0.30813 | 0.28384 | 0.26041 | 0.20828 | 0.086195 | 0.027515 | -0.02655 | 0.18559 | 0.18456 | 0.1831 | 0.17274 | 0.16433 | 0.15755 | 0.14094 | 0.13277 | 0.11735 | 0.10684 | 0.074131 | -0.052853 | -0.11552 | -0.1645
| CRINAN | FS |  |  |  | 0.19624 | 0.19508 | 0.19341 | 0.18986 | 0.18556 | 0.18089 | 0.17557 | 0.16978 | 0.16159 | 0.1534 | 0.13296 | 0.029306 | -0.061356 | -0.078822 | 0.38962 | 0.38716 | 0.38426 | 0.37752 | 0.36996 | 0.36155 | 0.35305 | 0.34312 | 0.32973 | 0.31265 | 0.27825 | 0.18245 | 0.096323 | 0.065354 | 0.18569 | 0.18484 | 0.18364 | 0.18035 | 0.17652 | 0.1723 | 0.16762 | 0.1627 | 0.15531 | 0.14331 | 0.12745 | 0.035104 | -0.063826 | -0.081899
PORT ANN | CROMALT | MINIMUM HEADROOM | NN 0839507755 | YES | NO | 1.1336 | 0.73396 | 0.29849 | 0.22028 | 0.09937 | 0.037714 | -0.020842 | -0.086694 | -0.1358 | -0.17622 | -0.27125 | -0.18764 | -0.27711 | -0.35363 | 1.4029 | 0.96665 | 0.48929 | 0.40817 | 0.2788 | 0.22041 | 0.18155 | 0.14785 | 0.10495 | 0.068723 | -0.015824 | -0.041304 | -0.15745 | -0.27876 | 1.4172 | 1.0057 | 0.57249 | 0.48605 | 0.35717 | 0.29045 | 0.23463 | 0.17357 | 0.13224 | 0.090989 | 0.0053919 | -0.03358 | -0.13433 | -0.22425
| CROMALT | CT |  |  |  | 1.1935 | 0.81997 | 0.40389 | 0.29607 | 0.18559 | 0.076366 | -0.020842 | -0.086694 | -0.1358 | -0.17622 | -0.27125 | -0.18764 | -0.27711 | -0.35363 | 1.4609 | 1.0537 | 0.62172 | 0.51468 | 0.40348 | 0.29423 | 0.20414 | 0.14785 | 0.10495 | 0.068723 | -0.015824 | -0.026026 | -0.11217 | -0.20068 | 1.4745 | 1.1002 | 0.70226 | 0.58943 | 0.46878 | 0.34822 | 0.24251 | 0.17357 | 0.13224 | 0.090989 | 0.0053919 | -0.03358 | -0.13433 | -0.22425
| CROMALT | LW |  |  |  | 1.1336 | 0.73396 | 0.29849 | 0.22028 | 0.09937 | 0.037714 | -0.013858 | -0.04951 | -0.087049 | -0.12639 | -0.20486 | -0.064587 | -0.1848 | -0.33928 | 1.4029 | 0.96665 | 0.48929 | 0.40817 | 0.2788 | 0.22041 | 0.18155 | 0.16514 | 0.14371 | 0.12195 | 0.058676 | 0.13545 | 0.0037 | -0.18647 | 1.4172 | 1.0057 | 0.57249 | 0.48605 | 0.35717 | 0.29045 | 0.23463 | 0.19303 | 0.15478 | 0.1183 | 0.040706 | 0.12135 | -0.023055 | -0.21525
| CROMALT | ST |  |  |  | 1.2055 | 0.85288 | 0.45006 | 0.34046 | 0.23558 | 0.15363 | 0.064661 | 0.010519 | -0.041091 | -0.081358 | -0.1821 | -0.13878 | -0.23549 | -0.33169 | 1.4675 | 1.0759 | 0.64453 | 0.52339 | 0.4112 | 0.32766 | 0.23644 | 0.19031 | 0.14726 | 0.11361 | 0.022026 | -0.041304 | -0.15745 | -0.27876 | 1.486 | 1.1314 | 0.74223 | 0.63136 | 0.52947 | 0.45242 | 0.36334 | 0.31425 | 0.26249 | 0.22536 | 0.14656 | 0.032961 | -0.084461 | -0.20787
| CROMALT | FS |  |  |  | 1.3591 | 1.0929 | 0.79841 | 0.71943 | 0.63929 | 0.56768 | 0.50532 | 0.44236 | 0.37255 | 0.30298 | 0.14763 | 0.018424 | -0.015344 | -0.0428 | 1.6411 | 1.3429 | 1.0226 | 0.94139 | 0.85919 | 0.7863 | 0.7233 | 0.66017 | 0.58942 | 0.51994 | 0.36582 | 0.14353 | 0.098847 | 0.056568 | 1.6306 | 1.3744 | 1.0777 | 0.9989 | 0.91931 | 0.85113 | 0.7892 | 0.73053 | 0.66293 | 0.5928 | 0.45111 | 0.21711 | 0.15805 | 0.12998
ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | NO | 7.044 | 6.0328 | 5.2011 | 3.9545 | 3.2696 | 2.6059 | 1.6911 | 0.78763 | 0.1176 | -0.48836 | -1.6065 | -1.5028 | -2.6491 | -3.1846 | 8.2635 | 7.1842 | 6.3736 | 5.3004 | 4.8705 | 4.4717 | 4.043 | 3.5938 | 3.2801 | 2.985 | 2.3875 | 2.6445 | 2.0081 | 1.4912 | 7.4936 | 6.5476 | 5.7615 | 4.6301 | 4.0283 | 3.4478 | 2.6963 | 1.8982 | 1.3007 | 0.74772 | -0.28527 | -0.12262 | -1.1351 | -1.6115
| CROSSHILLS | CT |  |  |  | 7.2762 | 6.4264 | 5.7354 | 4.5212 | 3.8527 | 3.2428 | 2.4165 | 1.6338 | 0.93439 | 0.29293 | -0.90775 | -1.5028 | -2.6491 | -3.1846 | 8.4012 | 7.4449 | 6.7217 | 5.6719 | 5.255 | 4.8806 | 4.4298 | 3.9969 | 3.6461 | 3.3526 | 2.7577 | 2.6445 | 2.0081 | 1.4912 | 7.5912 | 6.7448 | 6.0304 | 4.9747 | 4.5094 | 4.0442 | 3.3225 | 2.6323 | 2.0106 | 1.4321 | 0.34216 | -0.12262 | -1.1351 | -1.6115
| CROSSHILLS | LW |  |  |  | 7.044 | 6.0328 | 5.2011 | 3.9545 | 3.2696 | 2.6059 | 1.6911 | 0.78763 | 0.1176 | -0.48836 | -1.6065 | -1.4806 | -2.1041 | -2.3445 | 8.2635 | 7.1842 | 6.3736 | 5.3004 | 4.8705 | 4.4717 | 4.043 | 3.5938 | 3.2801 | 2.985 | 2.3875 | 2.8083 | 2.5216 | 2.3639 | 7.4936 | 6.5476 | 5.7615 | 4.6301 | 4.0283 | 3.4478 | 2.6963 | 1.8982 | 1.3007 | 0.74772 | -0.28527 | -0.083265 | -0.63981 | -0.86881
| CROSSHILLS | ST |  |  |  | 7.3392 | 6.5613 | 5.982 | 5.1052 | 4.7795 | 4.4736 | 4.021 | 3.5836 | 3.2068 | 2.8777 | 2.1516 | 1.6164 | 0.76836 | -0.17545 | 8.4276 | 7.5111 | 6.8515 | 5.9433 | 5.6659 | 5.4198 | 5.1159 | 4.8119 | 4.5752 | 4.3846 | 3.9444 | 3.8052 | 3.2339 | 2.5393 | 7.6126 | 6.8398 | 6.2503 | 5.3847 | 5.1019 | 4.8214 | 4.451 | 4.0564 | 3.7031 | 3.3634 | 2.5493 | 2.6598 | 1.8938 | 1.0244
| CROSSHILLS | FS |  |  |  | 7.5427 | 6.9481 | 6.5042 | 5.8115 | 5.4788 | 5.2255 | 4.7939 | 4.4195 | 4.0498 | 3.6117 | 2.8583 | 1.771 | 0.63279 | -0.16746 | 8.6245 | 7.9683 | 7.4657 | 6.7614 | 6.4718 | 6.2759 | 5.9705 | 5.7079 | 5.4615 | 5.1217 | 4.5748 | 3.9092 | 3.035 | 2.0696 | 7.8051 | 7.2157 | 6.7707 | 6.1156 | 5.84 | 5.6241 | 5.292 | 4.9894 | 4.699 | 4.3146 | 3.6356 | 2.8063 | 1.791 | 1.066
KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | NO | 6.2063 | 6.0912 | 5.9503 | 5.726 | 5.4947 | 5.2819 | 5.0225 | 4.7066 | 4.4464 | 4.1694 | 3.5708 | 2.8321 | 2.0994 | 1.2285 | 6.2631 | 6.2065 | 6.1304 | 6.0234 | 5.9116 | 5.716 | 5.5078 | 5.3337 | 5.1401 | 4.9208 | 4.4756 | 3.8862 | 3.2267 | 2.1657 | 6.1373 | 6.0373 | 5.9139 | 5.7192 | 5.5171 | 5.329 | 5.0546 | 4.8018 | 4.5316 | 4.2291 | 3.658 | 2.9076 | 2.1249 | 1.0053
| CULLEN | CT |  |  |  | 6.2852 | 6.2177 | 6.123 | 5.8716 | 5.6123 | 5.3382 | 5.0471 | 4.7765 | 4.4949 | 4.1747 | 3.5708 | 2.8321 | 2.0994 | 1.5333 | 6.2925 | 6.2545 | 6.1972 | 6.06 | 5.912 | 5.716 | 5.5078 | 5.3337 | 5.1401 | 4.9208 | 4.4756 | 3.8862 | 3.2267 | 2.5264 | 6.2067 | 6.1495 | 6.0687 | 5.8462 | 5.6135 | 5.3426 | 5.0546 | 4.8018 | 4.5316 | 4.2291 | 3.658 | 2.9076 | 2.1249 | 1.4789
| CULLEN | LW |  |  |  | 6.2063 | 6.0912 | 5.9503 | 5.726 | 5.4947 | 5.2819 | 5.0225 | 4.7066 | 4.4464 | 4.1694 | 3.6345 | 3.1863 | 2.283 | 1.2285 | 6.2631 | 6.2065 | 6.1304 | 6.0234 | 5.9116 | 5.8113 | 5.6785 | 5.4893 | 5.3128 | 5.1239 | 4.7136 | 4.3786 | 3.4333 | 2.1657 | 6.1373 | 6.0373 | 5.9139 | 5.7192 | 5.5171 | 5.329 | 5.1008 | 4.8162 | 4.5723 | 4.3128 | 3.8139 | 3.3538 | 2.3006 | 1.0053
| CULLEN | ST |  |  |  | 6.3089 | 6.2685 | 6.2187 | 6.071 | 5.9491 | 5.8475 | 5.6616 | 5.4978 | 5.275 | 5.1149 | 4.7677 | 3.9464 | 3.0419 | 2.0978 | 6.3018 | 6.2789 | 6.2507 | 6.1195 | 6.0163 | 5.9346 | 5.751 | 5.6137 | 5.3932 | 5.2617 | 4.9688 | 4.1898 | 3.2829 | 2.3059 | 6.2285 | 6.1961 | 6.1555 | 6.0051 | 5.8853 | 5.7877 | 5.5877 | 5.4302 | 5.1897 | 5.034 | 4.6954 | 3.8648 | 2.8914 | 1.8385
| CULLEN | FS |  |  |  | 6.3206 | 6.2888 | 6.2476 | 6.1671 | 6.0855 | 6.0056 | 5.9246 | 5.8014 | 5.6671 | 5.5382 | 5.2638 | 4.6387 | 4.0207 | 3.6402 | 6.3069 | 6.2879 | 6.2637 | 6.2085 | 6.1516 | 6.0935 | 6.033 | 5.9363 | 5.8246 | 5.7237 | 5.5075 | 5.0511 | 4.4912 | 4.0066 | 6.2386 | 6.2139 | 6.1809 | 6.1105 | 6.0383 | 5.9653 | 5.8919 | 5.7768 | 5.6427 | 5.5185 | 5.2556 | 4.7008 | 4.1451 | 3.7764
INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 8.6415 | 7.3634 | 8.4846 | 7.2852 | 5.8799 | 4.5952 | 3.1836 | 1.7426 | 0.48088 | -0.83611 | -3.0158 | -3.0914 | -4.829 | -5.9075 | 10.8327 | 9.848 | 11.5628 | 10.8855 | 10.042 | 9.2941 | 8.4449 | 7.6176 | 6.8674 | 6.0746 | 4.7032 | 5.1271 | 3.8487 | 2.4851 | 10.6777 | 9.5529 | 11.1032 | 10.051 | 8.8063 | 7.6485 | 6.3532 | 5.0463 | 3.9051 | 2.7095 | 0.68354 | 0.72843 | -0.72676 | -1.7524
| CULLODEN | CT |  |  |  | 9.0166 | 7.9628 | 9.3066 | 8.1718 | 6.9468 | 5.7966 | 4.6754 | 3.5792 | 2.3379 | 0.9991 | -1.3046 | -2.8897 | -4.829 | -5.9075 | 11.0395 | 10.1744 | 12.0014 | 11.3285 | 10.6009 | 9.9192 | 9.265 | 8.6843 | 8.004 | 7.2478 | 5.887 | 5.1867 | 3.8487 | 2.4851 | 11.0107 | 10.08 | 11.8279 | 10.8312 | 9.75 | 8.7232 | 7.7162 | 6.7563 | 5.6582 | 4.4658 | 2.3755 | 1.0387 | -0.72676 | -1.7524
| CULLODEN | LW |  |  |  | 8.6415 | 7.3634 | 8.4846 | 7.2852 | 5.8799 | 4.5952 | 3.1836 | 1.7426 | 0.48088 | -0.83611 | -3.0158 | -3.0914 | -4.5505 | -5.4329 | 10.8327 | 9.848 | 11.5628 | 10.8855 | 10.042 | 9.2941 | 8.4449 | 7.6176 | 6.8674 | 6.0746 | 4.7032 | 5.1271 | 4.2021 | 3.3611 | 10.6777 | 9.5529 | 11.1032 | 10.051 | 8.8063 | 7.6485 | 6.3532 | 5.0463 | 3.9051 | 2.7095 | 0.68354 | 0.72843 | -0.69066 | -1.6646
| CULLODEN | ST |  |  |  | 9.1497 | 8.2101 | 9.7102 | 9.1465 | 8.5719 | 8.0585 | 7.5103 | 7.0166 | 6.4553 | 5.8619 | 4.7731 | 3.5729 | 2.0957 | 0.19583 | 11.0927 | 10.2915 | 12.2162 | 11.782 | 11.3492 | 10.973 | 10.5332 | 10.1786 | 9.7692 | 9.352 | 8.5142 | 7.5475 | 6.2486 | 4.5158 | 11.1285 | 10.3036 | 12.1992 | 11.7027 | 11.2025 | 10.7592 | 10.2521 | 9.8203 | 9.3198 | 8.7995 | 7.7957 | 6.6855 | 5.2756 | 3.4985
| CULLODEN | FS |  |  |  | 9.5381 | 8.7891 | 10.432 | 9.9412 | 9.4365 | 8.9541 | 8.4866 | 7.9915 | 7.4199 | 6.8362 | 5.75 | 4.0514 | 2.2408 | 0.87651 | 11.4562 | 10.8237 | 12.87 | 12.5258 | 12.1724 | 11.8336 | 11.5001 | 11.1458 | 10.7368 | 10.3135 | 9.4658 | 8.0764 | 6.2773 | 4.165 | 11.482 | 10.8317 | 12.8585 | 12.4494 | 12.0272 | 11.6212 | 11.2237 | 10.8016 | 10.3085 | 9.8043 | 8.8276 | 7.3058 | 5.6358 | 4.4344
CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | NO | 16.939 | 16.6327 | 16.2264 | 15.6835 | 15.1042 | 14.4876 | 13.7298 | 12.9448 | 12.2903 | 11.646 | 10.3154 | 11.2682 | 10.6084 | 10.1373 | 18.0461 | 17.8814 | 17.6439 | 17.3392 | 17.0052 | 16.6218 | 16.1248 | 15.6274 | 15.1954 | 14.7559 | 13.893 | 14.5628 | 13.8608 | 13.012 | 17.3559 | 17.0914 | 16.7222 | 16.2277 | 15.6926 | 15.1112 | 14.3714 | 13.6087 | 12.9564 | 12.2997 | 11.0132 | 12.1063 | 11.5562 | 11.1254
| CULTER | CT |  |  |  | 17.0707 | 16.864 | 16.5783 | 16.0437 | 15.47 | 14.8846 | 14.2652 | 13.6919 | 13.1062 | 12.5082 | 11.3309 | 11.3534 | 10.6084 | 10.1373 | 18.0861 | 17.9563 | 17.7733 | 17.4653 | 17.1245 | 16.7458 | 16.3418 | 16.0061 | 15.6323 | 15.2332 | 14.4375 | 14.5628 | 13.8608 | 13.012 | 17.4622 | 17.2802 | 17.021 | 16.5264 | 15.9881 | 15.4337 | 14.846 | 14.3222 | 13.7632 | 13.1734 | 12.0129 | 12.2103 | 11.5562 | 11.1254
| CULTER | LW |  |  |  | 16.939 | 16.6327 | 16.2264 | 15.6835 | 15.1042 | 14.4876 | 13.7298 | 12.9448 | 12.2903 | 11.646 | 10.3154 | 11.2682 | 10.8072 | 10.4719 | 18.0461 | 17.8814 | 17.6439 | 17.3392 | 17.0052 | 16.6218 | 16.1248 | 15.6274 | 15.1954 | 14.7559 | 13.893 | 14.7827 | 14.4469 | 14.11 | 17.3559 | 17.0914 | 16.7222 | 16.2277 | 15.6926 | 15.1112 | 14.3714 | 13.6087 | 12.9564 | 12.2997 | 11.0132 | 12.1063 | 11.6582 | 11.2894
| CULTER | ST |  |  |  | 17.1539 | 17.0059 | 16.818 | 16.5887 | 16.3646 | 16.1387 | 15.8042 | 15.5251 | 15.2081 | 14.8982 | 14.1632 | 13.7151 | 12.9145 | 12.1666 | 18.1319 | 18.0411 | 17.9264 | 17.7304 | 17.5477 | 17.371 | 17.0681 | 16.8459 | 16.5898 | 16.3428 | 15.7828 | 15.4115 | 14.6172 | 13.6306 | 17.5366 | 17.4135 | 17.2553 | 17.0214 | 16.7963 | 16.5734 | 16.2188 | 15.9382 | 15.6146 | 15.2932 | 14.5718 | 14.1644 | 13.4088 | 12.7159
| CULTER | FS |  |  |  | 17.182 | 17.0641 | 16.9253 | 16.7706 | 16.6104 | 16.4234 | 16.2289 | 16.0154 | 15.758 | 15.5096 | 14.9967 | 14.3779 | 13.2042 | 12.4515 | 18.1448 | 18.0671 | 17.9736 | 17.8637 | 17.7442 | 17.6069 | 17.4582 | 17.2956 | 17.1058 | 16.9159 | 16.5001 | 15.9815 | 14.7845 | 13.3812 | 17.5601 | 17.4632 | 17.3475 | 17.2057 | 17.0549 | 16.8795 | 16.6933 | 16.4878 | 16.2425 | 15.998 | 15.4755 | 14.9279 | 13.8259 | 13.1946
ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | NO | 10.4928 | 10.3587 | 10.1368 | 9.8507 | 9.5586 | 9.0329 | 8.3388 | 7.7323 | 7.2611 | 6.7551 | 5.5647 | 6.6454 | 6.0766 | 5.7164 | 12.754 | 12.6571 | 12.4982 | 12.2861 | 12.0447 | 11.636 | 11.0682 | 10.442 | 9.9267 | 9.3603 | 8.2109 | 11.1259 | 10.9754 | 10.7963 | 12.4719 | 12.3044 | 12.0323 | 11.6872 | 11.3419 | 10.8804 | 10.2969 | 9.7028 | 9.2208 | 8.5373 | 7.1047 | 8.9971 | 8.4634 | 8.1809
| CUMMING STREET | CT |  |  |  | 10.4928 | 10.3587 | 10.1368 | 9.8507 | 9.5586 | 9.1771 | 8.748 | 8.4036 | 7.9903 | 7.5574 | 6.5154 | 7.1849 | 6.2496 | 5.7164 | 12.754 | 12.6571 | 12.4982 | 12.2861 | 12.0447 | 11.6631 | 11.1406 | 10.754 | 10.3362 | 9.9685 | 9.1711 | 11.7452 | 11.5937 | 11.3289 | 12.4719 | 12.3044 | 12.0323 | 11.6872 | 11.3419 | 10.8804 | 10.3598 | 9.9945 | 9.6101 | 9.1654 | 8.1601 | 9.6797 | 8.847 | 8.3653
| CUMMING STREET | LW |  |  |  | 10.4945 | 10.395 | 10.2159 | 9.9592 | 9.6101 | 9.0329 | 8.3388 | 7.7323 | 7.2611 | 6.7551 | 5.5647 | 6.6454 | 6.0766 | 5.806 | 12.758 | 12.6877 | 12.5601 | 12.325 | 12.056 | 11.636 | 11.0682 | 10.442 | 9.9267 | 9.3603 | 8.2109 | 11.1259 | 10.9754 | 10.7963 | 12.4759 | 12.3548 | 12.1372 | 11.8284 | 11.474 | 10.9678 | 10.2969 | 9.7028 | 9.2208 | 8.5373 | 7.1047 | 8.9971 | 8.4634 | 8.1809
| CUMMING STREET | ST |  |  |  | 10.5108 | 10.4614 | 10.3954 | 10.1705 | 9.957 | 9.7456 | 9.3581 | 9.084 | 8.8016 | 8.4724 | 7.4556 | 9.3398 | 8.9378 | 7.9466 | 12.7667 | 12.7306 | 12.683 | 12.4527 | 12.2541 | 12.0728 | 11.6888 | 11.455 | 11.1975 | 10.7954 | 9.732 | 11.5253 | 11.3033 | 11.0578 | 12.4945 | 12.4343 | 12.3554 | 12.0818 | 11.8263 | 11.5735 | 11.1004 | 10.7649 | 10.4174 | 10.0129 | 9.0034 | 11.1762 | 10.9961 | 10.2951
| CUMMING STREET | FS |  |  |  | 10.5197 | 10.4829 | 10.4347 | 10.3394 | 10.2239 | 10.0888 | 9.9349 | 9.7748 | 9.6186 | 9.4403 | 9.0118 | 9.9504 | 9.2523 | 8.5195 | 12.7728 | 12.7454 | 12.7102 | 12.6279 | 12.5318 | 12.4192 | 12.2928 | 12.1621 | 12.041 | 11.9046 | 11.4625 | 12.1776 | 11.9134 | 11.5726 | 12.5053 | 12.4606 | 12.4038 | 12.2915 | 12.1576 | 11.9995 | 11.8187 | 11.6256 | 11.435 | 11.2171 | 10.6916 | 11.9177 | 11.6097 | 10.9636
ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | NO | 5.8788 | 5.8109 | 5.7034 | 5.5405 | 5.3626 | 5.1902 | 4.9966 | 4.7947 | 4.61 | 4.4207 | 4.041 | 3.7497 | 3.4149 | 3.2152 | 6.7162 | 6.6809 | 6.617 | 6.5328 | 6.4392 | 6.328 | 6.2149 | 6.1228 | 6.0033 | 5.8705 | 5.6033 | 5.3919 | 5.1569 | 4.9413 | 6.2744 | 6.2124 | 6.1149 | 5.9699 | 5.8109 | 5.6579 | 5.4806 | 5.2938 | 5.1188 | 4.9386 | 4.5782 | 4.2809 | 3.9678 | 3.7718
| DALCHONZIE | CT |  |  |  | 5.9357 | 5.8951 | 5.8189 | 5.6385 | 5.4484 | 5.2603 | 5.0849 | 4.9301 | 4.7476 | 4.5358 | 4.1252 | 3.7497 | 3.4149 | 3.2152 | 6.7276 | 6.7083 | 6.6645 | 6.559 | 6.4452 | 6.328 | 6.2149 | 6.1245 | 6.009 | 5.8705 | 5.6033 | 5.3919 | 5.1569 | 4.9413 | 6.3245 | 6.2867 | 6.217 | 6.0522 | 5.8773 | 5.7012 | 5.5342 | 5.3915 | 5.2196 | 5.0184 | 4.6292 | 4.2809 | 3.9678 | 3.7718
| DALCHONZIE | LW |  |  |  | 5.8788 | 5.8109 | 5.7034 | 5.5405 | 5.3626 | 5.1902 | 4.9966 | 4.7947 | 4.61 | 4.4207 | 4.041 | 3.8374 | 3.5845 | 3.4069 | 6.7162 | 6.6809 | 6.617 | 6.5328 | 6.4392 | 6.3506 | 6.2407 | 6.1228 | 6.0033 | 5.8785 | 5.63 | 5.5604 | 5.3745 | 5.1872 | 6.2744 | 6.2124 | 6.1149 | 5.9699 | 5.8109 | 5.6579 | 5.4806 | 5.2938 | 5.1188 | 4.9386 | 4.5782 | 4.3998 | 4.1447 | 3.9398
| DALCHONZIE | ST |  |  |  | 5.9569 | 5.9402 | 5.9094 | 5.8433 | 5.7809 | 5.7192 | 5.6382 | 5.5755 | 5.485 | 5.3993 | 5.1927 | 4.7447 | 4.385 | 4.0141 | 6.7321 | 6.7251 | 6.7119 | 6.6648 | 6.6153 | 6.5684 | 6.494 | 6.4429 | 6.3643 | 6.2954 | 6.1304 | 5.7919 | 5.5273 | 5.2299 | 6.3432 | 6.3277 | 6.3011 | 6.2357 | 6.1751 | 6.1167 | 6.0315 | 5.9693 | 5.8763 | 5.7917 | 5.5874 | 5.147 | 4.7997 | 4.4467
| DALCHONZIE | FS |  |  |  | 5.9587 | 5.9469 | 5.9175 | 5.8718 | 5.8237 | 5.7693 | 5.7201 | 5.6688 | 5.5971 | 5.5246 | 5.3592 | 4.9501 | 4.4903 | 4.231 | 6.7335 | 6.7283 | 6.7174 | 6.6931 | 6.6595 | 6.622 | 6.5858 | 6.5478 | 6.4948 | 6.4412 | 6.3178 | 6.0362 | 5.6764 | 5.3995 | 6.3449 | 6.3339 | 6.3086 | 6.2673 | 6.2233 | 6.1738 | 6.1273 | 6.0783 | 6.0091 | 5.9394 | 5.7804 | 5.3961 | 4.9651 | 4.7354
NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | NO | 9.5177 | 9.1327 | 8.7188 | 8.0627 | 7.1886 | 6.1156 | 4.8983 | 3.9451 | 3.3423 | 2.7214 | 1.7842 | 1.5214 | 1.3127 | 1.225 | 9.7761 | 9.5586 | 9.3165 | 8.7619 | 8.0236 | 6.9891 | 5.8486 | 5.0763 | 4.7051 | 4.3186 | 3.6888 | 3.1679 | 2.973 | 2.9003 | 8.811 | 8.5159 | 8.1365 | 7.6373 | 6.8297 | 5.7549 | 4.5606 | 3.7241 | 3.2824 | 2.8151 | 2.0009 | 1.8804 | 1.6468 | 1.5521
| DALCROSS | CT |  |  |  | 9.6063 | 9.2161 | 8.8135 | 8.3689 | 7.8325 | 7.1121 | 6.3103 | 5.7181 | 5.2032 | 4.6451 | 3.7719 | 3.6008 | 3.3304 | 3.2104 | 9.8218 | 9.5826 | 9.3446 | 9.0838 | 8.748 | 8.1692 | 7.5404 | 7.216 | 6.9343 | 6.6366 | 6.1047 | 5.8301 | 5.6662 | 5.5733 | 8.8555 | 8.5159 | 8.1365 | 7.7818 | 7.3413 | 6.677 | 5.9524 | 5.5176 | 5.1484 | 4.8077 | 4.1679 | 4.5046 | 4.2478 | 4.1335
| DALCROSS | LW |  |  |  | 9.5177 | 9.1327 | 8.7188 | 8.0627 | 7.1886 | 6.1156 | 4.8983 | 3.9451 | 3.3423 | 2.7214 | 1.7842 | 1.5214 | 1.3127 | 1.225 | 9.7761 | 9.5586 | 9.3165 | 8.7619 | 8.0236 | 6.9891 | 5.8486 | 5.0763 | 4.7051 | 4.3186 | 3.6888 | 3.1679 | 2.973 | 2.9003 | 8.811 | 8.5301 | 8.2208 | 7.6373 | 6.8297 | 5.7549 | 4.5606 | 3.7241 | 3.2824 | 2.8151 | 2.0009 | 1.8804 | 1.6468 | 1.5521
| DALCROSS | ST |  |  |  | 9.6269 | 9.264 | 8.9433 | 8.4017 | 7.9161 | 7.546 | 6.8306 | 6.4174 | 6.0141 | 5.6412 | 4.9594 | 4.4096 | 4.1665 | 4.0249 | 9.8279 | 9.6033 | 9.411 | 8.9157 | 8.5075 | 8.2274 | 7.5378 | 7.2381 | 6.9669 | 6.75 | 6.3113 | 5.7591 | 5.5673 | 5.4706 | 8.8586 | 8.5702 | 8.3351 | 7.8084 | 7.3554 | 7.0355 | 6.2952 | 5.934 | 5.5897 | 5.2815 | 4.607 | 4.9827 | 4.7556 | 4.6482
| DALCROSS | FS |  |  |  | 9.9264 | 9.6219 | 9.3505 | 9.0679 | 8.7772 | 8.4741 | 8.1436 | 7.8079 | 7.4829 | 7.1594 | 6.5737 | 5.9339 | 5.5447 | 5.4334 | 10.0537 | 9.8605 | 9.6931 | 9.4982 | 9.297 | 9.0823 | 8.8534 | 8.6283 | 8.427 | 8.2315 | 7.8541 | 7.3965 | 7.0988 | 7.0189 | 9.1559 | 8.908 | 8.7046 | 8.501 | 8.2796 | 8.0375 | 7.7773 | 7.5157 | 7.2722 | 7.0276 | 6.513 | 6.7366 | 6.351 | 6.2758
TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.77846 | 0.75231 | 0.7193 | 0.6892 | 0.66764 | 0.6495 | 0.62991 | 0.60812 | 0.59737 | 0.58747 | 0.56516 | 0.55138 | 0.52188 | 0.51202 | 0.84299 | 0.83025 | 0.81422 | 0.79953 | 0.78963 | 0.78156 | 0.77166 | 0.76048 | 0.75286 | 0.74525 | 0.72931 | 0.72022 | 0.70339 | 0.69039 | 0.81232 | 0.79151 | 0.7644 | 0.73992 | 0.72092 | 0.70476 | 0.68695 | 0.66707 | 0.65674 | 0.64707 | 0.62571 | 0.61244 | 0.58725 | 0.57843
| DALMALLY | CT |  |  |  | 0.78843 | 0.76485 | 0.74302 | 0.70651 | 0.68308 | 0.66219 | 0.63802 | 0.61207 | 0.59984 | 0.58802 | 0.56516 | 0.55411 | 0.52188 | 0.51202 | 0.84677 | 0.83528 | 0.82376 | 0.80602 | 0.79459 | 0.78505 | 0.77405 | 0.76228 | 0.75455 | 0.7461 | 0.72996 | 0.72022 | 0.70339 | 0.69064 | 0.82097 | 0.80207 | 0.78454 | 0.75384 | 0.73291 | 0.71438 | 0.69314 | 0.67038 | 0.65932 | 0.6481 | 0.62623 | 0.61523 | 0.58725 | 0.57843
| DALMALLY | LW |  |  |  | 0.77846 | 0.75231 | 0.7193 | 0.6892 | 0.66764 | 0.6495 | 0.62991 | 0.60812 | 0.59737 | 0.58747 | 0.56538 | 0.55138 | 0.53521 | 0.52966 | 0.84299 | 0.83025 | 0.81422 | 0.79953 | 0.78963 | 0.78156 | 0.77166 | 0.76048 | 0.75286 | 0.74525 | 0.72931 | 0.72268 | 0.71669 | 0.7148 | 0.81232 | 0.79151 | 0.7644 | 0.73992 | 0.72092 | 0.70476 | 0.68695 | 0.66707 | 0.65674 | 0.64707 | 0.62571 | 0.61244 | 0.59891 | 0.59404
| DALMALLY | ST |  |  |  | 0.79038 | 0.77289 | 0.75324 | 0.73391 | 0.72303 | 0.71268 | 0.70423 | 0.69347 | 0.68024 | 0.66908 | 0.64426 | 0.59878 | 0.5726 | 0.55453 | 0.8475 | 0.83866 | 0.82887 | 0.81911 | 0.81386 | 0.80877 | 0.80394 | 0.79793 | 0.79069 | 0.784 | 0.76884 | 0.73773 | 0.72152 | 0.70676 | 0.82259 | 0.80923 | 0.79385 | 0.77864 | 0.76913 | 0.75998 | 0.75261 | 0.74322 | 0.73152 | 0.72129 | 0.69818 | 0.65258 | 0.62959 | 0.6147
| DALMALLY | FS |  |  |  | 0.79503 | 0.78358 | 0.76468 | 0.74491 | 0.73772 | 0.7287 | 0.71935 | 0.71183 | 0.69879 | 0.68922 | 0.66875 | 0.60234 | 0.56113 | 0.54665 | 0.84949 | 0.84298 | 0.83357 | 0.82371 | 0.81984 | 0.81535 | 0.81057 | 0.80634 | 0.79979 | 0.7943 | 0.78217 | 0.74524 | 0.71199 | 0.69039 | 0.82593 | 0.81695 | 0.8029 | 0.78803 | 0.782 | 0.77424 | 0.76615 | 0.75957 | 0.74803 | 0.73945 | 0.7209 | 0.6603 | 0.62064 | 0.60881
INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 4.5883 | 4.2306 | 3.7747 | 2.9379 | 2.0916 | 1.2177 | 0.13179 | -0.97418 | -1.915 | -2.91 | -4.8828 | -5.2388 | -7.0936 | -8.4618 | 6.6624 | 6.4655 | 6.2037 | 5.7419 | 5.2614 | 4.7251 | 4.0358 | 3.3664 | 2.784 | 2.1617 | 0.87719 | 1.0972 | -0.54824 | -2.3365 | 6.2192 | 5.9137 | 5.505 | 4.7757 | 3.9803 | 3.1379 | 2.0834 | 1.0255 | 0.12279 | -0.83446 | -2.7308 | -2.9535 | -4.4117 | -5.5753
| DALNEIGH | CT |  |  |  | 4.8766 | 4.6743 | 4.3698 | 3.5719 | 2.7652 | 2.019 | 1.2562 | 0.53373 | -0.34004 | -1.3167 | -3.2415 | -4.6876 | -7.0936 | -8.4618 | 6.7841 | 6.6469 | 6.4351 | 5.9805 | 5.5092 | 5.0466 | 4.5713 | 4.1571 | 3.6402 | 3.0471 | 1.8659 | 1.1364 | -0.54824 | -2.3365 | 6.4469 | 6.2659 | 5.9846 | 5.2848 | 4.5641 | 3.8791 | 3.1534 | 2.4845 | 1.6678 | 0.74671 | -1.0687 | -2.3002 | -4.3568 | -5.5753
| DALNEIGH | LW |  |  |  | 4.5883 | 4.2306 | 3.7747 | 2.9379 | 2.0916 | 1.2177 | 0.13179 | -0.97418 | -1.915 | -2.91 | -4.8828 | -5.2388 | -6.8101 | -7.6588 | 6.6624 | 6.4655 | 6.2037 | 5.7419 | 5.2614 | 4.7251 | 4.0358 | 3.3664 | 2.784 | 2.1617 | 0.87719 | 1.0972 | 0.15448 | -0.62517 | 6.2192 | 5.9137 | 5.505 | 4.7757 | 3.9803 | 3.1379 | 2.0834 | 1.0255 | 0.12279 | -0.83446 | -2.7308 | -2.9535 | -4.4117 | -5.3193
| DALNEIGH | ST |  |  |  | 4.9932 | 4.903 | 4.7943 | 4.5941 | 4.4124 | 4.2261 | 3.9338 | 3.672 | 3.3413 | 2.9786 | 2.1084 | 0.91199 | -0.69082 | -2.8244 | 6.8339 | 6.76 | 6.6707 | 6.4795 | 6.3085 | 6.1366 | 5.8539 | 5.6307 | 5.3456 | 5.049 | 4.3354 | 3.2905 | 1.787 | -0.36132 | 6.5396 | 6.4589 | 6.3588 | 6.1508 | 5.959 | 5.766 | 5.4492 | 5.1817 | 4.8418 | 4.4756 | 3.5952 | 2.4197 | 0.95321 | -0.89054
| DALNEIGH | FS |  |  |  | 5.0351 | 4.9547 | 4.8529 | 4.6764 | 4.5092 | 4.3244 | 4.1215 | 3.8945 | 3.5918 | 3.2653 | 2.532 | 1.0831 | -0.99336 | -2.5215 | 6.8785 | 6.8126 | 6.7277 | 6.5923 | 6.4578 | 6.3082 | 6.14 | 5.9526 | 5.7095 | 5.445 | 4.8313 | 3.5211 | 1.1944 | -1.8582 | 6.5777 | 6.5072 | 6.4156 | 6.256 | 6.0979 | 5.9228 | 5.7285 | 5.5106 | 5.2263 | 4.919 | 4.222 | 2.9304 | 1.0251 | -0.31925
COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | NO | 1.3744 | 1.3245 | 1.2584 | 1.1977 | 1.1249 | 1.0386 | 0.94058 | 0.85705 | 0.79249 | 0.70789 | 0.55589 | 0.48096 | 0.35625 | 0.27777 | 1.9168 | 1.8945 | 1.8614 | 1.8315 | 1.7763 | 1.719 | 1.6578 | 1.6123 | 1.5615 | 1.4949 | 1.3713 | 1.2833 | 1.1866 | 1.0875 | 1.4152 | 1.3734 | 1.325 | 1.2801 | 1.2261 | 1.1622 | 1.0765 | 1.007 | 0.96375 | 0.91623 | 0.82219 | 0.79927 | 0.67929 | 0.59837
| DALRULZION | CT |  |  |  | 1.4044 | 1.3692 | 1.3223 | 1.2277 | 1.1295 | 1.0386 | 0.94058 | 0.85705 | 0.79249 | 0.70789 | 0.55589 | 0.48096 | 0.35625 | 0.27777 | 1.9277 | 1.9108 | 1.8851 | 1.8326 | 1.7763 | 1.719 | 1.6578 | 1.6123 | 1.5615 | 1.4949 | 1.3713 | 1.2833 | 1.1866 | 1.0916 | 1.4444 | 1.4151 | 1.3817 | 1.3119 | 1.2421 | 1.1622 | 1.0765 | 1.007 | 0.96375 | 0.91623 | 0.82219 | 0.79927 | 0.67929 | 0.59837
| DALRULZION | LW |  |  |  | 1.3744 | 1.3245 | 1.2584 | 1.1977 | 1.1249 | 1.0591 | 0.97589 | 0.87748 | 0.80153 | 0.72169 | 0.56477 | 0.52367 | 0.42291 | 0.31004 | 1.9168 | 1.8945 | 1.8614 | 1.8315 | 1.7939 | 1.7613 | 1.7119 | 1.6535 | 1.5959 | 1.5345 | 1.415 | 1.3835 | 1.2896 | 1.1671 | 1.4152 | 1.3734 | 1.325 | 1.2801 | 1.2261 | 1.1738 | 1.121 | 1.0578 | 1.0063 | 0.94898 | 0.83334 | 0.86877 | 0.75855 | 0.62587
| DALRULZION | ST |  |  |  | 1.4208 | 1.4087 | 1.3865 | 1.3458 | 1.3066 | 1.2676 | 1.2095 | 1.164 | 1.1002 | 1.038 | 0.89851 | 0.62656 | 0.48167 | 0.37635 | 1.9338 | 1.9274 | 1.9165 | 1.886 | 1.8574 | 1.8303 | 1.7814 | 1.7482 | 1.6969 | 1.6519 | 1.5476 | 1.3283 | 1.2011 | 1.0875 | 1.4633 | 1.4551 | 1.4387 | 1.4024 | 1.3719 | 1.3427 | 1.2935 | 1.2632 | 1.2133 | 1.1625 | 1.0491 | 0.92674 | 0.78414 | 0.67502
| DALRULZION | FS |  |  |  | 1.4303 | 1.4186 | 1.406 | 1.3796 | 1.3474 | 1.3155 | 1.2812 | 1.2459 | 1.2027 | 1.1537 | 1.0517 | 0.77068 | 0.55948 | 0.5064 | 1.9372 | 1.931 | 1.9239 | 1.9089 | 1.8906 | 1.8707 | 1.8486 | 1.8253 | 1.795 | 1.7626 | 1.6914 | 1.5101 | 1.3447 | 1.2783 | 1.4719 | 1.4631 | 1.4551 | 1.4341 | 1.4091 | 1.3852 | 1.3599 | 1.3357 | 1.3061 | 1.273 | 1.1968 | 1.0861 | 0.90013 | 0.85453
BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | NO | 0.27867 | 0.27488 | 0.26928 | 0.26116 | 0.22997 | 0.20176 | 0.16728 | 0.12443 | 0.10165 | 0.078155 | 0.028276 | 0.009423 | -0.040073 | -0.059727 | 0.43375 | 0.42481 | 0.4127 | 0.40082 | 0.38638 | 0.37282 | 0.35697 | 0.33608 | 0.31929 | 0.30137 | 0.26555 | 0.25536 | 0.23424 | 0.22124 | 0.34398 | 0.32483 | 0.30234 | 0.27857 | 0.24981 | 0.22637 | 0.19466 | 0.15766 | 0.13431 | 0.10986 | 0.059363 | 0.039251 | 0.0035211 | -0.012154
| DALWHINNIE | CT |  |  |  | 0.27911 | 0.27488 | 0.26928 | 0.26116 | 0.24378 | 0.21371 | 0.17274 | 0.13541 | 0.11734 | 0.091816 | 0.042783 | 0.022482 | -0.040073 | -0.059727 | 0.43866 | 0.43222 | 0.4228 | 0.40554 | 0.38682 | 0.37282 | 0.35702 | 0.34219 | 0.32933 | 0.31092 | 0.27586 | 0.25712 | 0.23424 | 0.22124 | 0.35703 | 0.34468 | 0.32767 | 0.29506 | 0.25963 | 0.23124 | 0.19874 | 0.16887 | 0.15072 | 0.12477 | 0.075169 | 0.050459 | 0.0035211 | -0.012154
| DALWHINNIE | LW |  |  |  | 0.27867 | 0.27527 | 0.26937 | 0.2623 | 0.22997 | 0.20176 | 0.16728 | 0.12443 | 0.10165 | 0.078155 | 0.028276 | 0.009423 | -0.024815 | -0.03839 | 0.43375 | 0.42481 | 0.4127 | 0.40082 | 0.38638 | 0.37478 | 0.35697 | 0.33608 | 0.31929 | 0.30137 | 0.26555 | 0.25536 | 0.24518 | 0.24148 | 0.34398 | 0.32483 | 0.30234 | 0.27857 | 0.24981 | 0.22637 | 0.19466 | 0.15766 | 0.13431 | 0.10986 | 0.059363 | 0.039251 | 0.01386 | 0.0040651
| DALWHINNIE | ST |  |  |  | 0.27966 | 0.27815 | 0.27639 | 0.27395 | 0.27084 | 0.26725 | 0.26278 | 0.25456 | 0.23874 | 0.21803 | 0.16791 | 0.074343 | 0.014847 | -0.016868 | 0.44019 | 0.4357 | 0.43202 | 0.42573 | 0.41792 | 0.41164 | 0.40297 | 0.39208 | 0.38182 | 0.36878 | 0.33854 | 0.2769 | 0.25204 | 0.23766 | 0.36085 | 0.35101 | 0.34393 | 0.33111 | 0.31568 | 0.3045 | 0.28879 | 0.26879 | 0.25229 | 0.23113 | 0.18334 | 0.0899 | 0.042758 | 0.019699
| DALWHINNIE | FS |  |  |  | 0.27992 | 0.27871 | 0.27735 | 0.27543 | 0.27311 | 0.27047 | 0.26739 | 0.2638 | 0.25958 | 0.24576 | 0.20629 | 0.076118 | -0.007257 | -0.036369 | 0.44173 | 0.43837 | 0.43555 | 0.43079 | 0.42475 | 0.4186 | 0.41229 | 0.40471 | 0.39629 | 0.38598 | 0.36346 | 0.29769 | 0.24439 | 0.22798 | 0.3648 | 0.3577 | 0.35294 | 0.34297 | 0.33107 | 0.31891 | 0.30728 | 0.29348 | 0.27847 | 0.25971 | 0.2209 | 0.10605 | 0.027344 | 0.0057987
WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | YES | 7.2976 | 7.128 | 6.9024 | 6.471 | 6.029 | 5.5789 | 5.0387 | 4.4536 | 4.0275 | 3.5686 | 2.4609 | 3.574 | 2.4349 | 1.757 | 10.6509 | 10.5639 | 10.4267 | 10.2625 | 9.9963 | 9.6688 | 9.3089 | 8.9631 | 8.598 | 8.2349 | 7.4309 | 7.4536 | 5.3716 | 0.16039 | 8.2072 | 8.1136 | 7.9603 | 7.774 | 7.4976 | 7.0957 | 6.5837 | 5.9174 | 5.3439 | 4.7194 | 3.4571 | 5.18 | 4.0715 | 3.3526
| DENBURN | CT |  |  |  | 7.2976 | 7.201 | 7.0423 | 6.698 | 6.205 | 5.7163 | 5.2123 | 4.7276 | 4.3278 | 3.946 | 3.1285 | 3.574 | 2.4349 | 1.757 | 10.6509 | 10.5639 | 10.4267 | 10.2625 | 9.9963 | 9.6688 | 9.3089 | 8.9631 | 8.598 | 8.2349 | 7.4309 | 7.4536 | 5.554 | 2.8435 | 8.2072 | 8.1136 | 7.9603 | 7.774 | 7.5874 | 7.1752 | 6.7016 | 6.2497 | 5.7896 | 5.3245 | 4.3215 | 5.18 | 4.0715 | 3.3526
| DENBURN | LW |  |  |  | 7.3006 | 7.128 | 6.9024 | 6.471 | 6.029 | 5.5789 | 5.0387 | 4.4536 | 4.0275 | 3.5686 | 2.4609 | 3.9649 | 3.1994 | 2.3396 | 10.6648 | 10.613 | 10.5215 | 10.4121 | 10.192 | 9.9673 | 9.6634 | 9.298 | 8.9341 | 8.5373 | 7.6427 | 9.1616 | 8.4031 | 7.4044 | 8.2108 | 8.1464 | 8.0326 | 7.8839 | 7.4976 | 7.0957 | 6.5837 | 5.9174 | 5.3439 | 4.7194 | 3.4571 | 5.5744 | 4.6996 | 3.6599
| DENBURN | ST |  |  |  | 7.3095 | 7.277 | 7.2361 | 7.1472 | 7.0556 | 6.9559 | 6.7952 | 6.6509 | 6.4099 | 6.1895 | 5.6506 | 6.5348 | 5.5521 | 4.1321 | 10.66 | 10.6232 | 10.5777 | 10.4776 | 10.379 | 10.2758 | 10.1042 | 9.9621 | 9.7118 | 9.5006 | 8.8738 | 8.5431 | 6.5732 | 3.4779 | 8.2194 | 8.1884 | 8.1491 | 8.0531 | 7.9576 | 7.8563 | 7.6846 | 7.5399 | 7.2817 | 7.0585 | 6.5155 | 7.3413 | 6.7667 | 5.3684
| DENBURN | FS |  |  |  | 7.315 | 7.2905 | 7.2612 | 7.2147 | 7.1595 | 7.0938 | 7.0164 | 6.9272 | 6.8023 | 6.672 | 6.3656 | 6.5087 | 5.6829 | 4.7454 | 10.6627 | 10.6291 | 10.5893 | 10.5318 | 10.4647 | 10.3863 | 10.2947 | 10.1519 | 9.9159 | 9.6592 | 9.0482 | 8.1326 | 5.3716 | 0.16039 | 8.2244 | 8.2011 | 8.1729 | 8.1262 | 8.0709 | 8.005 | 7.9275 | 7.8387 | 7.7087 | 7.5761 | 7.266 | 7.8782 | 7.0908 | 6.2803
TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42445123 | YES | YES | 1.3065 | 1.2478 | 1.1968 | 1.1229 | 1.0523 | 0.97574 | 0.8902 | 0.80169 | 0.77091 | 0.72796 | 0.60721 | 0.74288 | 0.68584 | 0.64972 | 1.992 | 1.9596 | 1.924 | 1.8854 | 1.842 | 1.7996 | 1.7553 | 1.6925 | 1.6369 | 1.5758 | 1.4549 | 1.5503 | 1.516 | 1.4835 | 1.798 | 1.7745 | 1.7532 | 1.7168 | 1.6632 | 1.604 | 1.5361 | 1.4657 | 1.4455 | 1.4063 | 1.2226 | 1.3865 | 1.3493 | 1.3198
| DERVAIG | CT |  |  |  | 1.3305 | 1.2915 | 1.2488 | 1.1599 | 1.0622 | 0.97574 | 0.8902 | 0.80169 | 0.77091 | 0.737 | 0.65276 | 0.76243 | 0.68584 | 0.64972 | 2.0004 | 1.976 | 1.9486 | 1.8976 | 1.842 | 1.7996 | 1.7559 | 1.7114 | 1.6713 | 1.6204 | 1.5189 | 1.5549 | 1.516 | 1.4835 | 1.7988 | 1.794 | 1.7786 | 1.7355 | 1.6726 | 1.604 | 1.5361 | 1.4657 | 1.4455 | 1.4267 | 1.3187 | 1.4063 | 1.3493 | 1.3198
| DERVAIG | LW |  |  |  | 1.3065 | 1.2478 | 1.1968 | 1.1229 | 1.0523 | 0.98774 | 0.90322 | 0.81624 | 0.77586 | 0.72796 | 0.60721 | 0.74288 | 0.70054 | 0.69154 | 1.992 | 1.9596 | 1.924 | 1.8854 | 1.8458 | 1.811 | 1.7553 | 1.6925 | 1.6369 | 1.5758 | 1.4549 | 1.5503 | 1.5336 | 1.5305 | 1.798 | 1.7745 | 1.7532 | 1.7168 | 1.6632 | 1.6123 | 1.5491 | 1.4851 | 1.4589 | 1.4063 | 1.2226 | 1.3865 | 1.3568 | 1.351
| DERVAIG | ST |  |  |  | 1.3593 | 1.3331 | 1.3174 | 1.3019 | 1.276 | 1.2613 | 1.2378 | 1.2078 | 1.1705 | 1.1323 | 1.0406 | 1.0133 | 0.97291 | 0.93085 | 2.0082 | 1.9911 | 1.9789 | 1.9652 | 1.9471 | 1.9306 | 1.909 | 1.8829 | 1.8516 | 1.8157 | 1.7296 | 1.6368 | 1.5955 | 1.5657 | 1.8003 | 1.7966 | 1.7949 | 1.7932 | 1.7911 | 1.7894 | 1.7869 | 1.7795 | 1.7473 | 1.713 | 1.6308 | 1.5791 | 1.5329 | 1.5062
| DERVAIG | FS |  |  |  | 1.3634 | 1.3423 | 1.3277 | 1.3033 | 1.2829 | 1.2564 | 1.2342 | 1.21 | 1.1819 | 1.152 | 1.0895 | 0.97932 | 0.8595 | 0.82203 | 2.0106 | 1.9956 | 1.9845 | 1.9692 | 1.9542 | 1.9372 | 1.9198 | 1.8999 | 1.8768 | 1.8512 | 1.7928 | 1.6863 | 1.5601 | 1.521 | 1.8009 | 1.7975 | 1.7958 | 1.7938 | 1.7922 | 1.7903 | 1.7885 | 1.784 | 1.7603 | 1.7342 | 1.6785 | 1.6395 | 1.4638 | 1.439
BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 5.9256 | 5.7142 | 5.4337 | 4.9483 | 4.3884 | 3.7499 | 2.9166 | 2.1048 | 1.57 | 1.0473 | 0.0021297 | 0.5388 | -0.021693 | -0.25401 | 7.7066 | 7.5823 | 7.3895 | 7.0637 | 6.6816 | 6.196 | 5.5503 | 4.957 | 4.5331 | 4.0969 | 3.2234 | 3.9476 | 3.6891 | 3.266 | 7.3163 | 7.2312 | 7.0269 | 6.7235 | 6.3473 | 5.8098 | 5.0899 | 4.416 | 3.9352 | 3.4354 | 2.4062 | 3.1854 | 2.6934 | 2.5108
| DINGWALL | CT |  |  |  | 5.981 | 5.9037 | 5.7149 | 5.2394 | 4.7057 | 4.151 | 3.5214 | 2.9462 | 2.4598 | 1.9669 | 0.97962 | 1.1074 | 0.19068 | -0.25401 | 7.7564 | 7.6575 | 7.4944 | 7.1846 | 6.826 | 6.4309 | 5.9895 | 5.6342 | 5.2911 | 4.9107 | 4.1417 | 4.4286 | 3.8423 | 3.266 | 7.3163 | 7.2312 | 7.0269 | 6.7235 | 6.3653 | 5.9322 | 5.45 | 4.9819 | 4.5566 | 4.1805 | 3.3534 | 3.8767 | 3.0772 | 2.6763
| DINGWALL | LW |  |  |  | 5.9256 | 5.7142 | 5.4337 | 4.9483 | 4.3884 | 3.7499 | 2.9166 | 2.1048 | 1.57 | 1.0473 | 0.0021297 | 0.5388 | -0.021693 | -0.22427 | 7.7066 | 7.5823 | 7.3895 | 7.0637 | 6.6816 | 6.196 | 5.5503 | 4.957 | 4.5331 | 4.0969 | 3.2234 | 3.9476 | 3.6891 | 3.5736 | 7.3184 | 7.2442 | 7.0582 | 6.7287 | 6.3473 | 5.8098 | 5.0899 | 4.416 | 3.9352 | 3.4354 | 2.4062 | 3.1854 | 2.6934 | 2.5108
| DINGWALL | ST |  |  |  | 6.0134 | 5.9781 | 5.935 | 5.7852 | 5.6372 | 5.4715 | 5.1246 | 4.8551 | 4.6114 | 4.3478 | 3.7319 | 3.5307 | 2.9073 | 2.1553 | 7.8044 | 7.7567 | 7.6983 | 7.5023 | 7.3115 | 7.1402 | 6.7969 | 6.5589 | 6.346 | 6.1084 | 5.5399 | 5.2499 | 4.7225 | 4.0594 | 7.3539 | 7.3175 | 7.2727 | 7.0958 | 6.9142 | 6.7419 | 6.3975 | 6.1188 | 5.8527 | 5.5459 | 4.792 | 5.9075 | 5.3269 | 4.6937
| DINGWALL | FS |  |  |  | 6.021 | 5.9935 | 5.9616 | 5.9028 | 5.8203 | 5.6618 | 5.4638 | 5.2491 | 5.043 | 4.839 | 4.3834 | 3.7573 | 2.8165 | 2.1999 | 7.8105 | 7.7706 | 7.7227 | 7.6279 | 7.5087 | 7.3796 | 7.2202 | 7.0469 | 6.8829 | 6.711 | 6.31 | 5.7531 | 4.6932 | 3.6718 | 7.362 | 7.3344 | 7.302 | 7.2365 | 7.152 | 7.0451 | 6.9082 | 6.7264 | 6.554 | 6.3687 | 5.9324 | 6.3998 | 5.3717 | 4.8518
CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.32886 | 0.29618 | 0.25648 | 0.21591 | 0.1765 | 0.11928 | 0.051523 | 0.0045134 | -0.033873 | -0.083372 | -0.16501 | -0.224 | -0.32323 | -0.39865 | 0.54574 | 0.52972 | 0.50823 | 0.48806 | 0.46017 | 0.4125 | 0.36211 | 0.3336 | 0.30131 | 0.25977 | 0.18365 | 0.1104 | -0.0061289 | -0.11165 | 0.39157 | 0.36334 | 0.32815 | 0.29182 | 0.25581 | 0.19264 | 0.1238 | 0.079176 | 0.039575 | -0.011396 | -0.10299 | -0.17471 | -0.27964 | -0.39115
| DIPPEN | CT |  |  |  | 0.34557 | 0.31995 | 0.29069 | 0.23826 | 0.18445 | 0.11928 | 0.051523 | 0.0045134 | -0.033873 | -0.083372 | -0.16501 | -0.224 | -0.32323 | -0.39247 | 0.55208 | 0.53888 | 0.5221 | 0.49237 | 0.46017 | 0.4125 | 0.36211 | 0.3336 | 0.30131 | 0.25977 | 0.18365 | 0.11497 | 0.031145 | -0.048143 | 0.40624 | 0.38408 | 0.35816 | 0.30964 | 0.25869 | 0.19264 | 0.1238 | 0.079176 | 0.039575 | -0.011396 | -0.10299 | -0.17471 | -0.27964 | -0.35942
| DIPPEN | LW |  |  |  | 0.32886 | 0.29618 | 0.25648 | 0.21591 | 0.1765 | 0.14301 | 0.092087 | 0.04528 | 0.0073194 | -0.037058 | -0.1174 | -0.135 | -0.24533 | -0.37713 | 0.54574 | 0.52972 | 0.50823 | 0.48806 | 0.46782 | 0.45075 | 0.4226 | 0.39422 | 0.36298 | 0.32628 | 0.25802 | 0.2437 | 0.12766 | -0.030668 | 0.39157 | 0.36334 | 0.32815 | 0.29182 | 0.25581 | 0.22523 | 0.17814 | 0.13418 | 0.096114 | 0.048708 | -0.037094 | -0.057828 | -0.18658 | -0.34859
| DIPPEN | ST |  |  |  | 0.35442 | 0.33738 | 0.31933 | 0.28419 | 0.25506 | 0.22697 | 0.17808 | 0.14715 | 0.097709 | 0.058608 | -0.024078 | -0.17911 | -0.30151 | -0.39865 | 0.55544 | 0.54683 | 0.53734 | 0.5055 | 0.4806 | 0.45925 | 0.41175 | 0.3877 | 0.34393 | 0.31447 | 0.24557 | 0.1104 | -0.0061289 | -0.11165 | 0.41401 | 0.39975 | 0.38446 | 0.34664 | 0.31571 | 0.28721 | 0.23293 | 0.20169 | 0.14884 | 0.10949 | 0.021599 | -0.14408 | -0.27927 | -0.39115
| DIPPEN | FS |  |  |  | 0.35859 | 0.34638 | 0.33435 | 0.30932 | 0.29319 | 0.27255 | 0.24894 | 0.22464 | 0.19338 | 0.16786 | 0.1024 | -0.038737 | -0.14426 | -0.1752 | 0.55742 | 0.55062 | 0.54365 | 0.52877 | 0.51694 | 0.50267 | 0.48675 | 0.47054 | 0.44766 | 0.42831 | 0.38215 | 0.29359 | 0.21302 | 0.18349 | 0.41786 | 0.40756 | 0.39762 | 0.37429 | 0.35826 | 0.33803 | 0.31504 | 0.29149 | 0.26019 | 0.23462 | 0.17018 | 0.031877 | -0.073046 | -0.10329
BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | NO | 1.4142 | 1.1368 | 1.0085 | 0.82796 | 0.60819 | 0.37154 | 0.052095 | -0.17933 | -0.28084 | -0.38651 | -0.60334 | -0.18577 | -0.30295 | -0.3484 | 3.0764 | 2.8676 | 2.782 | 2.6466 | 2.4735 | 2.2732 | 2.001 | 1.8093 | 1.7053 | 1.5952 | 1.3786 | 1.3513 | 1.291 | 1.2708 | 1.6444 | 1.376 | 1.2572 | 1.0786 | 0.85918 | 0.61109 | 0.28787 | 0.056631 | -0.041807 | -0.1447 | -0.35505 | 0.043625 | -0.06706 | -0.11072
| DORNOCH | CT |  |  |  | 1.4862 | 1.2427 | 1.1316 | 0.93407 | 0.73826 | 0.51002 | 0.21888 | 0.028458 | -0.06102 | -0.14642 | -0.33125 | 0.1273 | -0.069214 | -0.15039 | 3.1146 | 2.9312 | 2.8573 | 2.7293 | 2.5912 | 2.4285 | 2.2253 | 2.1147 | 2.0367 | 1.9311 | 1.728 | 1.687 | 1.5565 | 1.4509 | 1.7102 | 1.4725 | 1.3677 | 1.1848 | 1.0024 | 0.77749 | 0.49692 | 0.32022 | 0.23526 | 0.15459 | -0.021404 | 0.41998 | 0.23131 | 0.15836
| DORNOCH | LW |  |  |  | 1.4142 | 1.1368 | 1.0085 | 0.82796 | 0.60819 | 0.37154 | 0.052095 | -0.17933 | -0.28084 | -0.38651 | -0.60334 | -0.18577 | -0.30295 | -0.3484 | 3.0764 | 2.8676 | 2.782 | 2.6466 | 2.4735 | 2.2732 | 2.001 | 1.8093 | 1.7053 | 1.5952 | 1.3786 | 1.3513 | 1.291 | 1.2708 | 1.6444 | 1.376 | 1.2572 | 1.0786 | 0.85918 | 0.61109 | 0.28787 | 0.056631 | -0.041807 | -0.1447 | -0.35505 | 0.043625 | -0.06706 | -0.11072
| DORNOCH | ST |  |  |  | 1.5323 | 1.329 | 1.2633 | 1.1408 | 1.0296 | 0.93072 | 0.75316 | 0.65338 | 0.56248 | 0.45868 | 0.21416 | 0.40433 | 0.26613 | 0.14277 | 3.1343 | 2.9696 | 2.9244 | 2.8167 | 2.7222 | 2.6444 | 2.4771 | 2.3984 | 2.3341 | 2.2583 | 2.0773 | 1.7932 | 1.6688 | 1.5608 | 1.7517 | 1.5512 | 1.4887 | 1.3594 | 1.245 | 1.1461 | 0.96006 | 0.8613 | 0.77675 | 0.67977 | 0.45017 | 0.64405 | 0.52185 | 0.41379
| DORNOCH | FS |  |  |  | 1.6056 | 1.4529 | 1.4042 | 1.3213 | 1.2423 | 1.1613 | 1.057 | 0.97323 | 0.88574 | 0.79497 | 0.59217 | 0.46487 | 0.29571 | 0.19632 | 3.1918 | 3.0653 | 3.0294 | 2.9708 | 2.9125 | 2.8541 | 2.7708 | 2.7076 | 2.6466 | 2.5808 | 2.4299 | 2.0698 | 1.7653 | 1.6173 | 1.8248 | 1.6741 | 1.6276 | 1.5473 | 1.4706 | 1.392 | 1.2931 | 1.2119 | 1.1306 | 1.0459 | 0.85588 | 0.75228 | 0.59986 | 0.51206
CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | NO | 1.9578 | 1.9428 | 1.9258 | 1.9057 | 1.8865 | 1.8655 | 1.8386 | 1.8083 | 1.7833 | 1.7537 | 1.6987 | 1.6722 | 1.6533 | 1.641 | 1.9814 | 1.9785 | 1.9738 | 1.9673 | 1.9614 | 1.9565 | 1.9511 | 1.9438 | 1.9341 | 1.9233 | 1.9018 | 1.9006 | 1.8846 | 1.8709 | 1.0698 | 1.056 | 1.0398 | 1.0212 | 1.003 | 0.98263 | 0.95789 | 0.92884 | 0.90409 | 0.87499 | 0.82075 | 0.79517 | 0.77841 | 0.76705
| DOUGLAS PIER | CT |  |  |  | 1.9635 | 1.9529 | 1.9397 | 1.9136 | 1.8876 | 1.8655 | 1.8425 | 1.8209 | 1.7997 | 1.77 | 1.7168 | 1.6803 | 1.6533 | 1.641 | 1.9818 | 1.9787 | 1.9741 | 1.9673 | 1.9614 | 1.9565 | 1.9511 | 1.9455 | 1.9384 | 1.931 | 1.9149 | 1.9006 | 1.8846 | 1.8709 | 1.0749 | 1.0651 | 1.0524 | 1.0278 | 1.0031 | 0.98263 | 0.96125 | 0.94111 | 0.92036 | 0.89126 | 0.83884 | 0.80279 | 0.77841 | 0.76705
| DOUGLAS PIER | LW |  |  |  | 1.9578 | 1.9428 | 1.9258 | 1.9057 | 1.8865 | 1.8657 | 1.8386 | 1.8083 | 1.7833 | 1.7537 | 1.6987 | 1.6722 | 1.6599 | 1.6565 | 1.9814 | 1.9785 | 1.9738 | 1.9697 | 1.965 | 1.9604 | 1.9528 | 1.9438 | 1.9341 | 1.9233 | 1.9018 | 1.9009 | 1.896 | 1.895 | 1.0698 | 1.056 | 1.0398 | 1.0212 | 1.003 | 0.98377 | 0.95789 | 0.92884 | 0.90409 | 0.87499 | 0.82075 | 0.79517 | 0.78406 | 0.78114
| DOUGLAS PIER | ST |  |  |  | 1.9677 | 1.9622 | 1.9588 | 1.9513 | 1.9407 | 1.9322 | 1.9225 | 1.9081 | 1.8942 | 1.8749 | 1.8356 | 1.7379 | 1.712 | 1.7007 | 1.9823 | 1.9811 | 1.9797 | 1.9777 | 1.9751 | 1.9722 | 1.9686 | 1.9641 | 1.9588 | 1.9521 | 1.9362 | 1.9266 | 1.9081 | 1.8969 | 1.0785 | 1.0734 | 1.0701 | 1.0631 | 1.0531 | 1.0449 | 1.0355 | 1.0217 | 1.0082 | 0.98943 | 0.9508 | 0.85481 | 0.83054 | 0.82058
| DOUGLAS PIER | FS |  |  |  | 1.9679 | 1.9658 | 1.963 | 1.9561 | 1.9468 | 1.9388 | 1.9296 | 1.9208 | 1.9093 | 1.8949 | 1.8636 | 1.7692 | 1.6949 | 1.6818 | 1.9824 | 1.9815 | 1.9804 | 1.9788 | 1.9768 | 1.9747 | 1.9721 | 1.9692 | 1.9657 | 1.9617 | 1.952 | 1.9567 | 1.9 | 1.8847 | 1.0787 | 1.0767 | 1.074 | 1.0675 | 1.0588 | 1.0513 | 1.0425 | 1.034 | 1.023 | 1.0093 | 0.97915 | 0.888 | 0.81549 | 0.804
ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | NO | 2.2119 | 2.1901 | 2.1647 | 2.1326 | 2.0936 | 2.049 | 2.0044 | 1.9562 | 1.9281 | 1.8929 | 1.8259 | 1.799 | 1.7738 | 1.757 | 2.478 | 2.4691 | 2.4601 | 2.446 | 2.4252 | 2.4033 | 2.3815 | 2.3576 | 2.3366 | 2.3053 | 2.245 | 2.2271 | 2.1992 | 2.1752 | 2.125 | 2.1052 | 2.082 | 2.0529 | 2.0196 | 1.9846 | 1.9499 | 1.9085 | 1.8804 | 1.8469 | 1.7828 | 1.7533 | 1.7292 | 1.7128
| DRIMORE | CT |  |  |  | 2.2199 | 2.2067 | 2.1848 | 2.1405 | 2.0942 | 2.049 | 2.0044 | 1.9563 | 1.9363 | 1.9056 | 1.8418 | 1.813 | 1.7738 | 1.757 | 2.4804 | 2.4741 | 2.4654 | 2.4483 | 2.4252 | 2.4033 | 2.3815 | 2.3583 | 2.3431 | 2.3187 | 2.2597 | 2.2271 | 2.1992 | 2.1752 | 2.1331 | 2.1215 | 2.1022 | 2.0619 | 2.0196 | 1.9846 | 1.9499 | 1.913 | 1.8926 | 1.8615 | 1.7995 | 1.7665 | 1.7292 | 1.7128
| DRIMORE | LW |  |  |  | 2.2119 | 2.1901 | 2.1647 | 2.1326 | 2.0936 | 2.0546 | 2.0098 | 1.9562 | 1.9281 | 1.8929 | 1.8259 | 1.799 | 1.7806 | 1.7764 | 2.478 | 2.4691 | 2.4601 | 2.446 | 2.4283 | 2.4109 | 2.3866 | 2.3576 | 2.3366 | 2.3053 | 2.245 | 2.2275 | 2.2184 | 2.2166 | 2.125 | 2.1052 | 2.082 | 2.0529 | 2.0205 | 1.9902 | 1.9529 | 1.9085 | 1.8804 | 1.8469 | 1.7828 | 1.7533 | 1.7351 | 1.7308
| DRIMORE | ST |  |  |  | 2.2259 | 2.2198 | 2.2088 | 2.1947 | 2.1798 | 2.1665 | 2.1485 | 2.1282 | 2.1034 | 2.0732 | 2.0093 | 1.8646 | 1.8227 | 1.8055 | 2.4837 | 2.4813 | 2.477 | 2.4717 | 2.4661 | 2.4612 | 2.4526 | 2.4422 | 2.4276 | 2.4092 | 2.3648 | 2.2548 | 2.2211 | 2.1991 | 2.1382 | 2.1321 | 2.1219 | 2.1087 | 2.0952 | 2.0828 | 2.0664 | 2.0483 | 2.0263 | 1.9998 | 1.9441 | 1.8123 | 1.771 | 1.7527
| DRIMORE | FS |  |  |  | 2.2316 | 2.2235 | 2.217 | 2.2042 | 2.195 | 2.1803 | 2.168 | 2.1504 | 2.1319 | 2.1114 | 2.064 | 1.9152 | 1.8027 | 1.7889 | 2.486 | 2.4827 | 2.4803 | 2.4754 | 2.4722 | 2.4666 | 2.4621 | 2.4533 | 2.444 | 2.4318 | 2.4025 | 2.3021 | 2.2108 | 2.1846 | 2.1433 | 2.136 | 2.1295 | 2.1177 | 2.1085 | 2.0951 | 2.0836 | 2.0677 | 2.0505 | 2.0321 | 1.9894 | 1.8547 | 1.755 | 1.7418
CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 2.4896 | 2.4819 | 2.4732 | 2.4629 | 2.4504 | 2.4203 | 2.2749 | 2.1204 | 2.0126 | 1.8981 | 1.6761 | 1.6517 | 1.5311 | 1.4603 | 3.7201 | 3.7055 | 3.6858 | 3.6664 | 3.6381 | 3.6214 | 3.6029 | 3.5703 | 3.5326 | 3.492 | 3.4084 | 3.4029 | 3.3037 | 3.2175 | 2.5675 | 2.5511 | 2.5276 | 2.5051 | 2.4423 | 2.3511 | 2.2283 | 2.0978 | 2.0063 | 1.9091 | 1.7204 | 1.6793 | 1.5749 | 1.511
| DRUMNADROCHIT | CT |  |  |  | 2.4925 | 2.4827 | 2.4738 | 2.4629 | 2.4504 | 2.4228 | 2.288 | 2.1532 | 2.0726 | 1.9635 | 1.7529 | 1.7068 | 1.5311 | 1.4603 | 3.7242 | 3.7084 | 3.6912 | 3.6664 | 3.6381 | 3.6214 | 3.6045 | 3.5877 | 3.5597 | 3.5212 | 3.4462 | 3.4029 | 3.3037 | 3.2175 | 2.572 | 2.5548 | 2.5348 | 2.5051 | 2.468 | 2.3559 | 2.2419 | 2.1277 | 2.0591 | 1.9657 | 1.786 | 1.7265 | 1.5749 | 1.511
| DRUMNADROCHIT | LW |  |  |  | 2.4896 | 2.4819 | 2.4732 | 2.4661 | 2.4511 | 2.4203 | 2.2749 | 2.1204 | 2.0126 | 1.8981 | 1.6761 | 1.6517 | 1.5593 | 1.5244 | 3.7201 | 3.7055 | 3.6858 | 3.6698 | 3.644 | 3.6304 | 3.6029 | 3.5703 | 3.5326 | 3.492 | 3.4084 | 3.4093 | 3.3709 | 3.3569 | 2.5675 | 2.5511 | 2.5276 | 2.5083 | 2.4423 | 2.3511 | 2.2283 | 2.0978 | 2.0063 | 1.9091 | 1.7204 | 1.6793 | 1.5984 | 1.5685
| DRUMNADROCHIT | ST |  |  |  | 2.4936 | 2.4859 | 2.4806 | 2.4764 | 2.4703 | 2.4661 | 2.4618 | 2.4566 | 2.45 | 2.4417 | 2.3023 | 1.949 | 1.8034 | 1.714 | 3.7244 | 3.7125 | 3.7034 | 3.6942 | 3.6815 | 3.6701 | 3.657 | 3.6416 | 3.6227 | 3.5998 | 3.5434 | 3.4381 | 3.4078 | 3.3257 | 2.5721 | 2.5599 | 2.5499 | 2.5395 | 2.525 | 2.5116 | 2.496 | 2.4774 | 2.4545 | 2.4179 | 2.2547 | 1.9327 | 1.8001 | 1.7196
| DRUMNADROCHIT | FS |  |  |  | 2.5088 | 2.5014 | 2.4962 | 2.4924 | 2.4885 | 2.4846 | 2.4799 | 2.4748 | 2.4688 | 2.462 | 2.4451 | 2.0254 | 1.7056 | 1.6302 | 3.7403 | 3.7291 | 3.7204 | 3.7121 | 3.7029 | 3.6931 | 3.6819 | 3.669 | 3.654 | 3.637 | 3.5959 | 3.5026 | 3.353 | 3.236 | 2.5879 | 2.5765 | 2.5673 | 2.5581 | 2.5475 | 2.5363 | 2.5234 | 2.5084 | 2.4909 | 2.4709 | 2.3681 | 1.9978 | 1.7236 | 1.66
GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0.79254 | 0.78689 | 0.77845 | 0.7739 | 0.76142 | 0.75552 | 0.74471 | 0.73479 | 0.72912 | 0.71581 | 0.69888 | 0.69319 | 0.68221 | 0.67689 | 0.83351 | 0.83073 | 0.8262 | 0.82335 | 0.81736 | 0.81306 | 0.8078 | 0.80146 | 0.79626 | 0.78799 | 0.77473 | 0.77244 | 0.76607 | 0.76171 | 0.80933 | 0.8042 | 0.79643 | 0.79214 | 0.78084 | 0.77537 | 0.7653 | 0.7559 | 0.74962 | 0.7366 | 0.71858 | 0.71252 | 0.70296 | 0.6982
| DRUMRUNIE | CT |  |  |  | 0.79828 | 0.7911 | 0.78653 | 0.77652 | 0.76501 | 0.75652 | 0.74756 | 0.7389 | 0.73142 | 0.72424 | 0.70472 | 0.698 | 0.68221 | 0.67689 | 0.83567 | 0.8323 | 0.82941 | 0.82376 | 0.81751 | 0.81306 | 0.80838 | 0.80379 | 0.79868 | 0.79286 | 0.77931 | 0.77368 | 0.76607 | 0.76171 | 0.81258 | 0.80791 | 0.80361 | 0.79434 | 0.78372 | 0.77595 | 0.76775 | 0.75982 | 0.75266 | 0.7448 | 0.72478 | 0.71689 | 0.70296 | 0.6982
| DRUMRUNIE | LW |  |  |  | 0.79254 | 0.78689 | 0.77845 | 0.7739 | 0.76142 | 0.75552 | 0.74471 | 0.73479 | 0.72912 | 0.71581 | 0.69888 | 0.69319 | 0.68555 | 0.6841 | 0.83351 | 0.83073 | 0.8262 | 0.82335 | 0.81736 | 0.81406 | 0.8078 | 0.80146 | 0.79626 | 0.78799 | 0.77473 | 0.77244 | 0.76931 | 0.76875 | 0.80933 | 0.8042 | 0.79643 | 0.79214 | 0.78084 | 0.77537 | 0.7653 | 0.7559 | 0.74962 | 0.7366 | 0.71858 | 0.71252 | 0.70576 | 0.70451
| DRUMRUNIE | ST |  |  |  | 0.79833 | 0.79396 | 0.79271 | 0.78816 | 0.7846 | 0.77898 | 0.77105 | 0.76671 | 0.76276 | 0.75688 | 0.73693 | 0.70474 | 0.69339 | 0.68598 | 0.83571 | 0.83378 | 0.83288 | 0.83062 | 0.82853 | 0.82558 | 0.82158 | 0.81866 | 0.81559 | 0.81145 | 0.7993 | 0.77784 | 0.77086 | 0.76628 | 0.81273 | 0.81053 | 0.80933 | 0.80521 | 0.80189 | 0.79675 | 0.78953 | 0.7854 | 0.78154 | 0.77582 | 0.75658 | 0.72326 | 0.71284 | 0.70636
| DRUMRUNIE | FS |  |  |  | 0.80024 | 0.79599 | 0.79338 | 0.79206 | 0.79074 | 0.78379 | 0.77882 | 0.77496 | 0.76883 | 0.76231 | 0.74977 | 0.71516 | 0.69005 | 0.68305 | 0.83644 | 0.83459 | 0.83325 | 0.83229 | 0.8312 | 0.82799 | 0.82537 | 0.82302 | 0.81966 | 0.81598 | 0.80828 | 0.78838 | 0.76929 | 0.7642 | 0.81281 | 0.81233 | 0.80995 | 0.80869 | 0.80739 | 0.80114 | 0.79659 | 0.79298 | 0.78734 | 0.78131 | 0.76955 | 0.73552 | 0.7099 | 0.70403
STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | NO | -2.8828 | -2.9586 | -3.0628 | -3.2065 | -3.3606 | -3.51 | -3.7055 | -3.9005 | -4.0614 | -4.2327 | -4.5709 | -4.946 | -5.4334 | -5.7637 | -0.76479 | -0.80196 | -0.85758 | -0.92662 | -1.0085 | -1.1306 | -1.2585 | -1.3502 | -1.4543 | -1.5752 | -1.8131 | -2.0903 | -2.4771 | -2.8941 | -0.99305 | -1.0149 | -1.0627 | -1.1855 | -1.3197 | -1.4562 | -1.638 | -1.8119 | -1.9582 | -2.1135 | -2.4376 | -2.8127 | -3.2795 | -3.6002
| DRYMEN | CT |  |  |  | -2.827 | -2.8822 | -2.9482 | -3.1207 | -3.2908 | -3.4822 | -3.6805 | -3.8452 | -4.0022 | -4.1856 | -4.5412 | -4.946 | -5.4334 | -5.7637 | -0.74423 | -0.77693 | -0.81844 | -0.91293 | -1.0085 | -1.1306 | -1.2585 | -1.3502 | -1.4543 | -1.5752 | -1.8131 | -2.0903 | -2.4771 | -2.8941 | -0.9927 | -1.0149 | -1.0433 | -1.1073 | -1.2575 | -1.4442 | -1.638 | -1.7919 | -1.9392 | -2.1087 | -2.4376 | -2.8127 | -3.2795 | -3.6002
| DRYMEN | LW |  |  |  | -2.8828 | -2.9586 | -3.0628 | -3.2065 | -3.3606 | -3.51 | -3.7055 | -3.9005 | -4.0614 | -4.2327 | -4.5709 | -4.8438 | -5.2645 | -5.6465 | -0.76479 | -0.80196 | -0.85758 | -0.92662 | -1.002 | -1.0736 | -1.1743 | -1.2782 | -1.3776 | -1.4837 | -1.6907 | -1.7951 | -2.0954 | -2.434 | -0.99305 | -1.0076 | -1.0627 | -1.1855 | -1.3197 | -1.4562 | -1.6345 | -1.8119 | -1.9582 | -2.1135 | -2.4201 | -2.6543 | -3.0762 | -3.4829
| DRYMEN | ST |  |  |  | -2.8078 | -2.8344 | -2.8679 | -2.9465 | -3.0184 | -3.0945 | -3.2116 | -3.2902 | -3.4083 | -3.5082 | -3.7456 | -4.2368 | -4.657 | -5.0654 | -0.73591 | -0.75166 | -0.7718 | -0.83778 | -0.89509 | -0.94981 | -1.0514 | -1.1113 | -1.2093 | -1.2849 | -1.4628 | -1.8355 | -2.2353 | -2.7108 | -0.99005 | -0.99659 | -1.0059 | -1.0572 | -1.0999 | -1.1373 | -1.2198 | -1.2825 | -1.4 | -1.4924 | -1.7126 | -2.1719 | -2.5772 | -2.9759
| DRYMEN | FS |  |  |  | -2.7947 | -2.8149 | -2.8372 | -2.8864 | -2.9437 | -3.0026 | -3.0673 | -3.1295 | -3.2165 | -3.3021 | -3.4986 | -3.9628 | -4.4147 | -4.6968 | -0.73072 | -0.74394 | -0.75958 | -0.79288 | -0.83136 | -0.87267 | -0.91827 | -0.96377 | -1.0286 | -1.0925 | -1.2391 | -1.5778 | -2.038 | -2.5942 | -0.98917 | -0.99451 | -1.0022 | -1.0207 | -1.0419 | -1.0666 | -1.0937 | -1.1208 | -1.1887 | -1.2676 | -1.4489 | -1.8557 | -2.2564 | -2.514
DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | NO | 1.9827 | 1.9318 | 1.8688 | 1.7957 | 1.7003 | 1.6121 | 1.5167 | 1.425 | 1.3609 | 1.274 | 1.104 | 1.1104 | 1.0437 | 1.0043 | 2.2063 | 2.1816 | 2.1455 | 2.1039 | 2.0387 | 1.9929 | 1.944 | 1.8953 | 1.8447 | 1.7775 | 1.6451 | 1.6548 | 1.5977 | 1.5511 | 1.9355 | 1.8911 | 1.8424 | 1.7832 | 1.7009 | 1.6244 | 1.5414 | 1.4598 | 1.4205 | 1.384 | 1.2584 | 1.2994 | 1.2406 | 1.2047
| DRYNOCH | CT |  |  |  | 2.0103 | 1.9736 | 1.9208 | 1.8162 | 1.7003 | 1.6121 | 1.5167 | 1.425 | 1.366 | 1.2858 | 1.1356 | 1.1458 | 1.0437 | 1.0043 | 2.2158 | 2.1962 | 2.1626 | 2.1039 | 2.0387 | 1.9929 | 1.944 | 1.8953 | 1.8495 | 1.786 | 1.6664 | 1.6551 | 1.5977 | 1.5511 | 1.9602 | 1.9252 | 1.8776 | 1.7905 | 1.7009 | 1.6244 | 1.5414 | 1.4598 | 1.4205 | 1.384 | 1.3053 | 1.3296 | 1.2406 | 1.2047
| DRYNOCH | LW |  |  |  | 1.9827 | 1.9318 | 1.8688 | 1.7957 | 1.7198 | 1.645 | 1.5456 | 1.438 | 1.3609 | 1.274 | 1.104 | 1.1104 | 1.0619 | 1.0467 | 2.2063 | 2.1816 | 2.1455 | 2.1083 | 2.0674 | 2.0297 | 1.9713 | 1.9054 | 1.8447 | 1.7775 | 1.6451 | 1.6548 | 1.6357 | 1.6305 | 1.9355 | 1.8911 | 1.8424 | 1.7832 | 1.7236 | 1.6593 | 1.5822 | 1.5001 | 1.449 | 1.3894 | 1.2584 | 1.2994 | 1.2564 | 1.2432
| DRYNOCH | ST |  |  |  | 2.0227 | 2.0013 | 1.9792 | 1.9491 | 1.9114 | 1.8757 | 1.8328 | 1.7869 | 1.7318 | 1.665 | 1.516 | 1.2713 | 1.1732 | 1.1184 | 2.2203 | 2.2096 | 2.1973 | 2.1809 | 2.1596 | 2.138 | 2.1115 | 2.0815 | 2.0448 | 2.0001 | 1.8953 | 1.7141 | 1.649 | 1.6032 | 1.9731 | 1.9537 | 1.9352 | 1.9102 | 1.8799 | 1.8506 | 1.816 | 1.7792 | 1.7369 | 1.6856 | 1.5621 | 1.446 | 1.3559 | 1.3078
| DRYNOCH | FS |  |  |  | 2.0327 | 2.0176 | 1.9987 | 1.9727 | 1.945 | 1.9139 | 1.8795 | 1.8449 | 1.8005 | 1.7521 | 1.6441 | 1.3499 | 1.1227 | 1.0795 | 2.224 | 2.2159 | 2.2055 | 2.1918 | 2.176 | 2.1586 | 2.1386 | 2.117 | 2.0901 | 2.0597 | 1.9894 | 1.8012 | 1.626 | 1.5718 | 1.9822 | 1.969 | 1.9531 | 1.931 | 1.909 | 1.8838 | 1.8558 | 1.8287 | 1.7946 | 1.7579 | 1.677 | 1.5172 | 1.3115 | 1.2736
KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | NO | 1.3333 | 1.2749 | 1.1697 | -0.71746 | -2.8355 | -6.9379 | -11.3028 | -13.9127 | -14.6198 | -15.3559 | -16.6896 | -19.1152 | -20.0918 | -20.5116 | 1.6629 | 1.615 | 1.5399 | -0.71501 | -3.2458 | -8.25 | -13.571 | -16.6909 | -17.4915 | -18.3245 | -19.8108 | -23.1856 | -24.2965 | -24.7931 | -3.5272 | -3.6209 | -3.7468 | -6.0799 | -8.6993 | -13.7935 | -19.2143 | -22.4385 | -23.298 | -24.1909 | -25.795 | -29.2464 | -30.4459 | -30.9677
| DUFFTOWN | CT |  |  |  | 1.3589 | 1.3114 | 1.2277 | 0.89767 | 0.36263 | -1.6482 | -3.7837 | -4.4766 | -4.8682 | -5.2632 | -6.0219 | -7.0203 | -7.659 | -7.9436 | 1.6896 | 1.6579 | 1.5994 | 1.2366 | 0.64815 | -1.7439 | -4.2896 | -5.0217 | -5.417 | -5.8302 | -6.6012 | -8.0869 | -8.696 | -9.0279 | -3.4616 | -3.5153 | -3.6024 | -4.043 | -4.7177 | -7.1967 | -9.829 | -10.6533 | -11.1126 | -11.5956 | -12.5039 | -14.1057 | -14.8527 | -15.1858
| DUFFTOWN | LW |  |  |  | 1.3333 | 1.2749 | 1.1697 | -0.71746 | -2.8355 | -6.9379 | -11.3028 | -13.9127 | -14.6198 | -15.3559 | -16.6896 | -19.1152 | -20.0918 | -20.5116 | 1.6629 | 1.615 | 1.5399 | -0.71501 | -3.2458 | -8.25 | -13.571 | -16.6909 | -17.4915 | -18.3245 | -19.8108 | -23.1856 | -24.2965 | -24.7931 | -3.5272 | -3.6209 | -3.7468 | -6.0799 | -8.6993 | -13.7935 | -19.2143 | -22.4385 | -23.298 | -24.1909 | -25.795 | -29.2464 | -30.4459 | -30.9677
| DUFFTOWN | ST |  |  |  | 1.4577 | 1.4364 | 1.3984 | -0.28286 | -1.4487 | -2.2435 | -4.8401 | -5.6224 | -6.226 | -6.5089 | -7.151 | -8.1336 | -8.8552 | -9.356 | 1.7374 | 1.7219 | 1.6896 | -0.39506 | -1.8295 | -2.7946 | -6.0067 | -6.9428 | -7.6526 | -7.9507 | -8.6136 | -10.2032 | -10.9714 | -11.4536 | -3.3858 | -3.4115 | -3.4602 | -5.5623 | -7.0179 | -8.005 | -11.2409 | -12.2006 | -12.9344 | -13.2586 | -13.9758 | -15.664 | -16.5492 | -17.1331
| DUFFTOWN | FS |  |  |  | 1.4649 | 1.4487 | 1.4191 | 1.056 | 0.67774 | 0.24047 | -0.20348 | -0.59507 | -0.84112 | -1.0317 | -1.4485 | -1.7328 | -2.0548 | -2.3354 | 1.7429 | 1.7303 | 1.7045 | 1.2624 | 0.80498 | 0.27745 | -0.25677 | -0.72233 | -1.0062 | -1.2176 | -1.6552 | -2.0625 | -2.4252 | -2.7368 | -3.3741 | -3.3942 | -3.431 | -3.8877 | -4.365 | -4.9101 | -5.4668 | -5.9519 | -6.2623 | -6.5 | -6.9934 | -7.5503 | -8.0004 | -8.2996
BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 2.0617 | 1.7338 | 1.3228 | 0.35357 | -0.73518 | -2.2724 | -3.9124 | -5.3361 | -6.3278 | -7.398 | -9.5626 | -11.6648 | -14.3747 | -16.5208 | 4.3784 | 4.1888 | 3.946 | 3.2714 | 2.5101 | 1.2778 | -0.04532 | -1.0758 | -1.7036 | -2.3846 | -3.7483 | -4.4549 | -5.8824 | -7.2006 | 3.5756 | 3.2802 | 2.9081 | 1.9556 | 0.89442 | -0.65515 | -2.3355 | -3.7393 | -4.6704 | -5.6749 | -7.6841 | -9.2762 | -11.5708 | -13.4535
| DUNBLANE | CT |  |  |  | 2.281 | 2.0764 | 1.7936 | 1.0324 | 0.16873 | -1.0541 | -2.2495 | -3.1451 | -4.0747 | -5.1137 | -7.2149 | -9.9683 | -13.0451 | -15.3149 | 4.4524 | 4.3057 | 4.1088 | 3.6504 | 3.1061 | 2.1407 | 1.204 | 0.65591 | 0.11166 | -0.52263 | -1.8075 | -3.0721 | -4.8776 | -6.7479 | 3.7677 | 3.5813 | 3.3232 | 2.622 | 1.817 | 0.59047 | -0.61752 | -1.4415 | -2.2826 | -3.2389 | -5.1611 | -7.3631 | -9.8942 | -11.8085
| DUNBLANE | LW |  |  |  | 2.0617 | 1.7338 | 1.3228 | 0.35357 | -0.73518 | -2.2724 | -3.9124 | -5.3361 | -6.3278 | -7.398 | -9.5626 | -11.6648 | -14.3747 | -16.5208 | 4.3784 | 4.1888 | 3.946 | 3.2714 | 2.5101 | 1.2778 | -0.04532 | -1.0758 | -1.7036 | -2.3846 | -3.7483 | -4.4549 | -5.8824 | -7.2006 | 3.5756 | 3.2802 | 2.9081 | 1.9556 | 0.89442 | -0.65515 | -2.3355 | -3.7393 | -4.6704 | -5.6749 | -7.6841 | -9.2762 | -11.5708 | -13.4535
| DUNBLANE | ST |  |  |  | 2.3451 | 2.2064 | 2.0673 | 1.4962 | 0.99754 | 0.44489 | -0.43413 | -0.93395 | -1.4043 | -1.8906 | -3.014 | -5.2039 | -7.4293 | -9.7594 | 4.4815 | 4.3783 | 4.2823 | 3.7001 | 3.2315 | 2.7544 | 1.8483 | 1.4196 | 1.0443 | 0.68495 | -0.16592 | -1.6809 | -3.351 | -5.3315 | 3.8252 | 3.7015 | 3.5815 | 2.952 | 2.4291 | 1.8871 | 0.916 | 0.41975 | -0.029167 | -0.47441 | -1.5142 | -3.4541 | -5.4156 | -7.4566
| DUNBLANE | FS |  |  |  | 2.3939 | 2.2969 | 2.1885 | 1.9327 | 1.6405 | 1.2459 | 0.89181 | 0.54017 | 0.15936 | -0.25487 | -1.1528 | -3.231 | -5.681 | -7.5587 | 4.511 | 4.4294 | 4.3482 | 4.1412 | 3.9091 | 3.5852 | 3.2991 | 3.016 | 2.7433 | 2.4515 | 1.7924 | 0.34841 | -1.7158 | -3.968 | 3.8703 | 3.7838 | 3.6911 | 3.4443 | 3.1663 | 2.7932 | 2.4577 | 2.1249 | 1.7801 | 1.4099 | 0.59978 | -1.1965 | -3.3426 | -4.9068
DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | NO | 16.0702 | 15.9424 | 15.7698 | 15.3993 | 15.0185 | 14.645 | 14.1974 | 13.711 | 13.2842 | 12.838 | 11.9303 | 11.5658 | 10.3723 | 9.7182 | 18.1008 | 18.0292 | 17.9168 | 17.7434 | 17.5575 | 17.3722 | 17.1349 | 16.8614 | 16.5927 | 16.3062 | 15.7272 | 15.4328 | 14.62 | 13.7706 | 17.8623 | 17.7422 | 17.5715 | 17.2395 | 16.8942 | 16.5586 | 16.1395 | 15.685 | 15.2808 | 14.8567 | 13.9954 | 13.67 | 12.6045 | 12.0153
| DUNOON | CT |  |  |  | 16.2114 | 16.1527 | 16.0512 | 15.6841 | 15.3042 | 14.9443 | 14.5721 | 14.2278 | 13.8046 | 13.3389 | 12.4069 | 11.5658 | 10.3723 | 9.7182 | 18.1485 | 18.0992 | 18.0135 | 17.8072 | 17.5868 | 17.3722 | 17.1475 | 16.951 | 16.6919 | 16.3962 | 15.7992 | 15.4328 | 14.62 | 13.7706 | 17.9812 | 17.9208 | 17.8154 | 17.4761 | 17.1232 | 16.7843 | 16.4326 | 16.1142 | 15.7176 | 15.2784 | 14.4001 | 13.67 | 12.6045 | 12.0153
| DUNOON | LW |  |  |  | 16.0702 | 15.9424 | 15.7698 | 15.3993 | 15.0185 | 14.645 | 14.1974 | 13.711 | 13.2842 | 12.838 | 11.9303 | 11.7351 | 10.9884 | 10.6688 | 18.1008 | 18.0292 | 17.9168 | 17.7434 | 17.5575 | 17.3799 | 17.1349 | 16.8614 | 16.5927 | 16.3062 | 15.7272 | 15.8976 | 15.4957 | 15.2036 | 17.8623 | 17.7422 | 17.5715 | 17.2395 | 16.8942 | 16.5586 | 16.1395 | 15.685 | 15.2808 | 14.8567 | 13.9954 | 13.8775 | 13.1706 | 12.8167
| DUNOON | ST |  |  |  | 16.2771 | 16.2627 | 16.2482 | 16.1885 | 16.1281 | 16.0596 | 15.9472 | 15.8432 | 15.6974 | 15.5385 | 15.1589 | 14.614 | 13.777 | 12.6262 | 18.1771 | 18.1564 | 18.1308 | 18.0591 | 17.9884 | 17.9157 | 17.7915 | 17.6897 | 17.5405 | 17.3917 | 17.034 | 16.5521 | 15.8115 | 14.7532 | 18.0376 | 18.0199 | 17.9998 | 17.9314 | 17.8652 | 17.7934 | 17.6692 | 17.5623 | 17.4072 | 17.2308 | 16.8081 | 16.225 | 15.4652 | 14.4801
| DUNOON | FS |  |  |  | 16.2771 | 16.2576 | 16.2428 | 16.191 | 16.1341 | 16.0695 | 15.9913 | 15.9059 | 15.7655 | 15.6221 | 15.2903 | 14.6308 | 13.5979 | 12.7704 | 18.18 | 18.1582 | 18.1343 | 18.0861 | 18.0326 | 17.9722 | 17.9009 | 17.8216 | 17.7013 | 17.5744 | 17.2747 | 16.6554 | 15.4834 | 13.9308 | 18.0374 | 18.0169 | 17.9985 | 17.945 | 17.8883 | 17.8242 | 17.747 | 17.6626 | 17.5263 | 17.3873 | 17.0651 | 16.4234 | 15.4494 | 14.7694
DUNVEGAN | DUNVEGAN GRID | MINIMUM HEADROOM | NG 27604720 | YES | NO | 3.3 | 3.3 | 3.3 | 3.2915 | 3.2857 | 3.2819 | 3.2687 | 3.2651 | 3.2552 | 3.2517 | 3.244 | 3.2218 | 3.1892 | 3.1558 | 3.3 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.23 | 3.2023 | 3.1615 | 3.1197 | 3.3 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.23 | 3.2023 | 3.1615 | 3.1197
| DUNVEGAN GRID | CT |  |  |  | 3.3 | 3.3 | 3.3 | 3.2989 | 3.2969 | 3.2874 | 3.2773 | 3.2747 | 3.2702 | 3.2657 | 3.2575 | 3.2348 | 3.2134 | 3.1902 | 3.3 | 3.3 | 3.3 | 3.2986 | 3.2961 | 3.2843 | 3.2716 | 3.2684 | 3.2628 | 3.2571 | 3.2469 | 3.2185 | 3.1917 | 3.1628 | 3.3 | 3.3 | 3.3 | 3.2986 | 3.2961 | 3.2843 | 3.2716 | 3.2684 | 3.2628 | 3.2571 | 3.2469 | 3.2185 | 3.1917 | 3.1628
| DUNVEGAN GRID | LW |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2982 | 3.2964 | 3.2932 | 3.2844 | 3.2446 | 3.1863 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2955 | 3.2916 | 3.2805 | 3.2307 | 3.1579 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2955 | 3.2916 | 3.2805 | 3.2307 | 3.1579
| DUNVEGAN GRID | ST |  |  |  | 3.3 | 3.3 | 3.3 | 3.2915 | 3.2857 | 3.2819 | 3.2687 | 3.2651 | 3.2552 | 3.2517 | 3.244 | 3.2218 | 3.1892 | 3.1558 | 3.3 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.23 | 3.2023 | 3.1615 | 3.1197 | 3.3 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.23 | 3.2023 | 3.1615 | 3.1197
| DUNVEGAN GRID | FS |  |  |  | 3.3 | 3.3 | 3.3 | 3.2983 | 3.2965 | 3.2945 | 3.2924 | 3.2907 | 3.2871 | 3.2847 | 3.2798 | 3.2769 | 3.2749 | 3.2711 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2956 | 3.2931 | 3.2905 | 3.2884 | 3.2839 | 3.2809 | 3.2748 | 3.2711 | 3.2686 | 3.2639 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2956 | 3.2931 | 3.2905 | 3.2884 | 3.2839 | 3.2809 | 3.2748 | 3.2711 | 3.2686 | 3.2639
DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 8.97 | 8.8491 | 8.6724 | 8.3799 | 7.6354 | 6.8676 | 5.9766 | 5.1111 | 4.5289 | 3.7039 | 1.9564 | 3.871 | 3.4703 | 3.2528 | 12.1312 | 11.9327 | 11.6565 | 11.294 | 10.7538 | 10.1041 | 9.2668 | 8.4646 | 7.8889 | 7.2582 | 5.985 | 9.2261 | 8.9569 | 8.7506 | 9.2953 | 9.1782 | 8.8915 | 8.521 | 8.0076 | 7.2253 | 6.2147 | 5.2239 | 4.5007 | 3.7139 | 2.1229 | 4.8268 | 4.4285 | 4.19
| DYCE NORTH | CT |  |  |  | 8.97 | 8.8491 | 8.6724 | 8.3843 | 7.8839 | 7.2626 | 6.576 | 5.9443 | 5.2981 | 4.7622 | 3.4821 | 4.8501 | 4.1542 | 3.7531 | 12.1318 | 11.9327 | 11.6565 | 11.294 | 10.7731 | 10.257 | 9.6917 | 9.2227 | 8.7676 | 8.3829 | 7.4585 | 10.245 | 9.7795 | 9.3122 | 9.2953 | 9.1782 | 8.8915 | 8.521 | 8.0211 | 7.39 | 6.679 | 6.0641 | 5.4429 | 4.9274 | 3.7415 | 6.024 | 5.3945 | 5.0247
| DYCE NORTH | LW |  |  |  | 8.9723 | 8.8849 | 8.7288 | 8.3799 | 7.6354 | 6.8676 | 5.9766 | 5.1111 | 4.5289 | 3.7039 | 1.9564 | 3.871 | 3.4703 | 3.2528 | 12.1312 | 11.9944 | 11.7541 | 11.3714 | 10.7538 | 10.1041 | 9.2668 | 8.4646 | 7.8889 | 7.2582 | 5.985 | 9.2261 | 8.9569 | 8.7506 | 9.2977 | 9.2131 | 9.0003 | 8.6177 | 8.0076 | 7.2253 | 6.2147 | 5.2239 | 4.5007 | 3.7139 | 2.1229 | 4.8268 | 4.4285 | 4.19
| DYCE NORTH | ST |  |  |  | 8.9842 | 8.9407 | 8.886 | 8.6446 | 8.2743 | 8.084 | 7.644 | 7.2133 | 6.805 | 6.295 | 4.9056 | 6.9198 | 6.1022 | 5.3226 | 12.1559 | 12.0889 | 12.005 | 11.6817 | 11.21 | 10.9373 | 10.3884 | 9.9468 | 9.5543 | 9.1194 | 8.0504 | 10.3967 | 10.2025 | 9.6345 | 9.3092 | 9.2674 | 9.2145 | 8.9243 | 8.4789 | 8.1998 | 7.6425 | 7.1886 | 6.7826 | 6.2966 | 4.951 | 7.4581 | 6.8406 | 6.2594
| DYCE NORTH | FS |  |  |  | 8.9923 | 8.9577 | 8.9176 | 8.8301 | 8.6119 | 8.4863 | 8.3449 | 8.1264 | 7.9156 | 7.6432 | 6.9102 | 7.571 | 6.6135 | 5.8295 | 12.1671 | 12.1156 | 12.0549 | 11.9293 | 11.6503 | 11.4701 | 11.2656 | 10.9833 | 10.7556 | 10.4948 | 9.8983 | 11.3044 | 10.8964 | 10.0221 | 9.3167 | 9.2836 | 9.2448 | 9.1503 | 8.9162 | 8.7343 | 8.5272 | 8.2401 | 8.0081 | 7.7422 | 7.0453 | 8.2927 | 7.6483 | 7.0365
THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | NO | 0.81841 | 0.80899 | 0.80468 | 0.79395 | 0.78415 | 0.77066 | 0.76027 | 0.74993 | 0.71721 | 0.68344 | 0.61172 | 0.4888 | 0.1221 | -0.39508 | 0.88194 | 0.87761 | 0.87431 | 0.86785 | 0.86088 | 0.85401 | 0.84818 | 0.84223 | 0.80441 | 0.7632 | 0.68598 | 0.52914 | 0.075019 | -0.5685 | 0.85063 | 0.84217 | 0.83796 | 0.8282 | 0.81857 | 0.80635 | 0.79678 | 0.78721 | 0.74666 | 0.70473 | 0.62159 | 0.46578 | 0.0093579 | -0.63576
| EDAY | CT |  |  |  | 0.82083 | 0.81527 | 0.80873 | 0.795 | 0.78415 | 0.77066 | 0.76027 | 0.74993 | 0.72495 | 0.6941 | 0.63849 | 0.546 | 0.36446 | 0.15619 | 0.88288 | 0.87997 | 0.87565 | 0.86785 | 0.86088 | 0.85401 | 0.84818 | 0.84223 | 0.81264 | 0.77949 | 0.71833 | 0.59625 | 0.37653 | 0.11605 | 0.85207 | 0.84772 | 0.84155 | 0.82885 | 0.81857 | 0.80635 | 0.79678 | 0.78721 | 0.75655 | 0.72014 | 0.65456 | 0.53612 | 0.31325 | 0.054418
| EDAY | LW |  |  |  | 0.81841 | 0.80899 | 0.80468 | 0.79395 | 0.78766 | 0.77855 | 0.76418 | 0.75411 | 0.71721 | 0.68344 | 0.61172 | 0.4888 | 0.1221 | -0.39508 | 0.88194 | 0.87761 | 0.87431 | 0.86891 | 0.86484 | 0.85999 | 0.85185 | 0.84476 | 0.80441 | 0.7632 | 0.68598 | 0.52914 | 0.075019 | -0.5685 | 0.85063 | 0.84217 | 0.83796 | 0.8282 | 0.82226 | 0.81392 | 0.8006 | 0.79038 | 0.74666 | 0.70473 | 0.62159 | 0.46578 | 0.0093579 | -0.63576
| EDAY | ST |  |  |  | 0.82273 | 0.82154 | 0.82002 | 0.8162 | 0.81071 | 0.80787 | 0.80447 | 0.80225 | 0.75031 | 0.72887 | 0.67521 | 0.55707 | 0.28598 | -0.01369 | 0.88359 | 0.88273 | 0.88159 | 0.87942 | 0.87639 | 0.8742 | 0.87154 | 0.86902 | 0.80944 | 0.78537 | 0.7289 | 0.58908 | 0.25347 | -0.12011 | 0.85227 | 0.8516 | 0.85075 | 0.84838 | 0.84334 | 0.84046 | 0.83685 | 0.83402 | 0.77159 | 0.74582 | 0.68259 | 0.54078 | 0.20446 | -0.16823
| EDAY | FS |  |  |  | 0.82285 | 0.8237 | 0.82091 | 0.81716 | 0.81183 | 0.8116 | 0.80734 | 0.80456 | 0.78216 | 0.76613 | 0.73377 | 0.69379 | 0.65419 | 0.61901 | 0.88368 | 0.88362 | 0.8821 | 0.88013 | 0.8774 | 0.87649 | 0.87394 | 0.87175 | 0.84823 | 0.8313 | 0.79665 | 0.76095 | 0.72222 | 0.6755 | 0.8524 | 0.85193 | 0.85128 | 0.84931 | 0.84448 | 0.84402 | 0.83997 | 0.83699 | 0.81107 | 0.79243 | 0.75442 | 0.71107 | 0.66854 | 0.62543
FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | NO | NO | 5.2707 | 5.1378 | 4.9647 | 4.722 | 4.5051 | 3.8203 | 3.0833 | 2.4601 | 1.9484 | 1.3659 | 0.16371 | -0.5981 | -1.0766 | -1.4402 | 6.0046 | 5.9803 | 5.9391 | 5.839 | 5.73 | 5.1604 | 4.5138 | 4.0003 | 3.5373 | 3.002 | 1.8614 | 1.1343 | 0.75815 | 0.38123 | 6.0531 | 5.9378 | 5.7875 | 5.5632 | 5.3537 | 4.6895 | 3.9735 | 3.3759 | 2.8884 | 2.3337 | 1.1905 | 0.43655 | -0.036457 | -0.50914
| EDZELL | CT |  |  |  | 5.362 | 5.2764 | 5.1518 | 4.9155 | 4.6973 | 3.9735 | 3.248 | 2.6993 | 2.1745 | 1.5301 | 0.2595 | -0.5981 | -1.0766 | -1.3558 | 6.0087 | 5.9826 | 5.9458 | 5.8794 | 5.8098 | 5.1816 | 4.5454 | 4.1176 | 3.6522 | 3.0643 | 1.9053 | 1.1846 | 0.86402 | 0.53307 | 6.1333 | 6.059 | 5.9515 | 5.7394 | 5.5342 | 4.828 | 4.1189 | 3.6026 | 3.1027 | 2.4872 | 1.2755 | 0.43655 | -0.036457 | -0.33748
| EDZELL | LW |  |  |  | 5.2707 | 5.1378 | 4.9647 | 4.722 | 4.5051 | 3.8203 | 3.0833 | 2.4601 | 1.9484 | 1.3659 | 0.16371 | -0.52314 | -1.0045 | -1.4402 | 6.0046 | 5.9803 | 5.9391 | 5.854 | 5.73 | 5.1604 | 4.5138 | 4.0003 | 3.5373 | 3.002 | 1.8884 | 1.3685 | 0.91521 | 0.42125 | 6.0531 | 5.9378 | 5.7875 | 5.5632 | 5.3537 | 4.6895 | 3.9735 | 3.3759 | 2.8884 | 2.3337 | 1.1905 | 0.53538 | 0.011443 | -0.50914
| EDZELL | ST |  |  |  | 5.3992 | 5.3359 | 5.2621 | 5.0682 | 4.9277 | 4.3762 | 3.723 | 3.263 | 2.7496 | 2.1526 | 0.96211 | -0.13598 | -0.67501 | -1.1385 | 6.0124 | 5.9993 | 5.9805 | 5.839 | 5.7425 | 5.1963 | 4.5283 | 4.0921 | 3.5951 | 3.0169 | 1.8614 | 1.1343 | 0.75815 | 0.38123 | 6.166 | 6.1124 | 6.0515 | 5.8497 | 5.7007 | 5.1706 | 4.5132 | 4.0707 | 3.5702 | 3.0021 | 1.866 | 0.79757 | 0.24264 | -0.24313
| EDZELL | FS |  |  |  | 5.4218 | 5.3777 | 5.3205 | 5.2153 | 5.135 | 4.7266 | 4.3715 | 3.9975 | 3.5824 | 3.1664 | 2.2529 | 0.88005 | -0.057316 | -0.35673 | 6.0138 | 6.003 | 5.9868 | 5.943 | 5.9056 | 5.5184 | 5.1819 | 4.8318 | 4.4566 | 4.0762 | 3.2412 | 2.3594 | 1.6149 | 1.3193 | 6.1859 | 6.149 | 6.1026 | 6.0068 | 5.9283 | 5.54 | 5.2014 | 4.8458 | 4.4511 | 4.0572 | 3.1923 | 1.9143 | 1.0364 | 0.76151
MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | NO | 10.1401 | 10.0518 | 9.899 | 9.6409 | 9.366 | 9.1045 | 8.7464 | 8.354 | 7.9497 | 7.5183 | 6.679 | 6.0658 | 5.4026 | 4.7046 | 11.0156 | 10.9575 | 10.8506 | 10.7139 | 10.5621 | 10.3927 | 10.2114 | 9.9694 | 9.6805 | 9.3708 | 8.7731 | 8.2149 | 7.6008 | 6.8655 | 10.6446 | 10.5572 | 10.4078 | 10.1706 | 9.9161 | 9.6765 | 9.3414 | 8.972 | 8.5768 | 8.1556 | 7.3381 | 6.7243 | 5.9904 | 5.1287
| EDZELL STREET | CT |  |  |  | 10.2222 | 10.1772 | 10.0831 | 9.7969 | 9.4937 | 9.227 | 8.959 | 8.7115 | 8.3499 | 7.9049 | 7.0373 | 6.0753 | 5.4467 | 4.9315 | 11.0454 | 11.0058 | 10.9316 | 10.7551 | 10.5621 | 10.3927 | 10.2189 | 10.0699 | 9.8213 | 9.5054 | 8.8953 | 8.2149 | 7.6008 | 6.8802 | 10.7135 | 10.6665 | 10.5743 | 10.3048 | 10.0173 | 9.762 | 9.5042 | 9.2718 | 8.9213 | 8.489 | 7.6499 | 6.7243 | 6.0835 | 5.528
| EDZELL STREET | LW |  |  |  | 10.1401 | 10.0518 | 9.899 | 9.6409 | 9.366 | 9.1045 | 8.7464 | 8.354 | 7.9497 | 7.5183 | 6.679 | 6.0658 | 5.4026 | 4.7046 | 11.0156 | 10.9575 | 10.8506 | 10.7139 | 10.5626 | 10.4256 | 10.2114 | 9.9694 | 9.6805 | 9.3708 | 8.7731 | 8.3905 | 7.7183 | 6.8655 | 10.6446 | 10.5572 | 10.4078 | 10.1706 | 9.9161 | 9.6765 | 9.3414 | 8.972 | 8.5768 | 8.1556 | 7.3381 | 6.7466 | 5.9904 | 5.1287
| EDZELL STREET | ST |  |  |  | 10.2399 | 10.2194 | 10.1885 | 10.1201 | 10.0497 | 9.9742 | 9.8621 | 9.7539 | 9.5622 | 9.381 | 8.9481 | 7.774 | 6.9465 | 6.1605 | 11.0514 | 11.0317 | 11.0039 | 10.9363 | 10.8673 | 10.7978 | 10.6853 | 10.589 | 10.3959 | 10.2329 | 9.8456 | 8.8516 | 8.0241 | 7.1175 | 10.7277 | 10.7064 | 10.6758 | 10.6023 | 10.5279 | 10.4505 | 10.3293 | 10.219 | 10.0103 | 9.8256 | 9.3852 | 8.2096 | 7.3397 | 6.5075
| EDZELL STREET | FS |  |  |  | 10.2382 | 10.22 | 10.1956 | 10.149 | 10.0953 | 10.0315 | 9.9621 | 9.8843 | 9.7455 | 9.5995 | 9.2726 | 8.3626 | 7.3415 | 6.8331 | 11.0517 | 11.0336 | 11.0101 | 10.9699 | 10.9218 | 10.8675 | 10.806 | 10.7364 | 10.6141 | 10.4882 | 10.2006 | 9.4282 | 8.4653 | 7.6252 | 10.7269 | 10.7075 | 10.6834 | 10.637 | 10.5827 | 10.5191 | 10.4493 | 10.3712 | 10.2306 | 10.0855 | 9.7603 | 8.884 | 7.9121 | 7.4511
ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | NO | 8.2104 | 7.5108 | 6.7118 | 6.0315 | 5.3324 | 4.6397 | 3.8056 | 2.699 | 1.7833 | 0.81892 | -1.1534 | -1.9099 | -2.9299 | -3.455 | 9.2671 | 8.779 | 8.2129 | 7.849 | 7.4734 | 7.1118 | 6.6427 | 5.9282 | 5.3438 | 4.717 | 3.4376 | 2.9093 | 2.1659 | 1.3861 | 9.4207 | 8.9096 | 8.3018 | 7.7844 | 7.2457 | 6.7102 | 5.9637 | 4.9465 | 4.0859 | 3.1727 | 1.3109 | 0.71423 | -0.17878 | -0.6575
| ELGIN | CT |  |  |  | 8.3966 | 7.8417 | 7.1936 | 6.5116 | 5.8165 | 5.1153 | 4.3611 | 3.4213 | 2.5011 | 1.4965 | -0.48994 | -1.9099 | -2.9299 | -3.455 | 9.3499 | 8.9376 | 8.454 | 8.0433 | 7.6224 | 7.2085 | 6.7671 | 6.1696 | 5.6079 | 4.967 | 3.7029 | 2.9093 | 2.1659 | 1.3861 | 9.547 | 9.1402 | 8.6513 | 8.1075 | 7.5431 | 6.9965 | 6.3793 | 5.5363 | 4.6938 | 3.7548 | 1.9044 | 0.71423 | -0.17878 | -0.6575
| ELGIN | LW |  |  |  | 8.2104 | 7.5108 | 6.7118 | 6.0315 | 5.3324 | 4.6397 | 3.8056 | 2.699 | 1.7833 | 0.81892 | -1.1534 | -1.7112 | -2.3331 | -2.674 | 9.2671 | 8.779 | 8.2129 | 7.849 | 7.4734 | 7.1118 | 6.6427 | 5.9282 | 5.3438 | 4.717 | 3.4376 | 3.3639 | 2.9924 | 2.6937 | 9.4207 | 8.9096 | 8.3018 | 7.7844 | 7.2457 | 6.7102 | 5.9637 | 4.9465 | 4.0859 | 3.1727 | 1.3109 | 0.95018 | 0.36696 | 0.0064545
| ELGIN | ST |  |  |  | 8.4402 | 7.9493 | 7.4098 | 7.0543 | 6.7057 | 6.3412 | 5.9261 | 5.3183 | 4.7866 | 4.1968 | 2.8802 | 1.6489 | 0.73511 | -0.25902 | 9.3695 | 9.0036 | 8.6019 | 8.3568 | 8.1145 | 7.8622 | 7.5587 | 7.0804 | 6.67 | 6.2153 | 5.1897 | 4.1679 | 3.3723 | 2.4136 | 9.5766 | 9.2232 | 8.8317 | 8.5445 | 8.2599 | 7.965 | 7.6113 | 7.1161 | 6.6462 | 6.127 | 4.8533 | 3.6002 | 2.8053 | 1.9743
| ELGIN | FS |  |  |  | 8.5326 | 8.1479 | 7.7203 | 7.4358 | 7.1361 | 6.8328 | 6.5198 | 6.0429 | 5.6008 | 5.1285 | 4.1097 | 2.4931 | 1.0737 | 0.26584 | 9.438 | 9.1503 | 8.8302 | 8.6394 | 8.4354 | 8.2283 | 8.0117 | 7.6365 | 7.3081 | 6.9523 | 6.1631 | 4.8054 | 3.3119 | 1.8692 | 9.6397 | 9.3591 | 9.0446 | 8.8203 | 8.5806 | 8.3366 | 8.0807 | 7.6947 | 7.3202 | 6.9192 | 6.0422 | 4.5024 | 3.2068 | 2.5743
ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | NO | -6.7418 | -7.1216 | -7.518 | -7.9896 | -8.3414 | -8.5482 | -8.7157 | -8.8636 | -9.0312 | -9.2216 | -9.6342 | -9.797 | -10.2786 | -10.6215 | -7.1015 | -7.528 | -7.9545 | -8.4707 | -8.8562 | -9.0982 | -9.323 | -9.4771 | -9.5773 | -9.6823 | -9.8911 | -10.0904 | -10.4763 | -10.8675 | -7.6602 | -8.0474 | -8.4472 | -8.9327 | -9.3006 | -9.5242 | -9.7249 | -9.922 | -10.0544 | -10.1916 | -10.4675 | -10.6365 | -11.1163 | -11.5347
| ELLIOT DEPOT | CT |  |  |  | -6.5978 | -6.9706 | -7.4059 | -7.8603 | -8.1059 | -8.3767 | -8.5843 | -8.6917 | -8.7904 | -8.8794 | -9.3295 | -9.797 | -10.2786 | -10.6215 | -6.9318 | -7.3534 | -7.8225 | -8.308 | -8.555 | -8.8514 | -9.0827 | -9.2155 | -9.3513 | -9.4762 | -9.7302 | -10.0904 | -10.4763 | -10.8675 | -7.5098 | -7.8912 | -8.3288 | -8.7866 | -9.0335 | -9.329 | -9.5616 | -9.6693 | -9.7705 | -9.9305 | -10.2473 | -10.6365 | -11.1163 | -11.4773
| ELLIOT DEPOT | LW |  |  |  | -6.7418 | -7.1216 | -7.518 | -7.9896 | -8.3414 | -8.5482 | -8.7157 | -8.8636 | -9.0312 | -9.2216 | -9.6342 | -9.6912 | -10.1034 | -10.5552 | -7.1015 | -7.528 | -7.9545 | -8.4707 | -8.8562 | -9.0982 | -9.323 | -9.4771 | -9.5773 | -9.6823 | -9.8911 | -9.9098 | -10.3236 | -10.8628 | -7.6602 | -8.0474 | -8.4472 | -8.9327 | -9.3006 | -9.5242 | -9.7249 | -9.922 | -10.0544 | -10.1916 | -10.4675 | -10.5085 | -10.9812 | -11.5347
| ELLIOT DEPOT | ST |  |  |  | -6.5959 | -6.9614 | -7.3641 | -7.8693 | -8.1208 | -8.3021 | -8.528 | -8.6298 | -8.7559 | -8.827 | -9.0057 | -9.148 | -9.4128 | -9.7915 | -6.9308 | -7.3475 | -7.7946 | -8.3665 | -8.6442 | -8.8413 | -9.1068 | -9.2145 | -9.3497 | -9.4142 | -9.5815 | -9.8531 | -10.2951 | -10.8483 | -7.5084 | -7.8836 | -8.2945 | -8.8323 | -9.1033 | -9.2965 | -9.5606 | -9.6705 | -9.8105 | -9.8827 | -10.0635 | -10.2968 | -10.6174 | -11.0137
| ELLIOT DEPOT | FS |  |  |  | -6.1686 | -6.4473 | -6.7802 | -7.1277 | -7.3077 | -7.4528 | -7.6015 | -7.7162 | -7.8462 | -8.0032 | -8.2963 | -8.5895 | -8.662 | -8.9529 | -6.4222 | -6.7386 | -7.108 | -7.4923 | -7.6837 | -7.8393 | -8.0073 | -8.1351 | -8.2807 | -8.4556 | -8.7809 | -9.2063 | -9.5092 | -9.9223 | -7.059 | -7.3449 | -7.6851 | -8.0435 | -8.2298 | -8.3819 | -8.539 | -8.6603 | -8.7979 | -8.9609 | -9.2653 | -9.6019 | -9.6804 | -9.8554
DYCE | ELLON 11 kV | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 0.066007 | -0.35224 | 10.2017 | 9.3062 | 8.2904 | 7.2848 | 5.7851 | 4.2087 | 2.9086 | 1.5704 | -0.75321 | -0.888 | -2.4962 | -3.6065 | 2.7246 | 2.506 | 12.7322 | 12.2318 | 11.6247 | 11.0154 | 9.9628 | 8.9027 | 8.0501 | 7.1569 | 5.6661 | 5.8525 | 4.4324 | 2.9618 | 1.2002 | 0.81838 | 10.8642 | 10.0168 | 9.0503 | 8.0783 | 6.6197 | 5.1489 | 4.0019 | 2.8215 | 0.80178 | 0.6885 | -0.88305 | -1.9116
| ELLON 11 kV | CT |  |  |  | 0.38213 | 0.090447 | 10.8289 | 9.886 | 8.8762 | 7.9101 | 6.6591 | 5.4884 | 4.2631 | 2.901 | 0.58325 | -0.58108 | -2.4962 | -3.6065 | 2.8515 | 2.6566 | 12.9516 | 12.4064 | 11.8064 | 11.1919 | 10.288 | 9.5092 | 8.7093 | 7.7942 | 6.3352 | 5.8525 | 4.4324 | 2.9618 | 1.511 | 1.2431 | 11.4545 | 10.5959 | 9.6792 | 8.7518 | 7.5037 | 6.3901 | 5.2728 | 4.0544 | 2.0084 | 0.96963 | -0.88305 | -1.9116
| ELLON 11 kV | LW |  |  |  | 0.066007 | -0.35224 | 10.2017 | 9.3062 | 8.2904 | 7.2848 | 5.7851 | 4.2087 | 2.9086 | 1.5704 | -0.75321 | -0.888 | -2.1709 | -2.8946 | 2.7246 | 2.506 | 12.7322 | 12.2318 | 11.6247 | 11.0154 | 9.9628 | 8.9027 | 8.0501 | 7.1569 | 5.6661 | 6.0581 | 5.3106 | 4.7258 | 1.2002 | 0.81838 | 10.8642 | 10.0168 | 9.0503 | 8.0783 | 6.6197 | 5.1489 | 4.0019 | 2.8215 | 0.80178 | 0.6885 | -0.58167 | -1.3412
| ELLON 11 kV | ST |  |  |  | 0.48239 | 0.32452 | 11.2802 | 10.9141 | 10.529 | 10.1581 | 9.382 | 8.6566 | 7.9046 | 7.0964 | 5.6326 | 4.1041 | 2.2827 | 0.42817 | 2.8959 | 2.7843 | 13.225 | 12.9158 | 12.6079 | 12.331 | 11.6149 | 11.0127 | 10.4154 | 9.7753 | 8.6761 | 7.5546 | 6.0934 | 4.3415 | 1.6115 | 1.4674 | 11.8703 | 11.5073 | 11.1434 | 10.8091 | 10.0093 | 9.33 | 8.6458 | 7.9234 | 6.6606 | 5.2319 | 3.5559 | 1.8771
| ELLON 11 kV | FS |  |  |  | 0.61434 | 0.48747 | 11.4896 | 11.2503 | 10.9747 | 10.6803 | 10.226 | 9.68 | 9.0739 | 8.4523 | 7.2934 | 5.241 | 2.6506 | 1.1828 | 3.0121 | 2.9154 | 13.3793 | 13.2079 | 13.01 | 12.794 | 12.4124 | 11.958 | 11.497 | 11.0169 | 10.1408 | 8.6649 | 6.2281 | 3.7738 | 1.7576 | 1.6417 | 12.0867 | 11.8678 | 11.6205 | 11.3558 | 10.9153 | 10.4037 | 9.8488 | 9.2818 | 8.2515 | 6.53 | 4.1236 | 2.8351
TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0.143 | 0.13667 | 0.12982 | 0.11918 | 0.10502 | 0.091203 | 0.067334 | 0.058822 | 0.028608 | 0.019793 | -0.0017683 | -0.063015 | -0.13654 | -0.20977 | 0.16671 | 0.16417 | 0.1611 | 0.14213 | 0.12626 | 0.11528 | 0.0813 | 0.071106 | 0.041712 | 0.031414 | 0.0077729 | -0.058698 | -0.14546 | -0.23374 | 0.15607 | 0.15059 | 0.14446 | 0.12867 | 0.11178 | 0.099766 | 0.065671 | 0.055325 | 0.021226 | 0.010658 | -0.014536 | -0.086283 | -0.17542 | -0.26461
| EREDINE | CT |  |  |  | 0.14489 | 0.14061 | 0.13753 | 0.12987 | 0.12225 | 0.091203 | 0.067662 | 0.061252 | 0.04826 | 0.034137 | 0.010279 | -0.044085 | -0.093965 | -0.1431 | 0.16742 | 0.16555 | 0.16389 | 0.15831 | 0.15116 | 0.12223 | 0.09492 | 0.087391 | 0.073656 | 0.05913 | 0.033248 | -0.028988 | -0.086819 | -0.1482 | 0.15777 | 0.15395 | 0.15103 | 0.14328 | 0.1349 | 0.10038 | 0.071956 | 0.064258 | 0.049245 | 0.033132 | 0.0054107 | -0.059796 | -0.11965 | -0.18027
| EREDINE | LW |  |  |  | 0.143 | 0.13667 | 0.12982 | 0.12715 | 0.12601 | 0.12129 | 0.11369 | 0.10612 | 0.099745 | 0.092687 | 0.080305 | 0.0572 | -0.027211 | -0.14513 | 0.16671 | 0.16417 | 0.1611 | 0.15961 | 0.1586 | 0.15641 | 0.15272 | 0.14888 | 0.14218 | 0.13501 | 0.12211 | 0.097509 | -0.0045658 | -0.15197 | 0.15607 | 0.15059 | 0.14446 | 0.14188 | 0.14062 | 0.13637 | 0.12947 | 0.12256 | 0.11532 | 0.10741 | 0.09348 | 0.066143 | -0.037723 | -0.18512
| EREDINE | ST |  |  |  | 0.14489 | 0.14287 | 0.1387 | 0.11918 | 0.10502 | 0.094747 | 0.067334 | 0.058822 | 0.028608 | 0.019793 | -0.0017683 | -0.063015 | -0.13654 | -0.20977 | 0.16743 | 0.16651 | 0.16482 | 0.14213 | 0.12626 | 0.11528 | 0.0813 | 0.071106 | 0.041712 | 0.031414 | 0.0077729 | -0.058698 | -0.14546 | -0.23374 | 0.15778 | 0.15591 | 0.15231 | 0.12867 | 0.11178 | 0.099766 | 0.065671 | 0.055325 | 0.021226 | 0.010658 | -0.014536 | -0.086283 | -0.17542 | -0.26461
| EREDINE | FS |  |  |  | 0.14492 | 0.14468 | 0.14075 | 0.1366 | 0.13071 | 0.12604 | 0.12127 | 0.11182 | 0.10179 | 0.093943 | 0.07595 | 0.051079 | 0.03888 | 0.024277 | 0.16745 | 0.16723 | 0.16558 | 0.16069 | 0.15514 | 0.14951 | 0.14378 | 0.13678 | 0.12625 | 0.1185 | 0.10193 | 0.084218 | 0.071489 | 0.057078 | 0.15781 | 0.1576 | 0.15406 | 0.14898 | 0.14243 | 0.13674 | 0.13094 | 0.12125 | 0.10966 | 0.10082 | 0.081088 | 0.056293 | 0.04294 | 0.027675
INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0.87396 | 0.86045 | 0.85252 | 0.83435 | 0.81751 | 0.80453 | 0.78538 | 0.7632 | 0.75402 | 0.74028 | 0.71677 | 0.70099 | 0.67958 | 0.66968 | 0.91474 | 0.90898 | 0.90409 | 0.89599 | 0.88802 | 0.88054 | 0.87174 | 0.86 | 0.85242 | 0.84219 | 0.82334 | 0.81436 | 0.79562 | 0.77959 | 0.89062 | 0.87884 | 0.8711 | 0.85503 | 0.8399 | 0.82819 | 0.81047 | 0.78991 | 0.78041 | 0.76721 | 0.74283 | 0.72754 | 0.7096 | 0.70094
| ERROGIE | CT |  |  |  | 0.8818 | 0.87416 | 0.86543 | 0.8468 | 0.8261 | 0.80931 | 0.79221 | 0.77164 | 0.76292 | 0.75159 | 0.72746 | 0.71244 | 0.67958 | 0.66968 | 0.91744 | 0.9136 | 0.90861 | 0.89905 | 0.88858 | 0.88054 | 0.87228 | 0.86276 | 0.85601 | 0.84707 | 0.82773 | 0.81436 | 0.79562 | 0.78077 | 0.8973 | 0.89049 | 0.88232 | 0.86533 | 0.84645 | 0.83144 | 0.81618 | 0.79801 | 0.78895 | 0.77788 | 0.75353 | 0.73778 | 0.7096 | 0.70094
| ERROGIE | LW |  |  |  | 0.87396 | 0.86045 | 0.85252 | 0.83435 | 0.81751 | 0.80453 | 0.78538 | 0.7632 | 0.75402 | 0.74028 | 0.71677 | 0.70099 | 0.68895 | 0.67989 | 0.91474 | 0.90898 | 0.90409 | 0.89599 | 0.88802 | 0.8818 | 0.87174 | 0.86 | 0.85242 | 0.84219 | 0.82334 | 0.81593 | 0.8111 | 0.80796 | 0.89062 | 0.87884 | 0.8711 | 0.85503 | 0.8399 | 0.82819 | 0.81047 | 0.78991 | 0.78041 | 0.76721 | 0.74283 | 0.72754 | 0.71711 | 0.70979
| ERROGIE | ST |  |  |  | 0.88537 | 0.87734 | 0.87045 | 0.86333 | 0.85555 | 0.84604 | 0.8372 | 0.8285 | 0.8167 | 0.8077 | 0.78182 | 0.72728 | 0.69858 | 0.68296 | 0.9187 | 0.91523 | 0.91198 | 0.90845 | 0.90439 | 0.89955 | 0.89462 | 0.88939 | 0.88267 | 0.87655 | 0.86001 | 0.82211 | 0.80323 | 0.78728 | 0.90028 | 0.89332 | 0.88727 | 0.88088 | 0.87382 | 0.86526 | 0.85708 | 0.84889 | 0.83788 | 0.82934 | 0.80508 | 0.75141 | 0.72565 | 0.71274
| ERROGIE | FS |  |  |  | 0.88578 | 0.88289 | 0.87816 | 0.87314 | 0.86402 | 0.85466 | 0.85243 | 0.84474 | 0.83388 | 0.8214 | 0.80166 | 0.73457 | 0.69173 | 0.67892 | 0.91886 | 0.91722 | 0.91475 | 0.91215 | 0.90784 | 0.90339 | 0.9012 | 0.89687 | 0.8912 | 0.88466 | 0.87271 | 0.83346 | 0.79881 | 0.77959 | 0.90065 | 0.89804 | 0.89382 | 0.88931 | 0.88122 | 0.87294 | 0.8705 | 0.86343 | 0.85356 | 0.84221 | 0.82391 | 0.76207 | 0.72005 | 0.70959
ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | NO | 4.1859 | 4.0416 | 3.8579 | 3.4679 | 3.0349 | 2.4459 | 1.7993 | 1.2667 | 0.96353 | 0.63986 | 0.0040874 | -0.21693 | -0.57423 | -0.77285 | 4.5995 | 4.5339 | 4.4441 | 4.1602 | 3.8414 | 3.33 | 2.7688 | 2.3649 | 2.1581 | 1.9253 | 1.4706 | 1.4122 | 1.2067 | 1.0499 | 5.034 | 4.904 | 4.7356 | 4.3373 | 3.8963 | 3.2626 | 2.5624 | 2.0109 | 1.7188 | 1.4066 | 0.79537 | 0.59527 | 0.25356 | 0.046838
| ERROL | CT |  |  |  | 4.2978 | 4.2078 | 4.0826 | 3.775 | 3.423 | 2.9629 | 2.5089 | 2.1877 | 1.9196 | 1.6189 | 1.0132 | 0.63577 | 0.071917 | -0.22069 | 4.64 | 4.591 | 4.5189 | 4.3507 | 4.1492 | 3.792 | 3.427 | 3.2327 | 3.083 | 2.8802 | 2.476 | 2.2869 | 1.922 | 1.5257 | 5.1323 | 5.0502 | 4.9339 | 4.6459 | 4.314 | 3.84 | 3.3643 | 3.0571 | 2.807 | 2.524 | 1.9557 | 1.6293 | 1.1226 | 0.85206
| ERROL | LW |  |  |  | 4.1859 | 4.0416 | 3.8579 | 3.4679 | 3.0349 | 2.4459 | 1.7993 | 1.2667 | 0.96353 | 0.63986 | 0.0040874 | -0.21693 | -0.57423 | -0.77285 | 4.5995 | 4.5339 | 4.4441 | 4.1602 | 3.8414 | 3.33 | 2.7688 | 2.3649 | 2.1581 | 1.9253 | 1.4706 | 1.4122 | 1.2067 | 1.0499 | 5.034 | 4.904 | 4.7356 | 4.3373 | 3.8963 | 3.2626 | 2.5624 | 2.0109 | 1.7188 | 1.4066 | 0.79537 | 0.59527 | 0.25356 | 0.046838
| ERROL | ST |  |  |  | 4.3356 | 4.2907 | 4.2327 | 3.9975 | 3.785 | 3.6001 | 3.254 | 3.0667 | 2.9132 | 2.7504 | 2.3771 | 1.7307 | 1.2417 | 0.7339 | 4.6577 | 4.6313 | 4.5985 | 4.3586 | 4.1674 | 4.0156 | 3.6506 | 3.4951 | 3.3885 | 3.2647 | 2.9731 | 2.495 | 2.0936 | 1.636 | 5.1704 | 5.1266 | 5.0727 | 4.805 | 4.5773 | 4.3871 | 3.9876 | 3.7917 | 3.6429 | 3.4879 | 3.1331 | 2.5506 | 2.0709 | 1.6124
| ERROL | FS |  |  |  | 4.3557 | 4.3204 | 4.2797 | 4.1813 | 4.0603 | 3.9321 | 3.8067 | 3.6813 | 3.5458 | 3.4079 | 3.104 | 2.376 | 1.6594 | 1.2504 | 4.667 | 4.6448 | 4.619 | 4.5413 | 4.4526 | 4.3548 | 4.2572 | 4.1615 | 4.0806 | 3.9969 | 3.7812 | 3.2823 | 2.6338 | 2.0476 | 5.191 | 5.1567 | 5.1184 | 5.0147 | 4.8959 | 4.7689 | 4.6416 | 4.5155 | 4.3897 | 4.2612 | 3.977 | 3.3152 | 2.6536 | 2.2951
TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0.061074 | 0.058653 | 0.055732 | 0.037842 | 0.022147 | 0.011542 | -0.023647 | -0.036046 | -0.063064 | -0.075563 | -0.099341 | -0.17049 | -0.2579 | -0.34581 | 0.073009 | 0.071897 | 0.07033 | 0.044239 | 0.024795 | 0.01174 | -0.031996 | -0.045444 | -0.078836 | -0.092211 | -0.12065 | -0.20188 | -0.31019 | -0.42006 | 0.064848 | 0.062695 | 0.059979 | 0.035914 | 0.016362 | 0.0031854 | -0.040702 | -0.055274 | -0.088896 | -0.10349 | -0.13271 | -0.21809 | -0.32685 | -0.43673
| FINCASTLE | CT |  |  |  | 0.061132 | 0.060668 | 0.057934 | 0.053694 | 0.043272 | 0.015489 | -0.013996 | -0.02362 | -0.038931 | -0.053118 | -0.079353 | -0.13806 | -0.19504 | -0.25633 | 0.073065 | 0.072661 | 0.071273 | 0.066428 | 0.057332 | 0.024652 | -0.010136 | -0.020093 | -0.036944 | -0.053911 | -0.085061 | -0.1604 | -0.23133 | -0.30772 | 0.064918 | 0.064419 | 0.061924 | 0.056799 | 0.045529 | 0.011724 | -0.0242 | -0.035293 | -0.053423 | -0.070671 | -0.10283 | -0.17706 | -0.24812 | -0.3246
| FINCASTLE | LW |  |  |  | 0.061074 | 0.058653 | 0.055732 | 0.054928 | 0.052023 | 0.051238 | 0.045779 | 0.043915 | 0.036884 | 0.02577 | 0.015361 | -0.0083364 | -0.11311 | -0.26628 | 0.073009 | 0.071897 | 0.07033 | 0.0696 | 0.068042 | 0.067337 | 0.064549 | 0.062864 | 0.054961 | 0.045369 | 0.031471 | 0.0019771 | -0.12888 | -0.32035 | 0.064848 | 0.062695 | 0.059979 | 0.059077 | 0.056373 | 0.055502 | 0.050499 | 0.048416 | 0.040133 | 0.028247 | 0.014828 | -0.014778 | -0.14569 | -0.33715
| FINCASTLE | ST |  |  |  | 0.061144 | 0.060948 | 0.060674 | 0.037842 | 0.022147 | 0.011542 | -0.023647 | -0.036046 | -0.063064 | -0.075563 | -0.099341 | -0.17049 | -0.2579 | -0.34581 | 0.073071 | 0.072896 | 0.072648 | 0.044239 | 0.024795 | 0.01174 | -0.031996 | -0.045444 | -0.078836 | -0.092211 | -0.12065 | -0.20188 | -0.31019 | -0.42006 | 0.064926 | 0.064709 | 0.064403 | 0.035914 | 0.016362 | 0.0031854 | -0.040702 | -0.055274 | -0.088896 | -0.10349 | -0.13271 | -0.21809 | -0.32685 | -0.43673
| FINCASTLE | FS |  |  |  | 0.061163 | 0.061001 | 0.060776 | 0.055889 | 0.050907 | 0.045137 | 0.03734 | 0.030209 | 0.020098 | 0.01289 | -0.00043125 | -0.019427 | -0.034225 | -0.0441 | 0.073088 | 0.072943 | 0.072739 | 0.066733 | 0.060638 | 0.053571 | 0.045744 | 0.038783 | 0.026393 | 0.017674 | 0.00044793 | -0.016432 | -0.029403 | -0.041721 | 0.064946 | 0.064767 | 0.064515 | 0.058446 | 0.052268 | 0.045112 | 0.036238 | 0.02821 | 0.015666 | 0.0067666 | -0.010248 | -0.031012 | -0.046751 | -0.05908
SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | NO | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95651 | 0.94109 | 0.90074 | 0.77055 | 0.40915 | -0.1046 | -0.57937 | -1.0496 | -1.5504 | -2.062 | -2.7637 | -3.4317 | -4.0468 | -4.5178 | -5.0198 | -5.6066 | -6.2955 | -6.5091 | -7.0148 | -7.657 | -0.93296 | -1.3686 | -1.837 | -2.3165 | -2.9468 | -3.5361 | -4.0965 | -4.5415 | -5.0151 | -5.5631 | -6.2495 | -6.2798 | -6.7767 | -7.4188
| FIRTH | CT |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98023 | 0.96039 | 0.92438 | 0.82425 | 0.65407 | 0.45016 | -0.51474 | -0.95407 | -1.4239 | -1.9159 | -2.5663 | -3.2251 | -3.8356 | -4.3016 | -4.8198 | -5.4601 | -6.1952 | -6.436 | -6.703 | -6.9813 | -0.87117 | -1.2787 | -1.7179 | -2.1865 | -2.7963 | -3.3878 | -3.9405 | -4.3711 | -4.8545 | -5.4264 | -6.1303 | -6.208 | -6.4643 | -6.7328
| FIRTH | LW |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97422 | 0.9475 | 0.90074 | 0.77055 | 0.40915 | -0.1046 | -0.57937 | -1.0496 | -1.5504 | -2.062 | -2.7637 | -3.4317 | -4.0468 | -4.5178 | -5.0198 | -5.6066 | -6.2955 | -6.5091 | -7.0148 | -7.657 | -0.93296 | -1.3686 | -1.837 | -2.3165 | -2.9468 | -3.5361 | -4.0965 | -4.5415 | -5.0151 | -5.5631 | -6.2495 | -6.2798 | -6.7767 | -7.4188
| FIRTH | ST |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95651 | 0.94109 | 0.90717 | 0.80934 | 0.54636 | 0.25164 | -0.51042 | -0.93388 | -1.3852 | -1.8554 | -2.5227 | -3.1753 | -3.778 | -4.2326 | -4.7702 | -5.3985 | -6.1294 | -6.3922 | -6.7665 | -7.1564 | -0.85619 | -1.2433 | -1.6589 | -2.0921 | -2.678 | -3.2447 | -3.7889 | -4.2038 | -4.6991 | -5.2736 | -5.9595 | -6.1414 | -6.5183 | -6.9016
| FIRTH | FS |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98426 | 0.97358 | 0.95223 | 0.9393 | 0.92488 | 0.89195 | -0.32037 | -0.64193 | -0.98995 | -1.3543 | -1.8588 | -2.3553 | -2.8297 | -3.2648 | -3.7502 | -4.3134 | -5.0797 | -5.7882 | -6.2554 | -6.395 | -0.68665 | -0.97938 | -1.2986 | -1.6369 | -2.1027 | -2.5488 | -2.9674 | -3.3552 | -3.7878 | -4.2881 | -4.9916 | -5.5725 | -5.9873 | -6.1028
THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | NO | 0.8779 | 0.8745 | 0.86685 | 0.85494 | 0.84682 | 0.84105 | 0.82874 | 0.81896 | 0.78599 | 0.75461 | 0.69334 | 0.56443 | 0.19841 | -0.31587 | 0.92292 | 0.92112 | 0.91727 | 0.91208 | 0.90743 | 0.90328 | 0.89754 | 0.893 | 0.85521 | 0.81784 | 0.74804 | 0.5889 | 0.13528 | -0.50715 | 0.89929 | 0.89615 | 0.88922 | 0.87878 | 0.87146 | 0.86577 | 0.85466 | 0.84573 | 0.80632 | 0.76817 | 0.69468 | 0.53337 | 0.077715 | -0.56492
| FLOTTA | CT |  |  |  | 0.88219 | 0.87876 | 0.87608 | 0.85943 | 0.84961 | 0.84131 | 0.82874 | 0.82016 | 0.79244 | 0.7692 | 0.71887 | 0.62266 | 0.43983 | 0.23245 | 0.9245 | 0.92269 | 0.92054 | 0.91283 | 0.90743 | 0.90328 | 0.89754 | 0.89316 | 0.86367 | 0.83522 | 0.78046 | 0.65763 | 0.43951 | 0.18218 | 0.90295 | 0.89982 | 0.89717 | 0.88236 | 0.87322 | 0.86577 | 0.85466 | 0.84692 | 0.81464 | 0.78599 | 0.7273 | 0.60447 | 0.3811 | 0.12305
| FLOTTA | LW |  |  |  | 0.8779 | 0.8745 | 0.86685 | 0.85494 | 0.84682 | 0.84105 | 0.82953 | 0.81896 | 0.78599 | 0.75461 | 0.69334 | 0.56443 | 0.19841 | -0.31587 | 0.92292 | 0.92112 | 0.91727 | 0.91208 | 0.90805 | 0.90499 | 0.89902 | 0.893 | 0.85559 | 0.81784 | 0.74804 | 0.5889 | 0.13528 | -0.50715 | 0.89929 | 0.89615 | 0.88922 | 0.87878 | 0.87146 | 0.86615 | 0.85565 | 0.84573 | 0.80632 | 0.76817 | 0.69468 | 0.53337 | 0.077715 | -0.56492
| FLOTTA | ST |  |  |  | 0.8875 | 0.88141 | 0.8822 | 0.87605 | 0.87437 | 0.8688 | 0.86505 | 0.86097 | 0.8127 | 0.78825 | 0.74376 | 0.62504 | 0.35267 | 0.050046 | 0.92646 | 0.92398 | 0.92395 | 0.92124 | 0.92004 | 0.91731 | 0.9151 | 0.91259 | 0.85521 | 0.83107 | 0.78098 | 0.6462 | 0.31242 | -0.059642 | 0.90699 | 0.90219 | 0.90281 | 0.89733 | 0.89572 | 0.89068 | 0.8872 | 0.88338 | 0.82453 | 0.79696 | 0.74128 | 0.60072 | 0.26348 | -0.11175
| FLOTTA | FS |  |  |  | 0.88942 | 0.8853 | 0.88102 | 0.88178 | 0.87675 | 0.8735 | 0.86893 | 0.86523 | 0.8436 | 0.82892 | 0.79656 | 0.75736 | 0.72488 | 0.68466 | 0.9272 | 0.92549 | 0.92364 | 0.92359 | 0.9213 | 0.91962 | 0.91737 | 0.91534 | 0.89268 | 0.87692 | 0.8439 | 0.81404 | 0.78324 | 0.73848 | 0.90711 | 0.90562 | 0.90181 | 0.9024 | 0.8979 | 0.89494 | 0.8908 | 0.8874 | 0.86237 | 0.84529 | 0.80841 | 0.76755 | 0.73133 | 0.68425
ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | NO | 7.7283 | 7.6384 | 7.3699 | 6.9441 | 6.5169 | 5.0663 | 3.3487 | 2.6499 | 1.9628 | 1.2033 | -0.34068 | -0.1746 | -1.0004 | -1.7229 | 8.6886 | 8.5823 | 8.4205 | 8.177 | 7.9188 | 6.5173 | 4.8173 | 4.2539 | 3.585 | 2.8281 | 1.2844 | 2.3895 | 1.6877 | 0.8783 | 8.3091 | 8.1248 | 7.8865 | 7.5173 | 7.1362 | 5.7213 | 4.0198 | 3.3381 | 2.629 | 1.8374 | 0.22498 | 0.61521 | -0.26858 | -1.1263
| FOCHABERS | CT |  |  |  | 7.7294 | 7.64 | 7.4928 | 7.2289 | 6.8096 | 5.3854 | 3.8024 | 3.237 | 2.5537 | 1.7622 | 0.25384 | 0.21097 | -0.62642 | -1.1168 | 8.7184 | 8.6117 | 8.4531 | 8.205 | 7.9654 | 6.5953 | 5.0459 | 4.6397 | 4.0226 | 3.3016 | 1.9185 | 2.7918 | 2.368 | 1.9413 | 8.3181 | 8.2368 | 8.074 | 7.7034 | 7.3415 | 5.9592 | 4.4034 | 3.8762 | 3.1951 | 2.4178 | 0.91927 | 1.0713 | 0.25403 | -0.27908
| FOCHABERS | LW |  |  |  | 7.7283 | 7.6384 | 7.3699 | 6.9441 | 6.5169 | 5.0663 | 3.3487 | 2.6499 | 1.9628 | 1.2033 | -0.34068 | -0.1746 | -1.0004 | -1.7229 | 8.6886 | 8.5823 | 8.4205 | 8.177 | 7.9188 | 6.5173 | 4.8173 | 4.2539 | 3.585 | 2.8281 | 1.2844 | 2.3895 | 1.6877 | 0.8783 | 8.3091 | 8.1248 | 7.8865 | 7.5173 | 7.1362 | 5.7213 | 4.0198 | 3.3381 | 2.629 | 1.8374 | 0.22498 | 0.61521 | -0.26858 | -1.1263
| FOCHABERS | ST |  |  |  | 7.7417 | 7.6998 | 7.6452 | 7.4786 | 7.3326 | 6.1984 | 4.8101 | 4.3993 | 3.719 | 2.911 | 1.1923 | 1.4148 | 0.4453 | -0.49369 | 8.7404 | 8.6897 | 8.6289 | 8.4354 | 8.2662 | 7.0518 | 5.5571 | 5.1947 | 4.5743 | 3.8502 | 2.3345 | 2.9162 | 2.3268 | 1.7414 | 8.3289 | 8.2917 | 8.2429 | 8.0565 | 7.849 | 6.713 | 5.2976 | 4.907 | 4.2712 | 3.5182 | 1.8641 | 2.1279 | 1.1512 | 0.23361
| FOCHABERS | FS |  |  |  | 7.7495 | 7.7168 | 7.6743 | 7.5932 | 7.5118 | 6.701 | 5.8911 | 5.587 | 5.1065 | 4.5569 | 3.3703 | 2.4023 | 1.1887 | 0.60558 | 8.7545 | 8.7165 | 8.6703 | 8.5812 | 8.4893 | 7.6214 | 6.759 | 6.4348 | 5.9325 | 5.43 | 4.3595 | 4.1146 | 3.3135 | 2.9636 | 8.3356 | 8.3067 | 8.269 | 8.1918 | 8.113 | 7.2843 | 6.4598 | 6.1434 | 5.6162 | 5.0881 | 3.9648 | 3.3345 | 2.0339 | 1.5214
NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | NO | 3.8037 | 2.9311 | 1.8639 | 0.22314 | -1.4855 | -3.4535 | -5.672 | -7.687 | -9.3106 | -10.8665 | -14.0076 | -13.6726 | -15.4476 | -16.7623 | 6.9338 | 6.3812 | 5.665 | 4.5854 | 3.4015 | 1.9331 | 0.20273 | -1.3099 | -2.5536 | -3.7108 | -6.0164 | -5.2769 | -6.6551 | -8.0724 | 6.3226 | 5.5925 | 4.6344 | 3.1536 | 1.5787 | -0.29702 | -2.4764 | -4.4346 | -6.0229 | -7.557 | -10.5978 | -9.9707 | -11.7359 | -13.2555
| FORRES | CT |  |  |  | 4.1525 | 3.4553 | 2.5987 | 1.0542 | -0.56201 | -2.4657 | -4.4626 | -6.0547 | -7.6686 | -9.2318 | -12.2229 | -12.7186 | -14.8633 | -16.1345 | 7.0652 | 6.5761 | 5.9552 | 4.9782 | 3.8894 | 2.4779 | 0.96131 | -0.10676 | -1.2767 | -2.4122 | -4.5719 | -4.6816 | -6.1836 | -7.6596 | 6.4504 | 5.7759 | 4.8907 | 3.7118 | 2.3456 | 0.56369 | -1.3502 | -2.7951 | -4.3116 | -5.8214 | -8.6834 | -8.9369 | -10.8701 | -12.1406
| FORRES | LW |  |  |  | 3.8037 | 2.9311 | 1.8639 | 0.22314 | -1.4855 | -3.4535 | -5.672 | -7.687 | -9.3106 | -10.8665 | -14.0076 | -13.6726 | -15.4476 | -16.7623 | 6.9338 | 6.3812 | 5.665 | 4.5854 | 3.4015 | 1.9331 | 0.20273 | -1.3099 | -2.5536 | -3.7108 | -6.0164 | -5.2769 | -6.6551 | -8.0724 | 6.3226 | 5.5925 | 4.6344 | 3.1536 | 1.5787 | -0.29702 | -2.4764 | -4.4346 | -6.0229 | -7.557 | -10.5978 | -9.9707 | -11.7359 | -13.2555
| FORRES | ST |  |  |  | 4.3129 | 3.7939 | 3.208 | 2.1436 | 1.1293 | 0.13593 | -1.309 | -2.3844 | -3.654 | -4.759 | -7.8282 | -8.004 | -10.1225 | -12.3379 | 7.1282 | 6.7538 | 6.33 | 5.3813 | 4.4929 | 3.6667 | 2.2846 | 1.3168 | -0.048472 | -1.1995 | -3.8682 | -3.4941 | -5.2854 | -7.2389 | 6.5106 | 6.0543 | 5.5304 | 4.4618 | 3.3992 | 2.3572 | 0.69757 | -0.56415 | -2.0675 | -3.418 | -6.5809 | -5.3334 | -7.3922 | -9.458
| FORRES | FS |  |  |  | 4.4817 | 4.0741 | 3.6144 | 2.9539 | 2.2436 | 1.4827 | 0.71441 | -0.094439 | -1.0355 | -1.9175 | -3.7405 | -5.6656 | -8.3471 | -9.897 | 7.2517 | 6.9552 | 6.6185 | 6.1194 | 5.5556 | 4.9543 | 4.3279 | 3.6594 | 2.8995 | 2.2076 | 0.75199 | -0.68473 | -3.0889 | -5.1311 | 6.6638 | 6.3089 | 5.906 | 5.3391 | 4.6757 | 3.9569 | 3.1837 | 2.3337 | 1.3904 | 0.50938 | -1.4019 | -2.3968 | -4.894 | -6.2017
DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | -0.044328 | -0.080455 | -0.12444 | -0.16539 | -0.21016 | -0.26063 | -0.31343 | -0.3723 | -0.43235 | -0.52241 | -0.73401 | -0.70605 | -1.1044 | -1.6318 | 0.34658 | 0.32961 | 0.30806 | 0.28868 | 0.26612 | 0.2433 | 0.21582 | 0.18344 | 0.10212 | 0.0072445 | -0.17691 | -0.17341 | -0.63902 | -1.286 | 0.010779 | -0.021213 | -0.060413 | -0.096715 | -0.14184 | -0.18991 | -0.24685 | -0.32438 | -0.42706 | -0.53703 | -0.75322 | -0.67582 | -1.1583 | -1.8119
| FORSS | CT |  |  |  | -0.025756 | -0.050641 | -0.080433 | -0.13615 | -0.1978 | -0.24628 | -0.30489 | -0.35851 | -0.40437 | -0.45282 | -0.56799 | -0.63137 | -0.87849 | -1.1081 | 0.3533 | 0.33971 | 0.32382 | 0.2959 | 0.26612 | 0.2433 | 0.2166 | 0.1914 | 0.14528 | 0.088502 | -0.036228 | -0.10348 | -0.35136 | -0.62778 | 0.027089 | 0.004311 | -0.030139 | -0.090695 | -0.14184 | -0.18991 | -0.24497 | -0.30029 | -0.37496 | -0.44071 | -0.58702 | -0.59037 | -0.86832 | -1.1461
| FORSS | LW |  |  |  | -0.044328 | -0.080455 | -0.12444 | -0.16539 | -0.21016 | -0.26063 | -0.31343 | -0.3723 | -0.43235 | -0.52241 | -0.73401 | -0.70605 | -1.1044 | -1.6318 | 0.34658 | 0.32961 | 0.30806 | 0.28868 | 0.267 | 0.24421 | 0.21582 | 0.18344 | 0.10212 | 0.0072445 | -0.17691 | -0.17341 | -0.63902 | -1.286 | 0.010779 | -0.021213 | -0.060413 | -0.096715 | -0.13664 | -0.18074 | -0.24685 | -0.32438 | -0.42706 | -0.53703 | -0.75322 | -0.67582 | -1.1583 | -1.8119
| FORSS | ST |  |  |  | -0.012347 | -0.031903 | -0.047041 | -0.068728 | -0.092356 | -0.11571 | -0.14411 | -0.17151 | -0.2475 | -0.29515 | -0.43686 | -0.59033 | -0.91997 | -1.2562 | 0.35942 | 0.35061 | 0.34316 | 0.33276 | 0.32096 | 0.3088 | 0.29395 | 0.27841 | 0.2054 | 0.16595 | 0.032647 | -0.097073 | -0.46105 | -0.85438 | 0.033177 | 0.021639 | 0.0079853 | -0.011554 | -0.032742 | -0.053725 | -0.084454 | -0.12362 | -0.22455 | -0.29746 | -0.47097 | -0.56048 | -0.9474 | -1.3498
| FORSS | FS |  |  |  | -0.0059174 | -0.0146 | -0.030981 | -0.044464 | -0.066202 | -0.085081 | -0.10369 | -0.12712 | -0.17488 | -0.21402 | -0.29618 | -0.44812 | -0.5702 | -0.63743 | 0.36203 | 0.35751 | 0.34984 | 0.34295 | 0.33248 | 0.32281 | 0.31269 | 0.3003 | 0.26453 | 0.23555 | 0.17395 | 0.091193 | 0.00055883 | -0.0674 | 0.034207 | 0.031241 | 0.022275 | 0.010044 | -0.0095512 | -0.026691 | -0.043716 | -0.069785 | -0.12352 | -0.17247 | -0.28051 | -0.3783 | -0.49712 | -0.56766
BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 5.459 | 5.3423 | 5.2067 | 4.9486 | 4.7148 | 4.3548 | 3.9559 | 3.6583 | 3.5144 | 3.3668 | 3.055 | 2.9339 | 2.7374 | 2.5992 | 5.5632 | 5.5045 | 5.4279 | 5.2157 | 5.0007 | 4.6295 | 4.2128 | 3.9281 | 3.8104 | 3.6858 | 3.4424 | 3.3668 | 3.2195 | 3.0815 | 5.2338 | 5.1386 | 5.0208 | 4.7557 | 4.4989 | 4.0859 | 3.6225 | 3.2874 | 3.1306 | 2.9674 | 2.6435 | 2.5215 | 2.3242 | 2.1695
| FORTEVIOT | CT |  |  |  | 5.4992 | 5.4101 | 5.3052 | 5.1403 | 4.9884 | 4.7277 | 4.449 | 4.2822 | 4.1523 | 4.0128 | 3.7411 | 3.5704 | 3.3348 | 3.1998 | 5.5753 | 5.5269 | 5.4627 | 5.356 | 5.2419 | 4.9952 | 4.7314 | 4.6135 | 4.5244 | 4.4192 | 4.2169 | 4.1129 | 3.9423 | 3.7611 | 5.2658 | 5.193 | 5.1014 | 4.9453 | 4.7886 | 4.5009 | 4.1939 | 4.03 | 3.9005 | 3.7533 | 3.4729 | 3.3154 | 3.1037 | 2.9734
| FORTEVIOT | LW |  |  |  | 5.459 | 5.3423 | 5.2067 | 4.9486 | 4.7148 | 4.3548 | 3.9559 | 3.6583 | 3.5144 | 3.3668 | 3.055 | 2.9339 | 2.7374 | 2.5992 | 5.5632 | 5.5045 | 5.4279 | 5.2157 | 5.0007 | 4.6295 | 4.2128 | 3.9281 | 3.8104 | 3.6858 | 3.4424 | 3.3668 | 3.2195 | 3.0815 | 5.2338 | 5.1386 | 5.0208 | 4.7557 | 4.4989 | 4.0859 | 3.6225 | 3.2874 | 3.1306 | 2.9674 | 2.6435 | 2.5215 | 2.3242 | 2.1695
| FORTEVIOT | ST |  |  |  | 5.5095 | 5.4404 | 5.3645 | 5.168 | 5.0429 | 4.9411 | 4.6839 | 4.5688 | 4.492 | 4.4193 | 4.2546 | 3.95 | 3.7236 | 3.4974 | 5.5785 | 5.5414 | 5.4995 | 5.2953 | 5.1562 | 5.0509 | 4.7546 | 4.6391 | 4.5693 | 4.5058 | 4.3573 | 4.1049 | 3.8984 | 3.6792 | 5.2738 | 5.2195 | 5.1585 | 4.9376 | 4.789 | 4.6726 | 4.3639 | 4.2339 | 4.1496 | 4.0697 | 3.8867 | 3.5828 | 3.3456 | 3.1374
| FORTEVIOT | FS |  |  |  | 5.5238 | 5.4665 | 5.401 | 5.3194 | 5.2583 | 5.1901 | 5.1162 | 5.0501 | 4.9876 | 4.9269 | 4.7999 | 4.5089 | 4.1991 | 4.0419 | 5.5838 | 5.5514 | 5.5141 | 5.448 | 5.3907 | 5.3255 | 5.2564 | 5.1917 | 5.1448 | 5.097 | 4.9897 | 4.7603 | 4.4683 | 4.2341 | 5.2851 | 5.2404 | 5.1885 | 5.1087 | 5.0423 | 4.9679 | 4.8875 | 4.8139 | 4.7513 | 4.6891 | 4.5549 | 4.259 | 3.9536 | 3.8234
INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0.62829 | 0.61717 | 0.60414 | 0.58684 | 0.56343 | 0.51301 | 0.45844 | 0.42431 | 0.39035 | 0.35711 | 0.29816 | 0.21823 | 0.093105 | -0.039035 | 0.699 | 0.69333 | 0.68503 | 0.65823 | 0.62949 | 0.60163 | 0.54512 | 0.52178 | 0.4715 | 0.44619 | 0.39054 | 0.2675 | 0.11489 | -0.036905 | 0.61613 | 0.6045 | 0.59096 | 0.57265 | 0.54594 | 0.48794 | 0.42633 | 0.39235 | 0.3556 | 0.3191 | 0.25376 | 0.14609 | -0.012788 | -0.17167
| FOYERS | CT |  |  |  | 0.63887 | 0.62744 | 0.61634 | 0.59443 | 0.56343 | 0.51301 | 0.45844 | 0.42431 | 0.39035 | 0.35711 | 0.29816 | 0.21823 | 0.11416 | 0.02677 | 0.70272 | 0.69698 | 0.69027 | 0.67429 | 0.65193 | 0.60163 | 0.54831 | 0.52591 | 0.49449 | 0.46096 | 0.39894 | 0.30454 | 0.20038 | 0.094248 | 0.62489 | 0.61448 | 0.60388 | 0.58042 | 0.54674 | 0.48794 | 0.42633 | 0.39235 | 0.3556 | 0.3191 | 0.25376 | 0.15561 | 0.036517 | -0.07008
| FOYERS | LW |  |  |  | 0.62829 | 0.61717 | 0.60414 | 0.58684 | 0.57113 | 0.54852 | 0.5227 | 0.49797 | 0.47426 | 0.44709 | 0.39655 | 0.38145 | 0.23197 | 0.023089 | 0.699 | 0.69333 | 0.68503 | 0.67583 | 0.66652 | 0.65654 | 0.64201 | 0.62633 | 0.60379 | 0.57915 | 0.53273 | 0.51652 | 0.34098 | 0.087337 | 0.61613 | 0.6045 | 0.59096 | 0.57265 | 0.55619 | 0.53571 | 0.5118 | 0.48858 | 0.46378 | 0.4357 | 0.38351 | 0.36232 | 0.18 | -0.078155
| FOYERS | ST |  |  |  | 0.6423 | 0.63907 | 0.63248 | 0.59739 | 0.5722 | 0.55093 | 0.49599 | 0.4716 | 0.42762 | 0.40127 | 0.34597 | 0.22783 | 0.093105 | -0.039035 | 0.70392 | 0.70198 | 0.69857 | 0.65823 | 0.62949 | 0.60787 | 0.54512 | 0.52178 | 0.4715 | 0.44619 | 0.39054 | 0.2675 | 0.11489 | -0.036905 | 0.62753 | 0.6245 | 0.61857 | 0.5762 | 0.54594 | 0.52147 | 0.4555 | 0.42775 | 0.37496 | 0.34499 | 0.28143 | 0.14609 | -0.012788 | -0.17167
| FOYERS | FS |  |  |  | 0.64349 | 0.64216 | 0.63591 | 0.62305 | 0.60981 | 0.59807 | 0.58274 | 0.56817 | 0.54464 | 0.52771 | 0.4851 | 0.41821 | 0.36315 | 0.33708 | 0.70447 | 0.70329 | 0.70017 | 0.68912 | 0.67749 | 0.66538 | 0.65169 | 0.63868 | 0.61658 | 0.59976 | 0.56202 | 0.51905 | 0.47657 | 0.45241 | 0.62873 | 0.62729 | 0.62175 | 0.60807 | 0.5937 | 0.58019 | 0.56333 | 0.54672 | 0.51954 | 0.50017 | 0.4527 | 0.38816 | 0.33424 | 0.30659
FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | NO | 19.9085 | 19.377 | 18.7069 | 17.6052 | 16.4296 | 15.1434 | 13.6818 | 11.8438 | 9.886 | 8.3494 | 5.4359 | 5.0824 | 2.7562 | 1.0729 | 24.8376 | 24.7288 | 24.5105 | 24.2279 | 23.9218 | 23.4946 | 22.7919 | 21.5987 | 20.1089 | 19.0163 | 17.0242 | 17.1714 | 15.2688 | 13.3123 | 23.4517 | 22.9768 | 22.3827 | 21.4008 | 20.3529 | 19.1784 | 17.8504 | 16.1844 | 14.3451 | 12.9558 | 10.2003 | 10.0085 | 7.9723 | 6.4058
| FRASERBURGH | CT |  |  |  | 20.3608 | 20.044 | 19.583 | 18.4207 | 17.1874 | 15.9306 | 14.6669 | 13.1657 | 11.3056 | 9.7445 | 6.8416 | 5.547 | 2.7562 | 1.0729 | 24.8376 | 24.7288 | 24.5105 | 24.2279 | 23.9218 | 23.4946 | 23.0498 | 22.1286 | 20.7641 | 19.6525 | 17.6806 | 17.1714 | 15.2688 | 13.3123 | 23.8483 | 23.5607 | 23.1357 | 22.111 | 21.0309 | 19.8703 | 18.7079 | 17.3527 | 15.6078 | 14.1843 | 11.5368 | 10.4558 | 7.9723 | 6.4058
| FRASERBURGH | LW |  |  |  | 19.9085 | 19.377 | 18.7069 | 17.6052 | 16.4296 | 15.1434 | 13.6818 | 11.8438 | 9.886 | 8.3494 | 5.4359 | 5.0824 | 3.199 | 1.8271 | 24.8379 | 24.7512 | 24.5946 | 24.3826 | 24.1348 | 23.6731 | 22.7919 | 21.5987 | 20.1089 | 19.0163 | 17.0242 | 17.328 | 16.024 | 14.7152 | 23.4517 | 22.9768 | 22.3827 | 21.4008 | 20.3529 | 19.1784 | 17.8504 | 16.1844 | 14.3451 | 12.9558 | 10.2003 | 10.0085 | 8.1596 | 6.6598
| FRASERBURGH | ST |  |  |  | 20.5964 | 20.4651 | 20.2949 | 19.9189 | 19.5343 | 19.0994 | 18.5196 | 17.7191 | 16.4068 | 15.4257 | 13.4917 | 11.7951 | 9.5695 | 7.0338 | 24.8493 | 24.8026 | 24.7405 | 24.5074 | 24.2995 | 24.0576 | 23.6691 | 23.0744 | 21.8129 | 21.0255 | 19.7015 | 19.4781 | 17.5341 | 15.0863 | 24.0558 | 23.938 | 23.7902 | 23.4339 | 23.0925 | 22.7144 | 22.1714 | 21.4477 | 20.1556 | 19.2561 | 17.5678 | 16.0863 | 13.9011 | 11.381
| FRASERBURGH | FS |  |  |  | 20.6471 | 20.5501 | 20.4198 | 20.1448 | 19.8391 | 19.475 | 19.1114 | 18.4869 | 17.4664 | 16.7404 | 15.2325 | 12.8287 | 9.9393 | 8.0751 | 24.8615 | 24.825 | 24.7773 | 24.6833 | 24.5745 | 24.4139 | 24.2679 | 23.8512 | 22.9767 | 22.5006 | 21.6057 | 20.5487 | 17.7462 | 14.6619 | 24.101 | 24.0142 | 23.902 | 23.6642 | 23.406 | 23.0919 | 22.787 | 22.2252 | 21.2307 | 20.5675 | 19.238 | 17.1922 | 14.5621 | 12.8482
LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | NO | 2.4455 | 2.3622 | 2.2607 | 2.1288 | 1.9943 | 1.8076 | 1.5593 | 1.3911 | 1.1958 | 1.0129 | 0.62935 | 0.25786 | -0.47614 | -1.3792 | 3.2527 | 3.199 | 3.1266 | 3.0361 | 2.938 | 2.7254 | 2.5013 | 2.3748 | 2.1947 | 1.9928 | 1.604 | 1.0629 | 0.37493 | -0.72429 | 3.0471 | 2.9528 | 2.8329 | 2.6724 | 2.4915 | 2.2829 | 1.9701 | 1.7592 | 1.5222 | 1.262 | 0.72527 | 0.044966 | -0.71248 | -1.8963
| FRIOCKHEIM | CT |  |  |  | 2.4996 | 2.4408 | 2.3659 | 2.199 | 2.0429 | 1.8076 | 1.5593 | 1.3911 | 1.1958 | 1.0129 | 0.62935 | 0.25786 | -0.47614 | -1.0646 | 3.2843 | 3.2499 | 3.1985 | 3.0738 | 2.938 | 2.7254 | 2.5013 | 2.3748 | 2.1947 | 1.9928 | 1.604 | 1.0629 | 0.4084 | -0.27866 | 3.1107 | 3.0569 | 2.9774 | 2.7772 | 2.5656 | 2.2829 | 1.9701 | 1.7592 | 1.5222 | 1.262 | 0.72527 | 0.044966 | -0.71248 | -1.3789
| FRIOCKHEIM | LW |  |  |  | 2.4455 | 2.3622 | 2.2607 | 2.1288 | 1.9943 | 1.8473 | 1.6694 | 1.4861 | 1.3014 | 1.104 | 0.71926 | 0.61787 | -0.27016 | -1.3792 | 3.2527 | 3.199 | 3.1266 | 3.0361 | 2.941 | 2.8423 | 2.7111 | 2.5759 | 2.4068 | 2.2276 | 1.8868 | 1.5957 | 0.61873 | -0.72429 | 3.0471 | 2.9528 | 2.8329 | 2.6724 | 2.4915 | 2.3001 | 2.0737 | 1.8461 | 1.6298 | 1.3903 | 0.91011 | 0.50917 | -0.53318 | -1.8963
| FRIOCKHEIM | ST |  |  |  | 2.5312 | 2.5016 | 2.4724 | 2.3506 | 2.2484 | 2.1539 | 1.9662 | 1.8639 | 1.6513 | 1.5131 | 1.1966 | 1.0793 | 0.29588 | -0.6484 | 3.3026 | 3.283 | 3.2617 | 3.1321 | 3.0287 | 2.9396 | 2.7367 | 2.6435 | 2.4148 | 2.285 | 1.989 | 1.2801 | 0.37493 | -0.58598 | 3.1456 | 3.1141 | 3.0818 | 2.9347 | 2.811 | 2.6991 | 2.4719 | 2.3541 | 2.0971 | 1.935 | 1.566 | 0.68234 | -0.30097 | -1.2994
| FRIOCKHEIM | FS |  |  |  | 2.5396 | 2.5178 | 2.4963 | 2.441 | 2.3814 | 2.3126 | 2.2397 | 2.1721 | 2.055 | 1.9481 | 1.7212 | 1.6404 | 1.282 | 0.90016 | 3.3073 | 3.292 | 3.2755 | 3.2279 | 3.1761 | 3.1144 | 3.0492 | 2.9898 | 2.8759 | 2.776 | 2.5628 | 2.1641 | 1.7323 | 1.3624 | 3.1548 | 3.1319 | 3.1086 | 3.0441 | 2.9735 | 2.8914 | 2.805 | 2.7262 | 2.5849 | 2.4555 | 2.1816 | 1.5887 | 1.0567 | 0.72861
KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | NO | 4.8871 | 4.728 | 4.5569 | 4.3741 | 4.186 | 4.0027 | 3.6513 | 3.4113 | 3.2634 | 3.0869 | 2.7309 | 2.4572 | 1.9985 | 1.7275 | 5.5721 | 5.5024 | 5.4136 | 5.3258 | 5.2188 | 5.0379 | 4.7852 | 4.6549 | 4.5314 | 4.3864 | 4.1109 | 3.8613 | 3.447 | 3.0031 | 3.0575 | 2.9116 | 2.7466 | 2.5755 | 2.3966 | 2.1853 | 1.83 | 1.6 | 1.4449 | 1.2696 | 0.93462 | 0.68211 | 0.21164 | -0.10614
| FYVIE | CT |  |  |  | 4.994 | 4.887 | 4.773 | 4.5344 | 4.289 | 4.0079 | 3.6513 | 3.4113 | 3.2634 | 3.0869 | 2.7309 | 2.4572 | 1.9985 | 1.7275 | 5.6098 | 5.5584 | 5.4924 | 5.3612 | 5.2188 | 5.0379 | 4.7852 | 4.6549 | 4.5314 | 4.3864 | 4.1109 | 3.8613 | 3.4972 | 3.1546 | 3.1518 | 3.0531 | 2.9418 | 2.71 | 2.4666 | 2.1853 | 1.83 | 1.6 | 1.4449 | 1.2696 | 0.93462 | 0.68211 | 0.21164 | -0.083303
| FYVIE | LW |  |  |  | 4.8871 | 4.728 | 4.5569 | 4.3741 | 4.186 | 4.0027 | 3.7162 | 3.4937 | 3.3332 | 3.1681 | 2.8065 | 2.6449 | 2.2481 | 1.8201 | 5.5721 | 5.5024 | 5.4136 | 5.3258 | 5.2309 | 5.143 | 4.9536 | 4.8205 | 4.699 | 4.572 | 4.3217 | 4.2504 | 3.877 | 3.3963 | 3.0575 | 2.9116 | 2.7466 | 2.5755 | 2.3966 | 2.2261 | 1.9457 | 1.7227 | 1.5659 | 1.4059 | 1.0851 | 0.95735 | 0.51255 | 0.0012755
| FYVIE | ST |  |  |  | 5.0486 | 4.9782 | 4.9086 | 4.7632 | 4.6269 | 4.4959 | 4.2381 | 4.1057 | 3.92 | 3.768 | 3.4341 | 2.6889 | 2.1723 | 1.7691 | 5.629 | 5.5968 | 5.5619 | 5.4502 | 5.3527 | 5.2661 | 5.0384 | 4.9432 | 4.7886 | 4.6742 | 4.4189 | 3.9019 | 3.447 | 3.0031 | 3.1996 | 3.1355 | 3.0706 | 2.919 | 2.7794 | 2.6484 | 2.3765 | 2.2401 | 2.0419 | 1.884 | 1.5414 | 0.87395 | 0.33434 | -0.10614
| FYVIE | FS |  |  |  | 5.0899 | 5.0418 | 4.9916 | 4.905 | 4.8132 | 4.7202 | 4.5787 | 4.4816 | 4.3447 | 4.2096 | 3.9379 | 3.1528 | 2.6106 | 2.4269 | 5.6434 | 5.6193 | 5.5921 | 5.541 | 5.485 | 5.4258 | 5.3234 | 5.2573 | 5.1622 | 5.0704 | 4.8767 | 4.4287 | 4.0251 | 3.7483 | 3.2347 | 3.1898 | 3.1421 | 3.0581 | 2.968 | 2.8759 | 2.7365 | 2.6381 | 2.4994 | 2.3627 | 2.0833 | 1.3779 | 0.90565 | 0.72699
GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115
| GARBAT FOREST | CT |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115
| GARBAT FOREST | LW |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115
| GARBAT FOREST | ST |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115
| GARBAT FOREST | FS |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.11548 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115
STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | NO | -0.65834 | -0.6733 | -0.71161 | -0.72872 | -0.75353 | -0.78636 | -0.82882 | -0.87785 | -0.90815 | -0.93724 | -1.0052 | -0.85634 | -0.88054 | -0.89552 | -0.31473 | -0.31758 | -0.34116 | -0.34909 | -0.36043 | -0.37158 | -0.39032 | -0.4127 | -0.42792 | -0.44452 | -0.47655 | -0.42929 | -0.432 | -0.43585 | -0.21696 | -0.23183 | -0.27117 | -0.28901 | -0.32203 | -0.35634 | -0.38535 | -0.41878 | -0.43116 | -0.44392 | -0.46911 | -0.38674 | -0.40911 | -0.42023
| GISLA | CT |  |  |  | -0.64598 | -0.65629 | -0.69051 | -0.7197 | -0.75219 | -0.78636 | -0.82882 | -0.87785 | -0.90815 | -0.93724 | -0.9956 | -0.83773 | -0.88054 | -0.89552 | -0.31438 | -0.31688 | -0.33888 | -0.34909 | -0.36043 | -0.37158 | -0.39032 | -0.4127 | -0.42792 | -0.44452 | -0.47655 | -0.42794 | -0.432 | -0.43585 | -0.20591 | -0.21689 | -0.25482 | -0.28684 | -0.32203 | -0.35634 | -0.38535 | -0.41878 | -0.43116 | -0.44392 | -0.46703 | -0.37523 | -0.40911 | -0.42023
| GISLA | LW |  |  |  | -0.65834 | -0.6733 | -0.71161 | -0.72872 | -0.75353 | -0.77453 | -0.80319 | -0.82656 | -0.85612 | -0.90367 | -1.0052 | -0.85634 | -0.87421 | -0.88234 | -0.31473 | -0.31758 | -0.34116 | -0.34764 | -0.35353 | -0.35957 | -0.37021 | -0.38159 | -0.40223 | -0.42591 | -0.47619 | -0.42929 | -0.43041 | -0.43043 | -0.21696 | -0.23183 | -0.27117 | -0.28901 | -0.3139 | -0.33588 | -0.36651 | -0.3934 | -0.41154 | -0.43021 | -0.46911 | -0.38674 | -0.40091 | -0.40768
| GISLA | ST |  |  |  | -0.64135 | -0.64611 | -0.66943 | -0.67925 | -0.68916 | -0.7016 | -0.70965 | -0.72175 | -0.73613 | -0.75475 | -0.84283 | -0.78511 | -0.82262 | -0.84207 | -0.31436 | -0.3156 | -0.33304 | -0.33647 | -0.34074 | -0.34543 | -0.35058 | -0.35718 | -0.36406 | -0.37255 | -0.40364 | -0.42226 | -0.42986 | -0.43175 | -0.20166 | -0.20665 | -0.23053 | -0.24079 | -0.25147 | -0.26486 | -0.27483 | -0.28916 | -0.30618 | -0.31897 | -0.36185 | -0.32635 | -0.35338 | -0.36951
| GISLA | FS |  |  |  | -0.63653 | -0.64101 | -0.65954 | -0.66707 | -0.67456 | -0.6867 | -0.6943 | -0.70468 | -0.71676 | -0.72713 | -0.75263 | -0.79455 | -0.84775 | -0.8692 | -0.31417 | -0.31516 | -0.32845 | -0.33075 | -0.33417 | -0.33775 | -0.34132 | -0.34547 | -0.35039 | -0.35606 | -0.36963 | -0.39975 | -0.42988 | -0.43276 | -0.19716 | -0.20167 | -0.22046 | -0.2281 | -0.23601 | -0.24818 | -0.25664 | -0.26776 | -0.28082 | -0.29273 | -0.32211 | -0.34515 | -0.37542 | -0.39089
ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | NO | 3.1135 | 3.0606 | 3.0065 | 2.9122 | 2.8128 | 2.668 | 2.5272 | 2.3938 | 2.3698 | 2.3407 | 2.2871 | 2.2133 | 1.7225 | 1.0789 | 3.2854 | 3.2616 | 3.232 | 3.1905 | 3.1319 | 3.0563 | 2.9807 | 2.9194 | 2.868 | 2.8069 | 2.6918 | 2.4891 | 1.9692 | 1.1901 | 2.8304 | 2.7834 | 2.7292 | 2.6467 | 2.5492 | 2.4188 | 2.2904 | 2.1741 | 2.122 | 2.0559 | 1.9349 | 1.7616 | 1.1826 | 0.39129
| GLASTULLICH | CT |  |  |  | 3.1343 | 3.1137 | 3.0795 | 2.9452 | 2.8128 | 2.668 | 2.5272 | 2.3938 | 2.3698 | 2.3407 | 2.2871 | 2.2133 | 1.8883 | 1.5977 | 3.2989 | 3.2812 | 3.2606 | 3.1974 | 3.1319 | 3.0563 | 2.9807 | 2.9194 | 2.868 | 2.8069 | 2.6918 | 2.4891 | 2.1652 | 1.8056 | 2.8606 | 2.8277 | 2.7922 | 2.6717 | 2.5492 | 2.4188 | 2.2904 | 2.1741 | 2.122 | 2.0559 | 1.9349 | 1.7616 | 1.4035 | 1.0552
| GLASTULLICH | LW |  |  |  | 3.1135 | 3.0606 | 3.0065 | 2.9122 | 2.8143 | 2.7241 | 2.6199 | 2.5149 | 2.4726 | 2.4315 | 2.3536 | 2.2133 | 1.7225 | 1.0789 | 3.2854 | 3.2616 | 3.232 | 3.1905 | 3.1457 | 3.1061 | 3.053 | 2.9965 | 2.9326 | 2.8664 | 2.7376 | 2.5315 | 1.9692 | 1.1901 | 2.8304 | 2.7834 | 2.7292 | 2.6467 | 2.559 | 2.4803 | 2.3811 | 2.2777 | 2.2046 | 2.1297 | 1.9891 | 1.772 | 1.1826 | 0.39129
| GLASTULLICH | ST |  |  |  | 3.1354 | 3.1326 | 3.1291 | 3.0969 | 3.0571 | 3.0238 | 2.9712 | 2.9389 | 2.8396 | 2.7809 | 2.6533 | 2.393 | 1.9891 | 1.5642 | 3.3052 | 3.2966 | 3.2874 | 3.2558 | 3.2267 | 3.2024 | 3.1553 | 3.1283 | 3.0271 | 2.9729 | 2.8502 | 2.5267 | 2.0625 | 1.5629 | 2.8743 | 2.8583 | 2.8422 | 2.8001 | 2.7579 | 2.7219 | 2.6618 | 2.6232 | 2.5055 | 2.4354 | 2.2781 | 1.8953 | 1.4083 | 0.90753
| GLASTULLICH | FS |  |  |  | 3.1358 | 3.1335 | 3.1306 | 3.1239 | 3.096 | 3.0654 | 3.0375 | 3.0016 | 2.9458 | 2.8978 | 2.7966 | 2.562 | 2.4141 | 2.3111 | 3.3087 | 3.3018 | 3.2939 | 3.2771 | 3.2594 | 3.2401 | 3.2207 | 3.1979 | 3.1495 | 3.1088 | 3.0215 | 2.8376 | 2.6717 | 2.5393 | 2.8809 | 2.8698 | 2.8561 | 2.828 | 2.7992 | 2.7681 | 2.7381 | 2.7011 | 2.6383 | 2.5835 | 2.466 | 2.1873 | 1.9938 | 1.8946
SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 1.7399 | 1.703 | 1.6447 | 1.5864 | 1.5195 | 1.4596 | 1.3857 | 1.2532 | 1.2056 | 1.1482 | 1.0429 | 0.99909 | 0.92326 | 0.88096 | 2.4465 | 2.427 | 2.3969 | 2.3685 | 2.3355 | 2.3034 | 2.2654 | 2.1957 | 2.1594 | 2.1183 | 2.0407 | 2.0246 | 1.9716 | 1.9311 | 2.0093 | 1.978 | 1.9369 | 1.8943 | 1.8459 | 1.8009 | 1.7503 | 1.6632 | 1.6426 | 1.6096 | 1.5072 | 1.4598 | 1.4044 | 1.3724
| GLEDFIELD | CT |  |  |  | 1.7689 | 1.74 | 1.71 | 1.6253 | 1.5503 | 1.4749 | 1.402 | 1.2808 | 1.2435 | 1.1889 | 1.0814 | 1.0304 | 0.92326 | 0.88096 | 2.4578 | 2.4418 | 2.4221 | 2.3793 | 2.3388 | 2.3034 | 2.2683 | 2.2123 | 2.1831 | 2.1435 | 2.066 | 2.0275 | 1.9716 | 1.9311 | 2.0326 | 2.0074 | 1.9826 | 1.9235 | 1.8751 | 1.8182 | 1.7632 | 1.6764 | 1.6567 | 1.6364 | 1.5442 | 1.4833 | 1.4044 | 1.3724
| GLEDFIELD | LW |  |  |  | 1.7399 | 1.703 | 1.6447 | 1.5864 | 1.5195 | 1.4596 | 1.3857 | 1.2532 | 1.2056 | 1.1482 | 1.0429 | 0.99909 | 0.94207 | 0.92351 | 2.4465 | 2.427 | 2.3969 | 2.3685 | 2.3355 | 2.3068 | 2.2654 | 2.1957 | 2.1594 | 2.1183 | 2.0407 | 2.0246 | 2.0015 | 1.9943 | 2.0093 | 1.978 | 1.9369 | 1.8943 | 1.8459 | 1.8009 | 1.7503 | 1.6632 | 1.6426 | 1.6096 | 1.5072 | 1.4598 | 1.4187 | 1.4055
| GLEDFIELD | ST |  |  |  | 1.7836 | 1.7697 | 1.7518 | 1.7318 | 1.7031 | 1.6792 | 1.6435 | 1.5844 | 1.5449 | 1.4992 | 1.3977 | 1.1933 | 1.1035 | 1.0412 | 2.4632 | 2.4553 | 2.4447 | 2.4326 | 2.417 | 2.4026 | 2.3827 | 2.3494 | 2.3251 | 2.2965 | 2.2303 | 2.0965 | 2.0418 | 1.9971 | 2.0436 | 2.0313 | 2.0155 | 1.9983 | 1.9776 | 1.96 | 1.9344 | 1.8984 | 1.8724 | 1.843 | 1.7787 | 1.6108 | 1.5411 | 1.4979
| GLEDFIELD | FS |  |  |  | 1.7923 | 1.7819 | 1.7683 | 1.7495 | 1.7256 | 1.6999 | 1.6708 | 1.6231 | 1.5853 | 1.5472 | 1.4652 | 1.213 | 1.0433 | 0.99645 | 2.4666 | 2.4604 | 2.4519 | 2.4408 | 2.4276 | 2.414 | 2.3982 | 2.371 | 2.3501 | 2.328 | 2.2783 | 2.1335 | 2.0102 | 1.9558 | 2.0505 | 2.0409 | 2.0291 | 2.0123 | 1.9934 | 1.9743 | 1.9531 | 1.9246 | 1.8988 | 1.8733 | 1.8201 | 1.6512 | 1.4963 | 1.464
FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | NO | 0.11195 | 0.11193 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11184 | 0.11181 | 0.11179 | 0.11176 | 0.11168 | 0.11157 | 0.11148 | 0.11391 | 0.11384 | 0.11376 | 0.1137 | 0.11364 | 0.11356 | 0.11348 | 0.11338 | 0.1133 | 0.1132 | 0.11297 | 0.11205 | 0.11014 | 0.10643 | 0.11214 | 0.11214 | 0.11213 | 0.11212 | 0.11211 | 0.11211 | 0.1121 | 0.11209 | 0.11208 | 0.11207 | 0.11206 | 0.11202 | 0.11195 | 0.11189
| GLEN LAOGH | CT |  |  |  | 0.11195 | 0.11194 | 0.11192 | 0.11191 | 0.11189 | 0.11188 | 0.11186 | 0.11185 | 0.11183 | 0.11181 | 0.11177 | 0.11172 | 0.11163 | 0.11155 | 0.11392 | 0.11386 | 0.11379 | 0.11373 | 0.11366 | 0.11358 | 0.11349 | 0.1134 | 0.11331 | 0.11322 | 0.113 | 0.11215 | 0.11064 | 0.10799 | 0.11214 | 0.11214 | 0.11213 | 0.11212 | 0.11212 | 0.11211 | 0.1121 | 0.1121 | 0.11209 | 0.11208 | 0.11207 | 0.11204 | 0.11199 | 0.11194
| GLEN LAOGH | LW |  |  |  | 0.11195 | 0.11193 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11184 | 0.11181 | 0.11179 | 0.11176 | 0.11168 | 0.11157 | 0.11148 | 0.11397 | 0.11396 | 0.11395 | 0.11394 | 0.11393 | 0.11392 | 0.11391 | 0.11389 | 0.11388 | 0.11386 | 0.11383 | 0.11378 | 0.11372 | 0.11366 | 0.11214 | 0.11214 | 0.11213 | 0.11212 | 0.11211 | 0.11211 | 0.1121 | 0.11209 | 0.11208 | 0.11207 | 0.11206 | 0.11202 | 0.11195 | 0.11189
| GLEN LAOGH | ST |  |  |  | 0.11195 | 0.11194 | 0.11192 | 0.11191 | 0.1119 | 0.11189 | 0.11188 | 0.11187 | 0.11185 | 0.11184 | 0.11181 | 0.11173 | 0.11163 | 0.11156 | 0.11392 | 0.11386 | 0.11379 | 0.11373 | 0.11367 | 0.11359 | 0.11351 | 0.11341 | 0.11333 | 0.11324 | 0.11303 | 0.11216 | 0.11064 | 0.108 | 0.11214 | 0.11214 | 0.11213 | 0.11213 | 0.11212 | 0.11211 | 0.11211 | 0.1121 | 0.11209 | 0.11209 | 0.11208 | 0.11205 | 0.11199 | 0.11194
| GLEN LAOGH | FS |  |  |  | 0.11195 | 0.11194 | 0.11193 | 0.11192 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11185 | 0.11183 | 0.11177 | 0.11168 | 0.11161 | 0.11391 | 0.11384 | 0.11376 | 0.1137 | 0.11364 | 0.11356 | 0.11348 | 0.11338 | 0.1133 | 0.1132 | 0.11297 | 0.11205 | 0.11014 | 0.10643 | 0.11215 | 0.11214 | 0.11213 | 0.11213 | 0.11212 | 0.11212 | 0.11211 | 0.1121 | 0.1121 | 0.11209 | 0.11208 | 0.11206 | 0.11202 | 0.11198
KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | NO | 1.1108 | 1.1026 | 1.0777 | 1.0652 | 1.0068 | 0.93179 | 0.83359 | 0.72711 | 0.66466 | 0.59641 | 0.46732 | 0.40939 | 0.30181 | 0.24855 | 1.8195 | 1.7888 | 1.7406 | 1.7046 | 1.6643 | 1.6234 | 1.5793 | 1.522 | 1.4758 | 1.4256 | 1.3294 | 1.3067 | 1.2361 | 1.1822 | 1.4469 | 1.3844 | 1.3003 | 1.2283 | 1.1495 | 1.0816 | 0.99121 | 0.89272 | 0.83198 | 0.76566 | 0.63979 | 0.58833 | 0.49391 | 0.44654
| GLENCOE | CT |  |  |  | 1.1114 | 1.1039 | 1.0833 | 1.0652 | 1.0422 | 0.94584 | 0.85 | 0.74508 | 0.69578 | 0.62925 | 0.50724 | 0.4511 | 0.30181 | 0.24855 | 1.8301 | 1.8063 | 1.7691 | 1.7189 | 1.666 | 1.6234 | 1.5802 | 1.5337 | 1.4978 | 1.4482 | 1.3551 | 1.3085 | 1.2361 | 1.1833 | 1.4757 | 1.4325 | 1.3714 | 1.2766 | 1.1778 | 1.091 | 1.0047 | 0.91068 | 0.86316 | 0.79864 | 0.67964 | 0.62578 | 0.49391 | 0.44654
| GLENCOE | LW |  |  |  | 1.1108 | 1.1026 | 1.0777 | 1.066 | 1.0068 | 0.93179 | 0.83359 | 0.72711 | 0.66466 | 0.59641 | 0.46732 | 0.40939 | 0.33372 | 0.30647 | 1.8195 | 1.7888 | 1.7406 | 1.7046 | 1.6643 | 1.6304 | 1.5793 | 1.522 | 1.4758 | 1.4256 | 1.3294 | 1.3067 | 1.279 | 1.2696 | 1.4469 | 1.3844 | 1.3003 | 1.2283 | 1.1495 | 1.0816 | 0.99121 | 0.89272 | 0.83198 | 0.76566 | 0.63979 | 0.58833 | 0.5221 | 0.49873
| GLENCOE | ST |  |  |  | 1.1129 | 1.1098 | 1.0958 | 1.0906 | 1.0835 | 1.0757 | 1.0653 | 1.0522 | 1.0371 | 0.97898 | 0.84785 | 0.56801 | 0.43765 | 0.35514 | 1.8386 | 1.8268 | 1.8011 | 1.7836 | 1.7638 | 1.7438 | 1.7183 | 1.6892 | 1.6584 | 1.6217 | 1.5387 | 1.3588 | 1.2853 | 1.2274 | 1.4928 | 1.4695 | 1.4248 | 1.3904 | 1.3539 | 1.3188 | 1.2739 | 1.2249 | 1.1765 | 1.1193 | 0.99555 | 0.73148 | 0.61443 | 0.54247
| GLENCOE | FS |  |  |  | 1.1133 | 1.1109 | 1.0985 | 1.094 | 1.0882 | 1.0817 | 1.0741 | 1.0654 | 1.055 | 1.043 | 0.95276 | 0.61592 | 0.38844 | 0.32504 | 1.8448 | 1.835 | 1.8142 | 1.8 | 1.7825 | 1.7649 | 1.7464 | 1.7253 | 1.6988 | 1.6704 | 1.6067 | 1.4186 | 1.2557 | 1.1822 | 1.508 | 1.4885 | 1.4547 | 1.4271 | 1.3938 | 1.3614 | 1.3296 | 1.2933 | 1.2468 | 1.199 | 1.0956 | 0.78485 | 0.57105 | 0.51575
DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | NO | 0.5641 | 0.55593 | 0.54342 | 0.52846 | 0.51187 | 0.4846 | 0.4565 | 0.43414 | 0.42213 | 0.40878 | 0.37486 | 0.35681 | 0.31009 | 0.27421 | 0.63299 | 0.62879 | 0.62183 | 0.61439 | 0.60126 | 0.58229 | 0.56245 | 0.54989 | 0.53855 | 0.52468 | 0.49477 | 0.46323 | 0.41747 | 0.37584 | 0.60676 | 0.59909 | 0.58724 | 0.57364 | 0.55707 | 0.52981 | 0.5016 | 0.48064 | 0.46784 | 0.45349 | 0.41738 | 0.39103 | 0.33854 | 0.2972
| GLENDARUEL | CT |  |  |  | 0.56982 | 0.56553 | 0.55558 | 0.53426 | 0.51187 | 0.4846 | 0.4565 | 0.43414 | 0.42213 | 0.40878 | 0.37486 | 0.35681 | 0.31442 | 0.29022 | 0.63504 | 0.63221 | 0.62634 | 0.61439 | 0.60126 | 0.58229 | 0.56245 | 0.54989 | 0.53855 | 0.52468 | 0.49477 | 0.46944 | 0.43482 | 0.40381 | 0.61157 | 0.60729 | 0.59801 | 0.57816 | 0.55707 | 0.52981 | 0.5016 | 0.48064 | 0.46784 | 0.45349 | 0.41738 | 0.393 | 0.34917 | 0.32087
| GLENDARUEL | LW |  |  |  | 0.5641 | 0.55593 | 0.54342 | 0.52846 | 0.51221 | 0.49721 | 0.47961 | 0.45851 | 0.44365 | 0.42923 | 0.39802 | 0.38953 | 0.34504 | 0.29518 | 0.63299 | 0.62879 | 0.62183 | 0.61447 | 0.60626 | 0.59888 | 0.58876 | 0.57667 | 0.56459 | 0.55156 | 0.52529 | 0.51829 | 0.47371 | 0.41471 | 0.60676 | 0.59909 | 0.58724 | 0.57364 | 0.55882 | 0.54519 | 0.52882 | 0.5092 | 0.49435 | 0.4796 | 0.44641 | 0.43605 | 0.38519 | 0.32426
| GLENDARUEL | ST |  |  |  | 0.57187 | 0.5672 | 0.56405 | 0.54787 | 0.53735 | 0.52689 | 0.50754 | 0.49441 | 0.47374 | 0.46087 | 0.42644 | 0.35815 | 0.31009 | 0.27421 | 0.63576 | 0.63349 | 0.63151 | 0.61863 | 0.60941 | 0.60143 | 0.58335 | 0.57378 | 0.55661 | 0.54615 | 0.51952 | 0.46323 | 0.41747 | 0.37584 | 0.61325 | 0.60904 | 0.60597 | 0.58906 | 0.57778 | 0.56714 | 0.54587 | 0.53276 | 0.51108 | 0.49796 | 0.46354 | 0.39103 | 0.33854 | 0.2972
| GLENDARUEL | FS |  |  |  | 0.57587 | 0.57287 | 0.56984 | 0.56322 | 0.55466 | 0.54498 | 0.53887 | 0.53031 | 0.52038 | 0.5029 | 0.47946 | 0.4195 | 0.36964 | 0.35692 | 0.63722 | 0.6356 | 0.63383 | 0.6294 | 0.62403 | 0.61796 | 0.61299 | 0.60708 | 0.59913 | 0.5889 | 0.5718 | 0.53386 | 0.4981 | 0.48359 | 0.61662 | 0.61387 | 0.61108 | 0.60459 | 0.59634 | 0.58701 | 0.58076 | 0.57238 | 0.56219 | 0.54566 | 0.52246 | 0.46442 | 0.41603 | 0.40375
ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | NO | 6.0611 | 5.9885 | 5.8498 | 5.7565 | 5.6453 | 5.4669 | 5.264 | 5.1111 | 4.9986 | 4.8683 | 4.6419 | 4.2892 | 3.9838 | 3.6736 | 6.5051 | 6.4725 | 6.3796 | 6.3324 | 6.2478 | 6.0982 | 5.9417 | 5.8521 | 5.7584 | 5.6508 | 5.4559 | 5.0241 | 4.6208 | 4.2121 | 6.3608 | 6.298 | 6.1737 | 6.0913 | 5.9934 | 5.7975 | 5.5924 | 5.4525 | 5.3367 | 5.2016 | 4.9633 | 4.5767 | 4.2 | 3.8169
| GLENDEVON | CT |  |  |  | 6.1044 | 6.0503 | 5.9449 | 5.8173 | 5.67 | 5.4669 | 5.264 | 5.1111 | 4.9986 | 4.8683 | 4.6419 | 4.2892 | 3.9838 | 3.7646 | 6.5206 | 6.4924 | 6.4147 | 6.3408 | 6.2514 | 6.0982 | 5.9417 | 5.8521 | 5.7584 | 5.6508 | 5.4559 | 5.0647 | 4.7679 | 4.4646 | 6.3975 | 6.3504 | 6.2552 | 6.1374 | 6.0003 | 5.7975 | 5.5924 | 5.4525 | 5.3367 | 5.2016 | 4.9633 | 4.5767 | 4.2481 | 3.9905
| GLENDEVON | LW |  |  |  | 6.0611 | 5.9885 | 5.8498 | 5.7565 | 5.6453 | 5.5284 | 5.3966 | 5.261 | 5.1489 | 5.0387 | 4.8465 | 4.6345 | 4.2701 | 3.8023 | 6.5051 | 6.4725 | 6.3796 | 6.3324 | 6.275 | 6.2187 | 6.1482 | 6.0746 | 5.9938 | 5.9113 | 5.7629 | 5.5636 | 5.161 | 4.6015 | 6.3608 | 6.298 | 6.1737 | 6.0913 | 5.9934 | 5.8931 | 5.7751 | 5.6525 | 5.5423 | 5.4323 | 5.2367 | 5.0176 | 4.5866 | 4.0137
| GLENDEVON | ST |  |  |  | 6.122 | 6.089 | 6.002 | 5.8878 | 5.7808 | 5.6842 | 5.5193 | 5.4223 | 5.2755 | 5.1681 | 4.9475 | 4.3832 | 4.0044 | 3.6736 | 6.5269 | 6.509 | 6.4447 | 6.3375 | 6.2478 | 6.1743 | 6.0139 | 5.938 | 5.8021 | 5.7195 | 5.541 | 5.0241 | 4.6208 | 4.2121 | 6.4121 | 6.3838 | 6.307 | 6.1832 | 6.0737 | 5.9795 | 5.7982 | 5.702 | 5.5441 | 5.4374 | 5.2124 | 4.6256 | 4.2 | 3.8169
| GLENDEVON | FS |  |  |  | 6.1478 | 6.1214 | 6.059 | 6.0015 | 5.9342 | 5.8692 | 5.7945 | 5.7266 | 5.6306 | 5.539 | 5.3686 | 4.8922 | 4.6251 | 4.5305 | 6.5418 | 6.5264 | 6.4773 | 6.4377 | 6.3914 | 6.3423 | 6.2899 | 6.2404 | 6.1673 | 6.1018 | 5.9716 | 5.6308 | 5.4004 | 5.247 | 6.4343 | 6.4118 | 6.3565 | 6.3017 | 6.2387 | 6.1771 | 6.1067 | 6.0425 | 5.9483 | 5.8607 | 5.6929 | 5.2412 | 4.983 | 4.8897
FORT AUGUSTUS | GLENDOE PRIMARY | MINIMUM HEADROOM | NH 40060 08894 | YES | NO | 1.1307 | 1.1171 | 1.0907 | 1.064 | 1.0347 | 1.0054 | 0.96601 | 0.91983 | 0.88007 | 0.8395 | 0.75307 | 0.91073 | 0.88666 | 0.8733 | 1.2883 | 1.2797 | 1.2631 | 1.2474 | 1.2277 | 1.2101 | 1.1859 | 1.1549 | 1.1248 | 1.093 | 1.0275 | 1.1585 | 1.1439 | 1.1332 | 1.1849 | 1.1726 | 1.1484 | 1.1212 | 1.0915 | 1.0615 | 1.0223 | 0.97668 | 0.93845 | 0.89989 | 0.81674 | 0.97403 | 0.94716 | 0.93256
| GLENDOE PRIMARY | CT |  |  |  | 1.1418 | 1.1296 | 1.1115 | 1.0756 | 1.0374 | 1.0079 | 0.9762 | 0.94273 | 0.91514 | 0.88295 | 0.81452 | 0.92182 | 0.88666 | 0.8733 | 1.2928 | 1.2852 | 1.2735 | 1.2515 | 1.2277 | 1.2101 | 1.1913 | 1.1716 | 1.151 | 1.1263 | 1.0746 | 1.1625 | 1.1439 | 1.1332 | 1.1944 | 1.1833 | 1.1667 | 1.1338 | 1.0957 | 1.0653 | 1.0327 | 0.99842 | 0.97146 | 0.94051 | 0.87459 | 0.98525 | 0.94716 | 0.93256
| GLENDOE PRIMARY | LW |  |  |  | 1.1307 | 1.1171 | 1.0907 | 1.064 | 1.0347 | 1.0054 | 0.96601 | 0.91983 | 0.88007 | 0.8395 | 0.75307 | 0.91073 | 0.89421 | 0.88537 | 1.2883 | 1.2797 | 1.2631 | 1.2474 | 1.2295 | 1.2122 | 1.1859 | 1.1549 | 1.1248 | 1.093 | 1.0275 | 1.1585 | 1.1508 | 1.147 | 1.1849 | 1.1726 | 1.1484 | 1.1212 | 1.0915 | 1.0615 | 1.0223 | 0.97668 | 0.93845 | 0.89989 | 0.81674 | 0.97403 | 0.95598 | 0.94629
| GLENDOE PRIMARY | ST |  |  |  | 1.1453 | 1.1404 | 1.1344 | 1.1218 | 1.1073 | 1.0966 | 1.0799 | 1.0607 | 1.0418 | 1.0137 | 0.95727 | 0.9763 | 0.94356 | 0.92443 | 1.2945 | 1.2912 | 1.287 | 1.2795 | 1.2706 | 1.2627 | 1.2515 | 1.2384 | 1.2245 | 1.2054 | 1.1639 | 1.1888 | 1.1686 | 1.1569 | 1.1977 | 1.1933 | 1.1878 | 1.1765 | 1.1634 | 1.1535 | 1.1382 | 1.1196 | 1.1015 | 1.0737 | 1.0192 | 1.0368 | 1.0082 | 0.98701
| GLENDOE PRIMARY | FS |  |  |  | 1.1483 | 1.1439 | 1.1388 | 1.1271 | 1.117 | 1.106 | 1.0936 | 1.0783 | 1.0631 | 1.0431 | 1.0012 | 0.99965 | 0.92275 | 0.90559 | 1.2959 | 1.2929 | 1.2893 | 1.2827 | 1.2762 | 1.2691 | 1.2608 | 1.2508 | 1.2403 | 1.2271 | 1.1981 | 1.2136 | 1.1598 | 1.1476 | 1.2002 | 1.1963 | 1.1916 | 1.1812 | 1.1721 | 1.1621 | 1.1509 | 1.1363 | 1.1211 | 1.1009 | 1.0594 | 1.0604 | 0.98651 | 0.9679
BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | -3.0837 | -0.80319 | -11.2345 | -12.2385 | -12.9765 | -13.9976 | -15.1711 | -16.1624 | -17.1221 | -18.1566 | -19.5191 | -19.5015 | -20.2659 | -20.922 | -1.4801 | -0.92551 | -13.5628 | -14.2838 | -14.8078 | -15.6218 | -16.5542 | -17.272 | -17.9477 | -18.6907 | -19.6388 | -19.4459 | -20.0707 | -20.7621 | -3.6496 | -3.2426 | -16.0488 | -17.0194 | -17.7495 | -18.7987 | -19.9949 | -20.971 | -21.8685 | -22.8397 | -24.1244 | -24.0803 | -24.8871 | -25.648
| GLENEAGLES | CT |  |  |  | 0.58127 | 8.2282 | 6.6002 | 5.7184 | 5.058 | 4.1779 | 3.2124 | 2.4926 | 1.5956 | 0.57274 | -0.80202 | -1.3114 | -2.3208 | -2.9642 | 2.9486 | 10.1146 | 8.3703 | 7.794 | 7.3749 | 6.7057 | 5.9817 | 5.5566 | 4.9522 | 4.2322 | 3.3142 | 3.0712 | 2.3674 | 1.6507 | 0.87193 | 7.9431 | 6.088 | 5.2702 | 4.6496 | 3.7619 | 2.7945 | 2.1275 | 1.295 | 0.33989 | -0.94186 | -1.3919 | -2.3472 | -2.9874
| GLENEAGLES | LW |  |  |  | -3.0837 | -0.80319 | -11.2345 | -12.2385 | -12.9765 | -13.9976 | -15.1711 | -16.1624 | -17.1221 | -18.1566 | -19.5191 | -19.5015 | -20.2659 | -20.922 | -1.4801 | -0.92551 | -13.5628 | -14.2838 | -14.8078 | -15.6218 | -16.5542 | -17.272 | -17.9477 | -18.6907 | -19.6388 | -19.4459 | -20.0707 | -20.7621 | -3.6496 | -3.2426 | -16.0488 | -17.0194 | -17.7495 | -18.7987 | -19.9949 | -20.971 | -21.8685 | -22.8397 | -24.1244 | -24.0803 | -24.8871 | -25.648
| GLENEAGLES | ST |  |  |  | -1.7193 | 3.9513 | -2.3187 | -3.0594 | -3.4673 | -3.8589 | -4.5818 | -5.0053 | -5.6674 | -6.3851 | -7.2738 | -8.1634 | -9.1184 | -10.1224 | -0.030269 | 4.6048 | -3.0179 | -3.6924 | -4.0704 | -4.3958 | -5.1104 | -5.4622 | -5.9955 | -6.5524 | -7.2474 | -8.0204 | -8.8464 | -9.7391 | -2.0473 | 2.5256 | -5.1709 | -5.936 | -6.3649 | -6.7532 | -7.5379 | -7.9546 | -8.5903 | -9.2633 | -10.1046 | -10.9646 | -11.916 | -12.9019
| GLENEAGLES | FS |  |  |  | 1.3774 | 9.7287 | 9.1978 | 8.7575 | 8.47 | 8.1772 | 7.8295 | 7.5248 | 7.0162 | 6.4587 | 5.7068 | 4.5089 | 3.2747 | 2.5381 | 3.8152 | 11.7552 | 11.2546 | 10.914 | 10.6923 | 10.4697 | 10.2077 | 9.9792 | 9.601 | 9.1829 | 8.6216 | 7.7695 | 6.6807 | 5.7905 | 1.8117 | 9.7087 | 9.155 | 8.738 | 8.4621 | 8.1845 | 7.8602 | 7.5752 | 7.1047 | 6.59 | 5.8936 | 4.8103 | 3.6615 | 3.0025
RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | NO | 0.30443 | 0.29528 | 0.27952 | 0.26595 | 0.25002 | 0.22501 | 0.19528 | 0.17554 | 0.14588 | 0.12487 | 0.075036 | 0.20604 | 0.17144 | 0.14021 | 0.26137 | 0.25619 | 0.24445 | 0.23399 | 0.22175 | 0.19909 | 0.17342 | 0.15674 | 0.1314 | 0.11285 | 0.069738 | 0.15216 | 0.11095 | 0.07074 | 0.24922 | 0.24482 | 0.23526 | 0.22255 | 0.20704 | 0.18043 | 0.1493 | 0.12961 | 0.099842 | 0.078381 | 0.02814 | 0.13253 | 0.09023 | 0.050696
| GLENETIVE | CT |  |  |  | 0.30443 | 0.29528 | 0.27952 | 0.26595 | 0.25002 | 0.22501 | 0.19528 | 0.17554 | 0.14588 | 0.12487 | 0.075036 | 0.21768 | 0.19459 | 0.16999 | 0.26137 | 0.25619 | 0.24445 | 0.23399 | 0.22175 | 0.19909 | 0.17342 | 0.15674 | 0.1314 | 0.11285 | 0.069738 | 0.16717 | 0.14005 | 0.11098 | 0.24922 | 0.24514 | 0.23526 | 0.22255 | 0.20704 | 0.18043 | 0.1493 | 0.12961 | 0.099842 | 0.078381 | 0.02814 | 0.14734 | 0.11925 | 0.08924
| GLENETIVE | LW |  |  |  | 0.30454 | 0.29933 | 0.29449 | 0.28839 | 0.28196 | 0.27398 | 0.26233 | 0.249 | 0.2308 | 0.2141 | 0.18393 | 0.26578 | 0.22519 | 0.16812 | 0.26143 | 0.25906 | 0.2564 | 0.25183 | 0.24702 | 0.24227 | 0.23356 | 0.22358 | 0.21032 | 0.19686 | 0.17146 | 0.22734 | 0.17818 | 0.10717 | 0.2493 | 0.24482 | 0.24254 | 0.24087 | 0.23791 | 0.23111 | 0.21992 | 0.2071 | 0.1893 | 0.17274 | 0.14279 | 0.20748 | 0.15743 | 0.086231
| GLENETIVE | ST |  |  |  | 0.30459 | 0.30374 | 0.3014 | 0.28774 | 0.27455 | 0.26117 | 0.23407 | 0.21574 | 0.18831 | 0.16237 | 0.098555 | 0.20604 | 0.17144 | 0.14021 | 0.26148 | 0.26086 | 0.26005 | 0.2461 | 0.23339 | 0.22157 | 0.19617 | 0.18076 | 0.15552 | 0.13437 | 0.081915 | 0.15216 | 0.11095 | 0.07074 | 0.24936 | 0.2486 | 0.2476 | 0.23594 | 0.22572 | 0.2123 | 0.18379 | 0.16516 | 0.13602 | 0.11017 | 0.046927 | 0.13253 | 0.09023 | 0.050696
| GLENETIVE | FS |  |  |  | 0.30472 | 0.30415 | 0.30349 | 0.29928 | 0.29257 | 0.28278 | 0.27145 | 0.26 | 0.24526 | 0.22979 | 0.19247 | 0.26198 | 0.25483 | 0.25102 | 0.26157 | 0.26115 | 0.26065 | 0.25773 | 0.25217 | 0.24442 | 0.23561 | 0.22624 | 0.21353 | 0.20085 | 0.17091 | 0.22159 | 0.21514 | 0.21046 | 0.24948 | 0.24895 | 0.24834 | 0.24524 | 0.24189 | 0.23635 | 0.22603 | 0.21488 | 0.19971 | 0.18417 | 0.14704 | 0.20203 | 0.19444 | 0.18973
FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0.051831 | 0.041081 | 0.039927 | 0.030634 | 0.022132 | 0.015615 | 0.0041756 | -0.0058244 | -0.010353 | -0.014462 | -0.026095 | -0.030389 | -0.034935 | -0.039892 | 0.071676 | 0.067175 | 0.065487 | 0.061003 | 0.055743 | 0.052157 | 0.046765 | 0.041858 | 0.036252 | 0.030925 | 0.020216 | 0.016902 | 0.013609 | 0.009869 | 0.062345 | 0.052885 | 0.051438 | 0.043029 | 0.035038 | 0.029041 | 0.018717 | 0.0096552 | 0.005087 | -0.00078169 | -0.012652 | -0.016871 | -0.020902 | -0.025379
| GLENUIG | CT |  |  |  | 0.053849 | 0.048823 | 0.042844 | 0.031645 | 0.022132 | 0.015615 | 0.0041756 | -0.0058244 | -0.010353 | -0.011575 | -0.025702 | -0.026062 | -0.034727 | -0.039892 | 0.072472 | 0.070019 | 0.066801 | 0.061003 | 0.055743 | 0.052157 | 0.046765 | 0.041858 | 0.037723 | 0.033634 | 0.022335 | 0.01811 | 0.013609 | 0.009869 | 0.064143 | 0.059587 | 0.05409 | 0.043839 | 0.035038 | 0.029041 | 0.018717 | 0.0096552 | 0.0051632 | 0.0022874 | -0.011713 | -0.012937 | -0.020716 | -0.025379
| GLENUIG | LW |  |  |  | 0.051831 | 0.041081 | 0.039927 | 0.030634 | 0.024174 | 0.018289 | 0.010123 | -0.0010214 | -0.0089765 | -0.014462 | -0.026095 | -0.030389 | -0.034935 | -0.035405 | 0.071676 | 0.067175 | 0.065487 | 0.061065 | 0.057489 | 0.054376 | 0.049192 | 0.042407 | 0.036252 | 0.030925 | 0.020216 | 0.016902 | 0.015077 | 0.014906 | 0.062345 | 0.052885 | 0.051438 | 0.043029 | 0.037048 | 0.031641 | 0.023967 | 0.013422 | 0.005087 | -0.00078169 | -0.012652 | -0.016871 | -0.020902 | -0.021292
| GLENUIG | ST |  |  |  | 0.053854 | 0.053204 | 0.050682 | 0.047443 | 0.0427 | 0.039232 | 0.035375 | 0.034462 | 0.031417 | 0.024335 | 0.011745 | -0.015515 | -0.0232 | -0.027538 | 0.072488 | 0.072012 | 0.070668 | 0.068985 | 0.066574 | 0.064558 | 0.062225 | 0.060438 | 0.057597 | 0.053092 | 0.043881 | 0.023347 | 0.018079 | 0.015218 | 0.064163 | 0.063612 | 0.061214 | 0.058254 | 0.053931 | 0.050707 | 0.047097 | 0.045731 | 0.042338 | 0.035516 | 0.023301 | -0.0031953 | -0.010429 | -0.014223
| GLENUIG | FS |  |  |  | 0.053916 | 0.053375 | 0.052615 | 0.047947 | 0.044973 | 0.043784 | 0.040174 | 0.038472 | 0.034971 | 0.027025 | 0.020878 | -0.0074036 | -0.02964 | -0.031546 | 0.072527 | 0.072119 | 0.071557 | 0.069368 | 0.067754 | 0.066763 | 0.06477 | 0.063235 | 0.060822 | 0.056883 | 0.051351 | 0.032432 | 0.015732 | 0.013039 | 0.064216 | 0.063758 | 0.063089 | 0.058753 | 0.056019 | 0.054842 | 0.051515 | 0.049745 | 0.046279 | 0.0391 | 0.032367 | 0.0053957 | -0.016084 | -0.017754
BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | NO | 2.7704 | 2.7648 | 2.6824 | 2.5351 | 2.4266 | 2.3181 | 2.2024 | 2.0843 | 2.0125 | 1.9433 | 1.8013 | 1.7446 | 1.6111 | 1.5355 | 3.1767 | 3.1384 | 3.032 | 2.9326 | 2.8763 | 2.8183 | 2.7455 | 2.6716 | 2.6199 | 2.5672 | 2.4619 | 2.443 | 2.3382 | 2.2546 | 2.7279 | 2.6736 | 2.5583 | 2.4281 | 2.3317 | 2.2349 | 2.1312 | 2.0287 | 1.9613 | 1.8946 | 1.7595 | 1.686 | 1.5907 | 1.5287
| GOLSPIE | CT |  |  |  | 2.7731 | 2.7685 | 2.7299 | 2.6189 | 2.4867 | 2.3518 | 2.2204 | 2.0913 | 2.0452 | 1.9726 | 1.8333 | 1.7986 | 1.6111 | 1.5355 | 3.1977 | 3.1679 | 3.0817 | 2.9739 | 2.8937 | 2.8245 | 2.7568 | 2.6896 | 2.6452 | 2.5911 | 2.487 | 2.443 | 2.3382 | 2.2546 | 2.7279 | 2.724 | 2.6472 | 2.5022 | 2.3813 | 2.2645 | 2.1477 | 2.0328 | 1.9957 | 1.9286 | 1.7953 | 1.7302 | 1.5907 | 1.5287
| GOLSPIE | LW |  |  |  | 2.7704 | 2.7648 | 2.6824 | 2.5351 | 2.4266 | 2.3181 | 2.2024 | 2.0843 | 2.0125 | 1.9433 | 1.8013 | 1.7446 | 1.6408 | 1.6025 | 3.1767 | 3.1384 | 3.032 | 2.9326 | 2.8763 | 2.8183 | 2.7455 | 2.6716 | 2.6199 | 2.5672 | 2.4619 | 2.4435 | 2.4016 | 2.3864 | 2.728 | 2.6736 | 2.5583 | 2.4281 | 2.3317 | 2.2349 | 2.1312 | 2.0287 | 1.9613 | 1.8946 | 1.7595 | 1.686 | 1.607 | 1.5794
| GOLSPIE | ST |  |  |  | 2.7756 | 2.7731 | 2.737 | 2.7125 | 2.7059 | 2.6996 | 2.6894 | 2.6428 | 2.5905 | 2.5369 | 2.4203 | 2.1667 | 2.0366 | 1.9357 | 3.2126 | 3.1972 | 3.1281 | 3.0661 | 3.0401 | 3.013 | 2.9852 | 2.9513 | 2.9125 | 2.871 | 2.7769 | 2.5941 | 2.5043 | 2.4136 | 2.7339 | 2.7343 | 2.698 | 2.6625 | 2.6238 | 2.5838 | 2.5425 | 2.4977 | 2.4449 | 2.3884 | 2.2636 | 1.9929 | 1.8802 | 1.7987
| GOLSPIE | FS |  |  |  | 2.7772 | 2.7753 | 2.7478 | 2.729 | 2.7211 | 2.716 | 2.7095 | 2.675 | 2.6286 | 2.5738 | 2.4656 | 2.1263 | 1.8827 | 1.7976 | 3.2175 | 3.2052 | 3.1522 | 3.1044 | 3.0742 | 3.0477 | 3.0166 | 2.9884 | 2.9558 | 2.9157 | 2.8341 | 2.6068 | 2.4061 | 2.2688 | 2.735 | 2.7356 | 2.7083 | 2.6917 | 2.6498 | 2.6117 | 2.5683 | 2.5269 | 2.482 | 2.43 | 2.3217 | 1.9946 | 1.7774 | 1.7161
BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | NO | 2.6863 | 2.5259 | 2.2707 | 1.684 | 1.0537 | 0.31239 | -0.53651 | -1.344 | -1.962 | -2.605 | -3.9256 | -3.8432 | -4.5139 | -5.2058 | 4.7274 | 4.6782 | 4.5348 | 4.2392 | 3.9106 | 3.4391 | 2.8779 | 2.3943 | 2.0448 | 1.6656 | 0.87978 | 1.5815 | 0.97002 | -0.10896 | 3.821 | 3.7336 | 3.6066 | 3.2582 | 2.8779 | 2.1993 | 1.3316 | 0.5188 | -0.11118 | -0.77587 | -2.1319 | -1.6467 | -2.1985 | -2.5243
| GOODLYBURN | CT |  |  |  | 2.7238 | 2.6709 | 2.55 | 2.1416 | 1.5972 | 1.0159 | 0.41691 | -0.098834 | -0.67619 | -1.2751 | -2.5132 | -3.2224 | -4.5137 | -5.2058 | 4.7289 | 4.6807 | 4.5679 | 4.302 | 4.0372 | 3.6796 | 3.3028 | 3.0265 | 2.7554 | 2.5121 | 1.9656 | 1.9018 | 0.97002 | -0.077074 | 3.8949 | 3.8424 | 3.7267 | 3.4459 | 3.1457 | 2.7612 | 2.2314 | 1.7503 | 1.2064 | 0.62298 | -0.57975 | -0.89357 | -1.9223 | -2.5243
| GOODLYBURN | LW |  |  |  | 2.6863 | 2.5259 | 2.2707 | 1.684 | 1.0537 | 0.31239 | -0.53651 | -1.344 | -1.962 | -2.605 | -3.9256 | -3.8432 | -4.5139 | -4.7475 | 4.7274 | 4.6782 | 4.5348 | 4.2392 | 3.9106 | 3.4391 | 2.8779 | 2.3943 | 2.0448 | 1.6656 | 0.87978 | 1.5815 | 1.2673 | 1.1212 | 3.821 | 3.7336 | 3.6066 | 3.2582 | 2.8779 | 2.1993 | 1.3316 | 0.5188 | -0.11118 | -0.77587 | -2.1319 | -1.6467 | -2.1985 | -2.4047
| GOODLYBURN | ST |  |  |  | 2.7565 | 2.7442 | 2.724 | 2.5859 | 2.4731 | 2.3685 | 2.1388 | 2.0116 | 1.8955 | 1.7194 | 1.2497 | 0.92959 | 0.0064047 | -1.2557 | 4.7351 | 4.7139 | 4.686 | 4.5147 | 4.3766 | 4.2577 | 3.9675 | 3.7856 | 3.6208 | 3.4312 | 2.9558 | 3.2878 | 2.4484 | 1.206 | 3.9411 | 3.9333 | 3.9194 | 3.7601 | 3.6366 | 3.5274 | 3.2656 | 3.1365 | 2.996 | 2.7944 | 2.2865 | 2.2397 | 1.4902 | 0.51153
| GOODLYBURN | FS |  |  |  | 2.7552 | 2.7434 | 2.7271 | 2.6785 | 2.6216 | 2.5542 | 2.4816 | 2.345 | 2.1814 | 1.9997 | 1.5939 | 0.99751 | -0.1977 | -1.2769 | 4.7393 | 4.7221 | 4.7005 | 4.6449 | 4.583 | 4.5099 | 4.4311 | 4.3198 | 4.2126 | 4.0921 | 3.8067 | 3.5122 | 2.0095 | -0.10896 | 3.9363 | 3.9272 | 3.915 | 3.8592 | 3.7955 | 3.7218 | 3.6426 | 3.5592 | 3.4748 | 3.3801 | 3.1617 | 2.6645 | 1.5388 | 0.70052
CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | NO | 5.0773 | 4.979 | 4.573 | 3.9719 | 3.7068 | 3.3331 | 2.9345 | 2.3251 | 1.8398 | 1.5877 | 1.0566 | 1.0187 | 0.4079 | -0.28639 | 6.1171 | 6.0609 | 5.7314 | 5.2583 | 5.0477 | 4.7183 | 4.3535 | 3.8314 | 3.397 | 3.1679 | 2.6879 | 2.6487 | 2.0013 | 1.1659 | 5.5607 | 5.4699 | 5.1179 | 4.5939 | 4.3214 | 3.9354 | 3.4928 | 2.9096 | 2.4268 | 2.1155 | 1.4775 | 1.4535 | 0.75929 | -0.088055
| GOURDIE | CT |  |  |  | 5.1052 | 5.0666 | 4.7399 | 4.2336 | 4.0001 | 3.6937 | 3.3823 | 2.8659 | 2.3825 | 2.106 | 1.5665 | 1.4514 | 0.90429 | 0.50272 | 6.1347 | 6.0936 | 5.8084 | 5.4221 | 5.2456 | 4.9853 | 4.7167 | 4.3129 | 3.8986 | 3.6583 | 3.1894 | 3.0655 | 2.5561 | 2.0198 | 5.6026 | 5.5453 | 5.2509 | 4.808 | 4.5672 | 4.2528 | 3.9287 | 3.4867 | 3.0356 | 2.7199 | 2.1058 | 1.9636 | 1.4339 | 0.99285
| GOURDIE | LW |  |  |  | 5.0773 | 4.979 | 4.573 | 3.9719 | 3.7068 | 3.3331 | 2.9345 | 2.3251 | 1.8398 | 1.5877 | 1.0566 | 1.0187 | 0.4079 | -0.28639 | 6.1171 | 6.0609 | 5.7314 | 5.2583 | 5.0477 | 4.7183 | 4.3535 | 3.8314 | 3.397 | 3.1679 | 2.6879 | 2.6487 | 2.0013 | 1.1659 | 5.5607 | 5.4699 | 5.1179 | 4.5939 | 4.3214 | 3.9354 | 3.4928 | 2.9096 | 2.4268 | 2.1155 | 1.4775 | 1.4535 | 0.75929 | -0.088055
| GOURDIE | ST |  |  |  | 5.1718 | 5.1496 | 4.8656 | 4.4233 | 4.2742 | 4.1286 | 3.8868 | 3.4632 | 3.0309 | 2.8501 | 2.4581 | 2.1393 | 1.4694 | 0.79573 | 6.1773 | 6.1535 | 5.9068 | 5.499 | 5.3481 | 5.2134 | 4.951 | 4.5771 | 4.1706 | 4.0024 | 3.6253 | 3.2349 | 2.5601 | 1.8386 | 5.6614 | 5.6282 | 5.3894 | 4.9746 | 4.8094 | 4.6554 | 4.3725 | 3.9944 | 3.5835 | 3.3789 | 2.9184 | 2.4166 | 1.7144 | 1.039
| GOURDIE | FS |  |  |  | 5.1875 | 5.1719 | 4.9597 | 4.6822 | 4.5722 | 4.4748 | 4.3506 | 4.0587 | 3.759 | 3.58 | 3.2497 | 2.7913 | 2.2399 | 1.8861 | 6.1888 | 6.1696 | 5.9817 | 5.7356 | 5.6313 | 5.5427 | 5.4319 | 5.1785 | 4.9103 | 4.7524 | 4.454 | 4.0495 | 3.4921 | 3.0603 | 5.6802 | 5.6556 | 5.4767 | 5.2243 | 5.1075 | 5.0056 | 4.8796 | 4.624 | 4.3528 | 4.1744 | 3.8244 | 3.3039 | 2.6929 | 2.4163
BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | NO | 7.9915 | 7.8183 | 7.6389 | 7.3755 | 7.1119 | 6.7797 | 6.4081 | 6.076 | 5.9251 | 5.7634 | 5.2299 | 5.2232 | 4.8612 | 4.5739 | 10.3785 | 10.2682 | 10.1358 | 9.9294 | 9.7122 | 9.4218 | 9.0648 | 8.758 | 8.5679 | 8.3629 | 7.9623 | 7.9866 | 7.7062 | 7.4125 | 8.62 | 8.4663 | 8.3047 | 8.0484 | 7.7885 | 7.4435 | 7.0578 | 6.7278 | 6.5803 | 6.422 | 5.9116 | 5.899 | 5.5436 | 5.2228
| GRANTOWN | CT |  |  |  | 8.0118 | 7.9525 | 7.8166 | 7.5444 | 7.2816 | 6.9337 | 6.5733 | 6.2864 | 6.1349 | 5.9934 | 5.6195 | 5.5355 | 5.0855 | 4.8419 | 10.4162 | 10.3305 | 10.2305 | 10.0361 | 9.8288 | 9.5504 | 9.2581 | 9.0649 | 8.9055 | 8.707 | 8.3216 | 8.2136 | 7.8751 | 7.5556 | 8.6294 | 8.5825 | 8.4589 | 8.21 | 7.9666 | 7.618 | 7.2554 | 6.9877 | 6.8406 | 6.7028 | 6.3648 | 6.2436 | 5.847 | 5.6116
| GRANTOWN | LW |  |  |  | 7.9915 | 7.8183 | 7.6389 | 7.3755 | 7.1119 | 6.7797 | 6.4081 | 6.076 | 5.9251 | 5.7634 | 5.2299 | 5.2232 | 4.8612 | 4.5739 | 10.3785 | 10.2682 | 10.1358 | 9.9294 | 9.7122 | 9.4218 | 9.0648 | 8.758 | 8.5679 | 8.3629 | 7.9623 | 7.9866 | 7.7062 | 7.4125 | 8.62 | 8.4663 | 8.3047 | 8.0484 | 7.7885 | 7.4435 | 7.0578 | 6.7278 | 6.5803 | 6.422 | 5.9116 | 5.899 | 5.5436 | 5.2228
| GRANTOWN | ST |  |  |  | 8.018 | 8.0069 | 7.9993 | 7.8547 | 7.7153 | 7.5871 | 7.3458 | 7.1987 | 7.0406 | 6.8825 | 6.5134 | 6.1942 | 5.8008 | 5.4957 | 10.4544 | 10.4008 | 10.3529 | 10.1823 | 10.0458 | 9.9284 | 9.6707 | 9.5316 | 9.3806 | 9.2406 | 8.9133 | 8.4084 | 8.0445 | 7.6795 | 8.6348 | 8.6247 | 8.6177 | 8.4621 | 8.3137 | 8.1825 | 7.9133 | 7.7645 | 7.6074 | 7.4652 | 7.1393 | 6.7188 | 6.3353 | 6.0434
| GRANTOWN | FS |  |  |  | 8.0197 | 8.01 | 8.0032 | 7.97 | 7.8685 | 7.7574 | 7.6427 | 7.529 | 7.4107 | 7.2937 | 7.038 | 6.6674 | 5.9919 | 5.8245 | 10.4629 | 10.4181 | 10.3776 | 10.2999 | 10.2208 | 10.1336 | 10.0402 | 9.9449 | 9.8445 | 9.7414 | 9.5071 | 8.9972 | 8.4366 | 8.0621 | 8.6364 | 8.6275 | 8.6212 | 8.5909 | 8.4946 | 8.3868 | 8.2753 | 8.1654 | 8.0533 | 7.9432 | 7.7023 | 7.3637 | 6.7162 | 6.5772
WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | YES | 15.1653 | 14.7933 | 14.126 | 13.1809 | 12.2693 | 11.2276 | 9.8419 | 8.3676 | 7.1687 | 5.8566 | 3.1782 | 8.7806 | 7.704 | 6.9424 | 18.1465 | 17.9868 | 17.5738 | 16.9959 | 16.4048 | 15.6905 | 14.7026 | 13.6795 | 12.7662 | 11.7594 | 9.7108 | 13.1348 | 10.5569 | 4.4028 | 15.2214 | 14.8677 | 14.2658 | 13.3426 | 12.4403 | 11.4094 | 10.0712 | 8.6348 | 7.4554 | 6.1632 | 3.5294 | 8.9121 | 7.9986 | 7.2244
| GREYFRIARS | CT |  |  |  | 15.3601 | 15.1086 | 14.6657 | 13.702 | 12.7554 | 11.879 | 10.9387 | 9.9996 | 9.1188 | 8.2441 | 6.3455 | 9.0682 | 7.704 | 6.9424 | 18.2097 | 18.0359 | 17.6903 | 17.0619 | 16.4048 | 15.759 | 15.0559 | 14.4145 | 13.7295 | 13.0376 | 11.4941 | 13.1348 | 10.9046 | 7.7613 | 15.4332 | 15.2025 | 14.8088 | 13.8979 | 12.9948 | 12.1067 | 11.1557 | 10.2726 | 9.4247 | 8.5805 | 6.7411 | 9.3318 | 7.9986 | 7.2244
| GREYFRIARS | LW |  |  |  | 15.1653 | 14.7933 | 14.126 | 13.1809 | 12.2693 | 11.2276 | 9.8419 | 8.3676 | 7.1687 | 5.8566 | 3.1782 | 8.7806 | 8.1523 | 7.4582 | 18.1465 | 17.9868 | 17.5738 | 16.9959 | 16.406 | 15.6905 | 14.7026 | 13.6795 | 12.7662 | 11.7594 | 9.7108 | 14.3334 | 13.7235 | 12.9545 | 15.2214 | 14.8677 | 14.2658 | 13.3426 | 12.4403 | 11.4094 | 10.0712 | 8.6348 | 7.4554 | 6.1632 | 3.5294 | 8.9121 | 8.2088 | 7.3907
| GREYFRIARS | ST |  |  |  | 15.5152 | 15.4244 | 15.2009 | 14.8533 | 14.578 | 14.28 | 13.8144 | 13.3706 | 12.8633 | 12.3025 | 10.9591 | 12.6497 | 11.563 | 10.1271 | 18.2811 | 18.2136 | 18.0192 | 17.6857 | 17.3918 | 17.081 | 16.5839 | 16.1467 | 15.6505 | 15.1159 | 13.8313 | 14.5314 | 12.301 | 8.77 | 15.5913 | 15.5138 | 15.3264 | 14.9944 | 14.7285 | 14.4434 | 13.9479 | 13.5033 | 12.9914 | 12.4335 | 11.0952 | 12.7972 | 11.703 | 10.1795
| GREYFRIARS | FS |  |  |  | 15.5247 | 15.453 | 15.2832 | 15.0147 | 14.7909 | 14.5298 | 14.2298 | 13.8915 | 13.5188 | 13.1031 | 12.1461 | 12.9181 | 11.5181 | 10.1998 | 18.2813 | 18.215 | 18.0437 | 17.8039 | 17.5688 | 17.2955 | 16.9772 | 16.6174 | 16.223 | 15.7813 | 14.7334 | 14.1215 | 10.5569 | 4.4028 | 15.5994 | 15.539 | 15.402 | 15.1603 | 14.95 | 14.7059 | 14.4288 | 14.0984 | 13.7302 | 13.3215 | 12.3816 | 13.0781 | 11.7503 | 10.4995
GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309623 | NO | NO | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
| GRUDIE BRIDGE | CT |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
| GRUDIE BRIDGE | LW |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
| GRUDIE BRIDGE | ST |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
| GRUDIE BRIDGE | FS |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28
SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | NO | 0.27821 | 0.26678 | 0.2507 | 0.23178 | 0.21569 | 0.19301 | 0.17157 | 0.14436 | 0.12886 | 0.11786 | 0.085354 | 0.11362 | 0.093608 | 0.088272 | 0.52328 | 0.51662 | 0.50567 | 0.49465 | 0.4805 | 0.4682 | 0.45484 | 0.43612 | 0.41903 | 0.40253 | 0.36296 | 0.35917 | 0.34649 | 0.3369 | 0.35759 | 0.35431 | 0.3495 | 0.34377 | 0.3383 | 0.33146 | 0.32326 | 0.31115 | 0.29442 | 0.27134 | 0.22026 | 0.28818 | 0.2731 | 0.2656
| GUTCHER | CT |  |  |  | 0.28501 | 0.2776 | 0.26273 | 0.2403 | 0.21696 | 0.19558 | 0.17201 | 0.14826 | 0.138 | 0.12581 | 0.099458 | 0.12208 | 0.093608 | 0.088272 | 0.526 | 0.52101 | 0.51163 | 0.49647 | 0.4805 | 0.4682 | 0.45484 | 0.44138 | 0.42898 | 0.41222 | 0.37645 | 0.36142 | 0.34649 | 0.3369 | 0.35886 | 0.35684 | 0.35237 | 0.34597 | 0.3383 | 0.33161 | 0.32326 | 0.31115 | 0.30914 | 0.29453 | 0.25982 | 0.29713 | 0.2731 | 0.2656
| GUTCHER | LW |  |  |  | 0.27821 | 0.26678 | 0.2507 | 0.23178 | 0.21569 | 0.19301 | 0.17157 | 0.14436 | 0.12886 | 0.11786 | 0.085354 | 0.11362 | 0.09986 | 0.094041 | 0.52328 | 0.51662 | 0.50567 | 0.49465 | 0.48364 | 0.47159 | 0.45568 | 0.43612 | 0.41903 | 0.40253 | 0.36296 | 0.35917 | 0.35355 | 0.35187 | 0.35759 | 0.35431 | 0.3495 | 0.34377 | 0.33923 | 0.33146 | 0.32575 | 0.3137 | 0.29442 | 0.27134 | 0.22026 | 0.28818 | 0.27665 | 0.27266
| GUTCHER | ST |  |  |  | 0.29449 | 0.29077 | 0.28861 | 0.28561 | 0.28174 | 0.27386 | 0.26696 | 0.25894 | 0.24999 | 0.24311 | 0.21445 | 0.1979 | 0.18721 | 0.17366 | 0.52924 | 0.52678 | 0.52435 | 0.52107 | 0.51677 | 0.51077 | 0.50441 | 0.49675 | 0.48778 | 0.47824 | 0.4487 | 0.39075 | 0.37597 | 0.36663 | 0.36385 | 0.36398 | 0.36422 | 0.36461 | 0.36562 | 0.36382 | 0.36352 | 0.36259 | 0.36173 | 0.36342 | 0.33294 | 0.35666 | 0.33885 | 0.32846
| GUTCHER | FS |  |  |  | 0.29462 | 0.29508 | 0.2913 | 0.28299 | 0.27429 | 0.27086 | 0.26301 | 0.25676 | 0.24802 | 0.24037 | 0.21934 | 0.18016 | 0.14792 | 0.13561 | 0.52937 | 0.52846 | 0.52569 | 0.52095 | 0.51563 | 0.51191 | 0.50615 | 0.50047 | 0.49336 | 0.48588 | 0.46712 | 0.41395 | 0.36433 | 0.35361 | 0.36387 | 0.3651 | 0.36449 | 0.36227 | 0.36046 | 0.36107 | 0.35982 | 0.35914 | 0.35796 | 0.3571 | 0.3538 | 0.34482 | 0.3134 | 0.30461
THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | NO | 0.54052 | 2.2022 | 2.0867 | 1.9518 | 1.8018 | 1.6754 | 1.5081 | 1.3468 | 1.2338 | 1.0995 | 0.84097 | 0.61166 | 0.01852 | -0.70293 | 1.1129 | 2.6957 | 2.6366 | 2.5708 | 2.4896 | 2.3875 | 2.2821 | 2.1998 | 2.1052 | 1.9941 | 1.7827 | 1.5371 | 0.98724 | 0.13287 | 0.65914 | 2.1969 | 2.0919 | 1.9703 | 1.8341 | 1.7111 | 1.5428 | 1.3949 | 1.2778 | 1.1395 | 0.87679 | 0.6109 | -0.054709 | -0.9386
| HALKIRK | CT |  |  |  | 0.61513 | 2.3109 | 2.2205 | 2.0467 | 1.8624 | 1.6838 | 1.5081 | 1.3468 | 1.2338 | 1.0995 | 0.84342 | 0.61166 | 0.13038 | -0.22534 | 1.148 | 2.7415 | 2.6881 | 2.5953 | 2.4945 | 2.3875 | 2.2821 | 2.1998 | 2.1052 | 1.9941 | 1.7827 | 1.5371 | 1.1226 | 0.70067 | 0.72536 | 2.2931 | 2.2101 | 2.051 | 1.8813 | 1.7111 | 1.5428 | 1.3949 | 1.2778 | 1.1395 | 0.87679 | 0.6109 | 0.10211 | -0.31058
| HALKIRK | LW |  |  |  | 0.54052 | 2.2022 | 2.0867 | 1.9518 | 1.8018 | 1.6754 | 1.5245 | 1.3648 | 1.2356 | 1.1019 | 0.84097 | 0.62272 | 0.01852 | -0.70293 | 1.1129 | 2.6957 | 2.6366 | 2.5708 | 2.4896 | 2.4312 | 2.3522 | 2.2657 | 2.1589 | 2.0466 | 1.8324 | 1.6374 | 0.99513 | 0.13287 | 0.65914 | 2.1969 | 2.0919 | 1.9703 | 1.8341 | 1.7203 | 1.5819 | 1.4348 | 1.3016 | 1.1633 | 0.89574 | 0.65082 | -0.054709 | -0.9386
| HALKIRK | ST |  |  |  | 0.64236 | 2.3571 | 2.2996 | 2.2048 | 2.1113 | 2.0275 | 1.9185 | 1.8252 | 1.6683 | 1.5491 | 1.282 | 0.73585 | 0.16413 | -0.35329 | 1.1589 | 2.7635 | 2.7311 | 2.664 | 2.6021 | 2.5492 | 2.4652 | 2.4076 | 2.2701 | 2.183 | 1.9837 | 1.5524 | 0.98724 | 0.40532 | 0.74942 | 2.3348 | 2.2829 | 2.1892 | 2.099 | 2.0191 | 1.9074 | 1.8185 | 1.6504 | 1.5314 | 1.264 | 0.7047 | 0.068145 | -0.52954
| HALKIRK | FS |  |  |  | 0.70722 | 2.4345 | 2.3894 | 2.3269 | 2.2599 | 2.1914 | 2.1205 | 2.048 | 1.9354 | 1.8304 | 1.607 | 1.0515 | 0.69278 | 0.54218 | 1.206 | 2.8172 | 2.7899 | 2.7529 | 2.7142 | 2.6738 | 2.631 | 2.5868 | 2.5076 | 2.4365 | 2.282 | 1.9651 | 1.7058 | 1.5292 | 0.80821 | 2.4049 | 2.3641 | 2.306 | 2.2439 | 2.1799 | 2.1136 | 2.0458 | 1.9346 | 1.8326 | 1.6155 | 1.1015 | 0.76131 | 0.61355
ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | NO | 10.3988 | 10.26 | 9.6617 | 8.5178 | 7.1361 | 5.771 | 4.2924 | 3.0801 | 2.3186 | 1.5224 | -0.069009 | 0.074026 | -0.75209 | -1.1159 | 11.9379 | 11.8568 | 11.4593 | 10.6687 | 9.7033 | 8.6946 | 7.61 | 6.8244 | 6.3985 | 5.9349 | 4.8529 | 5.3693 | 4.9146 | 4.3536 | 10.1531 | 10.0494 | 9.618 | 8.6519 | 7.2983 | 5.8636 | 4.2989 | 3.0685 | 2.3542 | 1.6042 | 0.10859 | 0.32699 | -0.44577 | -0.82222
| HARBOUR | CT |  |  |  | 10.4091 | 10.2885 | 9.8531 | 9.1526 | 8.024 | 7.0101 | 5.9812 | 5.2341 | 4.5313 | 3.7925 | 2.3228 | 1.8284 | 0.59076 | -0.13004 | 11.9546 | 11.8568 | 11.4593 | 10.9449 | 10.2541 | 9.5846 | 8.815 | 8.4003 | 8.0655 | 7.7717 | 7.0023 | 6.8832 | 5.7481 | 4.3536 | 10.1658 | 10.0494 | 9.618 | 9.0833 | 8.2372 | 7.2091 | 6.1532 | 5.4513 | 4.8126 | 4.1395 | 2.7972 | 2.4621 | 1.3582 | 0.70336
| HARBOUR | LW |  |  |  | 10.3988 | 10.26 | 9.6617 | 8.5178 | 7.1361 | 5.771 | 4.2924 | 3.0801 | 2.3186 | 1.5224 | -0.069009 | 0.074026 | -0.75209 | -1.1159 | 11.9379 | 11.8698 | 11.4614 | 10.6687 | 9.7033 | 8.6946 | 7.61 | 6.8244 | 6.3985 | 5.9349 | 4.8529 | 5.3693 | 4.9146 | 4.623 | 10.1531 | 10.0671 | 9.6368 | 8.6519 | 7.2983 | 5.8636 | 4.2989 | 3.0685 | 2.3542 | 1.6042 | 0.10859 | 0.32699 | -0.44577 | -0.82222
| HARBOUR | ST |  |  |  | 10.4191 | 10.3462 | 10.0179 | 9.3312 | 8.5971 | 8.2642 | 7.5761 | 7.2289 | 6.9748 | 6.6776 | 5.898 | 5.5876 | 4.6715 | 3.43 | 11.9721 | 11.9147 | 11.6 | 10.8527 | 10.0946 | 9.7739 | 9.0062 | 8.6732 | 8.4282 | 8.1203 | 7.3652 | 7.8646 | 6.8096 | 5.272 | 10.1767 | 10.1093 | 9.7884 | 9.0291 | 8.2547 | 7.9021 | 7.1 | 6.7285 | 6.4769 | 6.1994 | 5.3708 | 5.6348 | 4.7825 | 3.663
| HARBOUR | FS |  |  |  | 10.5024 | 10.4393 | 10.18 | 9.8373 | 9.364 | 9.113 | 8.8476 | 8.6072 | 8.3179 | 7.9804 | 7.3227 | 6.617 | 5.3532 | 4.3774 | 12.0559 | 12.0036 | 11.7541 | 11.4095 | 10.9431 | 10.707 | 10.4502 | 10.2314 | 10.0669 | 9.8528 | 9.4602 | 9.0527 | 7.2579 | 4.6987 | 10.2606 | 10.2027 | 9.9511 | 9.6011 | 9.1267 | 8.8731 | 8.6012 | 8.3657 | 8.1891 | 7.9635 | 7.544 | 6.9685 | 5.8201 | 4.965
STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | NO | NO | 35.1005 | 34.9454 | 34.9265 | 34.8905 | 34.8372 | 34.7931 | 34.7001 | 34.6703 | 34.5908 | 34.5618 | 34.4863 | 34.3205 | 34.0856 | 33.8473 | 32.5091 | 32.3579 | 32.3401 | 32.2853 | 32.223 | 32.1811 | 32.0533 | 32.0167 | 31.9245 | 31.8866 | 31.8003 | 31.6245 | 31.3336 | 31.0362 | 32.4219 | 32.2632 | 32.2444 | 32.1912 | 32.1283 | 32.0857 | 31.957 | 31.9192 | 31.8256 | 31.7859 | 31.695 | 31.5192 | 31.2277 | 30.9314
| HARRIS GRID | CT |  |  |  | 35.1042 | 34.9692 | 34.9519 | 34.9196 | 34.8855 | 34.7931 | 34.7053 | 34.671 | 34.6325 | 34.5948 | 34.5245 | 34.388 | 34.2303 | 34.0629 | 32.5104 | 32.3759 | 32.3577 | 32.3289 | 32.292 | 32.1963 | 32.0909 | 32.0597 | 32.0128 | 31.966 | 31.8783 | 31.728 | 31.5351 | 31.3269 | 32.4219 | 32.2811 | 32.2607 | 32.2294 | 32.1898 | 32.0923 | 31.9851 | 31.9479 | 31.8986 | 31.8518 | 31.7609 | 31.6119 | 31.4175 | 31.2102
| HARRIS GRID | LW |  |  |  | 35.1005 | 34.9454 | 34.9265 | 34.9175 | 34.9006 | 34.8853 | 34.8688 | 34.8552 | 34.833 | 34.8055 | 34.7666 | 34.7349 | 34.4498 | 34.0417 | 32.5091 | 32.3579 | 32.3401 | 32.3365 | 32.3229 | 32.3087 | 32.3012 | 32.2921 | 32.2656 | 32.2359 | 32.1794 | 32.1629 | 31.8122 | 31.3025 | 32.4221 | 32.2632 | 32.2444 | 32.24 | 32.2252 | 32.2099 | 32.1979 | 32.1832 | 32.1533 | 32.1195 | 32.0592 | 32.0452 | 31.6913 | 31.1814
| HARRIS GRID | ST |  |  |  | 35.1075 | 34.9785 | 34.9646 | 34.8905 | 34.8372 | 34.8059 | 34.7001 | 34.6703 | 34.5908 | 34.5618 | 34.4863 | 34.3205 | 34.0856 | 33.8473 | 32.5122 | 32.3819 | 32.3712 | 32.2853 | 32.223 | 32.1811 | 32.0533 | 32.0167 | 31.9245 | 31.8866 | 31.8003 | 31.6245 | 31.3336 | 31.0362 | 32.4242 | 32.2886 | 32.2776 | 32.1912 | 32.1283 | 32.0857 | 31.957 | 31.9192 | 31.8256 | 31.7859 | 31.695 | 31.5192 | 31.2277 | 30.9314
| HARRIS GRID | FS |  |  |  | 35.108 | 35.0108 | 35.0033 | 34.9772 | 34.9544 | 34.9338 | 34.9109 | 34.8916 | 34.8559 | 34.8288 | 34.7754 | 34.7107 | 34.6767 | 34.6429 | 32.5126 | 32.416 | 32.4105 | 32.3846 | 32.3586 | 32.3344 | 32.3098 | 32.2874 | 32.2484 | 32.219 | 32.1581 | 32.1131 | 32.0788 | 32.0384 | 32.4248 | 32.3232 | 32.3174 | 32.2913 | 32.2649 | 32.2403 | 32.2152 | 32.1921 | 32.1524 | 32.1221 | 32.059 | 32.0065 | 31.9696 | 31.9301
THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | NO | 2.9013 | 2.7619 | 2.5998 | 2.414 | 2.2175 | 1.9092 | 1.579 | 1.3189 | 1.1406 | 0.92609 | 0.52497 | 0.18907 | -0.61708 | -1.5308 | 2.8401 | 2.777 | 2.6968 | 2.6104 | 2.4666 | 2.2434 | 2.0098 | 1.8654 | 1.7103 | 1.533 | 1.1998 | 0.75155 | -0.13738 | -1.0317 | 3.0959 | 2.9688 | 2.8221 | 2.6533 | 2.4745 | 2.1513 | 1.8167 | 1.5707 | 1.3891 | 1.1774 | 0.78142 | 0.40098 | -0.57366 | -1.6374
| HASTIGROW | CT |  |  |  | 2.9916 | 2.8936 | 2.7725 | 2.5126 | 2.2291 | 1.9092 | 1.579 | 1.3189 | 1.1406 | 0.92609 | 0.52497 | 0.18907 | -0.52559 | -1.0717 | 2.8748 | 2.826 | 2.7594 | 2.622 | 2.4666 | 2.2434 | 2.0098 | 1.8654 | 1.7103 | 1.533 | 1.1998 | 0.82426 | 0.18549 | -0.45137 | 3.1784 | 3.0884 | 2.9779 | 2.7379 | 2.4745 | 2.1513 | 1.8167 | 1.5707 | 1.3891 | 1.1774 | 0.78142 | 0.40098 | -0.3779 | -1.0187
| HASTIGROW | LW |  |  |  | 2.9013 | 2.7619 | 2.5998 | 2.414 | 2.2175 | 2.0315 | 1.804 | 1.5564 | 1.369 | 1.1674 | 0.77368 | 0.51749 | -0.39745 | -1.5308 | 2.8401 | 2.777 | 2.6968 | 2.6104 | 2.517 | 2.4302 | 2.3134 | 2.1834 | 2.0343 | 1.8747 | 1.5695 | 1.3461 | 0.34374 | -1.0269 | 3.0959 | 2.9688 | 2.8221 | 2.6533 | 2.4751 | 2.3057 | 2.1 | 1.8765 | 1.6948 | 1.4999 | 1.1216 | 0.84649 | -0.23956 | -1.6374
| HASTIGROW | ST |  |  |  | 3.0185 | 2.9526 | 2.8876 | 2.7134 | 2.5563 | 2.4162 | 2.1743 | 2.0219 | 1.7501 | 1.5527 | 1.1159 | 0.2735 | -0.61708 | -1.4171 | 2.8859 | 2.8556 | 2.8241 | 2.677 | 2.5571 | 2.4587 | 2.24 | 2.132 | 1.8843 | 1.7379 | 1.4078 | 0.75155 | -0.13738 | -1.0317 | 3.2035 | 3.1435 | 3.0845 | 2.8978 | 2.7361 | 2.5963 | 2.3332 | 2.183 | 1.8892 | 1.6937 | 1.2616 | 0.42992 | -0.57366 | -1.5122
| HASTIGROW | FS |  |  |  | 3.0535 | 3.0077 | 2.962 | 2.8669 | 2.7733 | 2.6701 | 2.5622 | 2.4513 | 2.286 | 2.1248 | 1.795 | 1.0199 | 0.48773 | 0.26814 | 2.8999 | 2.8779 | 2.8547 | 2.797 | 2.7379 | 2.672 | 2.6023 | 2.532 | 2.4096 | 2.3004 | 2.0717 | 1.6692 | 1.3238 | 1.1075 | 3.2356 | 3.194 | 3.1527 | 3.0605 | 2.97 | 2.8696 | 2.7651 | 2.6589 | 2.492 | 2.3344 | 2.0129 | 1.32 | 0.8399 | 0.61621
STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | NO | 5.2585 | 5.124 | 4.9454 | 4.6554 | 4.3372 | 3.9506 | 3.4071 | 2.9258 | 2.6125 | 2.2879 | 1.6509 | 1.2416 | 0.35624 | -0.64862 | 5.9435 | 5.8737 | 5.7714 | 5.5688 | 5.343 | 5.0263 | 4.5695 | 4.1935 | 3.9598 | 3.7145 | 3.2384 | 2.9287 | 2.0181 | 0.83988 | 5.5731 | 5.4373 | 5.2669 | 4.9596 | 4.6253 | 4.1991 | 3.621 | 3.1279 | 2.8365 | 2.5361 | 1.9487 | 1.4883 | 0.43845 | -0.7899
| HATTON | CT |  |  |  | 5.3537 | 5.269 | 5.1546 | 4.8771 | 4.575 | 4.1953 | 3.7208 | 3.3762 | 3.0857 | 2.7561 | 2.1161 | 1.4905 | 0.73163 | 0.16193 | 5.9825 | 5.9326 | 5.8593 | 5.6893 | 5.4945 | 5.1842 | 4.7822 | 4.5366 | 4.3209 | 4.0737 | 3.5987 | 3.0921 | 2.4065 | 1.6942 | 5.6771 | 5.5942 | 5.4881 | 5.2137 | 4.9158 | 4.4998 | 3.9804 | 3.6199 | 3.3351 | 3.0246 | 2.4204 | 1.7585 | 0.89615 | 0.23463
| HATTON | LW |  |  |  | 5.2585 | 5.124 | 4.9454 | 4.6554 | 4.3372 | 3.9506 | 3.4071 | 2.9258 | 2.6125 | 2.2879 | 1.6509 | 1.2416 | 0.35624 | -0.64862 | 5.9435 | 5.8737 | 5.7714 | 5.5688 | 5.343 | 5.0263 | 4.5695 | 4.1935 | 3.9598 | 3.7145 | 3.2384 | 2.9287 | 2.0181 | 0.83988 | 5.5731 | 5.4373 | 5.2669 | 4.9596 | 4.6253 | 4.1991 | 3.621 | 3.1279 | 2.8365 | 2.5361 | 1.9487 | 1.4883 | 0.43845 | -0.7899
| HATTON | ST |  |  |  | 5.3902 | 5.3397 | 5.2796 | 5.0713 | 4.8887 | 4.7294 | 4.3438 | 4.1024 | 3.8497 | 3.6537 | 3.2113 | 2.2938 | 1.3683 | 0.47043 | 5.9982 | 5.9694 | 5.9337 | 5.7232 | 5.555 | 5.4195 | 5.0227 | 4.8095 | 4.574 | 4.4144 | 4.0529 | 3.3006 | 2.3939 | 1.4228 | 5.7184 | 5.6689 | 5.612 | 5.3754 | 5.1775 | 5.0113 | 4.5792 | 4.3298 | 4.0661 | 3.8805 | 3.4671 | 2.6216 | 1.5789 | 0.52657
| HATTON | FS |  |  |  | 5.4127 | 5.374 | 5.3303 | 5.2367 | 5.1303 | 5.0198 | 4.8569 | 4.6866 | 4.517 | 4.3561 | 4.0069 | 3.1984 | 2.4656 | 2.0905 | 6.0078 | 5.9843 | 5.9564 | 5.8836 | 5.8024 | 5.7144 | 5.577 | 5.4328 | 5.2983 | 5.1729 | 4.9012 | 4.3472 | 3.717 | 3.1824 | 5.7425 | 5.705 | 5.6645 | 5.5675 | 5.4593 | 5.3469 | 5.1798 | 5.0064 | 4.8351 | 4.6774 | 4.3409 | 3.6003 | 2.9321 | 2.5174
PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 23.8 | 23.8 | 23.8 | 23.6339 | 23.4706 | 23.1197 | 22.7482 | 22.535 | 22.4865 | 22.4362 | 22.3482 | 22.1032 | 21.718 | 21.2042 | 19.1438 | 18.8095 | 18.4688 | 17.9091 | 17.317 | 16.5085 | 15.4908 | 14.5847 | 13.9031 | 13.1608 | 11.6668 | 14.0608 | 13.3149 | 10.687 | 18.3483 | 17.8333 | 17.3302 | 16.5087 | 15.66 | 14.5955 | 13.2786 | 12.0519 | 11.1405 | 10.1534 | 8.1624 | 10.9806 | 10.3148 | 9.5933
| HAUDAGAIN | CT |  |  |  | 23.8 | 23.8 | 23.8 | 23.7784 | 23.74 | 23.5553 | 23.3584 | 23.3084 | 23.2887 | 23.2688 | 23.2328 | 23.1327 | 22.9625 | 22.7586 | 19.2077 | 18.9185 | 18.6451 | 18.161 | 17.6349 | 16.9928 | 16.2829 | 15.769 | 15.2339 | 14.6716 | 13.5065 | 14.6107 | 13.3149 | 11.6395 | 18.5296 | 18.132 | 17.7756 | 17.0534 | 16.2896 | 15.4268 | 14.4828 | 13.7453 | 13.0217 | 12.2759 | 10.7494 | 12.2122 | 11.191 | 10.58
| HAUDAGAIN | LW |  |  |  | 23.8 | 23.8 | 23.8 | 23.6443 | 23.4706 | 23.1197 | 22.7482 | 22.535 | 22.4865 | 22.4362 | 22.3482 | 22.1032 | 21.718 | 21.2042 | 19.1438 | 18.8095 | 18.4688 | 17.9091 | 17.317 | 16.5085 | 15.4908 | 14.5847 | 13.9031 | 13.1608 | 11.6668 | 14.0608 | 13.4747 | 12.7786 | 18.3483 | 17.8333 | 17.3302 | 16.5087 | 15.66 | 14.5955 | 13.2786 | 12.0519 | 11.1405 | 10.1534 | 8.1624 | 10.9806 | 10.3148 | 9.5933
| HAUDAGAIN | ST |  |  |  | 23.8 | 23.8 | 23.8 | 23.6339 | 23.5216 | 23.4474 | 23.1924 | 23.1215 | 23.078 | 23.0626 | 23.0287 | 22.9308 | 22.6678 | 22.3731 | 19.2549 | 19.0466 | 18.9101 | 18.557 | 18.2519 | 17.9553 | 17.383 | 17.0003 | 16.6031 | 16.1759 | 15.1355 | 15.5465 | 14.1079 | 12.1274 | 18.6191 | 18.3375 | 18.1688 | 17.7854 | 17.4514 | 17.119 | 16.5011 | 16.0688 | 15.6214 | 15.1344 | 13.9468 | 14.7616 | 13.6533 | 12.4668
| HAUDAGAIN | FS |  |  |  | 23.8 | 23.8 | 23.8 | 23.766 | 23.7321 | 23.6925 | 23.6529 | 23.6189 | 23.6032 | 23.5925 | 23.5712 | 23.5582 | 23.5438 | 23.5109 | 19.2887 | 19.1106 | 18.989 | 18.8024 | 18.6078 | 18.3852 | 18.1382 | 17.8665 | 17.5736 | 17.2505 | 16.4928 | 16.1379 | 13.95 | 10.687 | 18.6782 | 18.4584 | 18.3196 | 18.1052 | 17.8865 | 17.6392 | 17.3704 | 17.074 | 16.7533 | 16.4043 | 15.6081 | 15.7328 | 14.4106 | 13.4144
WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | YES | 15.8037 | 15.4805 | 15.0434 | 14.3622 | 13.6387 | 12.9201 | 12.0044 | 10.9958 | 10.1611 | 9.2421 | 7.2525 | 9.2954 | 7.8422 | 7.057 | 18.8118 | 18.6404 | 18.3777 | 18.0395 | 17.668 | 17.2835 | 16.7731 | 16.1305 | 15.4721 | 14.7539 | 13.3036 | 14.4223 | 12.7469 | 9.3441 | 17.6337 | 17.3468 | 16.9254 | 16.3418 | 15.6751 | 15.0133 | 14.1264 | 13.1317 | 12.2439 | 11.2826 | 9.3379 | 11.6797 | 10.3155 | 9.5203
| HAYTON | CT |  |  |  | 16.0534 | 15.8763 | 15.6417 | 14.928 | 14.1651 | 13.468 | 12.7502 | 12.0473 | 11.3599 | 10.6393 | 9.0921 | 9.2954 | 7.8422 | 7.057 | 18.8821 | 18.751 | 18.5735 | 18.1607 | 17.704 | 17.2835 | 16.8407 | 16.4195 | 15.895 | 15.3336 | 14.1178 | 14.4223 | 12.7469 | 10.6196 | 17.8103 | 17.6352 | 17.3953 | 16.7524 | 16.0503 | 15.4164 | 14.7362 | 14.0771 | 13.3823 | 12.6484 | 11.0842 | 11.6797 | 10.3155 | 9.5203
| HAYTON | LW |  |  |  | 15.8037 | 15.4805 | 15.0434 | 14.3622 | 13.6387 | 12.9201 | 12.0044 | 10.9958 | 10.1611 | 9.2421 | 7.2525 | 9.5508 | 8.6891 | 7.8263 | 18.8118 | 18.6404 | 18.3777 | 18.0395 | 17.668 | 17.2996 | 16.7731 | 16.1305 | 15.4721 | 14.7539 | 13.3036 | 15.5779 | 14.7731 | 13.7714 | 17.6337 | 17.3468 | 16.9254 | 16.3418 | 15.6751 | 15.0133 | 14.1264 | 13.1317 | 12.2439 | 11.2826 | 9.3379 | 11.9577 | 11.0154 | 9.9862
| HAYTON | ST |  |  |  | 16.1421 | 16.0523 | 15.9461 | 15.7694 | 15.5828 | 15.3831 | 15.1025 | 14.8324 | 14.4613 | 14.0893 | 13.1452 | 12.8938 | 11.3915 | 9.7783 | 18.9231 | 18.8483 | 18.7561 | 18.5969 | 18.4293 | 18.2502 | 17.9878 | 17.7438 | 17.3809 | 17.0115 | 16.1215 | 15.7289 | 13.8881 | 11.3514 | 17.8811 | 17.7948 | 17.6864 | 17.5011 | 17.3022 | 17.0878 | 16.7785 | 16.4779 | 16.0487 | 15.6222 | 14.6134 | 14.5904 | 13.2089 | 11.7351
| HAYTON | FS |  |  |  | 16.1687 | 16.1023 | 16.0195 | 15.872 | 15.7049 | 15.5246 | 15.3189 | 15.0988 | 14.7805 | 14.4507 | 13.7234 | 13.1167 | 11.5205 | 10.24 | 18.9325 | 18.865 | 18.7811 | 18.6559 | 18.5104 | 18.3479 | 18.1589 | 17.9486 | 17.66 | 17.354 | 16.6366 | 15.7394 | 13.2278 | 9.3441 | 17.9012 | 17.8348 | 17.7493 | 17.6103 | 17.4464 | 17.266 | 17.0572 | 16.8275 | 16.5069 | 16.1712 | 15.4177 | 15.105 | 13.648 | 12.5903
BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | NO | 3.706 | 3.6854 | 3.6552 | 3.5826 | 3.5349 | 3.4841 | 3.423 | 3.3558 | 3.3299 | 3.2985 | 3.2015 | 3.1717 | 3.1129 | 3.0783 | 3.6787 | 3.6597 | 3.6327 | 3.5792 | 3.5475 | 3.5168 | 3.4749 | 3.43 | 3.3928 | 3.3517 | 3.2722 | 3.2654 | 3.2263 | 3.1935 | 3.2528 | 3.2176 | 3.1804 | 3.1051 | 3.0579 | 3.0079 | 2.9548 | 2.9043 | 2.8873 | 2.8666 | 2.7919 | 2.7586 | 2.7063 | 2.6719
| HELMSDALE | CT |  |  |  | 3.7176 | 3.7009 | 3.6829 | 3.6162 | 3.5717 | 3.5064 | 3.4445 | 3.3726 | 3.3476 | 3.3168 | 3.2363 | 3.2002 | 3.1129 | 3.0783 | 3.6874 | 3.6735 | 3.6555 | 3.5937 | 3.5522 | 3.5168 | 3.4827 | 3.4481 | 3.4178 | 3.3782 | 3.3014 | 3.2738 | 3.2263 | 3.1935 | 3.2757 | 3.2529 | 3.2316 | 3.1471 | 3.091 | 3.0283 | 2.971 | 2.9115 | 2.8928 | 2.8739 | 2.8245 | 2.7865 | 2.7063 | 2.6719
| HELMSDALE | LW |  |  |  | 3.706 | 3.6854 | 3.6552 | 3.5826 | 3.5349 | 3.4841 | 3.423 | 3.3558 | 3.3299 | 3.2985 | 3.2015 | 3.1717 | 3.1238 | 3.1095 | 3.6787 | 3.6597 | 3.6327 | 3.5792 | 3.5475 | 3.5169 | 3.4749 | 3.43 | 3.3928 | 3.3517 | 3.2722 | 3.2654 | 3.2442 | 3.238 | 3.2528 | 3.2176 | 3.1804 | 3.1051 | 3.0579 | 3.0079 | 2.9548 | 2.9043 | 2.8873 | 2.8666 | 2.7919 | 2.7586 | 2.7132 | 2.7002
| HELMSDALE | ST |  |  |  | 3.7238 | 3.7153 | 3.7074 | 3.6637 | 3.6487 | 3.631 | 3.6135 | 3.5942 | 3.5726 | 3.5508 | 3.499 | 3.3395 | 3.2712 | 3.2252 | 3.6932 | 3.6859 | 3.6784 | 3.6433 | 3.6283 | 3.6107 | 3.5929 | 3.5723 | 3.5475 | 3.5208 | 3.4561 | 3.3329 | 3.286 | 3.2518 | 3.2925 | 3.2802 | 3.2706 | 3.2246 | 3.2058 | 3.1818 | 3.1626 | 3.1403 | 3.1162 | 3.0937 | 3.0366 | 2.9016 | 2.8313 | 2.7858
| HELMSDALE | FS |  |  |  | 3.728 | 3.7194 | 3.7128 | 3.678 | 3.6615 | 3.6456 | 3.6282 | 3.612 | 3.5947 | 3.5708 | 3.5282 | 3.3552 | 3.2092 | 3.1725 | 3.6968 | 3.6895 | 3.6828 | 3.6553 | 3.6404 | 3.6254 | 3.6091 | 3.5927 | 3.574 | 3.5487 | 3.4999 | 3.3691 | 3.2537 | 3.2082 | 3.3018 | 3.288 | 3.2791 | 3.2424 | 3.2217 | 3.1977 | 3.1777 | 3.156 | 3.1348 | 3.1052 | 3.0554 | 2.9181 | 2.7851 | 2.7515
INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 10.698 | 10.3183 | 9.7963 | 8.8621 | 7.8859 | 6.9395 | 5.6613 | 4.2699 | 3.0395 | 1.705 | -0.98626 | -1.0287 | -3.6277 | -5.2755 | 15.0145 | 14.803 | 14.4646 | 14.0107 | 13.5164 | 13.048 | 12.3254 | 11.507 | 10.6746 | 9.7893 | 8.0294 | 8.2449 | 6.349 | 4.2346 | 13.43 | 13.0785 | 12.5671 | 11.7346 | 10.8517 | 10.0019 | 8.8148 | 7.504 | 6.2868 | 5.0075 | 2.4576 | 2.8055 | 0.59796 | -0.86429
| HILTON | CT |  |  |  | 11.0327 | 10.8262 | 10.5438 | 9.6408 | 8.6946 | 7.8698 | 6.9433 | 5.9949 | 4.839 | 3.573 | 0.95404 | -0.91429 | -3.6277 | -5.2755 | 15.119 | 14.9628 | 14.7352 | 14.2091 | 13.6399 | 13.178 | 12.6597 | 12.1333 | 11.4224 | 10.6135 | 8.9507 | 8.2449 | 6.349 | 4.2346 | 13.7047 | 13.5006 | 13.2104 | 12.3667 | 11.4714 | 10.7152 | 9.875 | 9.0182 | 7.933 | 6.7334 | 4.2912 | 2.9133 | 0.59796 | -0.86429
| HILTON | LW |  |  |  | 10.698 | 10.3183 | 9.7963 | 8.8621 | 7.8859 | 6.9395 | 5.6613 | 4.2699 | 3.0395 | 1.705 | -0.98626 | -1.0287 | -2.8037 | -3.8422 | 15.0145 | 14.803 | 14.4646 | 14.0107 | 13.5164 | 13.048 | 12.3254 | 11.507 | 10.6746 | 9.7893 | 8.0294 | 8.8646 | 7.8429 | 6.9369 | 13.43 | 13.0785 | 12.5671 | 11.7346 | 10.8517 | 10.0019 | 8.8148 | 7.504 | 6.2868 | 5.0075 | 2.4576 | 2.8055 | 1.1795 | 0.086507
| HILTON | ST |  |  |  | 11.2234 | 11.1753 | 11.0989 | 10.9856 | 10.8377 | 10.6525 | 10.3526 | 10.0151 | 9.5641 | 9.0792 | 7.9179 | 6.5153 | 4.7266 | 2.191 | 15.1902 | 15.1236 | 15.032 | 14.9042 | 14.746 | 14.57 | 14.313 | 14.0277 | 13.6261 | 13.2086 | 12.2087 | 10.9812 | 9.2185 | 6.6911 | 13.8612 | 13.8039 | 13.7164 | 13.5862 | 13.4177 | 13.2325 | 12.9461 | 12.6258 | 12.1803 | 11.7018 | 10.5469 | 9.2349 | 7.5741 | 5.2378
| HILTON | FS |  |  |  | 11.2186 | 11.1647 | 11.094 | 10.9288 | 10.7442 | 10.5561 | 10.2851 | 9.9694 | 9.5619 | 9.132 | 8.1696 | 6.5465 | 4.0876 | 2.1828 | 15.1921 | 15.1249 | 15.0389 | 14.9068 | 14.7519 | 14.5855 | 14.3645 | 14.1137 | 13.785 | 13.4305 | 12.6098 | 11.1206 | 8.3518 | 4.8752 | 13.8585 | 13.8001 | 13.7222 | 13.5607 | 13.3743 | 13.1813 | 12.9214 | 12.6308 | 12.2494 | 11.8458 | 10.9373 | 9.4745 | 7.1969 | 5.5232
ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | NO | 13.6616 | 13.356 | 12.6158 | 12.016 | 11.4196 | 10.7951 | 10.0328 | 9.2576 | 8.6542 | 8.0154 | 6.7538 | 7.4139 | 6.0602 | 5.2184 | 16.8686 | 16.7053 | 16.2905 | 15.9675 | 15.636 | 15.2333 | 14.7039 | 14.2831 | 13.8749 | 13.4431 | 12.4694 | 12.7001 | 11.4056 | 9.8393 | 15.8735 | 15.6202 | 15.0205 | 14.4711 | 13.9128 | 13.3126 | 12.5617 | 11.8029 | 11.1909 | 10.5392 | 9.2513 | 10.0431 | 8.8056 | 7.9903
| HUME STREET | CT |  |  |  | 13.859 | 13.6348 | 13.0446 | 12.4506 | 11.8511 | 11.1708 | 10.4213 | 9.7473 | 9.129 | 8.5158 | 7.2871 | 7.4139 | 6.0602 | 5.2184 | 16.9315 | 16.7809 | 16.4216 | 16.077 | 15.7133 | 15.2333 | 14.7039 | 14.3007 | 13.8749 | 13.4461 | 12.5638 | 12.7001 | 11.4056 | 9.8393 | 16.0429 | 15.8514 | 15.3859 | 14.8333 | 14.2617 | 13.5914 | 12.858 | 12.2379 | 11.6383 | 11.0317 | 9.8105 | 10.0431 | 8.8056 | 7.9903
| HUME STREET | LW |  |  |  | 13.6616 | 13.356 | 12.6158 | 12.016 | 11.4196 | 10.7951 | 10.0328 | 9.2576 | 8.6542 | 8.0154 | 6.7538 | 7.6565 | 6.7853 | 6.051 | 16.8686 | 16.7053 | 16.2905 | 15.9675 | 15.636 | 15.2559 | 14.7647 | 14.2831 | 13.8779 | 13.4431 | 12.4694 | 13.5909 | 12.8853 | 12.0667 | 15.8735 | 15.6202 | 15.0205 | 14.4711 | 13.9128 | 13.3126 | 12.5617 | 11.8029 | 11.1909 | 10.5392 | 9.2513 | 10.3405 | 9.4287 | 8.5598
| HUME STREET | ST |  |  |  | 13.9956 | 13.908 | 13.4877 | 13.2696 | 13.099 | 12.9334 | 12.5659 | 12.2971 | 11.9701 | 11.6666 | 10.9643 | 11.1378 | 10.1257 | 8.7007 | 16.987 | 16.9162 | 16.6636 | 16.4146 | 16.2143 | 16.0319 | 15.626 | 15.3702 | 15.0366 | 14.7483 | 14.0726 | 13.8998 | 12.6029 | 10.766 | 16.1652 | 16.1012 | 15.7851 | 15.5323 | 15.3305 | 15.1422 | 14.7203 | 14.4382 | 14.0784 | 13.756 | 12.7871 | 13.0092 | 12.0235 | 10.7204
| HUME STREET | FS |  |  |  | 13.9893 | 13.9065 | 13.5646 | 13.414 | 13.2685 | 13.098 | 12.9095 | 12.7222 | 12.4803 | 12.2311 | 11.6753 | 11.4855 | 10.4164 | 9.4429 | 16.9872 | 16.9203 | 16.7047 | 16.574 | 16.4394 | 16.2818 | 16.1061 | 15.9249 | 15.6944 | 15.4557 | 14.9054 | 14.4194 | 12.6905 | 9.9374 | 16.158 | 16.0983 | 15.8514 | 15.7047 | 15.5568 | 15.3849 | 15.1941 | 15.0008 | 14.7543 | 14.5019 | 13.9354 | 13.7663 | 12.7515 | 11.9189
KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | NO | 8.0614 | 7.8753 | 7.6451 | 7.2298 | 6.7884 | 6.2571 | 5.5673 | 4.7097 | 4.0862 | 3.6772 | 2.8207 | 2.5058 | 1.4188 | 0.71993 | 9.4253 | 9.337 | 9.2118 | 8.9602 | 8.6842 | 8.3035 | 7.7815 | 7.1337 | 6.6667 | 6.3859 | 5.7976 | 5.5435 | 4.7301 | 3.9299 | 7.8594 | 7.6931 | 7.4847 | 7.0879 | 6.664 | 6.1305 | 5.4434 | 4.6169 | 4.029 | 3.6393 | 2.827 | 2.5457 | 1.479 | 0.60906
| HUNTLY | CT |  |  |  | 8.2071 | 8.0967 | 7.9452 | 7.5605 | 7.1536 | 6.6029 | 5.9559 | 5.2692 | 4.6313 | 4.1557 | 3.2265 | 2.5367 | 1.4188 | 0.71993 | 9.4438 | 9.4002 | 9.3088 | 9.094 | 8.8467 | 8.4246 | 7.9119 | 7.414 | 6.9401 | 6.6078 | 5.9591 | 5.5435 | 4.7301 | 3.9299 | 7.987 | 7.8866 | 7.7474 | 7.392 | 7.0104 | 6.4478 | 5.7914 | 5.142 | 4.538 | 4.0835 | 3.1979 | 2.5457 | 1.479 | 0.77278
| HUNTLY | LW |  |  |  | 8.0614 | 7.8753 | 7.6451 | 7.2298 | 6.7884 | 6.2571 | 5.5673 | 4.7097 | 4.0862 | 3.6772 | 2.8207 | 2.5058 | 1.5799 | 0.74661 | 9.4253 | 9.337 | 9.2118 | 8.9602 | 8.6842 | 8.3035 | 7.7815 | 7.1337 | 6.6667 | 6.3859 | 5.7976 | 5.7331 | 4.9692 | 4.0677 | 7.8594 | 7.6931 | 7.4847 | 7.0879 | 6.664 | 6.1305 | 5.4434 | 4.6169 | 4.029 | 3.6393 | 2.827 | 2.5552 | 1.5791 | 0.60906
| HUNTLY | ST |  |  |  | 8.2698 | 8.212 | 8.1417 | 7.8639 | 7.6328 | 7.4297 | 6.9504 | 6.4545 | 5.9557 | 5.6926 | 5.1196 | 4.422 | 3.3403 | 2.1873 | 9.4607 | 9.4434 | 9.4174 | 9.1381 | 8.9193 | 8.7428 | 8.2509 | 7.8078 | 7.3497 | 7.1295 | 6.6396 | 6.0082 | 5.0861 | 4.0309 | 8.0434 | 7.9919 | 7.9293 | 7.6179 | 7.3684 | 7.1581 | 6.6279 | 6.1391 | 5.6386 | 5.3799 | 4.814 | 4.1151 | 3.0288 | 1.8827
| HUNTLY | FS |  |  |  | 8.3334 | 8.2864 | 8.2347 | 8.1115 | 7.9841 | 7.843 | 7.651 | 7.2927 | 6.9256 | 6.7041 | 6.224 | 5.3694 | 4.3695 | 3.6716 | 9.5001 | 9.4869 | 9.4663 | 9.3725 | 9.2713 | 9.1574 | 9.0005 | 8.6924 | 8.3897 | 8.217 | 7.8358 | 7.2275 | 6.3101 | 5.3618 | 8.1024 | 8.0606 | 8.0149 | 7.8926 | 7.7663 | 7.6256 | 7.4374 | 7.0914 | 6.7403 | 6.5281 | 6.0684 | 5.2984 | 4.3829 | 3.7596
BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | NO | 2.0315 | 2.0091 | 1.9772 | 1.9259 | 1.8396 | 1.6984 | 1.5155 | 1.4073 | 1.2706 | 1.1379 | 0.85842 | 0.95025 | 0.52132 | 0.10147 | 2.3849 | 2.369 | 2.3462 | 2.2558 | 2.1591 | 2.0888 | 1.8839 | 1.8077 | 1.6402 | 1.5564 | 1.3147 | 1.1262 | 0.62765 | 0.12676 | 2.2477 | 2.2214 | 2.1769 | 2.1147 | 2.0093 | 1.8665 | 1.6726 | 1.5731 | 1.4069 | 1.2854 | 0.99362 | 0.99313 | 0.47697 | -0.0324
| INCHBARE | CT |  |  |  | 2.0352 | 2.0153 | 1.9844 | 1.9338 | 1.8662 | 1.6984 | 1.5155 | 1.4073 | 1.2706 | 1.1379 | 0.85842 | 1.0283 | 0.72336 | 0.44396 | 2.3878 | 2.3736 | 2.3516 | 2.3079 | 2.2509 | 2.0888 | 1.9143 | 1.8424 | 1.7416 | 1.6176 | 1.3645 | 1.2809 | 0.94186 | 0.5903 | 2.2477 | 2.2214 | 2.1769 | 2.1154 | 2.0462 | 1.8665 | 1.6726 | 1.5731 | 1.4336 | 1.2945 | 1.0071 | 1.1131 | 0.75378 | 0.41017
| INCHBARE | LW |  |  |  | 2.0315 | 2.0091 | 1.9772 | 1.9358 | 1.8967 | 1.8527 | 1.786 | 1.6935 | 1.5748 | 1.4446 | 1.1678 | 1.5744 | 1.0878 | 0.41933 | 2.3849 | 2.369 | 2.3462 | 2.3241 | 2.3017 | 2.277 | 2.2411 | 2.2026 | 2.138 | 2.039 | 1.8161 | 1.9857 | 1.4074 | 0.57879 | 2.2525 | 2.2292 | 2.1917 | 2.1608 | 2.1247 | 2.0852 | 2.0226 | 1.9475 | 1.8365 | 1.7133 | 1.4523 | 1.8012 | 1.2058 | 0.37331
| INCHBARE | ST |  |  |  | 2.058 | 2.0479 | 2.0361 | 1.9259 | 1.8396 | 1.7757 | 1.5997 | 1.5204 | 1.3427 | 1.2219 | 0.93303 | 0.95025 | 0.52132 | 0.10147 | 2.4034 | 2.3957 | 2.3869 | 2.2558 | 2.1591 | 2.0896 | 1.8839 | 1.8077 | 1.6402 | 1.5564 | 1.3147 | 1.1262 | 0.62765 | 0.12676 | 2.2791 | 2.2679 | 2.254 | 2.1147 | 2.0093 | 1.9257 | 1.7028 | 1.6045 | 1.4069 | 1.2854 | 0.99362 | 0.99313 | 0.47697 | -0.0324
| INCHBARE | FS |  |  |  | 2.063 | 2.0558 | 2.0483 | 2.017 | 1.9865 | 1.9501 | 1.9118 | 1.872 | 1.8108 | 1.7518 | 1.5955 | 1.5881 | 1.4841 | 1.3954 | 2.4068 | 2.4015 | 2.3952 | 2.3621 | 2.3291 | 2.2903 | 2.2499 | 2.2106 | 2.1448 | 2.0911 | 1.9776 | 1.9395 | 1.8389 | 1.7447 | 2.2825 | 2.2751 | 2.2663 | 2.2302 | 2.1918 | 2.1464 | 2.0977 | 2.0488 | 1.9697 | 1.9015 | 1.7484 | 1.7932 | 1.683 | 1.5892
DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | NO | 2.003 | 1.9804 | 1.9588 | 1.8986 | 1.8037 | 1.6927 | 1.5149 | 1.4082 | 1.2709 | 1.1298 | 0.85491 | 0.38616 | -0.10451 | -0.46207 | 2.4783 | 2.4546 | 2.4238 | 2.37 | 2.2843 | 2.1433 | 1.9717 | 1.8925 | 1.7755 | 1.6481 | 1.4036 | 1.0503 | 0.65389 | 0.10769 | 2.2453 | 2.2095 | 2.1616 | 2.086 | 2.0031 | 1.82 | 1.6229 | 1.5169 | 1.3655 | 1.1984 | 0.87566 | 0.44354 | -0.047514 | -0.44169
| INNELLAN | CT |  |  |  | 2.0234 | 2.0056 | 1.9909 | 1.9329 | 1.8655 | 1.6927 | 1.5149 | 1.4082 | 1.2709 | 1.1298 | 0.85491 | 0.38616 | -0.10451 | -0.46207 | 2.4932 | 2.4747 | 2.4529 | 2.3866 | 2.3064 | 2.1433 | 1.9717 | 1.8925 | 1.7755 | 1.6481 | 1.4036 | 1.0503 | 0.65389 | 0.27135 | 2.2727 | 2.2472 | 2.2162 | 2.1202 | 2.0088 | 1.82 | 1.6229 | 1.5169 | 1.3655 | 1.1984 | 0.87566 | 0.44354 | -0.047514 | -0.44169
| INNELLAN | LW |  |  |  | 2.003 | 1.9804 | 1.9588 | 1.8986 | 1.8037 | 1.7121 | 1.6089 | 1.5006 | 1.3999 | 1.2932 | 1.082 | 0.87533 | 0.31225 | -0.31037 | 2.4783 | 2.4546 | 2.4238 | 2.378 | 2.3274 | 2.2802 | 2.2149 | 2.1419 | 2.0512 | 1.954 | 1.764 | 1.6903 | 1.1344 | 0.39254 | 2.2453 | 2.2095 | 2.1616 | 2.086 | 2.0031 | 1.9257 | 1.8213 | 1.7054 | 1.5764 | 1.4381 | 1.1687 | 1.0607 | 0.43725 | -0.31939
| INNELLAN | ST |  |  |  | 2.0356 | 2.0328 | 2.0304 | 1.9409 | 1.8774 | 1.8313 | 1.6929 | 1.6464 | 1.5353 | 1.4838 | 1.3679 | 1.0312 | 0.48847 | -0.13488 | 2.5011 | 2.4947 | 2.487 | 2.37 | 2.2843 | 2.221 | 2.0393 | 1.9718 | 1.8222 | 1.7463 | 1.573 | 1.1781 | 0.66413 | 0.10769 | 2.2839 | 2.2758 | 2.2658 | 2.145 | 2.0541 | 1.9844 | 1.7959 | 1.7196 | 1.5591 | 1.4693 | 1.2632 | 0.80386 | 0.24375 | -0.34989
| INNELLAN | FS |  |  |  | 2.0374 | 2.0366 | 2.0346 | 2.0115 | 1.9871 | 1.9603 | 1.9335 | 1.9045 | 1.8561 | 1.8139 | 1.7224 | 1.5229 | 1.2712 | 1.0191 | 2.5029 | 2.4979 | 2.491 | 2.4592 | 2.4249 | 2.3865 | 2.3467 | 2.3056 | 2.2387 | 2.181 | 2.0584 | 1.8909 | 1.6742 | 1.4741 | 2.2863 | 2.2807 | 2.2722 | 2.2362 | 2.1963 | 2.1527 | 2.1073 | 2.0576 | 1.9813 | 1.9108 | 1.7612 | 1.5335 | 1.2606 | 1.0802
KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | NO | 6.4281 | 6.0809 | 5.688 | 5.2154 | 4.7156 | 4.162 | 3.2596 | 2.4042 | 2.0753 | 1.728 | 1.0245 | 0.84916 | 0.17728 | -0.41517 | 9.3983 | 9.2488 | 9.0587 | 8.7969 | 8.5103 | 8.1544 | 7.4824 | 6.8762 | 6.6214 | 6.3492 | 5.7991 | 5.6363 | 4.8897 | 4.1316 | 7.4968 | 7.1938 | 6.8401 | 6.4003 | 5.9306 | 5.3941 | 4.5199 | 3.7024 | 3.3597 | 2.9959 | 2.2642 | 2.0747 | 1.3984 | 0.68712
| INSCH | CT |  |  |  | 6.6552 | 6.4195 | 6.1381 | 5.5639 | 4.9619 | 4.2962 | 3.3612 | 2.568 | 2.2664 | 1.9211 | 1.2646 | 1.0761 | 0.17728 | -0.27515 | 9.4769 | 9.3649 | 9.2127 | 8.9159 | 8.5898 | 8.1679 | 7.5013 | 7.0031 | 6.7603 | 6.472 | 5.9287 | 5.6363 | 4.9865 | 4.3795 | 7.6884 | 7.4806 | 7.2239 | 6.7011 | 6.1452 | 5.5052 | 4.6144 | 3.8912 | 3.5804 | 3.2147 | 2.5226 | 2.2569 | 1.422 | 0.95746
| INSCH | LW |  |  |  | 6.4281 | 6.0809 | 5.688 | 5.2154 | 4.7156 | 4.162 | 3.2596 | 2.4042 | 2.0753 | 1.728 | 1.0245 | 0.84916 | 0.20606 | -0.41517 | 9.3983 | 9.2488 | 9.0587 | 8.7969 | 8.5103 | 8.1544 | 7.4824 | 6.8762 | 6.6214 | 6.3492 | 5.7991 | 5.7112 | 5.1714 | 4.5231 | 7.4968 | 7.1938 | 6.8401 | 6.4003 | 5.9306 | 5.3941 | 4.5199 | 3.7024 | 3.3597 | 2.9959 | 2.2642 | 2.0747 | 1.3984 | 0.68712
| INSCH | ST |  |  |  | 6.7727 | 6.6222 | 6.4612 | 6.1199 | 5.8047 | 5.5153 | 4.8144 | 4.2787 | 3.8965 | 3.5477 | 2.7961 | 1.5205 | 0.52153 | -0.19629 | 9.5202 | 9.4517 | 9.3745 | 9.112 | 8.8885 | 8.6965 | 8.0864 | 7.6732 | 7.3893 | 7.1499 | 6.6226 | 5.6855 | 4.8897 | 4.1316 | 7.7868 | 7.6559 | 7.5144 | 7.1659 | 6.853 | 6.5726 | 5.8656 | 5.3543 | 4.9721 | 4.6323 | 3.8915 | 2.5817 | 1.6073 | 0.89593
| INSCH | FS |  |  |  | 6.8586 | 6.7531 | 6.6388 | 6.442 | 6.2375 | 6.0173 | 5.6481 | 5.2473 | 4.9414 | 4.6328 | 3.9925 | 2.3402 | 1.2318 | 0.82601 | 9.5515 | 9.5 | 9.441 | 9.3268 | 9.2041 | 9.0696 | 8.7972 | 8.4973 | 8.3046 | 8.1081 | 7.6954 | 6.7354 | 5.825 | 5.2162 | 7.8593 | 7.7671 | 7.666 | 7.4831 | 7.2912 | 7.084 | 6.7381 | 6.3625 | 6.0744 | 5.784 | 5.1766 | 3.6398 | 2.5647 | 2.2132
BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | NO | 15.8303 | 15.2189 | 14.9974 | 14.8108 | 14.2447 | 14.0354 | 13.773 | 13.2923 | 12.8173 | 12.3262 | 11.2986 | 10.3976 | 9.9566 | 9.908 | 16.0545 | 15.4703 | 15.3011 | 15.1668 | 14.6384 | 14.5006 | 14.3356 | 14.188 | 14.0042 | 13.8044 | 13.2723 | 13.1987 | 13.0149 | 12.9947 | 14.6078 | 13.9942 | 13.7964 | 13.6333 | 13.072 | 12.9062 | 12.709 | 12.4729 | 12.0649 | 11.6418 | 10.7563 | 10.1174 | 9.749 | 9.7075
| INVERALMOND | CT |  |  |  | 15.9009 | 15.3359 | 15.0768 | 14.8108 | 14.2611 | 14.0354 | 13.8074 | 13.5996 | 13.1899 | 12.7086 | 11.7009 | 11.3361 | 10.8753 | 10.6728 | 16.1257 | 15.585 | 15.3791 | 15.1709 | 14.6685 | 14.5006 | 14.3356 | 14.1945 | 14.0457 | 13.8983 | 13.4997 | 13.5287 | 13.2613 | 13.0212 | 14.6813 | 14.115 | 13.8809 | 13.6421 | 13.1051 | 12.9065 | 12.709 | 12.5342 | 12.3499 | 11.9614 | 11.1022 | 10.88 | 10.4828 | 10.3082
| INVERALMOND | LW |  |  |  | 15.8303 | 15.2189 | 14.9974 | 14.8112 | 14.2447 | 14.0528 | 13.773 | 13.2923 | 12.8173 | 12.3262 | 11.2986 | 10.3976 | 9.9566 | 9.908 | 16.0545 | 15.4703 | 15.3011 | 15.1668 | 14.6384 | 14.5033 | 14.3559 | 14.188 | 14.0042 | 13.8044 | 13.2723 | 13.1987 | 13.0149 | 12.9947 | 14.6078 | 13.9942 | 13.7964 | 13.6333 | 13.072 | 12.9062 | 12.7228 | 12.4729 | 12.0649 | 11.6418 | 10.7563 | 10.1174 | 9.749 | 9.7075
| INVERALMOND | ST |  |  |  | 15.9086 | 15.3727 | 15.1919 | 15.0146 | 14.5461 | 14.3656 | 14.186 | 14.0108 | 13.8111 | 13.5811 | 13.0312 | 13.5366 | 13.3075 | 12.9104 | 16.1315 | 15.6133 | 15.4679 | 15.3274 | 14.8869 | 14.7528 | 14.6237 | 14.5061 | 14.3703 | 14.2119 | 13.8251 | 14.2302 | 14.1475 | 13.836 | 14.6878 | 14.1464 | 13.9797 | 13.8179 | 13.3523 | 13.1932 | 13.0378 | 12.8916 | 12.7246 | 12.5316 | 12.0587 | 12.4931 | 12.4463 | 12.2422
| INVERALMOND | FS |  |  |  | 16.1237 | 15.7031 | 15.5456 | 15.3806 | 15.0201 | 14.8498 | 14.6703 | 14.4802 | 14.2848 | 14.0721 | 13.6238 | 13.4062 | 12.9382 | 12.5374 | 16.3501 | 15.9494 | 15.825 | 15.695 | 15.363 | 15.2336 | 15.0974 | 14.9533 | 14.8066 | 14.6451 | 14.3086 | 14.1642 | 13.7868 | 13.2273 | 14.9109 | 14.4891 | 14.3451 | 14.1947 | 13.84 | 13.6878 | 13.5278 | 13.3586 | 13.186 | 12.9975 | 12.6038 | 12.3994 | 12.1743 | 11.9839
CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | NO | 2.1996 | 2.1959 | 2.1901 | 2.1646 | 2.143 | 2.1241 | 2.0744 | 2.0583 | 2.0194 | 2.0003 | 1.9624 | 1.8769 | 1.7506 | 1.6215 | 2.1495 | 2.1474 | 2.1441 | 2.1084 | 2.0816 | 2.0614 | 2.0004 | 1.982 | 1.9353 | 1.9153 | 1.8737 | 1.7691 | 1.6157 | 1.4586 | 1.9342 | 1.9317 | 1.9278 | 1.8928 | 1.8659 | 1.8455 | 1.7846 | 1.7658 | 1.7187 | 1.6983 | 1.6553 | 1.5427 | 1.384 | 1.2231
| INVERARAY | CT |  |  |  | 2.2023 | 2.1985 | 2.1947 | 2.1823 | 2.1664 | 2.1258 | 2.0815 | 2.0658 | 2.0442 | 2.0253 | 1.9862 | 1.9122 | 1.8246 | 1.7385 | 2.151 | 2.1489 | 2.1463 | 2.1361 | 2.1219 | 2.0754 | 2.0251 | 2.0094 | 1.9856 | 1.9628 | 1.9188 | 1.8218 | 1.7186 | 1.6104 | 1.9357 | 1.9331 | 1.9299 | 1.9189 | 1.9037 | 1.8564 | 1.8055 | 1.7865 | 1.7601 | 1.7365 | 1.6879 | 1.5878 | 1.4787 | 1.3703
| INVERARAY | LW |  |  |  | 2.1996 | 2.1959 | 2.1901 | 2.183 | 2.1757 | 2.1715 | 2.1678 | 2.1575 | 2.1477 | 2.1375 | 2.1135 | 2.0923 | 1.9419 | 1.7303 | 2.1495 | 2.1474 | 2.1441 | 2.1403 | 2.1362 | 2.1335 | 2.1306 | 2.1245 | 2.1137 | 2.1022 | 2.0791 | 2.0468 | 1.8637 | 1.6003 | 1.9342 | 1.9317 | 1.9278 | 1.9231 | 1.9182 | 1.9154 | 1.9115 | 1.8998 | 1.888 | 1.8754 | 1.8472 | 1.8123 | 1.6242 | 1.3599
| INVERARAY | ST |  |  |  | 2.2039 | 2.2023 | 2.2004 | 2.1646 | 2.143 | 2.1241 | 2.0744 | 2.0583 | 2.0194 | 2.0003 | 1.9624 | 1.8769 | 1.7506 | 1.6215 | 2.1518 | 2.1507 | 2.1496 | 2.1084 | 2.0816 | 2.0614 | 2.0004 | 1.982 | 1.9353 | 1.9153 | 1.8737 | 1.7691 | 1.6157 | 1.4586 | 1.9367 | 1.9358 | 1.9345 | 1.8928 | 1.8659 | 1.8455 | 1.7846 | 1.7658 | 1.7187 | 1.6983 | 1.6553 | 1.5427 | 1.384 | 1.2231
| INVERARAY | FS |  |  |  | 2.2054 | 2.204 | 2.2022 | 2.194 | 2.1857 | 2.175 | 2.1655 | 2.1539 | 2.1405 | 2.1275 | 2.1011 | 2.0752 | 2.0559 | 2.032 | 2.1526 | 2.1515 | 2.1505 | 2.1415 | 2.1324 | 2.1211 | 2.1106 | 2.0997 | 2.0825 | 2.069 | 2.0416 | 2.0185 | 1.9999 | 1.975 | 1.9376 | 1.9368 | 1.9356 | 1.9265 | 1.9172 | 1.906 | 1.8952 | 1.8839 | 1.8673 | 1.8535 | 1.8251 | 1.7914 | 1.7667 | 1.7381
LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | NO | 0.1812 | 0.1551 | 0.12247 | 0.036886 | -0.060995 | -0.20886 | -0.39692 | -0.49857 | -0.56462 | -0.66345 | -0.87867 | -0.94877 | -1.2751 | -1.6253 | 0.38023 | 0.36762 | 0.35014 | 0.21079 | 0.096723 | 0.015317 | -0.23731 | -0.32 | -0.44093 | -0.49982 | -0.63319 | -0.87419 | -1.2418 | -1.6162 | 0.098147 | 0.082476 | 0.062065 | -0.072638 | -0.18732 | -0.28397 | -0.52598 | -0.61161 | -0.7363 | -0.80045 | -0.94536 | -1.0871 | -1.4479 | -1.8373
| INVERARITY | CT |  |  |  | 0.19377 | 0.17533 | 0.1468 | 0.072843 | -0.016444 | -0.19784 | -0.39692 | -0.48433 | -0.56462 | -0.6483 | -0.8198 | -0.85 | -1.0822 | -1.2949 | 0.38484 | 0.37488 | 0.35482 | 0.30162 | 0.23016 | 0.032625 | -0.17993 | -0.25526 | -0.3237 | -0.39695 | -0.53303 | -0.68832 | -0.93926 | -1.204 | 0.10338 | 0.090783 | 0.06429 | 0.0027016 | -0.075555 | -0.27871 | -0.49815 | -0.58168 | -0.65214 | -0.72398 | -0.85971 | -0.90627 | -1.1524 | -1.3999
| INVERARITY | LW |  |  |  | 0.1812 | 0.1551 | 0.12247 | 0.039188 | -0.055976 | -0.20886 | -0.37642 | -0.49857 | -0.56018 | -0.66345 | -0.87867 | -0.76957 | -1.1315 | -1.6253 | 0.38023 | 0.36762 | 0.35014 | 0.27001 | 0.17925 | 0.016492 | -0.16199 | -0.28063 | -0.33774 | -0.3996 | -0.5182 | -0.5695 | -0.99895 | -1.6054 | 0.098147 | 0.082476 | 0.062065 | -0.021162 | -0.11583 | -0.28397 | -0.46777 | -0.59321 | -0.65468 | -0.72296 | -0.85605 | -0.79704 | -1.2289 | -1.8373
| INVERARITY | ST |  |  |  | 0.20556 | 0.19271 | 0.18096 | 0.036886 | -0.060995 | -0.13696 | -0.3495 | -0.4284 | -0.53886 | -0.602 | -0.78613 | -0.94877 | -1.2751 | -1.5932 | 0.38935 | 0.383 | 0.37658 | 0.21079 | 0.096723 | 0.015317 | -0.23731 | -0.32 | -0.44093 | -0.49982 | -0.63319 | -0.87419 | -1.2418 | -1.6162 | 0.10962 | 0.10213 | 0.094936 | -0.072638 | -0.18732 | -0.27112 | -0.52598 | -0.61161 | -0.7363 | -0.80045 | -0.94536 | -1.0871 | -1.4479 | -1.8121
| INVERARITY | FS |  |  |  | 0.21171 | 0.20362 | 0.19096 | 0.15586 | 0.11731 | 0.074317 | 0.026071 | -0.013639 | -0.066739 | -0.112 | -0.20419 | -0.31638 | -0.42158 | -0.4877 | 0.39186 | 0.38756 | 0.38121 | 0.34377 | 0.3045 | 0.25955 | 0.21213 | 0.17075 | 0.1203 | 0.080204 | -0.0035408 | -0.075687 | -0.16041 | -0.23434 | 0.11307 | 0.10825 | 0.10117 | 0.063328 | 0.023761 | -0.021921 | -0.070774 | -0.1125 | -0.16484 | -0.20677 | -0.29495 | -0.31139 | -0.36776 | -0.42398
INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 1.737 | 1.7154 | 1.6879 | 1.6589 | 1.6189 | 1.5485 | 1.4699 | 1.4161 | 1.379 | 1.3404 | 1.2636 | 1.2298 | 1.0617 | 0.91058 | 1.8552 | 1.844 | 1.8279 | 1.8045 | 1.7689 | 1.716 | 1.6497 | 1.6174 | 1.5765 | 1.5412 | 1.4589 | 1.416 | 1.2427 | 1.0646 | 1.6774 | 1.6515 | 1.6216 | 1.5856 | 1.5448 | 1.459 | 1.3681 | 1.3117 | 1.271 | 1.2199 | 1.1305 | 1.0144 | 0.81441 | 0.62912
| INVERARNIE | CT |  |  |  | 1.7471 | 1.7306 | 1.7078 | 1.6625 | 1.6189 | 1.5485 | 1.4699 | 1.4161 | 1.379 | 1.3404 | 1.2636 | 1.2298 | 1.0967 | 0.98768 | 1.8589 | 1.8485 | 1.8344 | 1.8062 | 1.7781 | 1.716 | 1.6497 | 1.6174 | 1.5786 | 1.5413 | 1.4659 | 1.4587 | 1.3332 | 1.1969 | 1.692 | 1.6777 | 1.6551 | 1.6027 | 1.5448 | 1.459 | 1.3681 | 1.3117 | 1.271 | 1.2199 | 1.1305 | 1.0222 | 0.86538 | 0.73595
| INVERARNIE | LW |  |  |  | 1.737 | 1.7154 | 1.6879 | 1.6589 | 1.6264 | 1.5914 | 1.5479 | 1.5002 | 1.4648 | 1.4248 | 1.3385 | 1.395 | 1.2231 | 1.0003 | 1.8552 | 1.844 | 1.8279 | 1.8126 | 1.7952 | 1.7781 | 1.7534 | 1.725 | 1.6914 | 1.6555 | 1.5847 | 1.69 | 1.4987 | 1.2286 | 1.6774 | 1.6515 | 1.6216 | 1.5856 | 1.546 | 1.5099 | 1.4652 | 1.417 | 1.3809 | 1.3441 | 1.2707 | 1.2337 | 1.0217 | 0.74456
| INVERARNIE | ST |  |  |  | 1.7525 | 1.7422 | 1.7323 | 1.6879 | 1.6501 | 1.6189 | 1.5508 | 1.5148 | 1.4537 | 1.4125 | 1.3161 | 1.2328 | 1.0617 | 0.91058 | 1.8615 | 1.8562 | 1.8508 | 1.8045 | 1.7689 | 1.7412 | 1.669 | 1.6381 | 1.5765 | 1.5412 | 1.4589 | 1.416 | 1.2427 | 1.0646 | 1.6979 | 1.6864 | 1.6761 | 1.6224 | 1.5767 | 1.541 | 1.4595 | 1.4209 | 1.352 | 1.3095 | 1.213 | 1.0144 | 0.81441 | 0.62912
| INVERARNIE | FS |  |  |  | 1.757 | 1.7486 | 1.7418 | 1.723 | 1.7045 | 1.6845 | 1.6609 | 1.6393 | 1.6061 | 1.574 | 1.5116 | 1.4387 | 1.3556 | 1.3068 | 1.8633 | 1.859 | 1.8551 | 1.8407 | 1.826 | 1.8094 | 1.791 | 1.7737 | 1.7455 | 1.7208 | 1.67 | 1.6756 | 1.6224 | 1.5681 | 1.7019 | 1.6943 | 1.688 | 1.6656 | 1.6443 | 1.6217 | 1.5946 | 1.5712 | 1.5329 | 1.4957 | 1.4285 | 1.2832 | 1.1819 | 1.1344
FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | NO | 3.6723 | 3.564 | 3.4401 | 3.2464 | 3.0496 | 2.8492 | 2.5059 | 2.1676 | 1.9887 | 1.8263 | 1.4893 | 1.15 | 0.64035 | 0.35904 | 4.6261 | 4.5805 | 4.5224 | 4.4416 | 4.3572 | 4.2706 | 4.0507 | 3.859 | 3.7379 | 3.6196 | 3.3876 | 3.1355 | 2.7792 | 2.4124 | 4.0744 | 3.9845 | 3.877 | 3.7158 | 3.5454 | 3.3732 | 3.0674 | 2.7622 | 2.5948 | 2.4407 | 2.1227 | 1.7942 | 1.3437 | 1.0824
| INVERBERVIE | CT |  |  |  | 3.7691 | 3.7071 | 3.6376 | 3.4356 | 3.225 | 3.001 | 2.6669 | 2.3573 | 2.1557 | 1.9651 | 1.5848 | 1.15 | 0.64035 | 0.35904 | 4.6587 | 4.6278 | 4.5885 | 4.4927 | 4.3898 | 4.2706 | 4.0507 | 3.8624 | 3.7379 | 3.6196 | 3.3876 | 3.1355 | 2.7792 | 2.4124 | 4.1506 | 4.0977 | 4.035 | 3.8621 | 3.6794 | 3.4812 | 3.1769 | 2.9003 | 2.7148 | 2.5353 | 2.1793 | 1.7942 | 1.3437 | 1.0824
| INVERBERVIE | LW |  |  |  | 3.6723 | 3.564 | 3.4401 | 3.2464 | 3.0496 | 2.8492 | 2.5059 | 2.1676 | 1.9887 | 1.8263 | 1.4893 | 1.2188 | 0.87093 | 0.62337 | 4.6261 | 4.5805 | 4.5224 | 4.4416 | 4.3572 | 4.2731 | 4.0657 | 3.859 | 3.749 | 3.6528 | 3.4526 | 3.3682 | 3.1418 | 2.9098 | 4.0744 | 3.9845 | 3.877 | 3.7158 | 3.5454 | 3.3732 | 3.0674 | 2.7622 | 2.5948 | 2.4407 | 2.1227 | 1.9042 | 1.5715 | 1.3035
| INVERBERVIE | ST |  |  |  | 3.8169 | 3.7915 | 3.7574 | 3.6873 | 3.6221 | 3.5596 | 3.3599 | 3.1863 | 3.07 | 2.9795 | 2.7856 | 2.3915 | 1.9523 | 1.45 | 4.6757 | 4.6611 | 4.6416 | 4.5873 | 4.539 | 4.4948 | 4.3185 | 4.1772 | 4.0766 | 4.0057 | 3.852 | 3.5506 | 3.1848 | 2.7195 | 4.1871 | 4.1646 | 4.1346 | 4.0648 | 4.0008 | 3.9407 | 3.7519 | 3.5929 | 3.4759 | 3.3852 | 3.1873 | 2.7914 | 2.3944 | 1.9553
| INVERBERVIE | FS |  |  |  | 3.8287 | 3.8086 | 3.7819 | 3.7279 | 3.6746 | 3.6186 | 3.4967 | 3.355 | 3.2482 | 3.1566 | 2.9619 | 2.4641 | 1.9986 | 1.6404 | 4.68 | 4.6673 | 4.6506 | 4.6191 | 4.586 | 4.5502 | 4.455 | 4.3439 | 4.2663 | 4.1995 | 4.0571 | 3.7186 | 3.2613 | 2.7046 | 4.1966 | 4.1787 | 4.1552 | 4.1072 | 4.0587 | 4.0075 | 3.899 | 3.7721 | 3.6745 | 3.5891 | 3.4067 | 2.9638 | 2.5432 | 2.2433
GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0.22377 | 0.21692 | 0.21304 | 0.20588 | 0.19829 | 0.19164 | 0.18019 | 0.17414 | 0.17283 | 0.16577 | 0.15772 | 0.14655 | 0.144 | 0.1387 | 0.25179 | 0.24885 | 0.24653 | 0.24316 | 0.23948 | 0.23534 | 0.23023 | 0.22679 | 0.22442 | 0.22025 | 0.21159 | 0.205 | 0.20044 | 0.19514 | 0.23563 | 0.22952 | 0.22588 | 0.21941 | 0.21252 | 0.20633 | 0.19608 | 0.19032 | 0.18809 | 0.18162 | 0.17121 | 0.16074 | 0.15848 | 0.15373
| INVERBROOM | CT |  |  |  | 0.22577 | 0.22126 | 0.2194 | 0.20929 | 0.20074 | 0.19164 | 0.18019 | 0.17462 | 0.17283 | 0.16577 | 0.15817 | 0.15101 | 0.144 | 0.1387 | 0.25254 | 0.25047 | 0.24904 | 0.24408 | 0.23955 | 0.23534 | 0.23023 | 0.22726 | 0.22508 | 0.22025 | 0.21262 | 0.20527 | 0.20044 | 0.19514 | 0.23578 | 0.23337 | 0.23155 | 0.22237 | 0.21452 | 0.20633 | 0.19608 | 0.19097 | 0.18902 | 0.18162 | 0.17235 | 0.16476 | 0.15848 | 0.15373
| INVERBROOM | LW |  |  |  | 0.22377 | 0.21692 | 0.21304 | 0.20588 | 0.19829 | 0.19453 | 0.1854 | 0.17414 | 0.17302 | 0.16818 | 0.15772 | 0.14655 | 0.14516 | 0.14333 | 0.25179 | 0.24885 | 0.24653 | 0.24316 | 0.23948 | 0.2374 | 0.23261 | 0.22679 | 0.22442 | 0.22051 | 0.21159 | 0.205 | 0.20424 | 0.20353 | 0.23563 | 0.22952 | 0.22588 | 0.21941 | 0.21252 | 0.20904 | 0.20064 | 0.19032 | 0.18809 | 0.18255 | 0.17121 | 0.16074 | 0.1595 | 0.15792
| INVERBROOM | ST |  |  |  | 0.2276 | 0.22687 | 0.22445 | 0.22335 | 0.21715 | 0.21566 | 0.21573 | 0.21212 | 0.20807 | 0.20328 | 0.19344 | 0.17243 | 0.1675 | 0.16011 | 0.25321 | 0.25271 | 0.2515 | 0.2507 | 0.24788 | 0.24675 | 0.24605 | 0.24386 | 0.24133 | 0.23829 | 0.23159 | 0.21442 | 0.20964 | 0.20399 | 0.23582 | 0.23567 | 0.23546 | 0.23509 | 0.22953 | 0.22808 | 0.22765 | 0.22414 | 0.22012 | 0.21524 | 0.2051 | 0.18389 | 0.17923 | 0.17276
| INVERBROOM | FS |  |  |  | 0.22764 | 0.2273 | 0.2265 | 0.22371 | 0.22103 | 0.21799 | 0.21695 | 0.21168 | 0.21026 | 0.20665 | 0.19995 | 0.17478 | 0.15568 | 0.15647 | 0.25323 | 0.25289 | 0.2523 | 0.25094 | 0.24953 | 0.24796 | 0.24703 | 0.24445 | 0.24318 | 0.24099 | 0.23644 | 0.21974 | 0.20472 | 0.2009 | 0.23583 | 0.23573 | 0.23556 | 0.23532 | 0.233 | 0.23023 | 0.22911 | 0.22438 | 0.22268 | 0.21918 | 0.21224 | 0.18721 | 0.16885 | 0.16955
FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | NO | 0.63243 | 0.61792 | 0.60477 | 0.58288 | 0.54958 | 0.50698 | 0.45991 | 0.4292 | 0.40649 | 0.3828 | 0.337 | 0.33537 | 0.2581 | 0.17001 | 0.76156 | 0.75356 | 0.74628 | 0.729 | 0.70711 | 0.66888 | 0.62755 | 0.60689 | 0.58502 | 0.56166 | 0.51739 | 0.46652 | 0.36336 | 0.25862 | 0.65458 | 0.64123 | 0.6291 | 0.60512 | 0.5752 | 0.52899 | 0.47829 | 0.44823 | 0.42341 | 0.39744 | 0.34627 | 0.32441 | 0.2189 | 0.11336
| INVERGARRY | CT |  |  |  | 0.63775 | 0.6289 | 0.61206 | 0.58288 | 0.54958 | 0.50698 | 0.45991 | 0.4292 | 0.40649 | 0.3828 | 0.337 | 0.33537 | 0.2581 | 0.19876 | 0.76336 | 0.75727 | 0.74702 | 0.729 | 0.70711 | 0.66888 | 0.62755 | 0.60689 | 0.58502 | 0.56166 | 0.51739 | 0.48631 | 0.4114 | 0.337 | 0.65793 | 0.64696 | 0.63015 | 0.60512 | 0.5752 | 0.52899 | 0.47829 | 0.44823 | 0.42341 | 0.39744 | 0.34627 | 0.32622 | 0.24145 | 0.16956
| INVERGARRY | LW |  |  |  | 0.63243 | 0.61792 | 0.60477 | 0.58648 | 0.57065 | 0.55188 | 0.5287 | 0.50671 | 0.48413 | 0.4631 | 0.42125 | 0.43741 | 0.33398 | 0.19769 | 0.76156 | 0.75356 | 0.74628 | 0.73738 | 0.7289 | 0.71952 | 0.70661 | 0.69327 | 0.6753 | 0.65706 | 0.61747 | 0.6255 | 0.50765 | 0.34108 | 0.65458 | 0.64123 | 0.6291 | 0.61252 | 0.59798 | 0.58092 | 0.5595 | 0.53891 | 0.5161 | 0.4944 | 0.44622 | 0.45765 | 0.33379 | 0.16528
| INVERGARRY | ST |  |  |  | 0.64628 | 0.64067 | 0.64006 | 0.61235 | 0.59232 | 0.57392 | 0.53569 | 0.51704 | 0.48535 | 0.46445 | 0.41432 | 0.34637 | 0.25817 | 0.17001 | 0.76783 | 0.76482 | 0.76371 | 0.73528 | 0.71483 | 0.69864 | 0.65614 | 0.63926 | 0.60454 | 0.58574 | 0.54153 | 0.46652 | 0.36336 | 0.25862 | 0.66292 | 0.66065 | 0.65909 | 0.6294 | 0.60661 | 0.58684 | 0.54173 | 0.52167 | 0.48475 | 0.46214 | 0.40278 | 0.32441 | 0.2189 | 0.11336
| INVERGARRY | FS |  |  |  | 0.6489 | 0.64739 | 0.64424 | 0.63419 | 0.62067 | 0.61325 | 0.60126 | 0.58966 | 0.57355 | 0.55667 | 0.52515 | 0.4747 | 0.43266 | 0.41444 | 0.76909 | 0.7679 | 0.76602 | 0.75798 | 0.74843 | 0.74043 | 0.7305 | 0.72101 | 0.70592 | 0.69247 | 0.66525 | 0.63336 | 0.59785 | 0.57602 | 0.66401 | 0.66288 | 0.66185 | 0.65457 | 0.641 | 0.63251 | 0.61996 | 0.60793 | 0.59032 | 0.57292 | 0.53959 | 0.48842 | 0.44468 | 0.42602
ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | NO | 8.6128 | -20.7426 | -21.123 | -22.7107 | -24.6103 | -27.0647 | -29.2724 | -31.0107 | -31.8612 | -32.7698 | -34.4628 | -35.3904 | -36.6164 | -37.4658 | 7.5513 | -28.78 | -28.9661 | -30.4143 | -32.1789 | -34.7507 | -37.0406 | -38.6665 | -39.3954 | -40.2444 | -41.8417 | -42.8376 | -43.944 | -44.9085 | 13.8 | -21.9143 | -21.9143 | -22.7447 | -23.6717 | -25.5435 | -27.5255 | -28.6627 | -28.9633 | -29.275 | -29.8202 | -31.3385 | -32.2539 | -33.1769
| INVERGORDON | CT |  |  |  | 8.8139 | 8.1494 | 7.8193 | 6.8162 | -23.0009 | -24.643 | -26.001 | -26.9311 | -27.7177 | -28.5468 | -30.0715 | -30.8106 | -32.038 | -32.715 | 7.6243 | 7.0509 | 6.8312 | 6.1508 | -30.5489 | -32.1627 | -33.4263 | -34.1008 | -34.6973 | -35.3193 | -36.5462 | -37.1879 | -38.0668 | -38.8187 | 13.8 | 13.8 | 13.8 | 13.6957 | -22.2037 | -23.0939 | -24.0431 | -24.2838 | -24.4298 | -24.5763 | -24.8423 | -25.5817 | -25.992 | -26.3584
| INVERGORDON | LW |  |  |  | 8.6128 | -20.7426 | -21.123 | -22.7107 | -24.6103 | -27.0647 | -29.2724 | -31.0107 | -31.8612 | -32.7698 | -34.4628 | -35.3904 | -36.6164 | -37.4658 | 7.5513 | -28.78 | -28.9661 | -30.4143 | -32.1789 | -34.7507 | -37.0406 | -38.6665 | -39.3954 | -40.2444 | -41.8417 | -42.8376 | -43.944 | -44.9085 | 13.8 | -21.9143 | -21.9143 | -22.7447 | -23.6717 | -25.5435 | -27.5255 | -28.6627 | -28.9633 | -29.275 | -29.8202 | -31.3385 | -32.2539 | -33.1769
| INVERGORDON | ST |  |  |  | 8.867 | 8.2649 | 8.0414 | 6.7944 | 5.6081 | 4.6646 | -25.1672 | -25.8561 | -26.5273 | -27.1007 | -28.2871 | -28.9496 | -30.0948 | -31.2832 | 7.6313 | 7.088 | 6.9388 | 5.6455 | 4.4558 | 3.4968 | -33.6164 | -34.2907 | -35.0089 | -35.5971 | -36.8898 | -37.2679 | -38.2941 | -39.3006 | 13.8 | 13.8 | 13.8 | 12.9993 | 12.4579 | 12.1003 | -24.8432 | -25.1851 | -25.5063 | -25.6202 | -25.8707 | -26.5931 | -27.2008 | -27.7303
| INVERGORDON | FS |  |  |  | 9.097 | 8.6328 | 8.4466 | 7.8158 | 7.0691 | 6.3845 | 5.9116 | 5.3778 | 4.8872 | 4.3657 | 3.3798 | 2.5211 | 1.5743 | 0.88327 | 7.856 | 7.4364 | 7.3096 | 6.7454 | 6.0661 | 5.406 | 4.9917 | 4.5216 | 4.1023 | 3.6305 | 2.679 | 2.1277 | 1.125 | 0.31298 | 13.8 | 13.8 | 13.8 | 13.6363 | 13.4726 | 13.2817 | 13.0909 | 12.9271 | 12.8109 | 12.7321 | 12.5744 | 12.4788 | 12.4332 | 12.3741
FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 5.6025 | 5.3531 | 5.0871 | 4.7844 | 4.4747 | 4.0962 | 3.6763 | 3.2472 | 3.0785 | 2.9104 | 2.4303 | 3.1973 | 2.7667 | 2.5626 | 6.7416 | 6.6076 | 6.4511 | 6.2947 | 6.0636 | 5.8374 | 5.598 | 5.3567 | 5.1691 | 4.9508 | 4.4564 | 4.9586 | 4.5831 | 4.0445 | 4.3496 | 4.2112 | 4.0539 | 3.8844 | 3.6485 | 3.4156 | 3.1674 | 2.751 | 2.5383 | 2.2859 | 1.6471 | 2.4131 | 2.0087 | 1.8083
| INVERLOCHY | CT |  |  |  | 5.6871 | 5.5266 | 5.3069 | 4.9103 | 4.4988 | 4.0962 | 3.6763 | 3.2472 | 3.0785 | 2.9104 | 2.4676 | 3.252 | 2.7667 | 2.5626 | 6.768 | 6.6728 | 6.5326 | 6.3134 | 6.0636 | 5.8374 | 5.598 | 5.3567 | 5.1691 | 4.9508 | 4.5002 | 4.9586 | 4.5831 | 4.1949 | 4.3854 | 4.267 | 4.1114 | 3.8844 | 3.6485 | 3.4156 | 3.1674 | 2.751 | 2.5383 | 2.2936 | 1.7481 | 2.446 | 2.0087 | 1.8083
| INVERLOCHY | LW |  |  |  | 5.6025 | 5.3531 | 5.0871 | 4.7844 | 4.4747 | 4.1667 | 3.8054 | 3.4122 | 3.2245 | 2.972 | 2.4303 | 3.1973 | 2.8884 | 2.711 | 6.7416 | 6.6076 | 6.4511 | 6.2947 | 6.1181 | 5.9488 | 5.7091 | 5.4361 | 5.2128 | 4.9639 | 4.4564 | 5.1102 | 4.9353 | 4.8023 | 4.3496 | 4.2112 | 4.0539 | 3.8923 | 3.7211 | 3.5494 | 3.2867 | 2.866 | 2.6014 | 2.2859 | 1.6471 | 2.4131 | 2.1225 | 1.9447
| INVERLOCHY | ST |  |  |  | 5.833 | 5.7416 | 5.6596 | 5.5563 | 5.4406 | 5.3189 | 5.1643 | 5.0056 | 4.8115 | 4.6031 | 4.1219 | 4.1759 | 3.8337 | 3.5507 | 6.8442 | 6.7919 | 6.7278 | 6.6576 | 6.5783 | 6.4861 | 6.3577 | 6.2267 | 6.062 | 5.8811 | 5.4486 | 5.3102 | 4.9515 | 4.5389 | 4.5004 | 4.4357 | 4.377 | 4.3136 | 4.2413 | 4.1621 | 4.0501 | 3.9363 | 3.7873 | 3.6237 | 2.9957 | 3.2369 | 2.9044 | 2.6443
| INVERLOCHY | FS |  |  |  | 5.8645 | 5.7916 | 5.729 | 5.6435 | 5.5365 | 5.4242 | 5.3074 | 5.1848 | 5.0424 | 4.8916 | 4.5614 | 4.1288 | 3.5813 | 3.3497 | 6.8601 | 6.8232 | 6.7711 | 6.7106 | 6.6447 | 6.5727 | 6.4862 | 6.3908 | 6.2746 | 6.1472 | 5.8529 | 5.4395 | 4.7342 | 4.0445 | 4.523 | 4.4714 | 4.4264 | 4.3759 | 4.3218 | 4.2617 | 4.196 | 4.1242 | 4.0353 | 3.9382 | 3.7138 | 3.3458 | 2.7338 | 2.5346
PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | NO | 6.8506 | 6.8493 | 6.837 | 6.8072 | 6.7568 | 6.6879 | 6.6179 | 6.5687 | 6.4965 | 6.4138 | 6.2426 | 6.212 | 5.803 | 5.0953 | 6.3339 | 6.333 | 6.3215 | 6.2985 | 6.271 | 6.2134 | 6.153 | 6.122 | 6.0443 | 5.9776 | 5.8253 | 5.658 | 5.1796 | 4.3308 | 5.1397 | 5.1384 | 5.1363 | 5.1047 | 5.0805 | 5.0527 | 4.9763 | 4.9271 | 4.8466 | 4.7561 | 4.5851 | 4.4947 | 3.992 | 3.1092
| INVERNEIL | CT |  |  |  | 6.8509 | 6.8496 | 6.8481 | 6.811 | 6.7568 | 6.6879 | 6.6179 | 6.5687 | 6.4965 | 6.4138 | 6.2578 | 6.212 | 5.945 | 5.6536 | 6.334 | 6.3331 | 6.3316 | 6.3042 | 6.271 | 6.2134 | 6.153 | 6.122 | 6.053 | 5.9776 | 5.8253 | 5.6996 | 5.3743 | 4.9933 | 5.1399 | 5.1387 | 5.1372 | 5.1297 | 5.1184 | 5.0527 | 4.9763 | 4.9271 | 4.8466 | 4.7561 | 4.5851 | 4.4947 | 4.1703 | 3.8101
| INVERNEIL | LW |  |  |  | 6.8506 | 6.8493 | 6.837 | 6.8072 | 6.7719 | 6.7354 | 6.6822 | 6.6196 | 6.5301 | 6.4337 | 6.2426 | 6.3072 | 5.803 | 5.0953 | 6.3339 | 6.333 | 6.3215 | 6.3059 | 6.2872 | 6.2688 | 6.2392 | 6.2038 | 6.1284 | 6.0366 | 5.8604 | 5.8309 | 5.2113 | 4.3308 | 5.1397 | 5.1384 | 5.1363 | 5.1344 | 5.132 | 5.1111 | 5.0594 | 4.9986 | 4.9016 | 4.7974 | 4.5936 | 4.6174 | 3.992 | 3.1092
| INVERNEIL | ST |  |  |  | 6.8516 | 6.8513 | 6.8509 | 6.8227 | 6.8033 | 6.7899 | 6.7349 | 6.7043 | 6.5983 | 6.5391 | 6.4016 | 6.2464 | 5.8606 | 5.4477 | 6.3343 | 6.334 | 6.3336 | 6.2985 | 6.2737 | 6.2491 | 6.1838 | 6.156 | 6.0443 | 5.9908 | 5.8695 | 5.658 | 5.1796 | 4.6578 | 5.1405 | 5.1402 | 5.1398 | 5.1047 | 5.0805 | 5.0641 | 5.0095 | 4.9934 | 4.8968 | 4.8542 | 4.703 | 4.5052 | 4.0276 | 3.515
| INVERNEIL | FS |  |  |  | 6.8516 | 6.8515 | 6.851 | 6.8451 | 6.8386 | 6.8313 | 6.8175 | 6.794 | 6.7481 | 6.7083 | 6.6169 | 6.5721 | 6.4749 | 6.4202 | 6.3343 | 6.3341 | 6.3337 | 6.3263 | 6.3186 | 6.304 | 6.2859 | 6.2681 | 6.2223 | 6.1858 | 6.1067 | 6.0645 | 5.9779 | 5.8703 | 5.1405 | 5.1404 | 5.14 | 5.1326 | 5.1247 | 5.1157 | 5.1065 | 5.0982 | 5.0629 | 5.0383 | 4.9601 | 4.912 | 4.8111 | 4.7462
INVERNESS | INVERNESS 11 kV | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 5.7188 | 5.3337 | 4.8348 | 4.2025 | 3.5176 | 2.8027 | 2.0133 | 1.1565 | 0.38123 | -0.31346 | -1.467 | -2.1149 | -3.4662 | -4.3109 | 7.781 | 7.6471 | 7.4539 | 7.2561 | 7.0638 | 6.817 | 6.492 | 6.1303 | 5.7454 | 5.3709 | 4.6998 | 4.861 | 3.7856 | 2.4964 | 6.7915 | 6.4763 | 6.0469 | 5.5414 | 4.9718 | 4.3764 | 3.6806 | 2.9163 | 2.1874 | 1.5098 | 0.34531 | -0.147 | -1.3116 | -2.0971
| INVERNESS 11 kV | CT |  |  |  | 5.8717 | 5.5991 | 5.2167 | 4.6286 | 3.9992 | 3.3447 | 2.6641 | 1.9224 | 1.1207 | 0.35314 | -0.95673 | -2.1149 | -3.4662 | -4.3109 | 7.7912 | 7.6551 | 7.462 | 7.2561 | 7.0638 | 6.8447 | 6.5606 | 6.2605 | 5.9005 | 5.5855 | 4.9845 | 4.861 | 3.7856 | 2.4964 | 6.9016 | 6.6726 | 6.341 | 5.8399 | 5.298 | 4.7564 | 4.1753 | 3.5498 | 2.8356 | 2.1148 | 0.85863 | -0.147 | -1.3116 | -2.0971
| INVERNESS 11 kV | LW |  |  |  | 5.7188 | 5.3337 | 4.8348 | 4.2025 | 3.5176 | 2.8027 | 2.0133 | 1.1565 | 0.38123 | -0.31346 | -1.467 | -1.9697 | -3.0658 | -3.8903 | 7.781 | 7.6471 | 7.4539 | 7.2921 | 7.0821 | 6.817 | 6.492 | 6.1303 | 5.7454 | 5.3709 | 4.6998 | 5.2948 | 4.5377 | 3.7209 | 6.7915 | 6.4763 | 6.0469 | 5.5414 | 4.9718 | 4.3764 | 3.6806 | 2.9163 | 2.1874 | 1.5098 | 0.34531 | -0.040633 | -1.0864 | -1.9975
| INVERNESS 11 kV | ST |  |  |  | 5.9255 | 5.6972 | 5.3917 | 5.1296 | 4.8516 | 4.5551 | 4.2422 | 3.9192 | 3.522 | 3.1735 | 2.5457 | 1.7653 | 0.66688 | -0.72885 | 7.8 | 7.7075 | 7.5876 | 7.4696 | 7.3427 | 7.2031 | 7.0381 | 6.8646 | 6.6094 | 6.3849 | 5.9085 | 6.1573 | 5.0415 | 3.5424 | 6.9382 | 6.7508 | 6.4996 | 6.2731 | 6.0287 | 5.768 | 5.4825 | 5.1851 | 4.7973 | 4.4518 | 3.7848 | 2.8165 | 1.8153 | 0.64168
| INVERNESS 11 kV | FS |  |  |  | 5.9667 | 5.7725 | 5.5174 | 5.2709 | 5.0157 | 4.7421 | 4.4696 | 4.1845 | 3.8529 | 3.5452 | 3.0065 | 2.1526 | 1.1487 | 0.25412 | 7.8148 | 7.7298 | 7.6223 | 7.5207 | 7.4119 | 7.2919 | 7.1664 | 7.0308 | 6.8642 | 6.7082 | 6.3995 | 6.4436 | 5.0132 | 3.1083 | 6.9711 | 6.8099 | 6.5983 | 6.3911 | 6.1719 | 5.9372 | 5.6985 | 5.4451 | 5.1434 | 4.8585 | 4.3306 | 3.4318 | 2.4346 | 1.7297
KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | NO | 15.5197 | 14.996 | 14.3112 | 13.3254 | 12.28 | 11.2425 | 9.942 | 8.4358 | 7.202 | 5.9456 | 3.2763 | 4.3618 | 2.0224 | 0.62159 | 19.2802 | 19.0099 | 18.6013 | 18.1148 | 17.5809 | 16.9907 | 16.3186 | 15.3954 | 14.5602 | 13.6923 | 11.938 | 12.7165 | 11.1516 | 9.495 | 18.5893 | 18.1138 | 17.4662 | 16.5811 | 15.6342 | 14.7027 | 13.4884 | 12.0654 | 10.8512 | 9.6011 | 7.0712 | 8.2481 | 6.2189 | 4.9738
| INVERURIE | CT |  |  |  | 15.9074 | 15.5737 | 15.1125 | 14.0461 | 12.9327 | 11.8758 | 10.7445 | 9.572 | 8.4208 | 7.2166 | 4.7636 | 4.3618 | 2.0224 | 0.62159 | 19.4092 | 19.1965 | 18.8774 | 18.2638 | 17.6079 | 16.9907 | 16.3186 | 15.6234 | 14.8839 | 14.0798 | 12.4678 | 12.7165 | 11.1516 | 9.495 | 18.5923 | 18.4252 | 18.1088 | 17.1624 | 16.117 | 15.1352 | 14.0813 | 13.0047 | 11.9062 | 10.7316 | 8.3861 | 8.2481 | 6.2189 | 4.9738
| INVERURIE | LW |  |  |  | 15.5197 | 14.996 | 14.3112 | 13.3254 | 12.28 | 11.2425 | 9.942 | 8.4358 | 7.202 | 5.9456 | 3.2763 | 4.4673 | 3.1183 | 2.2783 | 19.2802 | 19.0099 | 18.6013 | 18.1148 | 17.5809 | 17.0631 | 16.3223 | 15.3954 | 14.5602 | 13.6923 | 11.938 | 13.5021 | 12.7438 | 12.0756 | 18.5893 | 18.1138 | 17.4662 | 16.5811 | 15.6342 | 14.7027 | 13.4884 | 12.0654 | 10.8512 | 9.6011 | 7.0712 | 8.4554 | 7.2217 | 6.3711
| INVERURIE | ST |  |  |  | 16.0731 | 15.9146 | 15.714 | 15.3775 | 15.011 | 14.6154 | 14.1055 | 13.4959 | 12.8684 | 12.2134 | 10.5933 | 9.844 | 7.9229 | 5.6797 | 19.4762 | 19.3711 | 19.2345 | 18.9806 | 18.7074 | 18.4159 | 17.9992 | 17.5174 | 16.9946 | 16.4615 | 15.1851 | 14.6925 | 13.123 | 11.1068 | 18.6153 | 18.544 | 18.4486 | 18.2504 | 18.0166 | 17.6398 | 17.1211 | 16.5219 | 15.8813 | 15.2149 | 13.5819 | 12.9789 | 11.2062 | 9.1733
| INVERURIE | FS |  |  |  | 16.1393 | 16.0188 | 15.8694 | 15.6103 | 15.3124 | 14.9924 | 14.6391 | 14.1821 | 13.672 | 13.1454 | 11.9779 | 10.4598 | 7.9506 | 6.1683 | 19.5035 | 19.4173 | 19.3073 | 19.1351 | 18.9313 | 18.7066 | 18.4503 | 18.0983 | 17.719 | 17.3204 | 16.4019 | 15.3295 | 12.9169 | 10.17 | 18.6276 | 18.5731 | 18.5009 | 18.3944 | 18.2653 | 18.03 | 17.6911 | 17.2511 | 16.7586 | 16.2456 | 15.0971 | 13.741 | 11.4356 | 9.8731
DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | NO | 2.6022 | 2.5556 | 2.4942 | 2.4235 | 2.3476 | 2.2762 | 2.1945 | 2.1002 | 2.0418 | 1.9783 | 1.8482 | 1.9305 | 1.8696 | 1.8342 | 2.9246 | 2.9012 | 2.8669 | 2.8308 | 2.7883 | 2.7455 | 2.702 | 2.6455 | 2.5994 | 2.5493 | 2.4482 | 2.5187 | 2.4819 | 2.4546 | 2.8147 | 2.7734 | 2.7171 | 2.653 | 2.5837 | 2.5163 | 2.4418 | 2.3533 | 2.2952 | 2.2321 | 2.1032 | 2.1865 | 2.127 | 2.0918
| KAMES | CT |  |  |  | 2.6249 | 2.5926 | 2.5507 | 2.4548 | 2.359 | 2.2762 | 2.1945 | 2.1079 | 2.068 | 2.0118 | 1.9041 | 1.952 | 1.8696 | 1.8342 | 2.9335 | 2.916 | 2.891 | 2.8404 | 2.7883 | 2.7455 | 2.702 | 2.6562 | 2.624 | 2.5805 | 2.4959 | 2.5252 | 2.4819 | 2.4546 | 2.8199 | 2.806 | 2.7673 | 2.6797 | 2.5915 | 2.5163 | 2.4418 | 2.363 | 2.3233 | 2.2678 | 2.1611 | 2.2064 | 2.127 | 2.0918
| KAMES | LW |  |  |  | 2.6022 | 2.5556 | 2.4942 | 2.4235 | 2.3476 | 2.285 | 2.1981 | 2.1002 | 2.0418 | 1.9783 | 1.8482 | 1.9305 | 1.8874 | 1.872 | 2.9246 | 2.9012 | 2.8669 | 2.8308 | 2.7905 | 2.7564 | 2.7047 | 2.6455 | 2.5994 | 2.5493 | 2.4482 | 2.5187 | 2.4998 | 2.4941 | 2.8147 | 2.7734 | 2.7171 | 2.653 | 2.5837 | 2.5263 | 2.4451 | 2.3533 | 2.2952 | 2.2321 | 2.1032 | 2.1865 | 2.1453 | 2.13
| KAMES | ST |  |  |  | 2.6478 | 2.6313 | 2.6112 | 2.5871 | 2.5614 | 2.5378 | 2.5124 | 2.4801 | 2.4395 | 2.3973 | 2.2939 | 2.1729 | 2.1297 | 2.0882 | 2.9422 | 2.9329 | 2.9213 | 2.9074 | 2.8919 | 2.8765 | 2.859 | 2.8371 | 2.8101 | 2.7798 | 2.7061 | 2.6199 | 2.5868 | 2.5571 | 2.8281 | 2.8283 | 2.8225 | 2.8006 | 2.7767 | 2.7544 | 2.7301 | 2.6992 | 2.6606 | 2.6198 | 2.5197 | 2.4027 | 2.362 | 2.3255
| KAMES | FS |  |  |  | 2.656 | 2.6381 | 2.6231 | 2.598 | 2.5749 | 2.5484 | 2.5225 | 2.494 | 2.4631 | 2.4296 | 2.3554 | 2.1789 | 2.0317 | 1.9983 | 2.946 | 2.9363 | 2.9271 | 2.9135 | 2.9002 | 2.8855 | 2.87 | 2.8525 | 2.8328 | 2.8108 | 2.7604 | 2.6532 | 2.5431 | 2.5087 | 2.8284 | 2.8281 | 2.8283 | 2.8106 | 2.7895 | 2.765 | 2.7409 | 2.7142 | 2.6851 | 2.6532 | 2.5823 | 2.4177 | 2.276 | 2.2467
KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | NO | 6.1293 | 6.082 | 6.0048 | 5.4262 | 4.4167 | 3.5366 | 2.563 | 1.7071 | 1.2474 | 0.77958 | -0.38017 | -1.2118 | -2.2382 | -3.1001 | 8.4539 | 8.3601 | 8.2295 | 7.756 | 6.909 | 6.094 | 5.1861 | 4.4617 | 4.126 | 3.776 | 2.8924 | 2.3229 | 1.4196 | 0.4336 | 5.0082 | 4.9596 | 4.8237 | 4.3003 | 3.3429 | 2.4197 | 1.4143 | 0.58796 | 0.2006 | -0.19722 | -1.2175 | -1.4947 | -2.5673 | -3.5885
| KEITH | CT |  |  |  | 6.1321 | 6.0834 | 6.0048 | 5.8639 | 5.1403 | 4.4504 | 3.725 | 3.1924 | 2.7176 | 2.2107 | 0.9939 | -0.23776 | -1.4189 | -2.117 | 8.5119 | 8.4466 | 8.3484 | 8.0897 | 7.453 | 6.8346 | 6.1785 | 5.8012 | 5.4826 | 5.1302 | 4.2468 | 3.4103 | 2.5519 | 1.7492 | 5.0119 | 4.9596 | 4.8698 | 4.6471 | 3.9405 | 3.2684 | 2.5558 | 2.0966 | 1.6989 | 1.3153 | 0.31263 | -0.30852 | -1.384 | -2.0664
| KEITH | LW |  |  |  | 6.1293 | 6.082 | 6.0095 | 5.4262 | 4.4167 | 3.5366 | 2.563 | 1.7071 | 1.2474 | 0.77958 | -0.38017 | -1.2118 | -2.2382 | -3.1001 | 8.4539 | 8.3601 | 8.2295 | 7.756 | 6.909 | 6.094 | 5.1861 | 4.4617 | 4.126 | 3.776 | 2.8924 | 2.3229 | 1.4196 | 0.4336 | 5.0082 | 4.9605 | 4.8237 | 4.3003 | 3.3429 | 2.4197 | 1.4143 | 0.58796 | 0.2006 | -0.19722 | -1.2175 | -1.4947 | -2.5673 | -3.5885
| KEITH | ST |  |  |  | 6.1354 | 6.1062 | 6.0703 | 5.6985 | 5.0423 | 4.8603 | 4.3086 | 4.0199 | 3.7717 | 3.6263 | 2.9769 | 1.9052 | 0.68195 | -0.62 | 8.5265 | 8.4853 | 8.4342 | 7.9597 | 7.2752 | 7.0331 | 6.3245 | 5.981 | 5.6526 | 5.4521 | 4.7889 | 3.8108 | 2.7788 | 1.6567 | 5.0167 | 4.9898 | 4.9568 | 4.504 | 3.7843 | 3.5594 | 2.8572 | 2.5 | 2.1679 | 1.9535 | 1.206 | 1.1267 | 0.084326 | -1.1078
| KEITH | FS |  |  |  | 6.1402 | 6.1138 | 6.0822 | 5.9785 | 5.5951 | 5.4704 | 5.3412 | 5.1479 | 5.0286 | 4.9128 | 4.4034 | 3.4327 | 2.3697 | 1.5828 | 8.5357 | 8.5013 | 8.4585 | 8.3193 | 7.932 | 7.7646 | 7.5882 | 7.3562 | 7.1688 | 6.9892 | 6.515 | 5.7976 | 4.862 | 3.9226 | 5.0213 | 4.9979 | 4.9698 | 4.8522 | 4.4474 | 4.2997 | 4.1467 | 3.9188 | 3.7551 | 3.5828 | 3.0746 | 2.9068 | 2.2682 | 1.6285
KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | NO | 10.2996 | 10.2808 | 10.2461 | 10.0486 | 9.8081 | 9.574 | 9.0901 | 8.6837 | 8.3163 | 8.0459 | 7.4899 | 7.1144 | 6.5392 | 6.2117 | 11.1684 | 11.1471 | 11.116 | 11.069 | 10.9529 | 10.8428 | 10.5151 | 10.2558 | 10.003 | 9.8358 | 9.4917 | 9.1828 | 8.7777 | 8.3579 | 10.6019 | 10.5359 | 10.399 | 10.2009 | 9.9892 | 9.7859 | 9.3491 | 8.9787 | 8.6326 | 8.3686 | 7.83 | 7.5 | 6.9968 | 6.6971
| KEMNAY | CT |  |  |  | 10.3013 | 10.2811 | 10.2511 | 10.2042 | 10.0021 | 9.7698 | 9.3403 | 9.0293 | 8.6605 | 8.3571 | 7.7574 | 7.1144 | 6.5392 | 6.2117 | 11.1693 | 11.1471 | 11.1162 | 11.069 | 10.9921 | 10.8621 | 10.5572 | 10.3551 | 10.1074 | 9.9153 | 9.541 | 9.1828 | 8.7777 | 8.3579 | 10.6129 | 10.5781 | 10.5314 | 10.3591 | 10.1338 | 9.9229 | 9.5355 | 9.2601 | 8.9212 | 8.6303 | 8.0595 | 7.5 | 6.9968 | 6.6971
| KEMNAY | LW |  |  |  | 10.2996 | 10.2808 | 10.2461 | 10.0486 | 9.8081 | 9.574 | 9.0901 | 8.6837 | 8.3163 | 8.0459 | 7.4899 | 7.1375 | 6.775 | 6.5491 | 11.1684 | 11.1499 | 11.116 | 11.0693 | 10.9529 | 10.8428 | 10.5151 | 10.2558 | 10.003 | 9.8358 | 9.4917 | 9.3756 | 9.1647 | 8.9796 | 10.6019 | 10.5359 | 10.399 | 10.2009 | 9.9892 | 9.7859 | 9.3491 | 8.9787 | 8.6326 | 8.3686 | 7.83 | 7.5542 | 7.2294 | 6.999
| KEMNAY | ST |  |  |  | 10.3031 | 10.2935 | 10.2798 | 10.2461 | 10.2124 | 10.179 | 9.9338 | 9.7896 | 9.6204 | 9.4808 | 9.1748 | 8.5253 | 7.9928 | 7.428 | 11.1718 | 11.163 | 11.1511 | 11.1156 | 11.082 | 11.0492 | 10.7909 | 10.6307 | 10.4551 | 10.3793 | 10.1823 | 9.7057 | 9.2842 | 8.7685 | 10.6187 | 10.6045 | 10.5862 | 10.5419 | 10.4977 | 10.4237 | 10.1471 | 9.9721 | 9.7542 | 9.6142 | 9.303 | 8.6523 | 8.1776 | 7.6952
| KEMNAY | FS |  |  |  | 10.3043 | 10.2964 | 10.285 | 10.2671 | 10.2456 | 10.2215 | 10.0844 | 9.9732 | 9.8531 | 9.7618 | 9.4828 | 8.7798 | 8.0528 | 7.6107 | 11.1729 | 11.1655 | 11.1556 | 11.1389 | 11.1193 | 11.0968 | 10.9561 | 10.834 | 10.7093 | 10.652 | 10.4629 | 9.947 | 9.262 | 8.5694 | 10.6214 | 10.6101 | 10.5951 | 10.5709 | 10.5427 | 10.5107 | 10.3466 | 10.208 | 10.0304 | 9.9069 | 9.6394 | 8.9765 | 8.2934 | 7.9335
TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0.38309 | 0.37311 | 0.36971 | 0.36204 | 0.3533 | 0.34694 | 0.33295 | 0.32655 | 0.31975 | 0.31393 | 0.29923 | 0.29614 | 0.29242 | 0.28883 | 0.43392 | 0.42931 | 0.42672 | 0.4228 | 0.41708 | 0.41346 | 0.40696 | 0.40264 | 0.39719 | 0.39161 | 0.37811 | 0.37627 | 0.37173 | 0.36617 | 0.41269 | 0.40317 | 0.39984 | 0.39283 | 0.38461 | 0.37872 | 0.36614 | 0.35987 | 0.35314 | 0.34778 | 0.33054 | 0.32782 | 0.32386 | 0.32058
| KENMORE | CT |  |  |  | 0.38348 | 0.37736 | 0.37308 | 0.36494 | 0.3533 | 0.34694 | 0.33295 | 0.32784 | 0.32102 | 0.31393 | 0.30235 | 0.29905 | 0.29411 | 0.28883 | 0.43413 | 0.43087 | 0.42814 | 0.42329 | 0.41708 | 0.41346 | 0.40696 | 0.4037 | 0.39894 | 0.39323 | 0.38146 | 0.37627 | 0.37173 | 0.36617 | 0.41306 | 0.40696 | 0.4029 | 0.3953 | 0.38461 | 0.37872 | 0.36614 | 0.36133 | 0.35478 | 0.34778 | 0.33454 | 0.33093 | 0.32552 | 0.32058
| KENMORE | LW |  |  |  | 0.38309 | 0.37311 | 0.36971 | 0.36204 | 0.35346 | 0.34881 | 0.33829 | 0.32655 | 0.31975 | 0.31576 | 0.29923 | 0.29614 | 0.29242 | 0.29206 | 0.43392 | 0.42931 | 0.42672 | 0.4228 | 0.41832 | 0.41553 | 0.40951 | 0.40264 | 0.39719 | 0.39161 | 0.37811 | 0.3765 | 0.37473 | 0.37462 | 0.41269 | 0.40317 | 0.39984 | 0.39283 | 0.38496 | 0.38061 | 0.37083 | 0.35987 | 0.35314 | 0.348 | 0.33054 | 0.32782 | 0.32386 | 0.32355
| KENMORE | ST |  |  |  | 0.38348 | 0.38265 | 0.38167 | 0.37883 | 0.37251 | 0.37038 | 0.36814 | 0.36654 | 0.35837 | 0.35199 | 0.33991 | 0.3151 | 0.30646 | 0.3033 | 0.43415 | 0.43347 | 0.4327 | 0.43089 | 0.42763 | 0.42598 | 0.42408 | 0.42234 | 0.41762 | 0.41324 | 0.40346 | 0.38416 | 0.37722 | 0.37267 | 0.41307 | 0.41225 | 0.41129 | 0.40845 | 0.40236 | 0.40029 | 0.39807 | 0.39631 | 0.38879 | 0.38258 | 0.37025 | 0.34638 | 0.33767 | 0.33438
| KENMORE | FS |  |  |  | 0.38355 | 0.3842 | 0.3834 | 0.37645 | 0.37669 | 0.37326 | 0.37168 | 0.36762 | 0.36206 | 0.35723 | 0.34868 | 0.32249 | 0.3001 | 0.29841 | 0.43419 | 0.43426 | 0.43359 | 0.43006 | 0.42956 | 0.42762 | 0.42625 | 0.42383 | 0.42069 | 0.41765 | 0.41139 | 0.39232 | 0.37414 | 0.36894 | 0.41313 | 0.41363 | 0.41284 | 0.40606 | 0.40618 | 0.40297 | 0.40141 | 0.39764 | 0.3925 | 0.38797 | 0.37975 | 0.35352 | 0.33183 | 0.33001
STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | NO | 4.848 | 4.6693 | 4.4511 | 4.067 | 3.6564 | 3.1869 | 2.6562 | 2.1536 | 1.8409 | 1.5071 | 0.85194 | 0.20033 | -0.71674 | -1.4622 | 6.5663 | 6.5101 | 6.4339 | 6.2808 | 6.113 | 5.8792 | 5.6106 | 5.3865 | 5.2468 | 5.0953 | 4.7299 | 4.5267 | 3.9923 | 3.4327 | 6.3056 | 6.1472 | 5.9522 | 5.5985 | 5.2195 | 4.7729 | 4.2656 | 3.7963 | 3.5085 | 3.2015 | 2.6002 | 2.0683 | 1.2355 | 0.5305
| KEPCULLOCH | CT |  |  |  | 4.9878 | 4.8812 | 4.7449 | 4.3643 | 3.9574 | 3.493 | 3.0075 | 2.593 | 2.299 | 1.9689 | 1.3152 | 0.44984 | -0.69321 | -1.4622 | 6.5987 | 6.5529 | 6.4948 | 6.3621 | 6.2279 | 6.0015 | 5.7619 | 5.6106 | 5.4833 | 5.3601 | 5.0301 | 4.6033 | 3.9923 | 3.4327 | 6.4282 | 6.3329 | 6.211 | 5.8687 | 5.5004 | 5.0593 | 4.5973 | 4.2237 | 3.9539 | 3.6502 | 3.0497 | 2.2972 | 1.2908 | 0.60883
| KEPCULLOCH | LW |  |  |  | 4.848 | 4.6693 | 4.4511 | 4.067 | 3.6564 | 3.1869 | 2.6562 | 2.1536 | 1.8409 | 1.5071 | 0.85194 | 0.20033 | -0.71674 | -1.4569 | 6.5663 | 6.5101 | 6.4339 | 6.2808 | 6.113 | 5.8792 | 5.6106 | 5.3865 | 5.2468 | 5.0953 | 4.7299 | 4.5267 | 4.0113 | 3.4982 | 6.3056 | 6.1472 | 5.9522 | 5.5985 | 5.2195 | 4.7729 | 4.2656 | 3.7963 | 3.5085 | 3.2015 | 2.6002 | 2.0683 | 1.2355 | 0.5305
| KEPCULLOCH | ST |  |  |  | 5.0413 | 4.9746 | 4.8959 | 4.701 | 4.5208 | 4.3461 | 4.07 | 3.8789 | 3.6769 | 3.4807 | 3.0511 | 2.1358 | 1.2759 | 0.38153 | 6.6129 | 6.5899 | 6.5617 | 6.4199 | 6.3051 | 6.2065 | 5.9897 | 5.881 | 5.7581 | 5.6567 | 5.426 | 5.108 | 4.5342 | 3.9018 | 6.4752 | 6.4166 | 6.3481 | 6.1482 | 5.9709 | 5.8059 | 5.5183 | 5.3374 | 5.1432 | 4.9634 | 4.5662 | 3.741 | 2.9621 | 2.1559
| KEPCULLOCH | FS |  |  |  | 5.0756 | 5.0277 | 4.971 | 4.8507 | 4.7248 | 4.5818 | 4.4337 | 4.2869 | 4.114 | 3.9341 | 3.5583 | 2.5588 | 1.6519 | 0.95366 | 6.6217 | 6.6042 | 6.5827 | 6.5271 | 6.4678 | 6.3994 | 6.3273 | 6.2567 | 6.1796 | 6.1024 | 5.9369 | 5.661 | 5.0237 | 4.4211 | 6.5053 | 6.4632 | 6.414 | 6.3037 | 6.1885 | 6.058 | 5.9227 | 5.7884 | 5.6312 | 5.4697 | 5.1302 | 4.2593 | 3.4626 | 2.8713
TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838
| KERRERA | CT |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838
| KERRERA | LW |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838
| KERRERA | ST |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838
| KERRERA | FS |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.29605 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838 | 0.28838
GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 5.4186 | 5.3684 | 5.3032 | 5.2299 | 5.1525 | 5.0784 | 4.9844 | 4.8826 | 4.8177 | 4.7537 | 4.6263 | 4.5567 | 4.4818 | 4.4339 | 5.2076 | 5.1833 | 5.1482 | 5.1121 | 5.0679 | 5.025 | 4.9798 | 4.926 | 4.8778 | 4.8281 | 4.7203 | 4.6797 | 4.62 | 4.5708 | 5.0131 | 4.9677 | 4.9076 | 4.8409 | 4.7701 | 4.7006 | 4.6158 | 4.521 | 4.4541 | 4.3831 | 4.2429 | 4.1761 | 4.1101 | 4.067
| KERRY FALLS | CT |  |  |  | 5.449 | 5.4134 | 5.3702 | 5.2722 | 5.1665 | 5.0784 | 4.9854 | 4.8961 | 4.8507 | 4.7866 | 4.6637 | 4.5926 | 4.4818 | 4.4339 | 5.219 | 5.1998 | 5.1746 | 5.1232 | 5.0679 | 5.025 | 4.9798 | 4.9358 | 4.9005 | 4.8507 | 4.7491 | 4.6827 | 4.62 | 4.5708 | 5.04 | 5.0074 | 4.9672 | 4.8774 | 4.7805 | 4.7006 | 4.6165 | 4.5355 | 4.4909 | 4.4217 | 4.2859 | 4.2089 | 4.1101 | 4.067
| KERRY FALLS | LW |  |  |  | 5.4186 | 5.3684 | 5.3032 | 5.2299 | 5.1525 | 5.0807 | 4.9844 | 4.8826 | 4.8177 | 4.7537 | 4.6263 | 4.5567 | 4.5018 | 4.4803 | 5.2076 | 5.1833 | 5.1482 | 5.1121 | 5.0726 | 5.0375 | 4.9843 | 4.926 | 4.8778 | 4.8281 | 4.7203 | 4.6797 | 4.6565 | 4.6483 | 5.0131 | 4.9677 | 4.9076 | 4.8409 | 4.7701 | 4.7049 | 4.6158 | 4.521 | 4.4541 | 4.3831 | 4.2429 | 4.1761 | 4.1277 | 4.1092
| KERRY FALLS | ST |  |  |  | 5.468 | 5.447 | 5.4278 | 5.3988 | 5.3643 | 5.3321 | 5.2927 | 5.253 | 5.2072 | 5.1518 | 5.0265 | 4.7573 | 4.6576 | 4.5962 | 5.2266 | 5.216 | 5.2053 | 5.1899 | 5.1709 | 5.1521 | 5.1289 | 5.1039 | 5.0743 | 5.0383 | 4.9545 | 4.7578 | 4.6911 | 4.6418 | 5.0436 | 5.0377 | 5.0201 | 4.9936 | 4.9619 | 4.932 | 4.8954 | 4.8577 | 4.8118 | 4.7561 | 4.6288 | 4.3572 | 4.266 | 4.2123
| KERRY FALLS | FS |  |  |  | 5.4796 | 5.4647 | 5.4448 | 5.4207 | 5.3907 | 5.3621 | 5.3289 | 5.2937 | 5.2515 | 5.2066 | 5.1116 | 4.8141 | 4.5905 | 4.5455 | 5.231 | 5.2231 | 5.2125 | 5.1998 | 5.1838 | 5.1679 | 5.1493 | 5.1288 | 5.1042 | 5.0772 | 5.0171 | 4.83 | 4.6573 | 4.5985 | 5.0444 | 5.0419 | 5.0354 | 5.0134 | 4.9859 | 4.9596 | 4.9291 | 4.8964 | 4.8573 | 4.814 | 4.7201 | 4.4249 | 4.207 | 4.1676
TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.34739 | 0.32667 | 0.30325 | 0.27635 | 0.24227 | 0.20783 | 0.17201 | 0.13415 | 0.11618 | 0.094572 | 0.045635 | 0.041385 | 0.013821 | -0.00011841 | 0.36804 | 0.35121 | 0.33426 | 0.31501 | 0.29545 | 0.28052 | 0.26469 | 0.24685 | 0.23017 | 0.21542 | 0.18236 | 0.21022 | 0.18911 | 0.17302 | 0.13177 | 0.11328 | 0.094928 | 0.074592 | 0.053696 | 0.038495 | 0.022219 | 0.0037461 | -0.014181 | -0.030325 | -0.066111 | -0.010138 | -0.037611 | -0.052761
| KILCHRENAN | CT |  |  |  | 0.35821 | 0.34316 | 0.32254 | 0.28396 | 0.24227 | 0.20783 | 0.17201 | 0.13415 | 0.11618 | 0.094572 | 0.047308 | 0.055284 | 0.013821 | -0.00011841 | 0.36804 | 0.35121 | 0.33426 | 0.31501 | 0.29545 | 0.28052 | 0.26469 | 0.24685 | 0.23017 | 0.21542 | 0.18236 | 0.21222 | 0.18911 | 0.17302 | 0.13177 | 0.11328 | 0.094928 | 0.074592 | 0.053696 | 0.038495 | 0.022219 | 0.0037461 | -0.014181 | -0.030325 | -0.066111 | 0.0048904 | -0.037611 | -0.052761
| KILCHRENAN | LW |  |  |  | 0.34739 | 0.32667 | 0.30325 | 0.27635 | 0.24585 | 0.2185 | 0.18241 | 0.14444 | 0.11951 | 0.09523 | 0.045635 | 0.041385 | 0.022206 | 0.015879 | 0.36868 | 0.35478 | 0.34525 | 0.33695 | 0.32712 | 0.31692 | 0.3008 | 0.28166 | 0.26051 | 0.23738 | 0.18797 | 0.21022 | 0.20184 | 0.19938 | 0.13307 | 0.11796 | 0.10845 | 0.10021 | 0.090405 | 0.080146 | 0.063404 | 0.043341 | 0.020569 | -0.0049673 | -0.059171 | -0.010138 | -0.030236 | -0.036865
| KILCHRENAN | ST |  |  |  | 0.36643 | 0.36078 | 0.35064 | 0.34229 | 0.32976 | 0.31527 | 0.30198 | 0.28429 | 0.26627 | 0.24745 | 0.20044 | 0.12148 | 0.094215 | 0.072908 | 0.37674 | 0.37252 | 0.369 | 0.36452 | 0.35874 | 0.35167 | 0.3429 | 0.33207 | 0.31896 | 0.30297 | 0.26245 | 0.24095 | 0.21963 | 0.20244 | 0.14175 | 0.13727 | 0.13389 | 0.1294 | 0.12355 | 0.11629 | 0.10721 | 0.095953 | 0.082064 | 0.06497 | 0.021472 | 0.067321 | 0.038653 | 0.016011
| KILCHRENAN | FS |  |  |  | 0.37001 | 0.36796 | 0.36097 | 0.3494 | 0.34057 | 0.3278 | 0.31786 | 0.30758 | 0.29005 | 0.27561 | 0.23605 | 0.13752 | 0.062319 | 0.043563 | 0.37872 | 0.37648 | 0.37406 | 0.37075 | 0.36681 | 0.36218 | 0.35672 | 0.35043 | 0.3427 | 0.33388 | 0.31195 | 0.2666 | 0.20693 | 0.1869 | 0.1438 | 0.14153 | 0.13929 | 0.13613 | 0.13232 | 0.12774 | 0.1223 | 0.11582 | 0.10801 | 0.098917 | 0.076192 | 0.088913 | 0.0091459 | -0.010655
STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | NO | -1.1249 | -1.2131 | -1.3311 | -1.5529 | -1.7982 | -2.0534 | -2.3462 | -2.6539 | -2.9065 | -3.1692 | -3.6714 | -4.6149 | -5.5684 | -6.2933 | -0.34037 | -0.37839 | -0.43731 | -0.52328 | -0.62911 | -0.79388 | -0.97421 | -1.1083 | -1.2625 | -1.4365 | -1.7714 | -2.3549 | -2.963 | -3.6092 | -0.63634 | -0.70622 | -0.80459 | -0.97568 | -1.1661 | -1.3609 | -1.5936 | -1.8409 | -2.0578 | -2.2844 | -2.7413 | -3.5675 | -4.3737 | -5.0194
| KILLEARN | CT |  |  |  | -1.0545 | -1.1039 | -1.1829 | -1.4077 | -1.656 | -1.9371 | -2.2393 | -2.5034 | -2.7689 | -3.0552 | -3.6063 | -4.6149 | -5.5684 | -6.2933 | -0.32266 | -0.35171 | -0.40035 | -0.5071 | -0.62911 | -0.79388 | -0.97421 | -1.1083 | -1.2625 | -1.4365 | -1.7714 | -2.3549 | -2.963 | -3.6092 | -0.58449 | -0.62548 | -0.69342 | -0.8768 | -1.0815 | -1.3213 | -1.5784 | -1.7885 | -2.0134 | -2.2633 | -2.7413 | -3.5675 | -4.3737 | -5.0194
| KILLEARN | LW |  |  |  | -1.1249 | -1.2131 | -1.3311 | -1.5529 | -1.7982 | -2.0534 | -2.3462 | -2.6539 | -2.9065 | -3.1692 | -3.6714 | -4.4963 | -5.39 | -6.1837 | -0.34037 | -0.37839 | -0.43731 | -0.52328 | -0.62683 | -0.73753 | -0.87608 | -1.0242 | -1.1671 | -1.3168 | -1.6039 | -1.9762 | -2.5058 | -3.0783 | -0.63634 | -0.70622 | -0.80459 | -0.97568 | -1.1661 | -1.3609 | -1.5936 | -1.8409 | -2.0578 | -2.2844 | -2.7183 | -3.3663 | -4.1392 | -4.9027
| KILLEARN | ST |  |  |  | -1.0368 | -1.074 | -1.1226 | -1.2335 | -1.3404 | -1.4517 | -1.614 | -1.7273 | -1.8816 | -2.0132 | -2.2951 | -3.0686 | -3.8202 | -4.6087 | -0.31785 | -0.33906 | -0.36729 | -0.45715 | -0.53728 | -0.61251 | -0.75033 | -0.83242 | -0.96039 | -1.0575 | -1.2751 | -1.8664 | -2.4669 | -3.174 | -0.57199 | -0.60154 | -0.64052 | -0.74804 | -0.84737 | -0.94566 | -1.1066 | -1.2097 | -1.3616 | -1.4839 | -1.7514 | -2.4818 | -3.1363 | -3.801
| KILLEARN | FS |  |  |  | -1.0229 | -1.053 | -1.0919 | -1.1589 | -1.2345 | -1.314 | -1.4068 | -1.4971 | -1.6178 | -1.7298 | -1.9712 | -2.6388 | -3.3294 | -3.9175 | -0.31363 | -0.33273 | -0.35787 | -0.40083 | -0.44991 | -0.50366 | -0.56434 | -0.625 | -0.707 | -0.78443 | -0.95723 | -1.4319 | -2.0271 | -2.7249 | -0.56158 | -0.58551 | -0.61668 | -0.67376 | -0.73844 | -0.80689 | -0.88616 | -0.96414 | -1.0705 | -1.1693 | -1.3839 | -1.9604 | -2.5404 | -2.9759
KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | NO | 1.8774 | 1.8755 | 1.8723 | 1.8528 | 1.7957 | 1.7018 | 1.6048 | 1.5258 | 1.4673 | 1.4057 | 1.2637 | 1.1594 | 0.9284 | 0.72815 | 2.0719 | 2.0518 | 2.0238 | 1.9903 | 1.9343 | 1.8649 | 1.792 | 1.742 | 1.6856 | 1.6193 | 1.4939 | 1.4107 | 1.2558 | 1.1034 | 1.7479 | 1.7409 | 1.7178 | 1.6754 | 1.6149 | 1.5252 | 1.4318 | 1.3605 | 1.303 | 1.2494 | 1.1381 | 1.0062 | 0.81047 | 0.63186
| KILLIN TOWN | CT |  |  |  | 1.8777 | 1.8759 | 1.8728 | 1.8652 | 1.7957 | 1.7018 | 1.6048 | 1.5258 | 1.4673 | 1.4057 | 1.2637 | 1.1594 | 0.9284 | 0.74599 | 2.0799 | 2.0629 | 2.0373 | 1.9903 | 1.9343 | 1.8649 | 1.792 | 1.742 | 1.6856 | 1.6193 | 1.4939 | 1.4107 | 1.2558 | 1.1034 | 1.7483 | 1.7465 | 1.7399 | 1.6825 | 1.6149 | 1.5252 | 1.4318 | 1.3605 | 1.303 | 1.2494 | 1.1381 | 1.0062 | 0.81047 | 0.64789
| KILLIN TOWN | LW |  |  |  | 1.8774 | 1.8755 | 1.8723 | 1.8566 | 1.798 | 1.7394 | 1.6641 | 1.5911 | 1.5371 | 1.4625 | 1.3014 | 1.2244 | 0.98431 | 0.72815 | 2.0719 | 2.0518 | 2.0238 | 1.9928 | 1.9568 | 1.9227 | 1.8713 | 1.8161 | 1.7584 | 1.6949 | 1.573 | 1.5498 | 1.3668 | 1.1393 | 1.7479 | 1.7409 | 1.7178 | 1.6754 | 1.6282 | 1.581 | 1.5205 | 1.4613 | 1.4156 | 1.3389 | 1.1948 | 1.1168 | 0.89206 | 0.63186
| KILLIN TOWN | ST |  |  |  | 1.8782 | 1.8774 | 1.876 | 1.8528 | 1.836 | 1.8234 | 1.7877 | 1.7643 | 1.7036 | 1.6561 | 1.5424 | 1.3461 | 1.1605 | 0.98936 | 2.0849 | 2.0775 | 2.0652 | 2.0246 | 1.9885 | 1.9558 | 1.893 | 1.8531 | 1.7921 | 1.7457 | 1.6381 | 1.4583 | 1.2847 | 1.116 | 1.7487 | 1.7479 | 1.7466 | 1.7183 | 1.6981 | 1.6659 | 1.6023 | 1.5567 | 1.4944 | 1.4486 | 1.343 | 1.1376 | 0.95112 | 0.78459
| KILLIN TOWN | FS |  |  |  | 1.8784 | 1.8778 | 1.8767 | 1.8707 | 1.8643 | 1.8568 | 1.849 | 1.8419 | 1.8221 | 1.7858 | 1.7063 | 1.5417 | 1.3602 | 1.2675 | 2.0867 | 2.0814 | 2.0723 | 2.054 | 2.0331 | 2.0102 | 1.9841 | 1.9584 | 1.9238 | 1.8905 | 1.8161 | 1.682 | 1.5322 | 1.4334 | 1.7488 | 1.7483 | 1.7473 | 1.7403 | 1.7331 | 1.7245 | 1.6948 | 1.6662 | 1.6287 | 1.5947 | 1.5199 | 1.367 | 1.2042 | 1.1335
TAYNUILT | KILMELFORD PS | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | -1.2446 | -1.2798 | -1.3213 | -1.3715 | -1.4153 | -1.4662 | -1.5157 | -1.568 | -1.6067 | -1.6486 | -1.7309 | -1.7103 | -1.7401 | -1.7605 | 0.043414 | 0.025922 | 0.0010044 | -0.023748 | -0.054882 | -0.08049 | -0.10534 | -0.14059 | -0.17651 | -0.21545 | -0.2916 | -0.27952 | -0.30275 | -0.32516 | -1.4962 | -1.5105 | -1.5236 | -1.546 | -1.5629 | -1.586 | -1.6088 | -1.6311 | -1.6338 | -1.6354 | -1.6415 | -1.6221 | -1.6405 | -1.6469
| KILMELFORD PS | CT |  |  |  | -1.2315 | -1.2581 | -1.293 | -1.3512 | -1.4144 | -1.4662 | -1.5157 | -1.5641 | -1.5936 | -1.6307 | -1.7048 | -1.7017 | -1.7401 | -1.7605 | 0.047384 | 0.032995 | 0.012425 | -0.019926 | -0.054882 | -0.08049 | -0.10534 | -0.13012 | -0.1569 | -0.19298 | -0.26297 | -0.27952 | -0.30275 | -0.32516 | -1.4909 | -1.4996 | -1.5119 | -1.5357 | -1.5621 | -1.586 | -1.6088 | -1.6311 | -1.6338 | -1.6354 | -1.6415 | -1.6221 | -1.6405 | -1.6469
| KILMELFORD PS | LW |  |  |  | -1.2446 | -1.2798 | -1.3213 | -1.3715 | -1.4153 | -1.4615 | -1.5138 | -1.568 | -1.6067 | -1.6486 | -1.7309 | -1.7103 | -1.7288 | -1.7335 | 0.043414 | 0.025922 | 0.0010044 | -0.023748 | -0.048113 | -0.071049 | -0.10386 | -0.14059 | -0.17651 | -0.21545 | -0.2916 | -0.27801 | -0.28494 | -0.28617 | -1.4962 | -1.5105 | -1.5236 | -1.546 | -1.5629 | -1.5836 | -1.6022 | -1.6196 | -1.6234 | -1.6276 | -1.6357 | -1.6207 | -1.6286 | -1.6307
| KILMELFORD PS | ST |  |  |  | -1.2226 | -1.2422 | -1.2592 | -1.2773 | -1.2976 | -1.318 | -1.3377 | -1.3603 | -1.3837 | -1.4128 | -1.4795 | -1.5936 | -1.6286 | -1.644 | 0.049948 | 0.040035 | 0.029832 | 0.01908 | 0.0065455 | -0.006834 | -0.020943 | -0.037655 | -0.056891 | -0.080388 | -0.13591 | -0.2341 | -0.26244 | -0.28003 | -1.4905 | -1.4929 | -1.4955 | -1.4984 | -1.5041 | -1.5096 | -1.514 | -1.5187 | -1.5218 | -1.5276 | -1.5381 | -1.5648 | -1.5722 | -1.5724
| KILMELFORD PS | FS |  |  |  | -1.2187 | -1.2344 | -1.2502 | -1.2674 | -1.2866 | -1.3081 | -1.3245 | -1.3408 | -1.364 | -1.3823 | -1.4321 | -1.5503 | -1.6592 | -1.6744 | 0.051596 | 0.042941 | 0.033623 | 0.023933 | 0.012935 | 0.0008258 | -0.01003 | -0.021956 | -0.037137 | -0.052277 | -0.090161 | -0.18302 | -0.27599 | -0.29937 | -1.4904 | -1.4926 | -1.495 | -1.4969 | -1.5012 | -1.5091 | -1.5129 | -1.5163 | -1.5231 | -1.5256 | -1.5362 | -1.5596 | -1.5741 | -1.5828
TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | -0.961 | -0.9822 | -1.0224 | 0.88987 | 1.1421 | 1.0937 | 1.0465 | 0.9808 | 0.92291 | 0.85852 | 0.72855 | 0.78815 | 0.76396 | 0.74246 | -0.29147 | -0.30458 | -0.3302 | 1.3757 | 1.8587 | 1.8303 | 1.8018 | 1.7599 | 1.7137 | 1.6629 | 1.5616 | 1.6123 | 1.5841 | 1.5573 | -0.41862 | -0.43984 | -0.47927 | 1.2136 | 1.6871 | 1.6397 | 1.5933 | 1.5287 | 1.4719 | 1.4087 | 1.2809 | 1.3413 | 1.3175 | 1.2953
| KILNINVER | CT |  |  |  | -0.94966 | -0.96791 | -0.9958 | 0.89776 | 1.1421 | 1.0937 | 1.0465 | 0.99984 | 0.95744 | 0.89975 | 0.79203 | 0.80567 | 0.76396 | 0.74246 | -0.28708 | -0.2989 | -0.31845 | 1.3757 | 1.8587 | 1.8303 | 1.8018 | 1.773 | 1.7394 | 1.6941 | 1.6072 | 1.613 | 1.5841 | 1.5573 | -0.40717 | -0.42526 | -0.45281 | 1.2218 | 1.6871 | 1.6397 | 1.5933 | 1.5473 | 1.5055 | 1.449 | 1.3431 | 1.3589 | 1.3175 | 1.2953
| KILNINVER | LW |  |  |  | -0.961 | -0.9822 | -1.0224 | 0.88987 | 1.148 | 1.1087 | 1.0473 | 0.9808 | 0.92291 | 0.85852 | 0.72855 | 0.78815 | 0.77139 | 0.76276 | -0.29147 | -0.30458 | -0.3302 | 1.3769 | 1.8705 | 1.8468 | 1.8061 | 1.7599 | 1.7137 | 1.6629 | 1.5616 | 1.6123 | 1.6043 | 1.601 | -0.41862 | -0.43984 | -0.47927 | 1.2136 | 1.6926 | 1.654 | 1.5938 | 1.5287 | 1.4719 | 1.4087 | 1.2809 | 1.3413 | 1.3239 | 1.3153
| KILNINVER | ST |  |  |  | -0.93868 | -0.9469 | -0.95716 | 0.9787 | 1.2627 | 1.2448 | 1.2221 | 1.1968 | 1.1637 | 1.1246 | 1.0355 | 0.9144 | 0.8769 | 0.86007 | -0.28283 | -0.28834 | -0.29554 | 1.4249 | 1.933 | 1.9197 | 1.903 | 1.8836 | 1.8592 | 1.8297 | 1.7604 | 1.6635 | 1.6302 | 1.6086 | -0.39681 | -0.40516 | -0.41554 | 1.3002 | 1.8042 | 1.7863 | 1.7637 | 1.7386 | 1.706 | 1.6676 | 1.5799 | 1.4625 | 1.4232 | 1.4051
| KILNINVER | FS |  |  |  | -0.93679 | -0.94411 | -0.95291 | 0.98499 | 1.2691 | 1.2538 | 1.2348 | 1.2136 | 1.1919 | 1.1647 | 1.1016 | 0.96551 | 0.8339 | 0.81473 | -0.28194 | -0.28681 | -0.29299 | 1.429 | 1.9386 | 1.928 | 1.9149 | 1.9 | 1.8836 | 1.8639 | 1.8172 | 1.7198 | 1.6114 | 1.5825 | -0.39491 | -0.40238 | -0.41117 | 1.3065 | 1.8107 | 1.7953 | 1.7762 | 1.7551 | 1.7334 | 1.7065 | 1.6442 | 1.5123 | 1.384 | 1.3649
BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 5.4143 | 5.358 | 5.2959 | 5.215 | 5.1379 | 5.0552 | 4.9687 | 4.8701 | 4.8446 | 4.8139 | 4.7461 | 4.7167 | 4.6161 | 4.5613 | 5.6431 | 5.6177 | 5.5809 | 5.5419 | 5.4949 | 5.4497 | 5.4024 | 5.3446 | 5.2928 | 5.2386 | 5.1312 | 5.099 | 5.0279 | 4.9696 | 5.3501 | 5.3049 | 5.256 | 5.19 | 5.1272 | 5.0589 | 4.987 | 4.903 | 4.8853 | 4.8295 | 4.7058 | 4.6453 | 4.5734 | 4.5303
| KILTARLITY | CT |  |  |  | 5.4501 | 5.4187 | 5.3743 | 5.2737 | 5.166 | 5.0705 | 4.9705 | 4.8701 | 4.8486 | 4.8223 | 4.7679 | 4.7601 | 4.6161 | 4.5613 | 5.6544 | 5.637 | 5.6093 | 5.5545 | 5.4949 | 5.4497 | 5.4024 | 5.3547 | 5.3169 | 5.2636 | 5.1613 | 5.099 | 5.0279 | 4.9696 | 5.3794 | 5.3537 | 5.3189 | 5.2359 | 5.1497 | 5.0703 | 4.987 | 4.903 | 4.8853 | 4.8577 | 4.7438 | 4.6784 | 4.5734 | 4.5303
| KILTARLITY | LW |  |  |  | 5.4143 | 5.358 | 5.2959 | 5.215 | 5.1379 | 5.0552 | 4.9687 | 4.8787 | 4.8446 | 4.8139 | 4.7461 | 4.7167 | 4.6456 | 4.6182 | 5.6431 | 5.6177 | 5.5809 | 5.5419 | 5.5007 | 5.462 | 5.4065 | 5.3446 | 5.2928 | 5.2386 | 5.1312 | 5.0994 | 5.0744 | 5.0657 | 5.3501 | 5.3049 | 5.256 | 5.19 | 5.1272 | 5.0589 | 4.988 | 4.9147 | 4.887 | 4.8295 | 4.7058 | 4.6453 | 4.5942 | 4.5755
| KILTARLITY | ST |  |  |  | 5.4672 | 5.4395 | 5.4126 | 5.375 | 5.3435 | 5.3035 | 5.2656 | 5.222 | 5.1801 | 5.1334 | 5.031 | 4.8681 | 4.7454 | 4.6653 | 5.6591 | 5.6467 | 5.6329 | 5.6142 | 5.5945 | 5.5714 | 5.5461 | 5.5162 | 5.4831 | 5.4439 | 5.352 | 5.1491 | 5.0723 | 5.0132 | 5.3939 | 5.3725 | 5.3515 | 5.322 | 5.2963 | 5.2635 | 5.2319 | 5.1959 | 5.1624 | 5.1253 | 5.0383 | 4.7738 | 4.674 | 4.6192
| KILTARLITY | FS |  |  |  | 5.4809 | 5.4629 | 5.4462 | 5.4132 | 5.3852 | 5.3526 | 5.3191 | 5.2863 | 5.2465 | 5.2053 | 5.117 | 4.8597 | 4.6889 | 4.623 | 5.6633 | 5.6541 | 5.6439 | 5.6279 | 5.6114 | 5.5931 | 5.5728 | 5.5507 | 5.5241 | 5.4947 | 5.4273 | 5.2221 | 5.0452 | 4.9703 | 5.4041 | 5.3895 | 5.3762 | 5.3507 | 5.3291 | 5.3022 | 5.2742 | 5.2471 | 5.2144 | 5.1807 | 5.1086 | 4.838 | 4.6357 | 4.5922
REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | NO | 5.2648 | 4.7343 | 4.4593 | 3.6555 | 2.7506 | 1.5669 | 0.66966 | -0.21373 | -0.81132 | -1.4492 | -2.7557 | -2.1806 | -3.2763 | -3.924 | 5.8211 | 5.6415 | 5.5377 | 5.0458 | 4.4491 | 3.4302 | 2.8134 | 2.3134 | 2.0165 | 1.6451 | 0.74093 | 0.94542 | -0.1164 | -1.3575 | 5.4848 | 5.1511 | 4.9736 | 4.3223 | 3.5745 | 2.4827 | 1.6534 | 0.83316 | 0.25721 | -0.35881 | -1.6148 | -1.0275 | -2.0746 | -2.7438
| KINCORTH | CT |  |  |  | 5.4318 | 5.0375 | 4.8759 | 4.0989 | 3.1679 | 1.9831 | 1.1496 | 0.44971 | -0.15079 | -0.74797 | -1.9405 | -2.1806 | -3.2763 | -3.924 | 5.85 | 5.6948 | 5.6016 | 5.1114 | 4.4739 | 3.4302 | 2.8134 | 2.3368 | 2.048 | 1.7823 | 1.0299 | 0.94542 | -0.1164 | -1.3575 | 5.5971 | 5.3452 | 5.2275 | 4.6004 | 3.8352 | 2.7271 | 1.9945 | 1.3967 | 0.82902 | 0.26026 | -0.87424 | -1.0275 | -2.0746 | -2.7438
| KINCORTH | LW |  |  |  | 5.2648 | 4.7343 | 4.4593 | 3.6555 | 2.7506 | 1.5669 | 0.66966 | -0.21373 | -0.81132 | -1.4492 | -2.7557 | -2.0525 | -2.8513 | -3.6564 | 5.8211 | 5.6415 | 5.5377 | 5.0458 | 4.4491 | 3.445 | 2.8477 | 2.3134 | 2.0165 | 1.6451 | 0.74093 | 1.4633 | 0.70803 | -0.2321 | 5.4848 | 5.1511 | 4.9736 | 4.3223 | 3.5745 | 2.4827 | 1.6534 | 0.83316 | 0.25721 | -0.35881 | -1.6148 | -0.87457 | -1.7529 | -2.7175
| KINCORTH | ST |  |  |  | 5.462 | 5.1254 | 5.0629 | 4.6778 | 4.154 | 3.3356 | 2.8454 | 2.4498 | 2.1231 | 1.8376 | 1.0208 | 0.90988 | -0.34803 | -1.6258 | 5.8614 | 5.7382 | 5.7052 | 5.3119 | 4.7776 | 3.8483 | 3.3112 | 2.901 | 2.6297 | 2.4211 | 1.9507 | 2.0281 | 0.81575 | -0.77038 | 5.6203 | 5.4142 | 5.3747 | 5.0009 | 4.4959 | 3.6533 | 3.1568 | 2.7747 | 2.489 | 2.2653 | 1.7008 | 1.6523 | 0.42038 | -0.84593
| KINCORTH | FS |  |  |  | 5.497 | 5.2295 | 5.1728 | 4.8649 | 4.4396 | 3.8182 | 3.452 | 3.1047 | 2.8091 | 2.4633 | 1.8602 | 1.3797 | 0.014196 | -1.0279 | 5.8723 | 5.7672 | 5.737 | 5.4486 | 5.0341 | 4.3419 | 3.951 | 3.585 | 3.3605 | 3.089 | 2.6658 | 2.4451 | 0.87064 | -1.2791 | 5.6431 | 5.4815 | 5.4476 | 5.1658 | 4.7694 | 4.1385 | 3.7794 | 3.4433 | 3.1996 | 2.9123 | 2.4478 | 2.2297 | 0.97968 | 0.052902
FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0.053188 | 0.05245 | 0.051465 | 0.050095 | 0.04912 | 0.048147 | 0.045701 | 0.040693 | 0.034611 | 0.027882 | 0.014209 | 0.043744 | 0.043579 | 0.043391 | 0.071919 | 0.071508 | 0.070893 | 0.069986 | 0.069174 | 0.068416 | 0.066316 | 0.062379 | 0.057857 | 0.052854 | 0.042241 | 0.064054 | 0.06321 | 0.061695 | 0.064159 | 0.062784 | 0.060511 | 0.05733 | 0.055113 | 0.052754 | 0.05019 | 0.045373 | 0.039632 | 0.033163 | 0.02002 | 0.054447 | 0.054293 | 0.054106
| KINGAIRLOCH | CT |  |  |  | 0.053188 | 0.05245 | 0.051465 | 0.050095 | 0.04912 | 0.048147 | 0.045701 | 0.042906 | 0.038673 | 0.035347 | 0.026913 | 0.044 | 0.043656 | 0.043391 | 0.071919 | 0.071508 | 0.070899 | 0.069986 | 0.069174 | 0.068416 | 0.066316 | 0.06402 | 0.06087 | 0.058377 | 0.052081 | 0.064054 | 0.06321 | 0.061971 | 0.064194 | 0.062784 | 0.060511 | 0.05733 | 0.055113 | 0.052754 | 0.05019 | 0.047386 | 0.043536 | 0.040337 | 0.032226 | 0.054698 | 0.054363 | 0.054106
| KINGAIRLOCH | LW |  |  |  | 0.05319 | 0.052618 | 0.05157 | 0.050753 | 0.049801 | 0.048831 | 0.045804 | 0.040693 | 0.034611 | 0.027882 | 0.014209 | 0.043744 | 0.043579 | 0.043535 | 0.071919 | 0.071569 | 0.070893 | 0.070351 | 0.069709 | 0.069125 | 0.066408 | 0.062379 | 0.057857 | 0.052854 | 0.042241 | 0.064517 | 0.064399 | 0.064374 | 0.064159 | 0.063235 | 0.060858 | 0.059015 | 0.056781 | 0.054405 | 0.050296 | 0.045373 | 0.039632 | 0.033163 | 0.02002 | 0.054447 | 0.054293 | 0.054257
| KINGAIRLOCH | ST |  |  |  | 0.053284 | 0.053034 | 0.052721 | 0.052301 | 0.05176 | 0.051086 | 0.050242 | 0.049201 | 0.047589 | 0.043831 | 0.033393 | 0.044607 | 0.043899 | 0.043844 | 0.071952 | 0.07178 | 0.071557 | 0.07127 | 0.070893 | 0.070449 | 0.069898 | 0.069227 | 0.067887 | 0.064741 | 0.056957 | 0.064526 | 0.063397 | 0.062321 | 0.064218 | 0.06405 | 0.063481 | 0.062525 | 0.061298 | 0.059756 | 0.05778 | 0.055239 | 0.052113 | 0.048272 | 0.038464 | 0.055304 | 0.054607 | 0.054559
| KINGAIRLOCH | FS |  |  |  | 0.053313 | 0.053108 | 0.052856 | 0.05254 | 0.05215 | 0.051688 | 0.051134 | 0.050476 | 0.049707 | 0.048812 | 0.044726 | 0.046931 | 0.043941 | 0.043868 | 0.071965 | 0.071814 | 0.071621 | 0.071394 | 0.071107 | 0.070785 | 0.070399 | 0.069942 | 0.06941 | 0.068792 | 0.065497 | 0.066282 | 0.063215 | 0.061695 | 0.064236 | 0.064096 | 0.063793 | 0.063077 | 0.062202 | 0.061153 | 0.059894 | 0.058398 | 0.056547 | 0.054389 | 0.049199 | 0.057617 | 0.054643 | 0.054577
DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 2.9049 | 2.7345 | 2.5322 | 2.2233 | 1.9331 | 1.6464 | 1.2153 | 0.74877 | 0.2107 | -0.10309 | -0.7548 | -1.1751 | -1.8219 | -2.2119 | 3.8691 | 3.7854 | 3.6814 | 3.5286 | 3.3888 | 3.2002 | 2.9102 | 2.6664 | 2.2805 | 2.0357 | 1.5625 | 1.1587 | 0.64991 | 0.11137 | 3.2285 | 3.0748 | 2.8896 | 2.6165 | 2.3549 | 2.0985 | 1.7037 | 1.2724 | 0.76159 | 0.46214 | -0.17441 | -0.60355 | -1.2057 | -1.5852
| KINGSEAT | CT |  |  |  | 3.0239 | 2.912 | 2.7783 | 2.4269 | 2.0875 | 1.7581 | 1.3386 | 0.94745 | 0.43904 | 0.087904 | -0.59225 | -1.1751 | -1.8219 | -2.2119 | 3.9134 | 3.8509 | 3.772 | 3.5815 | 3.3978 | 3.2002 | 2.9102 | 2.6664 | 2.2805 | 2.0357 | 1.5625 | 1.1587 | 0.64991 | 0.11137 | 3.3333 | 3.2314 | 3.1076 | 2.7897 | 2.4768 | 2.1655 | 1.7702 | 1.4099 | 0.92768 | 0.59163 | -0.059587 | -0.60355 | -1.2057 | -1.5852
| KINGSEAT | LW |  |  |  | 2.9049 | 2.7345 | 2.5322 | 2.2233 | 1.9331 | 1.6464 | 1.2153 | 0.74877 | 0.2107 | -0.10309 | -0.7548 | -1.0569 | -1.5121 | -1.8941 | 3.8691 | 3.7854 | 3.6814 | 3.5286 | 3.3888 | 3.2533 | 2.9835 | 2.6997 | 2.2881 | 2.0781 | 1.6426 | 1.5261 | 1.1889 | 0.81284 | 3.2285 | 3.0748 | 2.8896 | 2.6165 | 2.3549 | 2.0985 | 1.7037 | 1.2724 | 0.76159 | 0.46214 | -0.17441 | -0.41814 | -0.8784 | -1.3048
| KINGSEAT | ST |  |  |  | 3.0718 | 3.0085 | 2.939 | 2.7742 | 2.6444 | 2.5141 | 2.2505 | 2.0185 | 1.6045 | 1.3999 | 0.94927 | 0.068537 | -0.58673 | -1.225 | 3.9325 | 3.8946 | 3.8554 | 3.7337 | 3.6413 | 3.5538 | 3.3178 | 3.1356 | 2.7829 | 2.635 | 2.2822 | 1.5995 | 1.0243 | 0.36527 | 3.3754 | 3.3181 | 3.2556 | 3.098 | 2.9718 | 2.8478 | 2.5867 | 2.3653 | 1.9618 | 1.764 | 1.3136 | 0.40609 | -0.21574 | -0.79787
| KINGSEAT | FS |  |  |  | 3.096 | 3.049 | 2.9986 | 2.8882 | 2.7846 | 2.684 | 2.5249 | 2.3466 | 2.0256 | 1.8513 | 1.464 | 0.52749 | -0.32727 | -0.77308 | 3.9425 | 3.9122 | 3.881 | 3.8107 | 3.746 | 3.681 | 3.5561 | 3.4183 | 3.1598 | 3.0374 | 2.756 | 2.0914 | 1.2951 | 0.56704 | 3.3967 | 3.3541 | 3.3088 | 3.21 | 3.1145 | 3.0208 | 2.8733 | 2.7057 | 2.401 | 2.237 | 1.8705 | 0.98801 | 0.16234 | -0.20676
BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | NO | 1.8194 | 1.6558 | 1.4485 | 1.168 | 0.8714 | 0.51621 | 0.074228 | -0.34295 | -0.61211 | -0.88171 | -1.4213 | -1.1873 | -1.3467 | -1.4042 | 3.8294 | 3.7321 | 3.5963 | 3.3897 | 3.1657 | 2.867 | 2.4921 | 2.1637 | 1.9458 | 1.7211 | 1.2949 | 1.6019 | 1.5157 | 1.4875 | 2.4521 | 2.3062 | 2.1268 | 1.8636 | 1.586 | 1.2225 | 0.79118 | 0.40546 | 0.18739 | -0.034312 | -0.51192 | 0.23893 | 0.094922 | 0.044861
| KINGUSSIE | CT |  |  |  | 1.8907 | 1.7657 | 1.6102 | 1.3227 | 1.0138 | 0.6865 | 0.33226 | 0.026512 | -0.19493 | -0.45254 | -0.93041 | -0.75456 | -1.0397 | -1.1477 | 3.8611 | 3.7788 | 3.6683 | 3.4775 | 3.2695 | 3.0233 | 2.754 | 2.5521 | 2.3809 | 2.1859 | 1.822 | 2.0418 | 1.8406 | 1.6696 | 2.5143 | 2.3891 | 2.2324 | 1.986 | 1.7241 | 1.3929 | 1.0295 | 0.73117 | 0.53681 | 0.36404 | 0.00036517 | 0.7565 | 0.50297 | 0.40576
| KINGUSSIE | LW |  |  |  | 1.8194 | 1.6558 | 1.4485 | 1.168 | 0.8714 | 0.51621 | 0.074228 | -0.34295 | -0.61211 | -0.88171 | -1.4213 | -1.1873 | -1.3467 | -1.4042 | 3.8294 | 3.7321 | 3.5963 | 3.3897 | 3.1657 | 2.867 | 2.4921 | 2.1637 | 1.9458 | 1.7211 | 1.2949 | 1.6019 | 1.5157 | 1.4875 | 2.4521 | 2.3062 | 2.1268 | 1.8636 | 1.586 | 1.2225 | 0.79118 | 0.40546 | 0.18739 | -0.034312 | -0.51192 | 0.23893 | 0.094922 | 0.044861
| KINGUSSIE | ST |  |  |  | 1.9352 | 1.8592 | 1.7729 | 1.6035 | 1.4472 | 1.2976 | 1.0608 | 0.87509 | 0.68934 | 0.49511 | 0.057486 | -0.29081 | -0.53265 | -0.67262 | 3.8814 | 3.8326 | 3.7759 | 3.6283 | 3.4971 | 3.3754 | 3.153 | 3.0001 | 2.8589 | 2.7026 | 2.3394 | 2.1924 | 1.9835 | 1.8045 | 2.5476 | 2.4835 | 2.4102 | 2.2387 | 2.0822 | 1.9284 | 1.6683 | 1.4707 | 1.2797 | 1.0646 | 0.55297 | 1.144 | 0.92296 | 0.80021
| KINGUSSIE | FS |  |  |  | 1.9597 | 1.8977 | 1.8302 | 1.7195 | 1.606 | 1.4844 | 1.3552 | 1.2145 | 1.068 | 0.92047 | 0.60568 | 0.034577 | -0.47543 | -0.59618 | 3.8941 | 3.8535 | 3.8078 | 3.73 | 3.6476 | 3.5572 | 3.4585 | 3.3518 | 3.2468 | 3.1366 | 2.8917 | 2.5732 | 2.1046 | 1.8201 | 2.5671 | 2.5172 | 2.463 | 2.3665 | 2.2653 | 2.1521 | 2.0301 | 1.8971 | 1.7647 | 1.6236 | 1.3068 | 1.3815 | 1.0433 | 0.93649
TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | -0.39841 | -0.41582 | -0.4381 | -0.46757 | -0.51197 | -0.55381 | -0.59475 | -0.63827 | -0.6541 | -0.6679 | -0.7023 | -0.62173 | -0.64923 | -0.65784 | -0.17473 | -0.18725 | -0.20797 | -0.23198 | -0.26764 | -0.29436 | -0.32139 | -0.34935 | -0.38281 | -0.42081 | -0.49641 | -0.5032 | -0.53187 | -0.5561 | -0.58552 | -0.59719 | -0.61352 | -0.63941 | -0.67106 | -0.69983 | -0.7283 | -0.75881 | -0.77447 | -0.78877 | -0.82273 | -0.7384 | -0.75482 | -0.7734
| KINLOCH | CT |  |  |  | -0.38865 | -0.40285 | -0.42225 | -0.46757 | -0.51197 | -0.55381 | -0.59475 | -0.63827 | -0.6541 | -0.6679 | -0.7023 | -0.61268 | -0.64923 | -0.65784 | -0.17022 | -0.18047 | -0.19802 | -0.23198 | -0.26764 | -0.29436 | -0.32139 | -0.34935 | -0.37658 | -0.41336 | -0.48485 | -0.50275 | -0.53187 | -0.5561 | -0.58015 | -0.59123 | -0.60737 | -0.63941 | -0.67106 | -0.69983 | -0.7283 | -0.75881 | -0.77447 | -0.78877 | -0.82273 | -0.73337 | -0.75482 | -0.7734
| KINLOCH | LW |  |  |  | -0.39841 | -0.41582 | -0.4381 | -0.46704 | -0.49767 | -0.52884 | -0.56565 | -0.60713 | -0.62932 | -0.6486 | -0.69255 | -0.62173 | -0.64027 | -0.64565 | -0.17473 | -0.18725 | -0.20797 | -0.22899 | -0.25274 | -0.2738 | -0.30746 | -0.34637 | -0.38281 | -0.42081 | -0.49641 | -0.5032 | -0.51337 | -0.51551 | -0.58552 | -0.59719 | -0.61352 | -0.63296 | -0.65402 | -0.67515 | -0.70215 | -0.73311 | -0.75366 | -0.773 | -0.81546 | -0.7384 | -0.74871 | -0.75422
| KINLOCH | ST |  |  |  | -0.37746 | -0.38067 | -0.38907 | -0.39833 | -0.40754 | -0.41785 | -0.42842 | -0.44241 | -0.4606 | -0.48299 | -0.53273 | -0.52221 | -0.53771 | -0.55212 | -0.16681 | -0.17105 | -0.17814 | -0.18691 | -0.19755 | -0.20925 | -0.22284 | -0.2396 | -0.26036 | -0.28587 | -0.346 | -0.45786 | -0.49098 | -0.51246 | -0.57309 | -0.57553 | -0.58133 | -0.58791 | -0.595 | -0.60318 | -0.61217 | -0.62394 | -0.63928 | -0.65814 | -0.70184 | -0.67585 | -0.68373 | -0.69035
| KINLOCH | FS |  |  |  | -0.37439 | -0.37844 | -0.38323 | -0.39285 | -0.40048 | -0.41157 | -0.42049 | -0.4322 | -0.44668 | -0.46253 | -0.49243 | -0.53648 | -0.5881 | -0.60364 | -0.16546 | -0.16963 | -0.17485 | -0.18275 | -0.19136 | -0.20137 | -0.21201 | -0.22469 | -0.23997 | -0.25734 | -0.29616 | -0.40495 | -0.50829 | -0.5346 | -0.57124 | -0.57391 | -0.57733 | -0.5837 | -0.58921 | -0.597 | -0.60374 | -0.61269 | -0.62375 | -0.63614 | -0.66138 | -0.67827 | -0.71612 | -0.72492
TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | -0.03784 | -0.057943 | -0.08553 | -0.10997 | -0.1415 | -0.17634 | -0.21383 | -0.25548 | -0.26788 | -0.28373 | -0.3214 | -0.28725 | -0.30476 | -0.31861 | 0.38723 | 0.37799 | 0.36399 | 0.35185 | 0.33151 | 0.31464 | 0.29633 | 0.27662 | 0.26502 | 0.2498 | 0.21398 | 0.23983 | 0.22856 | 0.21816 | 0.14325 | 0.14171 | 0.13862 | 0.13488 | 0.13019 | 0.12711 | 0.12376 | 0.11952 | 0.11268 | 0.10527 | 0.090657 | 0.094915 | 0.094094 | 0.093221
| KINLOCH RANNOCH | CT |  |  |  | -0.027702 | -0.039737 | -0.059948 | -0.09976 | -0.14149 | -0.17634 | -0.21383 | -0.25548 | -0.26788 | -0.28373 | -0.31587 | -0.27191 | -0.30476 | -0.31861 | 0.39093 | 0.38446 | 0.37308 | 0.35286 | 0.33151 | 0.31464 | 0.29633 | 0.27662 | 0.26502 | 0.25003 | 0.22081 | 0.24424 | 0.22856 | 0.21816 | 0.14342 | 0.14199 | 0.1392 | 0.13488 | 0.13019 | 0.12711 | 0.12376 | 0.12044 | 0.11535 | 0.10844 | 0.095373 | 0.096153 | 0.09446 | 0.093221
| KINLOCH RANNOCH | LW |  |  |  | -0.03784 | -0.057943 | -0.08553 | -0.10997 | -0.1415 | -0.16821 | -0.1978 | -0.23691 | -0.25946 | -0.27815 | -0.3214 | -0.28725 | -0.29804 | -0.30269 | 0.38723 | 0.37799 | 0.36399 | 0.35185 | 0.33655 | 0.32354 | 0.30617 | 0.28419 | 0.26675 | 0.2498 | 0.21398 | 0.23983 | 0.2351 | 0.23331 | 0.14325 | 0.14171 | 0.13862 | 0.13605 | 0.13298 | 0.13042 | 0.12542 | 0.11952 | 0.11268 | 0.10527 | 0.090657 | 0.094915 | 0.094094 | 0.093886
| KINLOCH RANNOCH | ST |  |  |  | -0.013648 | -0.021708 | -0.028823 | -0.040329 | -0.05081 | -0.059314 | -0.070394 | -0.0886 | -0.10525 | -0.12391 | -0.17157 | -0.20378 | -0.23581 | -0.25859 | 0.39596 | 0.39208 | 0.38813 | 0.38217 | 0.37596 | 0.36999 | 0.36243 | 0.35158 | 0.34024 | 0.32695 | 0.29361 | 0.27071 | 0.25223 | 0.24005 | 0.14346 | 0.1428 | 0.14186 | 0.14058 | 0.13886 | 0.13688 | 0.13444 | 0.13148 | 0.12779 | 0.12327 | 0.11216 | 0.098804 | 0.095197 | 0.094902
| KINLOCH RANNOCH | FS |  |  |  | -0.011846 | -0.015587 | -0.021799 | -0.030853 | -0.042181 | -0.048544 | -0.06298 | -0.072609 | -0.085378 | -0.10131 | -0.13212 | -0.20002 | -0.25666 | -0.27817 | 0.39673 | 0.39454 | 0.3912 | 0.38657 | 0.38071 | 0.37641 | 0.36886 | 0.36256 | 0.35458 | 0.34495 | 0.32432 | 0.28727 | 0.24547 | 0.23169 | 0.14355 | 0.14302 | 0.14227 | 0.14129 | 0.14001 | 0.13862 | 0.13696 | 0.13499 | 0.13262 | 0.12986 | 0.12319 | 0.11045 | 0.095716 | 0.095187
GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0.42506 | 0.40741 | 0.38735 | 0.36924 | 0.34798 | 0.32465 | 0.30051 | 0.26959 | 0.25105 | 0.22774 | 0.18396 | 0.17101 | 0.14611 | 0.13321 | 0.53491 | 0.52654 | 0.51557 | 0.50597 | 0.49244 | 0.48065 | 0.46732 | 0.45062 | 0.43605 | 0.41911 | 0.38495 | 0.37868 | 0.35987 | 0.34595 | 0.47123 | 0.45528 | 0.43677 | 0.42013 | 0.40057 | 0.37939 | 0.35674 | 0.32787 | 0.30753 | 0.2828 | 0.236 | 0.2229 | 0.20095 | 0.18927
| KINLOCHEWE | CT |  |  |  | 0.43312 | 0.4194 | 0.40661 | 0.37801 | 0.35149 | 0.32866 | 0.30213 | 0.27724 | 0.26175 | 0.23735 | 0.19849 | 0.18139 | 0.14611 | 0.13321 | 0.53792 | 0.53079 | 0.52293 | 0.50737 | 0.49244 | 0.48065 | 0.46732 | 0.45458 | 0.4429 | 0.42576 | 0.39476 | 0.37927 | 0.35987 | 0.34595 | 0.47273 | 0.46585 | 0.45388 | 0.42753 | 0.40295 | 0.38211 | 0.35798 | 0.3353 | 0.31981 | 0.29413 | 0.25149 | 0.23239 | 0.20095 | 0.18927
| KINLOCHEWE | LW |  |  |  | 0.42506 | 0.40741 | 0.38735 | 0.36924 | 0.34798 | 0.32465 | 0.30051 | 0.26959 | 0.25105 | 0.22774 | 0.18396 | 0.17101 | 0.15202 | 0.14757 | 0.53491 | 0.52654 | 0.51557 | 0.50597 | 0.49465 | 0.48327 | 0.4687 | 0.45062 | 0.43605 | 0.41911 | 0.38495 | 0.37868 | 0.37084 | 0.36914 | 0.47123 | 0.45528 | 0.43677 | 0.42013 | 0.40057 | 0.37939 | 0.35674 | 0.32787 | 0.30753 | 0.2828 | 0.236 | 0.2229 | 0.20612 | 0.20228
| KINLOCHEWE | ST |  |  |  | 0.43886 | 0.43465 | 0.42645 | 0.41937 | 0.41074 | 0.40202 | 0.38837 | 0.3806 | 0.36584 | 0.34794 | 0.31198 | 0.24058 | 0.21489 | 0.20156 | 0.5402 | 0.53776 | 0.53357 | 0.52945 | 0.52424 | 0.51876 | 0.51095 | 0.50473 | 0.4952 | 0.48361 | 0.45826 | 0.40543 | 0.38711 | 0.37448 | 0.47357 | 0.47244 | 0.47107 | 0.46555 | 0.4575 | 0.44932 | 0.43668 | 0.42815 | 0.41345 | 0.39566 | 0.35847 | 0.28547 | 0.26176 | 0.25009
| KINLOCHEWE | FS |  |  |  | 0.43899 | 0.43728 | 0.43287 | 0.42265 | 0.41726 | 0.40756 | 0.39898 | 0.38818 | 0.37591 | 0.36493 | 0.33796 | 0.25936 | 0.19339 | 0.17776 | 0.54032 | 0.5389 | 0.53623 | 0.53124 | 0.52766 | 0.52237 | 0.51715 | 0.51075 | 0.50338 | 0.49603 | 0.47817 | 0.42811 | 0.37771 | 0.3611 | 0.47378 | 0.47296 | 0.47186 | 0.4686 | 0.46351 | 0.45461 | 0.44661 | 0.43658 | 0.42475 | 0.41365 | 0.38655 | 0.30678 | 0.24288 | 0.22918
KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | NO | 2.3169 | 2.3154 | 2.3132 | 2.2901 | 2.2256 | 2.1307 | 2.0357 | 1.9449 | 1.9227 | 1.899 | 1.853 | 1.8714 | 1.7697 | 1.6985 | 2.4635 | 2.4481 | 2.4257 | 2.3653 | 2.3288 | 2.275 | 2.221 | 2.1771 | 2.1514 | 2.1194 | 2.047 | 2.0093 | 1.9251 | 1.8345 | 2.1299 | 2.1285 | 2.1264 | 2.0768 | 2.029 | 1.9558 | 1.8745 | 1.7903 | 1.763 | 1.7325 | 1.6734 | 1.6812 | 1.5765 | 1.5042
| KINLOCHLEVEN | CT |  |  |  | 2.3176 | 2.3163 | 2.3145 | 2.2914 | 2.2281 | 2.1307 | 2.0357 | 1.9449 | 1.9227 | 1.899 | 1.853 | 1.8714 | 1.7697 | 1.6985 | 2.4719 | 2.4598 | 2.4434 | 2.3777 | 2.3288 | 2.275 | 2.221 | 2.1771 | 2.1514 | 2.1194 | 2.047 | 2.0093 | 1.9251 | 1.8345 | 2.1305 | 2.1293 | 2.1276 | 2.1051 | 2.0348 | 1.9558 | 1.8745 | 1.7903 | 1.763 | 1.7325 | 1.6734 | 1.6812 | 1.5765 | 1.5042
| KINLOCHLEVEN | LW |  |  |  | 2.3169 | 2.3154 | 2.3132 | 2.2901 | 2.2256 | 2.1548 | 2.0782 | 2.001 | 1.9761 | 1.9509 | 1.8945 | 1.9055 | 1.8087 | 1.7167 | 2.4635 | 2.4481 | 2.4257 | 2.3653 | 2.3331 | 2.2991 | 2.2597 | 2.2189 | 2.1881 | 2.1518 | 2.0814 | 2.0891 | 2.0099 | 1.9133 | 2.1299 | 2.1285 | 2.1264 | 2.0768 | 2.029 | 1.9762 | 1.9205 | 1.8465 | 1.8162 | 1.7849 | 1.7245 | 1.7329 | 1.6288 | 1.5213
| KINLOCHLEVEN | ST |  |  |  | 2.3198 | 2.3195 | 2.3193 | 2.2917 | 2.2831 | 2.2767 | 2.2586 | 2.2525 | 2.2376 | 2.2315 | 2.2174 | 2.0961 | 2.0232 | 1.9393 | 2.4817 | 2.4766 | 2.4707 | 2.4282 | 2.4091 | 2.3909 | 2.3567 | 2.3356 | 2.3002 | 2.2731 | 2.2093 | 2.0855 | 1.9939 | 1.8885 | 2.1324 | 2.1322 | 2.1319 | 2.1023 | 2.0919 | 2.0844 | 2.0623 | 2.0551 | 2.0373 | 2.0301 | 2.0022 | 1.9199 | 1.8302 | 1.742
| KINLOCHLEVEN | FS |  |  |  | 2.3193 | 2.3197 | 2.3194 | 2.3038 | 2.2987 | 2.295 | 2.2894 | 2.2864 | 2.2804 | 2.2733 | 2.2627 | 2.1347 | 2.0188 | 1.9824 | 2.4801 | 2.478 | 2.4724 | 2.4431 | 2.4271 | 2.4124 | 2.3941 | 2.3778 | 2.3558 | 2.331 | 2.2809 | 2.1713 | 2.0467 | 1.9397 | 2.132 | 2.1323 | 2.132 | 2.1163 | 2.1108 | 2.1066 | 2.1004 | 2.0969 | 2.0898 | 2.0763 | 2.0309 | 1.9538 | 1.8611 | 1.8233
FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 0.9442 | 0.94352 | 0.9421 | 0.94067 | 0.93861 | 0.93735 | 0.93603 | 0.93341 | 0.93027 | 0.92688 | 0.92033 | 0.9184 | 0.91811 | 0.91758 | 0.96018 | 0.95971 | 0.95865 | 0.95752 | 0.9559 | 0.95491 | 0.95388 | 0.95182 | 0.94935 | 0.94669 | 0.94154 | 0.94019 | 0.93996 | 0.93955 | 0.95338 | 0.95271 | 0.95129 | 0.94988 | 0.94782 | 0.94657 | 0.94526 | 0.94265 | 0.93953 | 0.93617 | 0.92965 | 0.92767 | 0.92738 | 0.92685
| KINLOCHMOIDART | CT |  |  |  | 0.94425 | 0.94369 | 0.94258 | 0.94067 | 0.93861 | 0.93735 | 0.93603 | 0.93471 | 0.9324 | 0.92906 | 0.92276 | 0.91899 | 0.91818 | 0.91758 | 0.96025 | 0.95981 | 0.95903 | 0.95752 | 0.9559 | 0.95491 | 0.95388 | 0.95284 | 0.95102 | 0.94841 | 0.94346 | 0.94065 | 0.94002 | 0.93955 | 0.95348 | 0.95288 | 0.95178 | 0.94988 | 0.94782 | 0.94657 | 0.94526 | 0.94395 | 0.94165 | 0.93833 | 0.93206 | 0.92826 | 0.92745 | 0.92685
| KINLOCHMOIDART | LW |  |  |  | 0.9442 | 0.94352 | 0.9421 | 0.94092 | 0.9395 | 0.93839 | 0.93611 | 0.93341 | 0.93027 | 0.92688 | 0.92033 | 0.9184 | 0.91811 | 0.91811 | 0.96018 | 0.95971 | 0.95865 | 0.95772 | 0.95661 | 0.95574 | 0.95394 | 0.95182 | 0.94935 | 0.94669 | 0.94154 | 0.94019 | 0.93996 | 0.93996 | 0.95338 | 0.95271 | 0.95129 | 0.95012 | 0.94871 | 0.94761 | 0.94534 | 0.94265 | 0.93953 | 0.93617 | 0.92965 | 0.92767 | 0.92738 | 0.92738
| KINLOCHMOIDART | ST |  |  |  | 0.94427 | 0.94402 | 0.94363 | 0.94309 | 0.94235 | 0.94153 | 0.94051 | 0.93928 | 0.93773 | 0.93583 | 0.93121 | 0.92065 | 0.9189 | 0.91886 | 0.96025 | 0.96006 | 0.95979 | 0.95942 | 0.95885 | 0.9582 | 0.9574 | 0.95643 | 0.95521 | 0.95371 | 0.95008 | 0.94194 | 0.94058 | 0.94054 | 0.95348 | 0.95321 | 0.95281 | 0.95228 | 0.95154 | 0.95073 | 0.94972 | 0.94849 | 0.94695 | 0.94506 | 0.94047 | 0.92991 | 0.92817 | 0.92812
| KINLOCHMOIDART | FS |  |  |  | 0.94429 | 0.94409 | 0.94377 | 0.94334 | 0.94277 | 0.94217 | 0.94144 | 0.94058 | 0.93952 | 0.9383 | 0.93536 | 0.92675 | 0.91891 | 0.91884 | 0.96027 | 0.96011 | 0.95989 | 0.9596 | 0.95918 | 0.95871 | 0.95813 | 0.95745 | 0.95663 | 0.95566 | 0.95335 | 0.9467 | 0.94058 | 0.94053 | 0.95351 | 0.95328 | 0.95295 | 0.95253 | 0.95196 | 0.95136 | 0.95064 | 0.94978 | 0.94873 | 0.94751 | 0.94459 | 0.93599 | 0.92818 | 0.92811
ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | NO | 11.6137 | 11.549 | 11.4636 | 11.3605 | 11.2482 | 11.1155 | 10.9758 | 10.8304 | 10.6931 | 10.5463 | 10.2408 | 10.7856 | 10.5944 | 10.4875 | 11.4222 | 11.3785 | 11.313 | 11.2393 | 11.1453 | 11.0468 | 10.9433 | 10.8414 | 10.7207 | 10.5914 | 10.3309 | 10.368 | 10.1771 | 9.9941 | 11.8298 | 11.8125 | 11.7774 | 11.7305 | 11.6834 | 11.635 | 11.5835 | 11.4256 | 11.2582 | 11.0816 | 10.7222 | 10.7825 | 10.5187 | 10.372
| KINLOSS | CT |  |  |  | 11.6499 | 11.5966 | 11.5213 | 11.3799 | 11.2482 | 11.1155 | 10.9758 | 10.8415 | 10.7235 | 10.616 | 10.3799 | 10.7856 | 10.5944 | 10.4875 | 11.4418 | 11.4086 | 11.3573 | 11.2552 | 11.1453 | 11.0468 | 10.9433 | 10.8507 | 10.7507 | 10.6309 | 10.3933 | 10.368 | 10.1771 | 9.9941 | 11.8306 | 11.8125 | 11.7774 | 11.7305 | 11.6834 | 11.635 | 11.5835 | 11.468 | 11.3552 | 11.1885 | 10.8591 | 10.7825 | 10.5187 | 10.372
| KINLOSS | LW |  |  |  | 11.6137 | 11.549 | 11.4636 | 11.3605 | 11.2491 | 11.1354 | 10.9883 | 10.8304 | 10.6931 | 10.5463 | 10.2408 | 10.8424 | 10.7174 | 10.617 | 11.4222 | 11.3785 | 11.313 | 11.2393 | 11.1571 | 11.0797 | 10.9664 | 10.8414 | 10.7207 | 10.5914 | 10.3309 | 10.4752 | 10.3628 | 10.2532 | 11.8298 | 11.8127 | 11.7838 | 11.7589 | 11.7299 | 11.7009 | 11.5969 | 11.4256 | 11.2582 | 11.0816 | 10.7222 | 10.8349 | 10.6665 | 10.5371
| KINLOSS | ST |  |  |  | 11.6717 | 11.6462 | 11.6214 | 11.5758 | 11.5276 | 11.4764 | 11.4068 | 11.3416 | 11.2568 | 11.1683 | 10.9511 | 11.2238 | 11.0495 | 10.8608 | 11.4534 | 11.4347 | 11.4145 | 11.3741 | 11.3317 | 11.2892 | 11.226 | 11.1716 | 11.0979 | 11.0243 | 10.8464 | 10.6284 | 10.4167 | 10.1859 | 11.8324 | 11.8238 | 11.8134 | 11.7868 | 11.7612 | 11.7356 | 11.6909 | 11.6566 | 11.607 | 11.56 | 11.4451 | 11.39 | 11.1247 | 10.873
| KINLOSS | FS |  |  |  | 11.6795 | 11.6601 | 11.6393 | 11.6086 | 11.5731 | 11.5339 | 11.4922 | 11.4439 | 11.3837 | 11.3204 | 11.1771 | 11.242 | 11.0814 | 10.9442 | 11.4577 | 11.4426 | 11.4246 | 11.3993 | 11.3691 | 11.3365 | 11.3005 | 11.2595 | 11.2072 | 11.1517 | 11.0244 | 10.7855 | 10.4531 | 10.188 | 11.8338 | 11.8268 | 11.8184 | 11.8054 | 11.7905 | 11.7734 | 11.7539 | 11.7327 | 11.7065 | 11.6788 | 11.6137 | 11.5481 | 11.1737 | 10.9961
BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 3.1892 | 3.0329 | 2.8462 | 2.6263 | 2.3821 | 2.1037 | 1.7847 | 1.4599 | 1.2294 | 0.96233 | 0.38077 | 0.23043 | -0.34716 | -0.81877 | 4.6756 | 4.5999 | 4.4951 | 4.3842 | 4.2116 | 4.0431 | 3.8657 | 3.688 | 3.5354 | 3.3514 | 2.9312 | 2.8313 | 2.418 | 1.9973 | 3.7162 | 3.5928 | 3.4435 | 3.2783 | 3.0413 | 2.7798 | 2.5039 | 2.22 | 2.0285 | 1.8076 | 1.2359 | 1.1682 | 0.6442 | 0.26144
| KIPPEN | CT |  |  |  | 3.2747 | 3.1579 | 3.0139 | 2.7245 | 2.4095 | 2.1037 | 1.7847 | 1.4599 | 1.2565 | 1.0181 | 0.48769 | 0.31534 | -0.34716 | -0.79268 | 4.7038 | 4.6392 | 4.5498 | 4.389 | 4.2116 | 4.0431 | 3.8657 | 3.688 | 3.5354 | 3.3514 | 2.9378 | 2.8313 | 2.418 | 1.9973 | 3.7785 | 3.6586 | 3.5147 | 3.28 | 3.0413 | 2.7798 | 2.5039 | 2.22 | 2.0285 | 1.8602 | 1.3377 | 1.1956 | 0.6442 | 0.2687
| KIPPEN | LW |  |  |  | 3.1892 | 3.0329 | 2.8462 | 2.6263 | 2.3821 | 2.1356 | 1.8278 | 1.4708 | 1.2294 | 0.96233 | 0.38077 | 0.23043 | -0.33445 | -0.81877 | 4.6756 | 4.5999 | 4.4951 | 4.3842 | 4.2577 | 4.135 | 3.9595 | 3.744 | 3.5646 | 3.3675 | 2.9312 | 2.976 | 2.6738 | 2.3754 | 3.7162 | 3.5928 | 3.4435 | 3.2783 | 3.0981 | 2.9113 | 2.6437 | 2.3145 | 2.0733 | 1.8076 | 1.2359 | 1.1682 | 0.68828 | 0.26144
| KIPPEN | ST |  |  |  | 3.3075 | 3.2308 | 3.1524 | 3.0288 | 2.8952 | 2.7501 | 2.5741 | 2.392 | 2.1988 | 1.9929 | 1.4802 | 0.86644 | 0.34706 | -0.05235 | 4.7158 | 4.6756 | 4.6317 | 4.5527 | 4.4687 | 4.3798 | 4.2571 | 4.1325 | 3.9946 | 3.8525 | 3.4786 | 3.0296 | 2.6246 | 2.2127 | 3.8062 | 3.7436 | 3.6777 | 3.5695 | 3.4558 | 3.3312 | 3.1702 | 3.0013 | 2.8188 | 2.6267 | 2.0803 | 1.6494 | 1.1911 | 0.85046
| KIPPEN | FS |  |  |  | 3.3412 | 3.2847 | 3.2231 | 3.1352 | 3.0279 | 2.9171 | 2.7967 | 2.6552 | 2.5046 | 2.3404 | 1.9569 | 1.1889 | 0.53293 | 0.23269 | 4.7282 | 4.6959 | 4.6595 | 4.6083 | 4.5457 | 4.4787 | 4.4039 | 4.3105 | 4.2128 | 4.1058 | 3.8369 | 3.3497 | 2.7698 | 2.3133 | 3.8326 | 3.7882 | 3.74 | 3.6673 | 3.5812 | 3.4896 | 3.3891 | 3.2659 | 3.1361 | 2.9951 | 2.652 | 2.0287 | 1.4125 | 1.1771
THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | NO | 11.0344 | -2.1412 | -23.3479 | -24.5878 | -26.1125 | -27.6631 | -29.9321 | -30.9404 | -31.3623 | -31.8355 | -32.8357 | -32.371 | -33.125 | -33.9017 | 14.8241 | -1.2285 | -27.2979 | -28.3246 | -29.6285 | -30.9998 | -33.1221 | -33.745 | -34.089 | -34.5081 | -35.4221 | -34.7339 | -35.3748 | -36.1306 | 12.9742 | -3.0629 | -29.0744 | -30.0336 | -31.5384 | -33.0875 | -35.3074 | -36.3202 | -36.7959 | -37.3282 | -38.4394 | -38.0775 | -38.8699 | -39.7215
| KIRKWALL | CT |  |  |  | 18.2767 | 15.7488 | 12.0299 | 10.7058 | 9.1206 | 7.5455 | 5.3662 | 4.3918 | 4.0719 | 3.6914 | 2.9098 | 3.4267 | 2.7277 | 2.1493 | 23.7184 | 20.8831 | 16.5747 | 15.625 | 14.4086 | 13.1687 | 11.2706 | 10.7686 | 10.416 | 10.0694 | 9.3234 | 9.6663 | 8.9784 | 8.1531 | 21.8673 | 19.0427 | 14.7837 | 13.907 | 12.4078 | 10.8807 | 8.8343 | 7.9387 | 7.5812 | 7.1413 | 6.2494 | 6.6039 | 5.9265 | 5.3441
| KIRKWALL | LW |  |  |  | 11.0344 | -2.1412 | -23.3479 | -24.5878 | -26.1125 | -27.6631 | -29.9321 | -30.9404 | -31.3623 | -31.8355 | -32.8357 | -32.371 | -33.125 | -33.9017 | 14.8241 | -1.2285 | -27.2979 | -28.3246 | -29.6285 | -30.9998 | -33.1221 | -33.745 | -34.089 | -34.5081 | -35.4221 | -34.7339 | -35.3748 | -36.1306 | 12.9742 | -3.0629 | -29.0744 | -30.0336 | -31.5384 | -33.0875 | -35.3074 | -36.3202 | -36.7959 | -37.3282 | -38.4394 | -38.0775 | -38.8699 | -39.7215
| KIRKWALL | ST |  |  |  | 13.629 | 7.1103 | -5.9771 | -6.8124 | -7.8582 | -8.8032 | -10.4798 | -11.0115 | -11.4284 | -11.883 | -12.9633 | -13.1807 | -13.7139 | -14.3025 | 17.6746 | 9.7222 | -6.4331 | -7.4047 | -8.5945 | -9.6658 | -11.5724 | -12.0165 | -12.2983 | -12.639 | -13.4292 | -13.1335 | -13.6528 | -14.4856 | 15.8304 | 7.8988 | -8.1913 | -9.095 | -10.2205 | -11.2281 | -13.0184 | -13.458 | -13.7526 | -14.0532 | -14.754 | -14.9768 | -15.5918 | -16.2058
| KIRKWALL | FS |  |  |  | 20.1585 | 19.0885 | 17.6039 | 16.9783 | 16.1322 | 15.3483 | 14.2571 | 13.7897 | 13.3819 | 12.8874 | 11.9077 | 10.1882 | 8.9578 | 8.6573 | 25.7726 | 24.5967 | 22.9043 | 22.244 | 21.3438 | 20.5098 | 19.3181 | 18.8535 | 18.4592 | 17.954 | 17.1056 | 16.234 | 15.0263 | 13.9943 | 23.9344 | 22.7743 | 21.1322 | 20.523 | 19.6783 | 18.8961 | 17.7872 | 17.3397 | 16.9484 | 16.4619 | 15.619 | 14.3337 | 13.0427 | 12.7795
BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | NO | 0.15284 | 0.12555 | 0.095176 | 0.056574 | 0.019487 | -0.028913 | -0.089066 | -0.16268 | -0.21563 | -0.2726 | -0.38302 | -0.41301 | -0.45756 | -0.4933 | 0.018293 | 0.0025454 | -0.023078 | -0.049474 | -0.087468 | -0.11854 | -0.14929 | -0.19233 | -0.23508 | -0.28116 | -0.37035 | -0.39128 | -0.42589 | -0.45853 | -0.18777 | -0.21141 | -0.23888 | -0.27339 | -0.30669 | -0.34481 | -0.38611 | -0.43091 | -0.45021 | -0.47397 | -0.52136 | -0.48315 | -0.52251 | -0.55482
| KISHORNHILL | CT |  |  |  | 0.16418 | 0.14379 | 0.12384 | 0.075616 | 0.026784 | -0.028913 | -0.089066 | -0.15275 | -0.19091 | -0.24761 | -0.35571 | -0.38837 | -0.45756 | -0.4933 | 0.024656 | 0.012399 | -0.0067765 | -0.045885 | -0.087468 | -0.11854 | -0.14929 | -0.18128 | -0.21292 | -0.25922 | -0.34706 | -0.3878 | -0.42589 | -0.45853 | -0.17787 | -0.19686 | -0.21533 | -0.25729 | -0.30101 | -0.34466 | -0.38611 | -0.43091 | -0.44641 | -0.46276 | -0.49968 | -0.46049 | -0.52251 | -0.55482
| KISHORNHILL | LW |  |  |  | 0.15284 | 0.12555 | 0.095176 | 0.056574 | 0.019487 | -0.023153 | -0.085872 | -0.16268 | -0.21563 | -0.2726 | -0.38302 | -0.41301 | -0.45191 | -0.46268 | 0.018293 | 0.0025454 | -0.023078 | -0.049474 | -0.078362 | -0.10517 | -0.1453 | -0.19233 | -0.23508 | -0.28116 | -0.37035 | -0.39128 | -0.40641 | -0.41016 | -0.18777 | -0.21141 | -0.23888 | -0.27339 | -0.30669 | -0.34481 | -0.38383 | -0.42831 | -0.45021 | -0.47397 | -0.52136 | -0.48315 | -0.51754 | -0.52675
| KISHORNHILL | ST |  |  |  | 0.17478 | 0.16868 | 0.15995 | 0.15081 | 0.13731 | 0.12207 | 0.10672 | 0.088166 | 0.067368 | 0.036947 | -0.057203 | -0.2477 | -0.30864 | -0.34387 | 0.032336 | 0.026068 | 0.018235 | 0.0090931 | -0.0044199 | -0.019083 | -0.035785 | -0.056022 | -0.080322 | -0.10985 | -0.17928 | -0.33058 | -0.37183 | -0.39923 | -0.16625 | -0.17356 | -0.18177 | -0.1902 | -0.20259 | -0.21661 | -0.23089 | -0.24817 | -0.26766 | -0.29067 | -0.34273 | -0.33389 | -0.39052 | -0.42129
| KISHORNHILL | FS |  |  |  | 0.17617 | 0.17284 | 0.1666 | 0.15512 | 0.14407 | 0.12989 | 0.11584 | 0.10023 | 0.07976 | 0.061477 | 0.0033034 | -0.19712 | -0.36399 | -0.39041 | 0.033558 | 0.02908 | 0.022198 | 0.012855 | 0.0024308 | -0.009889 | -0.023402 | -0.038804 | -0.057852 | -0.078142 | -0.12597 | -0.26209 | -0.3938 | -0.42713 | -0.16389 | -0.16862 | -0.17572 | -0.18611 | -0.19619 | -0.20908 | -0.22195 | -0.23582 | -0.2534 | -0.27015 | -0.30756 | -0.32628 | -0.43914 | -0.46225
BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | NO | 4.416 | 4.3699 | 2.5154 | 2.4464 | 2.349 | 2.2113 | 2.0738 | 1.974 | 1.9104 | 1.8312 | 1.6887 | 1.6064 | 1.4278 | 1.2718 | 4.8717 | 4.8491 | 3.5188 | 3.4809 | 3.4148 | 3.3108 | 3.2038 | 3.1442 | 3.0852 | 3.0153 | 2.8858 | 2.7324 | 2.5048 | 2.254 | 3.9856 | 3.9464 | 2.5982 | 2.5394 | 2.4459 | 2.3109 | 2.1743 | 2.0849 | 2.0151 | 1.9289 | 1.7721 | 1.6443 | 1.4517 | 1.2706
| KYLE | CT |  |  |  | 4.4392 | 4.4048 | 2.5701 | 2.4627 | 2.349 | 2.2113 | 2.0738 | 1.974 | 1.9104 | 1.8312 | 1.6887 | 1.6064 | 1.4278 | 1.2718 | 4.8783 | 4.8603 | 3.5393 | 3.4809 | 3.4148 | 3.3108 | 3.2038 | 3.1442 | 3.0852 | 3.0153 | 2.8858 | 2.7324 | 2.5544 | 2.3595 | 4.0036 | 3.9736 | 2.642 | 2.5478 | 2.4459 | 2.3109 | 2.1743 | 2.0849 | 2.0151 | 1.9289 | 1.7721 | 1.6443 | 1.4517 | 1.2735
| KYLE | LW |  |  |  | 4.416 | 4.3699 | 2.5154 | 2.4464 | 2.3716 | 2.3015 | 2.2131 | 2.1143 | 2.0465 | 1.9783 | 1.8444 | 1.8295 | 1.5873 | 1.2778 | 4.8717 | 4.8491 | 3.5188 | 3.4845 | 3.4466 | 3.412 | 3.3632 | 3.3078 | 3.2547 | 3.1996 | 3.0921 | 3.0496 | 2.7858 | 2.414 | 3.9856 | 3.9464 | 2.5982 | 2.5394 | 2.4751 | 2.4157 | 2.3369 | 2.2483 | 2.1778 | 2.1058 | 1.9656 | 1.933 | 1.6496 | 1.2706
| KYLE | ST |  |  |  | 4.4756 | 4.4647 | 2.6557 | 2.5976 | 2.551 | 2.5068 | 2.4209 | 2.3768 | 2.2882 | 2.229 | 2.0899 | 1.8164 | 1.6074 | 1.3972 | 4.8913 | 4.8851 | 3.5786 | 3.5158 | 3.4674 | 3.4282 | 3.3305 | 3.2885 | 3.2002 | 3.148 | 3.0261 | 2.7504 | 2.5048 | 2.254 | 4.0328 | 4.0232 | 2.7147 | 2.647 | 2.594 | 2.5471 | 2.445 | 2.3968 | 2.2976 | 2.235 | 2.0885 | 1.7828 | 1.5369 | 1.2945
| KYLE | FS |  |  |  | 4.4847 | 4.4726 | 2.6605 | 2.6281 | 2.5934 | 2.5617 | 2.5259 | 2.4858 | 2.4402 | 2.3968 | 2.3021 | 2.0959 | 1.9265 | 1.8728 | 4.8954 | 4.889 | 3.5818 | 3.5596 | 3.536 | 3.5113 | 3.4842 | 3.4558 | 3.4151 | 3.3789 | 3.2992 | 3.1454 | 2.9931 | 2.9078 | 4.0397 | 4.0297 | 2.7191 | 2.6883 | 2.6549 | 2.623 | 2.5874 | 2.5485 | 2.5002 | 2.4555 | 2.3579 | 2.1568 | 1.9877 | 1.9366
LAIRG | LAIRG GRID | MINIMUM HEADROOM | NC 58798 07111 | YES | NO | -0.24751 | -0.32712 | -0.34436 | -0.4054 | -0.48482 | -0.58907 | -0.7212 | -0.81517 | -0.87935 | -0.95447 | -1.1064 | -1.2735 | -1.5165 | -1.7362 | 0.21525 | 0.13795 | 0.10051 | 0.067737 | 0.014699 | -0.081671 | -0.18359 | -0.23812 | -0.30036 | -0.37513 | -0.51397 | -0.72464 | -0.97807 | -1.213 | -0.34997 | -0.4285 | -0.4812 | -0.53364 | -0.59574 | -0.71333 | -0.83783 | -0.9161 | -0.98607 | -1.0712 | -1.2264 | -1.4285 | -1.7091 | -1.953
| LAIRG GRID | CT |  |  |  | -0.24751 | -0.3205 | -0.33478 | -0.35877 | -0.46114 | -0.58907 | -0.7212 | -0.81517 | -0.87935 | -0.95447 | -1.1064 | -1.2735 | -1.4918 | -1.6434 | 0.22805 | 0.16093 | 0.13402 | 0.078129 | 0.014699 | -0.081671 | -0.18359 | -0.23812 | -0.30036 | -0.37513 | -0.51397 | -0.69007 | -0.87325 | -1.0439 | -0.3242 | -0.38991 | -0.42602 | -0.50551 | -0.59371 | -0.71333 | -0.83783 | -0.9161 | -0.98607 | -1.0712 | -1.2264 | -1.4248 | -1.6424 | -1.8123
| LAIRG GRID | LW |  |  |  | -0.24746 | -0.32712 | -0.34436 | -0.4054 | -0.48482 | -0.55543 | -0.63735 | -0.72318 | -0.78501 | -0.84791 | -0.99183 | -1.0802 | -1.3221 | -1.6171 | 0.21525 | 0.13795 | 0.10051 | 0.067737 | 0.026777 | -0.0086471 | -0.056579 | -0.10972 | -0.16671 | -0.22641 | -0.34111 | -0.40927 | -0.66671 | -1.0189 | -0.34997 | -0.4285 | -0.4812 | -0.53364 | -0.59574 | -0.64988 | -0.71936 | -0.79413 | -0.86069 | -0.92926 | -1.0616 | -1.1635 | -1.4398 | -1.7991
| LAIRG GRID | ST |  |  |  | -0.24386 | -0.3092 | -0.31685 | -0.36601 | -0.40345 | -0.43085 | -0.52889 | -0.58764 | -0.68048 | -0.74755 | -0.89624 | -1.2512 | -1.5165 | -1.7362 | 0.23156 | 0.17507 | 0.15907 | 0.089452 | 0.033112 | -0.010518 | -0.11559 | -0.16255 | -0.25062 | -0.30567 | -0.43116 | -0.72464 | -0.97807 | -1.213 | -0.31907 | -0.36975 | -0.39268 | -0.47063 | -0.53604 | -0.588 | -0.70408 | -0.76088 | -0.85929 | -0.92518 | -1.0737 | -1.4285 | -1.7091 | -1.953
| LAIRG GRID | FS |  |  |  | -0.24301 | -0.29237 | -0.29717 | -0.31319 | -0.33011 | -0.34673 | -0.3643 | -0.38787 | -0.44782 | -0.50428 | -0.6277 | -0.93426 | -1.1482 | -1.2133 | 0.2364 | 0.19495 | 0.18336 | 0.15543 | 0.12671 | 0.097513 | 0.066429 | 0.034657 | -0.011771 | -0.053646 | -0.14558 | -0.3398 | -0.49417 | -0.56197 | -0.30994 | -0.34512 | -0.36204 | -0.39834 | -0.43413 | -0.47096 | -0.50986 | -0.55009 | -0.6065 | -0.65854 | -0.77273 | -1.0451 | -1.2327 | -1.2901
MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | NO | 0.87692 | 0.7794 | 0.66455 | 0.4729 | 0.33074 | 0.1308 | -0.12687 | -0.30931 | -0.4483 | -0.60906 | -0.90869 | -1.3475 | -2.1283 | -2.9936 | 1.5774 | 1.5375 | 1.4817 | 1.3636 | 1.2778 | 1.092 | 0.89413 | 0.78998 | 0.65789 | 0.51086 | 0.23703 | -0.36953 | -1.2058 | -2.0907 | 1.0435 | 0.97075 | 0.88085 | 0.74148 | 0.63252 | 0.40956 | 0.16592 | 0.015639 | -0.1322 | -0.30416 | -0.62216 | -1.1924 | -2.0911 | -3.086
| LATHERON | CT |  |  |  | 0.9478 | 0.88165 | 0.80526 | 0.57233 | 0.38106 | 0.1308 | -0.12687 | -0.30931 | -0.4483 | -0.60906 | -0.90869 | -1.3475 | -1.979 | -2.4902 | 1.5999 | 1.5713 | 1.5328 | 1.3903 | 1.281 | 1.092 | 0.89413 | 0.78998 | 0.65789 | 0.51086 | 0.23703 | -0.26259 | -0.84096 | -1.4391 | 1.0938 | 1.044 | 0.98351 | 0.80371 | 0.64444 | 0.40956 | 0.16592 | 0.015639 | -0.1322 | -0.30416 | -0.62216 | -1.1567 | -1.8149 | -2.4138
| LATHERON | LW |  |  |  | 0.87692 | 0.7794 | 0.66455 | 0.4729 | 0.33074 | 0.20144 | 0.045507 | -0.11913 | -0.2494 | -0.39161 | -0.65031 | -0.99159 | -1.8719 | -2.9936 | 1.5774 | 1.5375 | 1.4817 | 1.3636 | 1.2957 | 1.233 | 1.1529 | 1.0667 | 0.95122 | 0.82756 | 0.59613 | 0.25963 | -0.72309 | -2.0907 | 1.0435 | 0.97075 | 0.88085 | 0.74148 | 0.63252 | 0.53522 | 0.41095 | 0.27764 | 0.14166 | -0.0053554 | -0.27329 | -0.6726 | -1.7043 | -3.086
| LATHERON | ST |  |  |  | 0.96955 | 0.92053 | 0.87194 | 0.66886 | 0.54054 | 0.43105 | 0.22313 | 0.10797 | -0.12701 | -0.26701 | -0.57983 | -1.3196 | -2.1283 | -2.8822 | 1.6064 | 1.5872 | 1.5664 | 1.3848 | 1.2778 | 1.1939 | 0.99137 | 0.9035 | 0.6757 | 0.56139 | 0.30384 | -0.36953 | -1.2058 | -2.0515 | 1.1092 | 1.0734 | 1.037 | 0.84789 | 0.72258 | 0.62055 | 0.3982 | 0.29038 | 0.039719 | -0.097185 | -0.40472 | -1.1924 | -2.0911 | -2.9609
| LATHERON | FS |  |  |  | 0.99845 | 0.96403 | 0.92605 | 0.815 | 0.73084 | 0.65203 | 0.56559 | 0.48396 | 0.34953 | 0.22504 | -0.024286 | -0.61892 | -0.99602 | -1.1704 | 1.6155 | 1.6013 | 1.5847 | 1.5063 | 1.4506 | 1.3965 | 1.335 | 1.2808 | 1.1746 | 1.0802 | 0.89406 | 0.5553 | 0.28038 | 0.11587 | 1.1294 | 1.1039 | 1.0751 | 0.98718 | 0.91562 | 0.84582 | 0.77009 | 0.69817 | 0.5695 | 0.45593 | 0.22464 | -0.29041 | -0.63269 | -0.79195
FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | NO | 1.1729 | 0.99414 | 0.76408 | 0.32903 | -0.14559 | -0.76083 | -1.965 | -2.7895 | -3.1629 | -3.5317 | -4.2861 | -4.5792 | -5.2895 | -5.9839 | 2.8216 | 2.7353 | 2.6098 | 2.2996 | 1.9553 | 1.4324 | 0.38482 | -0.2772 | -0.54031 | -0.81436 | -1.3697 | -1.5253 | -2.1556 | -2.9182 | 2.3896 | 2.2274 | 2.029 | 1.5932 | 1.123 | 0.47108 | -0.77728 | -1.5842 | -1.9105 | -2.2304 | -2.8789 | -3.1648 | -3.942 | -4.7623
| LAURENCEKIRK | CT |  |  |  | 1.3047 | 1.1895 | 1.0253 | 0.63951 | 0.2116 | -0.3637 | -1.4395 | -2.0677 | -2.4465 | -2.8412 | -3.6008 | -4.1206 | -4.9427 | -5.4627 | 2.8692 | 2.8044 | 2.7022 | 2.4727 | 2.2011 | 1.7224 | 0.80505 | 0.35281 | 0.083894 | -0.20011 | -0.75732 | -1.1441 | -1.7681 | -2.3914 | 2.4477 | 2.4102 | 2.271 | 1.9185 | 1.525 | 0.91673 | -0.20462 | -0.80633 | -1.1512 | -1.4992 | -2.1667 | -2.6328 | -3.4405 | -3.9781
| LAURENCEKIRK | LW |  |  |  | 1.1729 | 0.99414 | 0.76408 | 0.32903 | -0.14559 | -0.76083 | -1.965 | -2.7895 | -3.1629 | -3.5317 | -4.2861 | -4.5792 | -5.2895 | -5.9839 | 2.8216 | 2.7353 | 2.6098 | 2.2996 | 1.9553 | 1.4324 | 0.38482 | -0.2772 | -0.54031 | -0.81436 | -1.3697 | -1.5253 | -2.1556 | -2.9182 | 2.3896 | 2.2274 | 2.029 | 1.5932 | 1.123 | 0.47108 | -0.77728 | -1.5842 | -1.9105 | -2.2304 | -2.8789 | -3.1648 | -3.942 | -4.7623
| LAURENCEKIRK | ST |  |  |  | 1.3645 | 1.3004 | 1.2282 | 0.90241 | 0.6397 | 0.41773 | -0.51718 | -0.96716 | -1.2749 | -1.528 | -2.076 | -2.9972 | -3.8606 | -4.6904 | 2.8921 | 2.8567 | 2.8141 | 2.4755 | 2.2182 | 2.0178 | 1.0862 | 0.68097 | 0.41197 | 0.2169 | -0.21523 | -0.9508 | -1.7195 | -2.5382 | 2.4508 | 2.4361 | 2.4162 | 2.0923 | 1.8102 | 1.5832 | 0.54842 | 0.098852 | -0.20256 | -0.42855 | -0.90683 | -1.638 | -2.5348 | -3.4371
| LAURENCEKIRK | FS |  |  |  | 1.3904 | 1.344 | 1.2932 | 1.1541 | 1.0084 | 0.85588 | 0.42803 | 0.097691 | -0.13437 | -0.36124 | -0.81501 | -1.8054 | -2.7675 | -3.2348 | 2.9024 | 2.8745 | 2.8416 | 2.7332 | 2.6178 | 2.4911 | 2.1197 | 1.8377 | 1.6602 | 1.4916 | 1.1493 | 0.48277 | -0.33368 | -0.96388 | 2.4537 | 2.4427 | 2.4281 | 2.3506 | 2.2423 | 2.0928 | 1.6487 | 1.3246 | 1.1057 | 0.89712 | 0.49147 | -0.31291 | -1.1197 | -1.5847
STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | NO | -0.97578 | -1.055 | -1.148 | -1.2574 | -1.3757 | -1.5434 | -1.7198 | -1.8667 | -1.9731 | -2.1043 | -2.348 | -2.5523 | -3.0681 | -3.8272 | -0.070461 | -0.085073 | -0.10824 | -0.14259 | -0.19356 | -0.30173 | -0.41601 | -0.495 | -0.58747 | -0.70234 | -0.94149 | -1.2296 | -1.7916 | -2.6619 | -0.77719 | -0.8377 | -0.91575 | -1.0022 | -1.1195 | -1.2666 | -1.4216 | -1.5405 | -1.6609 | -1.8116 | -2.091 | -2.3856 | -2.9594 | -3.8926
| LAXAY | CT |  |  |  | -0.92801 | -0.98314 | -1.052 | -1.2108 | -1.3757 | -1.5434 | -1.7198 | -1.8667 | -1.9731 | -2.1043 | -2.348 | -2.5523 | -2.976 | -3.3262 | -0.070379 | -0.085073 | -0.10824 | -0.14259 | -0.19356 | -0.30173 | -0.41601 | -0.495 | -0.58747 | -0.70234 | -0.94149 | -1.2296 | -1.6185 | -2.0348 | -0.74519 | -0.78881 | -0.84862 | -0.97948 | -1.1195 | -1.2666 | -1.4216 | -1.5405 | -1.6609 | -1.8116 | -2.091 | -2.3856 | -2.8212 | -3.2302
| LAXAY | LW |  |  |  | -0.97578 | -1.055 | -1.148 | -1.2574 | -1.371 | -1.4808 | -1.6187 | -1.7664 | -1.8913 | -2.0236 | -2.275 | -2.4745 | -3.0681 | -3.8272 | -0.070461 | -0.083366 | -0.099291 | -0.11301 | -0.16375 | -0.21574 | -0.28768 | -0.36693 | -0.47304 | -0.59959 | -0.83864 | -1.0718 | -1.738 | -2.6619 | -0.77719 | -0.8377 | -0.91575 | -1.0022 | -1.0945 | -1.1802 | -1.2994 | -1.4303 | -1.5712 | -1.7207 | -2.0041 | -2.2639 | -2.9594 | -3.8926
| LAXAY | ST |  |  |  | -0.90214 | -0.93538 | -0.96898 | -1.0459 | -1.1204 | -1.1869 | -1.2938 | -1.3709 | -1.5274 | -1.635 | -1.8866 | -2.4021 | -2.9401 | -3.4528 | -0.065564 | -0.070387 | -0.075541 | -0.12284 | -0.15922 | -0.18811 | -0.2636 | -0.29753 | -0.42846 | -0.51868 | -0.73085 | -1.225 | -1.7916 | -2.3695 | -0.72771 | -0.75268 | -0.77935 | -0.85539 | -0.9265 | -0.98867 | -1.1007 | -1.1747 | -1.3456 | -1.4576 | -1.72 | -2.3081 | -2.9094 | -3.4939
| LAXAY | FS |  |  |  | -0.88842 | -0.91064 | -0.93558 | -0.98372 | -1.0342 | -1.0863 | -1.1419 | -1.1979 | -1.2899 | -1.3768 | -1.5643 | -2.0153 | -2.3341 | -2.4579 | -0.064192 | -0.067494 | -0.071309 | -0.084624 | -0.099193 | -0.11599 | -0.13424 | -0.15273 | -0.20152 | -0.25332 | -0.39147 | -0.68885 | -0.94782 | -1.0684 | -0.71813 | -0.73519 | -0.75506 | -0.7955 | -0.83918 | -0.88501 | -0.93465 | -0.98565 | -1.0763 | -1.1603 | -1.3434 | -1.7706 | -2.0963 | -2.2068
COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | NO | -2.5129 | -2.6185 | -2.7539 | -2.9411 | -3.1333 | -3.3594 | -3.661 | -3.8926 | -4.1546 | -4.4539 | -5.0397 | -5.5547 | -6.2892 | -7.2598 | -0.9764 | -1.029 | -1.1033 | -1.195 | -1.3223 | -1.5528 | -1.793 | -1.9376 | -2.141 | -2.37 | -2.8141 | -3.3099 | -4.176 | -5.329 | -1.7382 | -1.8342 | -1.9598 | -2.1298 | -2.3055 | -2.5673 | -2.8804 | -3.1018 | -3.3694 | -3.6738 | -4.266 | -4.8368 | -5.6346 | -6.878
| LEOCH | CT |  |  |  | -2.4375 | -2.5004 | -2.5959 | -2.8203 | -3.0627 | -3.3594 | -3.661 | -3.8926 | -4.1546 | -4.4539 | -5.0397 | -5.5547 | -6.2892 | -6.8974 | -0.94829 | -0.98532 | -1.0449 | -1.1748 | -1.3223 | -1.5528 | -1.793 | -1.9376 | -2.141 | -2.37 | -2.8141 | -3.3099 | -4.0706 | -4.9138 | -1.6719 | -1.7301 | -1.8199 | -2.0307 | -2.2617 | -2.5673 | -2.8804 | -3.1018 | -3.3694 | -3.6738 | -4.266 | -4.8368 | -5.6346 | -6.3398
| LEOCH | LW |  |  |  | -2.5129 | -2.6185 | -2.7539 | -2.9411 | -3.1333 | -3.3203 | -3.5575 | -3.8111 | -4.0724 | -4.343 | -4.8836 | -5.1084 | -6.0695 | -7.2598 | -0.9764 | -1.029 | -1.1033 | -1.195 | -1.2919 | -1.3846 | -1.513 | -1.6545 | -1.8436 | -2.0425 | -2.4316 | -2.6156 | -3.6804 | -5.1341 | -1.7382 | -1.8342 | -1.9598 | -2.1298 | -2.3055 | -2.4755 | -2.6953 | -2.9319 | -3.1942 | -3.4668 | -4.0072 | -4.2658 | -5.4062 | -6.878
| LEOCH | ST |  |  |  | -2.4022 | -2.4382 | -2.4811 | -2.6313 | -2.7601 | -2.8696 | -3.0946 | -3.2263 | -3.4803 | -3.6576 | -4.0639 | -4.8173 | -5.7796 | -6.7451 | -0.92989 | -0.95087 | -0.97671 | -1.1269 | -1.2461 | -1.3415 | -1.5729 | -1.6834 | -1.943 | -2.0954 | -2.4465 | -3.1326 | -4.176 | -5.329 | -1.6399 | -1.6729 | -1.7124 | -1.8816 | -2.0218 | -2.1377 | -2.3938 | -2.5308 | -2.8182 | -3.0039 | -3.4293 | -4.2422 | -5.3236 | -6.4156
| LEOCH | FS |  |  |  | -2.3857 | -2.4099 | -2.4415 | -2.508 | -2.5824 | -2.6586 | -2.7453 | -2.8282 | -2.9721 | -3.1125 | -3.4132 | -3.9934 | -4.5843 | -4.9389 | -0.92277 | -0.9386 | -0.95909 | -1.0111 | -1.0685 | -1.1307 | -1.1994 | -1.2667 | -1.3938 | -1.5082 | -1.757 | -2.1711 | -2.7272 | -3.3495 | -1.6252 | -1.6476 | -1.6767 | -1.7441 | -1.8192 | -1.8973 | -1.9852 | -2.0694 | -2.2212 | -2.3643 | -2.6706 | -3.2218 | -3.7856 | -4.1243
NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | NO | 0.15582 | 0.080857 | -0.0067266 | -0.099604 | -0.1942 | -0.38102 | -0.58892 | -0.72424 | -0.82543 | -0.93989 | -1.1554 | -1.4238 | -1.925 | -2.3505 | 0.87082 | 0.83781 | 0.79349 | 0.7322 | 0.63701 | 0.49661 | 0.32147 | 0.23602 | 0.13374 | 0.027071 | -0.18102 | -0.58159 | -1.0747 | -1.5505 | 0.62069 | 0.58355 | 0.53157 | 0.46136 | 0.36835 | 0.19285 | 0.0067526 | -0.10965 | -0.22758 | -0.34067 | -0.57067 | -0.90907 | -1.4372 | -1.9028
| LETHEN | CT |  |  |  | 0.20746 | 0.15198 | 0.089913 | -0.033489 | -0.17881 | -0.38102 | -0.58892 | -0.72424 | -0.82543 | -0.93989 | -1.1554 | -1.3749 | -1.7788 | -2.0609 | 0.88915 | 0.86287 | 0.82735 | 0.75375 | 0.66346 | 0.49661 | 0.32147 | 0.23602 | 0.13826 | 0.027071 | -0.18102 | -0.46899 | -0.82368 | -1.1653 | 0.63672 | 0.6008 | 0.54925 | 0.46136 | 0.36835 | 0.19285 | 0.0067526 | -0.10965 | -0.22758 | -0.34067 | -0.57067 | -0.81785 | -1.207 | -1.5287
| LETHEN | LW |  |  |  | 0.15582 | 0.080857 | -0.0067266 | -0.099604 | -0.1942 | -0.28594 | -0.3971 | -0.51669 | -0.60508 | -0.69213 | -0.87413 | -0.95696 | -1.4378 | -2.0307 | 0.87082 | 0.83781 | 0.79349 | 0.7496 | 0.70275 | 0.65933 | 0.598 | 0.52963 | 0.45257 | 0.37254 | 0.21474 | 0.12257 | -0.39091 | -1.0998 | 0.62069 | 0.58355 | 0.53157 | 0.48339 | 0.43121 | 0.37823 | 0.28991 | 0.18544 | 0.078387 | -0.035505 | -0.26764 | -0.26866 | -0.80988 | -1.5284
| LETHEN | ST |  |  |  | 0.21988 | 0.18194 | 0.14274 | 0.010267 | -0.09663 | -0.19253 | -0.37719 | -0.47467 | -0.64264 | -0.74817 | -0.98431 | -1.4238 | -1.925 | -2.3505 | 0.89356 | 0.87663 | 0.85812 | 0.7322 | 0.63701 | 0.56151 | 0.37277 | 0.29367 | 0.13374 | 0.046656 | -0.15135 | -0.58159 | -1.0747 | -1.5505 | 0.64287 | 0.62448 | 0.60493 | 0.47659 | 0.37842 | 0.2978 | 0.101 | 0.011594 | -0.16036 | -0.26384 | -0.51121 | -0.90907 | -1.4372 | -1.9028
| LETHEN | FS |  |  |  | 0.24453 | 0.21348 | 0.18847 | 0.13446 | 0.072211 | 0.0068146 | -0.060443 | -0.1163 | -0.22011 | -0.30671 | -0.49108 | -0.88568 | -1.1467 | -1.281 | 0.90228 | 0.88816 | 0.87503 | 0.83623 | 0.79301 | 0.74581 | 0.69657 | 0.65221 | 0.57394 | 0.50959 | 0.37158 | 0.13022 | -0.073598 | -0.20719 | 0.65058 | 0.63616 | 0.62187 | 0.5821 | 0.53749 | 0.48805 | 0.43559 | 0.38589 | 0.30371 | 0.23304 | 0.079541 | -0.16796 | -0.43884 | -0.54609
GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0.11124 | 0.1112 | 0.10922 | 0.10917 | 0.10912 | 0.10712 | 0.10702 | 0.10681 | 0.10624 | 0.10095 | 0.10068 | 0.10155 | 0.099611 | 0.099992 | 0.11244 | 0.11241 | 0.11169 | 0.11166 | 0.11162 | 0.1109 | 0.11063 | 0.11014 | 0.10957 | 0.10838 | 0.10682 | 0.10903 | 0.10835 | 0.1085 | 0.11158 | 0.11144 | 0.11007 | 0.11003 | 0.10979 | 0.10818 | 0.10775 | 0.10727 | 0.10666 | 0.10256 | 0.10181 | 0.10336 | 0.10166 | 0.10195
| LETTEREWE | CT |  |  |  | 0.11124 | 0.1112 | 0.11115 | 0.11094 | 0.11066 | 0.10902 | 0.10702 | 0.10695 | 0.10662 | 0.10095 | 0.10068 | 0.10155 | 0.099611 | 0.10155 | 0.11244 | 0.11241 | 0.11226 | 0.11196 | 0.11177 | 0.11129 | 0.11063 | 0.11034 | 0.10995 | 0.10838 | 0.1076 | 0.10903 | 0.10835 | 0.10903 | 0.11158 | 0.11144 | 0.1112 | 0.11081 | 0.11056 | 0.10928 | 0.10775 | 0.10747 | 0.10709 | 0.10256 | 0.10181 | 0.10336 | 0.10166 | 0.10336
| LETTEREWE | LW |  |  |  | 0.11124 | 0.11121 | 0.10922 | 0.10917 | 0.10912 | 0.10712 | 0.10702 | 0.10681 | 0.10624 | 0.10399 | 0.10109 | 0.10155 | 0.10155 | 0.10155 | 0.11244 | 0.11242 | 0.11169 | 0.11166 | 0.11162 | 0.1109 | 0.11064 | 0.11014 | 0.10957 | 0.10852 | 0.10682 | 0.10903 | 0.10903 | 0.10903 | 0.11158 | 0.11149 | 0.11007 | 0.11003 | 0.10979 | 0.10818 | 0.10777 | 0.10727 | 0.10666 | 0.1047 | 0.10205 | 0.10336 | 0.10336 | 0.10336
| LETTEREWE | ST |  |  |  | 0.11125 | 0.11123 | 0.11122 | 0.11119 | 0.11117 | 0.11113 | 0.111 | 0.11067 | 0.11026 | 0.10862 | 0.10484 | 0.10193 | 0.099992 | 0.099992 | 0.11244 | 0.11243 | 0.11242 | 0.1124 | 0.11234 | 0.11219 | 0.11201 | 0.11178 | 0.11147 | 0.11085 | 0.10919 | 0.10918 | 0.1085 | 0.1085 | 0.11159 | 0.11156 | 0.11151 | 0.11142 | 0.1113 | 0.11111 | 0.11087 | 0.11057 | 0.1102 | 0.10871 | 0.10566 | 0.10364 | 0.10195 | 0.10195
| LETTEREWE | FS |  |  |  | 0.11125 | 0.11124 | 0.11122 | 0.11121 | 0.11119 | 0.11116 | 0.11114 | 0.11108 | 0.11085 | 0.11057 | 0.10699 | 0.10156 | 0.099997 | 0.099992 | 0.11244 | 0.11244 | 0.11243 | 0.11241 | 0.1124 | 0.11233 | 0.11221 | 0.11207 | 0.1119 | 0.1117 | 0.11053 | 0.10904 | 0.1085 | 0.1085 | 0.11159 | 0.11157 | 0.11154 | 0.11147 | 0.11139 | 0.11128 | 0.11113 | 0.11094 | 0.11073 | 0.11047 | 0.10766 | 0.10336 | 0.10196 | 0.10195
ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | NO | 5.213 | 5.074 | 4.9138 | 4.7441 | 4.572 | 4.4067 | 4.2138 | 4.008 | 3.8523 | 3.6886 | 3.3659 | 3.0592 | 2.607 | 2.3628 | 5.5352 | 5.4687 | 5.3838 | 5.3074 | 5.2262 | 5.1259 | 4.997 | 4.8994 | 4.7873 | 4.6554 | 4.3996 | 4.1784 | 3.8738 | 3.5729 | 5.4427 | 5.3275 | 5.1912 | 5.0399 | 4.8854 | 4.7374 | 4.5619 | 4.3739 | 4.2192 | 4.0534 | 3.7272 | 3.4188 | 3.0068 | 2.767
| LHANBRYDE | CT |  |  |  | 5.3005 | 5.2044 | 5.0953 | 4.9171 | 4.7296 | 4.527 | 4.3141 | 4.1283 | 3.9614 | 3.7768 | 3.421 | 3.0592 | 2.607 | 2.3628 | 5.5634 | 5.5129 | 5.4493 | 5.3532 | 5.2473 | 5.1259 | 4.997 | 4.8994 | 4.7873 | 4.6554 | 4.3996 | 4.1784 | 3.8738 | 3.5729 | 5.519 | 5.4405 | 5.3486 | 5.186 | 5.0138 | 4.8215 | 4.6199 | 4.4509 | 4.2907 | 4.1071 | 3.7533 | 3.4188 | 3.0068 | 2.767
| LHANBRYDE | LW |  |  |  | 5.213 | 5.074 | 4.9138 | 4.7441 | 4.572 | 4.4067 | 4.2138 | 4.008 | 3.8523 | 3.6886 | 3.3659 | 3.1994 | 2.8817 | 2.6316 | 5.5352 | 5.4687 | 5.3838 | 5.3074 | 5.2262 | 5.1511 | 5.0468 | 4.9304 | 4.8173 | 4.6963 | 4.4593 | 4.4466 | 4.2142 | 3.9513 | 5.4427 | 5.3275 | 5.1912 | 5.0399 | 4.8854 | 4.7374 | 4.5619 | 4.3739 | 4.2192 | 4.0534 | 3.7272 | 3.6001 | 3.2781 | 2.9891
| LHANBRYDE | ST |  |  |  | 5.3336 | 5.2603 | 5.1899 | 5.1129 | 5.0432 | 4.9764 | 4.8689 | 4.789 | 4.6835 | 4.5903 | 4.3788 | 3.9053 | 3.4817 | 3.052 | 5.5733 | 5.5367 | 5.4977 | 5.4347 | 5.3788 | 5.3275 | 5.2298 | 5.1664 | 5.0707 | 4.9923 | 4.8136 | 4.4511 | 4.1008 | 3.7062 | 5.5482 | 5.4905 | 5.4345 | 5.3551 | 5.2851 | 5.2203 | 5.1065 | 5.026 | 4.9131 | 4.8165 | 4.604 | 4.157 | 3.7293 | 3.2995
| LHANBRYDE | FS |  |  |  | 5.3532 | 5.2953 | 5.2332 | 5.1834 | 5.1305 | 5.0728 | 5.0098 | 4.952 | 4.8639 | 4.7723 | 4.5898 | 4.1016 | 3.6575 | 3.3655 | 5.5806 | 5.5494 | 5.515 | 5.4822 | 5.4458 | 5.4056 | 5.3611 | 5.3165 | 5.252 | 5.1862 | 5.0436 | 4.7099 | 4.3006 | 3.8884 | 5.5644 | 5.5201 | 5.4715 | 5.4255 | 5.3763 | 5.3227 | 5.2637 | 5.2068 | 5.1208 | 5.0321 | 4.8518 | 4.3953 | 3.98 | 3.7228
FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0.094644 | 0.092327 | 0.087619 | 0.083019 | 0.078709 | 0.076085 | 0.072688 | 0.068923 | 0.068542 | 0.06276 | 0.057399 | 0.053601 | 0.0479 | 0.047398 | 0.10178 | 0.10072 | 0.098548 | 0.096514 | 0.094493 | 0.093178 | 0.091193 | 0.088866 | 0.087454 | 0.08412 | 0.079715 | 0.077387 | 0.075209 | 0.074805 | 0.097784 | 0.095686 | 0.091446 | 0.087374 | 0.083491 | 0.081085 | 0.077852 | 0.074326 | 0.07365 | 0.068238 | 0.06264 | 0.059029 | 0.054011 | 0.05351
| LIDDESDALE | CT |  |  |  | 0.096403 | 0.094321 | 0.091701 | 0.084812 | 0.081495 | 0.078756 | 0.075978 | 0.073605 | 0.070117 | 0.06395 | 0.060718 | 0.055412 | 0.0479 | 0.047398 | 0.10252 | 0.10151 | 0.10021 | 0.097093 | 0.09523 | 0.093834 | 0.092371 | 0.091029 | 0.088897 | 0.085429 | 0.081805 | 0.078268 | 0.075209 | 0.074805 | 0.099383 | 0.097452 | 0.095065 | 0.088869 | 0.085787 | 0.083281 | 0.080737 | 0.078546 | 0.075296 | 0.069607 | 0.06578 | 0.060675 | 0.054011 | 0.05351
| LIDDESDALE | LW |  |  |  | 0.094644 | 0.092327 | 0.087619 | 0.083019 | 0.078709 | 0.076085 | 0.072688 | 0.068923 | 0.068542 | 0.06276 | 0.057399 | 0.053601 | 0.048223 | 0.049575 | 0.10178 | 0.10072 | 0.098548 | 0.096514 | 0.094493 | 0.093178 | 0.091193 | 0.088866 | 0.087454 | 0.08412 | 0.079715 | 0.077387 | 0.0753 | 0.075798 | 0.097784 | 0.095686 | 0.091446 | 0.087374 | 0.083491 | 0.081085 | 0.077852 | 0.074326 | 0.07365 | 0.068238 | 0.06264 | 0.059029 | 0.054286 | 0.055471
| LIDDESDALE | ST |  |  |  | 0.096391 | 0.094529 | 0.09425 | 0.092019 | 0.087766 | 0.083823 | 0.0832 | 0.082334 | 0.079385 | 0.078035 | 0.072995 | 0.057562 | 0.049273 | 0.048875 | 0.10252 | 0.10168 | 0.10146 | 0.10047 | 0.098685 | 0.097008 | 0.096429 | 0.095725 | 0.09416 | 0.092964 | 0.08935 | 0.07966 | 0.075976 | 0.075812 | 0.099372 | 0.097658 | 0.09738 | 0.09538 | 0.091615 | 0.088159 | 0.087443 | 0.086573 | 0.083859 | 0.082517 | 0.077449 | 0.062725 | 0.055286 | 0.054932
| LIDDESDALE | FS |  |  |  | 0.096413 | 0.09458 | 0.09435 | 0.094047 | 0.091792 | 0.087658 | 0.087152 | 0.08654 | 0.085794 | 0.081638 | 0.075852 | 0.062194 | 0.050987 | 0.049224 | 0.10253 | 0.10172 | 0.10154 | 0.10129 | 0.10029 | 0.098582 | 0.098168 | 0.097675 | 0.097075 | 0.095165 | 0.092018 | 0.083586 | 0.076608 | 0.075937 | 0.099393 | 0.097709 | 0.097479 | 0.097179 | 0.095154 | 0.091488 | 0.090976 | 0.090368 | 0.089625 | 0.08588 | 0.080562 | 0.067419 | 0.056789 | 0.055237
KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | NO | 1.1068 | 1.0293 | 0.94188 | 0.85636 | 0.77228 | 0.61409 | 0.42001 | 0.29033 | 0.19373 | 0.084287 | -0.12576 | -0.35914 | -0.80391 | -1.1994 | 1.6269 | 1.6138 | 1.5964 | 1.5208 | 1.4472 | 1.3946 | 1.2376 | 1.1823 | 1.056 | 0.99684 | 0.86196 | 0.57676 | 0.13055 | -0.30609 | 1.3727 | 1.317 | 1.2497 | 1.1855 | 1.1168 | 0.93845 | 0.74908 | 0.64147 | 0.53972 | 0.4209 | 0.19749 | -0.17618 | -0.65448 | -1.0904
| LIMEHILLOCKS | CT |  |  |  | 1.1544 | 1.104 | 1.0419 | 0.92472 | 0.79694 | 0.61409 | 0.42001 | 0.29033 | 0.19373 | 0.084287 | -0.12576 | -0.35914 | -0.70572 | -0.96625 | 1.6307 | 1.6185 | 1.6019 | 1.5654 | 1.5208 | 1.397 | 1.2652 | 1.2151 | 1.1441 | 1.0676 | 0.92172 | 0.66701 | 0.3513 | 0.039466 | 1.4053 | 1.3688 | 1.3212 | 1.2258 | 1.1168 | 0.93845 | 0.74908 | 0.64147 | 0.53972 | 0.4209 | 0.19749 | -0.12881 | -0.4767 | -0.77371
| LIMEHILLOCKS | LW |  |  |  | 1.1068 | 1.0293 | 0.94188 | 0.85636 | 0.77228 | 0.68585 | 0.58249 | 0.47339 | 0.38997 | 0.30057 | 0.12653 | 0.02407 | -0.39497 | -0.9347 | 1.6269 | 1.6138 | 1.5964 | 1.5807 | 1.5639 | 1.5472 | 1.5219 | 1.4889 | 1.4394 | 1.3861 | 1.2845 | 1.2094 | 0.74522 | 0.094576 | 1.3727 | 1.317 | 1.2497 | 1.1855 | 1.1205 | 1.0564 | 0.97345 | 0.8841 | 0.80017 | 0.71042 | 0.53809 | 0.37769 | -0.10838 | -0.76744
| LIMEHILLOCKS | ST |  |  |  | 1.179 | 1.1453 | 1.1097 | 0.98607 | 0.88609 | 0.80289 | 0.63579 | 0.54424 | 0.39735 | 0.30299 | 0.087275 | -0.3568 | -0.80391 | -1.1994 | 1.6349 | 1.6292 | 1.6232 | 1.5208 | 1.4472 | 1.3946 | 1.2376 | 1.1823 | 1.056 | 0.99684 | 0.86196 | 0.57676 | 0.13055 | -0.30609 | 1.4216 | 1.3975 | 1.3715 | 1.242 | 1.1412 | 1.0614 | 0.87678 | 0.78974 | 0.63243 | 0.54072 | 0.33111 | -0.17618 | -0.65448 | -1.0904
| LIMEHILLOCKS | FS |  |  |  | 1.1996 | 1.1742 | 1.1456 | 1.0945 | 1.0398 | 0.98352 | 0.9249 | 0.86561 | 0.77634 | 0.69989 | 0.52873 | 0.15063 | -0.098252 | -0.21175 | 1.6374 | 1.633 | 1.6278 | 1.6025 | 1.5758 | 1.5457 | 1.5145 | 1.485 | 1.433 | 1.3931 | 1.3073 | 1.2254 | 1.0492 | 0.93284 | 1.4354 | 1.417 | 1.3958 | 1.3502 | 1.3012 | 1.2496 | 1.1957 | 1.1419 | 1.0576 | 0.9868 | 0.82984 | 0.48734 | 0.25386 | 0.15925
ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | NO | 21.9348 | 21.9262 | 21.914 | 21.8938 | 21.8657 | 21.8443 | 21.8226 | 21.7962 | 21.7839 | 21.7741 | 21.7449 | 21.7881 | 21.7796 | 21.7684 | 22.069 | 22.0644 | 22.0572 | 22.0417 | 22.0243 | 22.0121 | 21.9996 | 21.9835 | 21.9718 | 21.9609 | 21.9381 | 21.9745 | 21.965 | 21.9545 | 21.9653 | 21.9574 | 21.946 | 21.9264 | 21.9001 | 21.8804 | 21.8604 | 21.836 | 21.824 | 21.812 | 21.7797 | 21.8206 | 21.8131 | 21.803
| LOCH CARNAN | CT |  |  |  | 21.9408 | 21.9361 | 21.9206 | 21.8938 | 21.8657 | 21.8443 | 21.8226 | 21.7962 | 21.7839 | 21.7741 | 21.7452 | 21.7936 | 21.7796 | 21.7684 | 22.0713 | 22.0683 | 22.0576 | 22.0417 | 22.0243 | 22.0121 | 21.9996 | 21.9835 | 21.9718 | 21.9609 | 21.9381 | 21.9745 | 21.965 | 21.9545 | 21.9682 | 21.9658 | 21.9486 | 21.9264 | 21.9001 | 21.8804 | 21.8604 | 21.836 | 21.824 | 21.812 | 21.7806 | 21.8257 | 21.8131 | 21.803
| LOCH CARNAN | LW |  |  |  | 21.9348 | 21.9262 | 21.914 | 21.8989 | 21.8828 | 21.8697 | 21.8453 | 21.8273 | 21.8085 | 21.7874 | 21.7449 | 21.7881 | 21.7809 | 21.7758 | 22.069 | 22.0644 | 22.0572 | 22.0492 | 22.0402 | 22.0325 | 22.0185 | 22.0058 | 21.9918 | 21.9759 | 21.9411 | 21.9748 | 21.9716 | 21.9697 | 21.9653 | 21.9574 | 21.946 | 21.9322 | 21.9173 | 21.9051 | 21.8824 | 21.8651 | 21.8458 | 21.8238 | 21.7797 | 21.8206 | 21.8142 | 21.8097
| LOCH CARNAN | ST |  |  |  | 21.9427 | 21.9393 | 21.9321 | 21.929 | 21.9196 | 21.915 | 21.9056 | 21.8913 | 21.8826 | 21.8684 | 21.8304 | 21.813 | 21.7946 | 21.7868 | 22.072 | 22.0701 | 22.0664 | 22.064 | 22.0588 | 22.055 | 22.0491 | 22.0407 | 22.0336 | 22.0237 | 21.9976 | 21.9843 | 21.9716 | 21.9633 | 21.9684 | 21.9671 | 21.9627 | 21.9596 | 21.951 | 21.9464 | 21.9376 | 21.9243 | 21.9155 | 21.9013 | 21.8638 | 21.8435 | 21.8266 | 21.8197
| LOCH CARNAN | FS |  |  |  | 21.9449 | 21.942 | 21.9388 | 21.9365 | 21.9303 | 21.9202 | 21.9165 | 21.9088 | 21.9017 | 21.8906 | 21.8681 | 21.8281 | 21.7903 | 21.7798 | 22.073 | 22.0714 | 22.0694 | 22.0676 | 22.0641 | 22.0591 | 22.0562 | 22.0514 | 22.0465 | 22.0398 | 22.0248 | 22.0003 | 21.969 | 21.9573 | 21.969 | 21.9681 | 21.9671 | 21.9657 | 21.9607 | 21.9516 | 21.948 | 21.9407 | 21.934 | 21.9236 | 21.9015 | 21.8609 | 21.8228 | 21.8135
GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0.58819 | 0.58819 | 0.58819 | 0.57587 | 0.56754 | 0.56204 | 0.54313 | 0.53787 | 0.52365 | 0.5186 | 0.50751 | 0.47551 | 0.42855 | 0.38035 | 0.54374 | 0.54374 | 0.54374 | 0.52834 | 0.51793 | 0.51106 | 0.48742 | 0.48084 | 0.46306 | 0.45676 | 0.44289 | 0.40289 | 0.34419 | 0.28394 | 0.5435 | 0.5435 | 0.5435 | 0.5281 | 0.51769 | 0.51081 | 0.48717 | 0.4806 | 0.46282 | 0.45651 | 0.44264 | 0.40265 | 0.34394 | 0.2837
| LOCH GLASCARNOCH | CT |  |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58659 | 0.58374 | 0.57004 | 0.55544 | 0.55174 | 0.54527 | 0.53878 | 0.527 | 0.49425 | 0.46336 | 0.43002 | 0.54374 | 0.54374 | 0.54374 | 0.54174 | 0.53818 | 0.52106 | 0.5028 | 0.49817 | 0.49009 | 0.48198 | 0.46726 | 0.42632 | 0.38771 | 0.34602 | 0.5435 | 0.5435 | 0.5435 | 0.54149 | 0.53793 | 0.52081 | 0.50256 | 0.49793 | 0.48985 | 0.48174 | 0.46701 | 0.42608 | 0.38746 | 0.34578
| LOCH GLASCARNOCH | LW |  |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58566 | 0.58304 | 0.57845 | 0.56568 | 0.50834 | 0.42432 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54058 | 0.5373 | 0.53157 | 0.5156 | 0.44393 | 0.33891 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.54034 | 0.53706 | 0.53132 | 0.51536 | 0.44368 | 0.33866
| LOCH GLASCARNOCH | ST |  |  |  | 0.58819 | 0.58819 | 0.58819 | 0.57587 | 0.56754 | 0.56204 | 0.54313 | 0.53787 | 0.52365 | 0.5186 | 0.50751 | 0.47551 | 0.42855 | 0.38035 | 0.54374 | 0.54374 | 0.54374 | 0.52834 | 0.51793 | 0.51106 | 0.48742 | 0.48084 | 0.46306 | 0.45676 | 0.44289 | 0.40289 | 0.34419 | 0.28394 | 0.5435 | 0.5435 | 0.5435 | 0.5281 | 0.51769 | 0.51081 | 0.48717 | 0.4806 | 0.46282 | 0.45651 | 0.44264 | 0.40265 | 0.34394 | 0.2837
| LOCH GLASCARNOCH | FS |  |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58567 | 0.58316 | 0.58022 | 0.57728 | 0.57476 | 0.56962 | 0.56612 | 0.55914 | 0.55491 | 0.55197 | 0.54659 | 0.54374 | 0.54374 | 0.54374 | 0.54059 | 0.53745 | 0.53378 | 0.53011 | 0.52696 | 0.52052 | 0.51616 | 0.50743 | 0.50214 | 0.49847 | 0.49174 | 0.5435 | 0.5435 | 0.5435 | 0.54035 | 0.5372 | 0.53353 | 0.52986 | 0.52671 | 0.52028 | 0.51591 | 0.50718 | 0.50189 | 0.49823 | 0.49149
FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 0.27026 | 0.26223 | 0.2479 | 0.23246 | 0.21425 | 0.19536 | 0.17387 | 0.14984 | 0.14419 | 0.1382 | 0.11875 | 0.12119 | 0.10808 | 0.097849 | 0.26682 | 0.26309 | 0.25605 | 0.24877 | 0.23793 | 0.22912 | 0.21979 | 0.20884 | 0.19928 | 0.18771 | 0.16609 | 0.15803 | 0.14908 | 0.14053 | 0.12735 | 0.1235 | 0.11623 | 0.10869 | 0.099437 | 0.090141 | 0.079531 | 0.068254 | 0.064793 | 0.059581 | 0.047229 | 0.064679 | 0.059154 | 0.055322
| LOCHALINE | CT |  |  |  | 0.27462 | 0.27234 | 0.2625 | 0.24089 | 0.21523 | 0.19536 | 0.17387 | 0.14984 | 0.14419 | 0.1382 | 0.11875 | 0.1284 | 0.10808 | 0.097849 | 0.26837 | 0.26663 | 0.26127 | 0.25047 | 0.23793 | 0.22912 | 0.21979 | 0.20964 | 0.20222 | 0.19196 | 0.1704 | 0.15926 | 0.14908 | 0.14053 | 0.12889 | 0.1271 | 0.12217 | 0.11158 | 0.099437 | 0.090141 | 0.079531 | 0.068254 | 0.064793 | 0.061209 | 0.050396 | 0.067848 | 0.059154 | 0.055322
| LOCHALINE | LW |  |  |  | 0.27026 | 0.26223 | 0.2479 | 0.23246 | 0.21425 | 0.20117 | 0.18021 | 0.15607 | 0.14971 | 0.13854 | 0.11916 | 0.12119 | 0.10968 | 0.10727 | 0.26682 | 0.26309 | 0.25605 | 0.24877 | 0.24015 | 0.2338 | 0.22224 | 0.20884 | 0.19928 | 0.18771 | 0.16609 | 0.15803 | 0.15379 | 0.15294 | 0.12735 | 0.1235 | 0.11623 | 0.10869 | 0.10043 | 0.09365 | 0.082925 | 0.07075 | 0.066444 | 0.059581 | 0.047229 | 0.064679 | 0.060237 | 0.059097
| LOCHALINE | ST |  |  |  | 0.27837 | 0.27577 | 0.27034 | 0.26468 | 0.25818 | 0.25169 | 0.24056 | 0.23658 | 0.22598 | 0.21575 | 0.18765 | 0.15173 | 0.13403 | 0.11774 | 0.26979 | 0.26838 | 0.26586 | 0.26291 | 0.25915 | 0.25527 | 0.24953 | 0.24532 | 0.23849 | 0.23089 | 0.21153 | 0.17063 | 0.15874 | 0.14994 | 0.13104 | 0.12952 | 0.12722 | 0.12434 | 0.12138 | 0.11815 | 0.11249 | 0.11007 | 0.10414 | 0.098887 | 0.082875 | 0.078605 | 0.072214 | 0.065285
| LOCHALINE | FS |  |  |  | 0.28235 | 0.27766 | 0.27461 | 0.27105 | 0.26337 | 0.25934 | 0.25308 | 0.24615 | 0.2353 | 0.23114 | 0.21189 | 0.15814 | 0.12321 | 0.11163 | 0.27113 | 0.26914 | 0.26736 | 0.26521 | 0.26153 | 0.25887 | 0.25519 | 0.25097 | 0.24524 | 0.24089 | 0.22791 | 0.1877 | 0.15424 | 0.14435 | 0.13284 | 0.13057 | 0.129 | 0.12753 | 0.12379 | 0.12222 | 0.11896 | 0.11571 | 0.1101 | 0.10789 | 0.098175 | 0.080956 | 0.066124 | 0.060578
TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.12841 | 0.11948 | 0.098408 | 0.07672 | 0.048394 | 0.019499 | -0.011968 | -0.042181 | -0.06693 | -0.096774 | -0.1526 | -0.12558 | -0.14831 | -0.15898 | 0.42576 | 0.418 | 0.40701 | 0.39597 | 0.379 | 0.36374 | 0.34783 | 0.33228 | 0.31989 | 0.30494 | 0.27475 | 0.30594 | 0.29011 | 0.28052 | 0.20253 | 0.18918 | 0.17053 | 0.1479 | 0.12518 | 0.10281 | 0.078539 | 0.053446 | 0.027527 | 0.0069651 | -0.046834 | -0.02129 | -0.039128 | -0.048288
| LOCHDONHEAD | CT |  |  |  | 0.13168 | 0.12032 | 0.11157 | 0.08349 | 0.049858 | 0.019499 | -0.011968 | -0.042181 | -0.062478 | -0.089659 | -0.14013 | -0.1162 | -0.14831 | -0.15898 | 0.42873 | 0.42021 | 0.41212 | 0.39597 | 0.379 | 0.36374 | 0.34783 | 0.33228 | 0.31989 | 0.30494 | 0.27582 | 0.30655 | 0.29011 | 0.28052 | 0.20498 | 0.18918 | 0.17053 | 0.1479 | 0.12518 | 0.10281 | 0.078539 | 0.053446 | 0.027527 | 0.0069651 | -0.041109 | -0.012976 | -0.039128 | -0.048288
| LOCHDONHEAD | LW |  |  |  | 0.12841 | 0.11948 | 0.098408 | 0.07672 | 0.048394 | 0.028282 | -0.0044466 | -0.040692 | -0.06693 | -0.096774 | -0.1526 | -0.12558 | -0.14049 | -0.14638 | 0.42576 | 0.418 | 0.40701 | 0.39656 | 0.38303 | 0.37313 | 0.35654 | 0.33797 | 0.32318 | 0.30646 | 0.27475 | 0.30594 | 0.29978 | 0.29745 | 0.20253 | 0.19224 | 0.17706 | 0.16391 | 0.14555 | 0.12773 | 0.09804 | 0.064744 | 0.038537 | 0.0089993 | -0.046834 | -0.02129 | -0.033291 | -0.037845
| LOCHDONHEAD | ST |  |  |  | 0.13432 | 0.13092 | 0.1273 | 0.12297 | 0.11535 | 0.1032 | 0.091918 | 0.077356 | 0.057198 | 0.036105 | -0.011027 | -0.063307 | -0.092194 | -0.1097 | 0.43041 | 0.42721 | 0.42334 | 0.41892 | 0.41348 | 0.4067 | 0.4001 | 0.39166 | 0.38031 | 0.36788 | 0.33946 | 0.32967 | 0.31401 | 0.30246 | 0.20693 | 0.20165 | 0.19493 | 0.18713 | 0.1777 | 0.16561 | 0.15195 | 0.13518 | 0.11435 | 0.09022 | 0.031415 | 0.030194 | 0.0052102 | -0.0083869
| LOCHDONHEAD | FS |  |  |  | 0.1356 | 0.13466 | 0.13147 | 0.1279 | 0.12337 | 0.11065 | 0.1051 | 0.089216 | 0.076288 | 0.060582 | 0.023246 | -0.047757 | -0.11453 | -0.12836 | 0.43122 | 0.42979 | 0.42654 | 0.42266 | 0.41823 | 0.41128 | 0.40778 | 0.3995 | 0.39235 | 0.38367 | 0.3629 | 0.33872 | 0.30367 | 0.29041 | 0.20785 | 0.20488 | 0.20033 | 0.1938 | 0.18647 | 0.1764 | 0.16766 | 0.15495 | 0.14171 | 0.12631 | 0.089557 | 0.052099 | -0.012235 | -0.023316
KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | NO | -0.32498 | -0.37771 | -0.44924 | -0.51676 | -0.59517 | -0.66683 | -0.76028 | -0.85389 | -0.91725 | -0.99481 | -1.1469 | -1.2113 | -1.3139 | -1.3877 | 0.22697 | 0.20229 | 0.16461 | 0.13032 | 0.08806 | 0.044462 | 0.0012276 | -0.055726 | -0.10848 | -0.16906 | -0.28708 | -0.31479 | -0.39504 | -0.4641 | -0.12864 | -0.13527 | -0.14901 | -0.20192 | -0.26741 | -0.32747 | -0.40401 | -0.48004 | -0.52785 | -0.58205 | -0.72716 | -0.78046 | -0.86975 | -0.93348
| LOCHEARNHEAD | CT |  |  |  | -0.28878 | -0.33273 | -0.37371 | -0.46542 | -0.5656 | -0.65375 | -0.73587 | -0.82873 | -0.88123 | -0.95338 | -1.0918 | -1.1675 | -1.3139 | -1.3877 | 0.23978 | 0.21781 | 0.19231 | 0.14234 | 0.08806 | 0.044462 | 0.0022591 | -0.043884 | -0.083998 | -0.14234 | -0.25435 | -0.31479 | -0.39504 | -0.4641 | -0.12773 | -0.13363 | -0.14446 | -0.1629 | -0.24045 | -0.31442 | -0.38289 | -0.46121 | -0.50167 | -0.55464 | -0.67427 | -0.74148 | -0.86975 | -0.93348
| LOCHEARNHEAD | LW |  |  |  | -0.32498 | -0.37771 | -0.44924 | -0.51676 | -0.59517 | -0.66683 | -0.76028 | -0.85389 | -0.91725 | -0.99481 | -1.1469 | -1.2113 | -1.3023 | -1.3488 | 0.22697 | 0.20229 | 0.16461 | 0.13032 | 0.090105 | 0.054551 | 0.0012276 | -0.055726 | -0.10848 | -0.16906 | -0.28708 | -0.31367 | -0.35035 | -0.36885 | -0.12864 | -0.13527 | -0.14901 | -0.20192 | -0.26741 | -0.32747 | -0.40401 | -0.48004 | -0.52785 | -0.58205 | -0.72716 | -0.78046 | -0.85836 | -0.89676
| LOCHEARNHEAD | ST |  |  |  | -0.2768 | -0.30166 | -0.32495 | -0.36104 | -0.39581 | -0.43566 | -0.4825 | -0.53253 | -0.58072 | -0.63817 | -0.76637 | -1.0269 | -1.1568 | -1.233 | 0.24402 | 0.23196 | 0.21918 | 0.20072 | 0.1808 | 0.15811 | 0.13113 | 0.101 | 0.068984 | 0.030443 | -0.061097 | -0.24989 | -0.33374 | -0.39996 | -0.12772 | -0.13051 | -0.13458 | -0.14013 | -0.14771 | -0.15618 | -0.17084 | -0.21212 | -0.25165 | -0.29876 | -0.39959 | -0.60999 | -0.72612 | -0.7946
| LOCHEARNHEAD | FS |  |  |  | -0.26955 | -0.27995 | -0.29985 | -0.32545 | -0.35881 | -0.39384 | -0.42838 | -0.4667 | -0.50859 | -0.5561 | -0.6654 | -0.96944 | -1.1958 | -1.2577 | 0.24675 | 0.24002 | 0.22892 | 0.21516 | 0.19728 | 0.17831 | 0.15827 | 0.13557 | 0.11017 | 0.081103 | 0.013121 | -0.17719 | -0.35442 | -0.42891 | -0.12745 | -0.12976 | -0.1331 | -0.13755 | -0.14345 | -0.14977 | -0.15732 | -0.1661 | -0.18932 | -0.22823 | -0.31717 | -0.5546 | -0.7656 | -0.81842
LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | NO | 17.1989 | 17.1342 | 16.946 | 16.7727 | 16.6133 | 16.4243 | 16.2081 | 15.9684 | 15.7385 | 15.4861 | 14.9961 | 14.9655 | 14.4462 | 13.8094 | 19.387 | 19.3523 | 19.249 | 19.1157 | 18.9917 | 18.8386 | 18.7099 | 18.5801 | 18.4266 | 18.2489 | 17.8872 | 17.4321 | 16.316 | 13.8716 | 18.8816 | 18.8217 | 18.6617 | 18.503 | 18.3563 | 18.1805 | 17.9831 | 17.7598 | 17.533 | 17.2853 | 16.8055 | 16.7661 | 16.153 | 15.366
| LOCHEE | CT |  |  |  | 17.2476 | 17.2061 | 17.0504 | 16.8463 | 16.6497 | 16.4431 | 16.2654 | 16.077 | 15.8859 | 15.6523 | 15.1943 | 14.9938 | 14.5675 | 14.2134 | 19.3917 | 19.3523 | 19.249 | 19.1157 | 18.9917 | 18.8386 | 18.7099 | 18.5801 | 18.4266 | 18.2489 | 17.8872 | 17.4321 | 16.4967 | 15.1101 | 18.9245 | 18.8852 | 18.7527 | 18.5617 | 18.377 | 18.1805 | 18.0109 | 17.8371 | 17.6481 | 17.42 | 16.974 | 16.7725 | 16.3221 | 15.9196
| LOCHEE | LW |  |  |  | 17.1989 | 17.1342 | 16.946 | 16.7727 | 16.6133 | 16.4243 | 16.2081 | 15.9684 | 15.7385 | 15.4861 | 14.9961 | 14.9655 | 14.4462 | 13.8094 | 19.387 | 19.3543 | 19.257 | 19.1642 | 19.087 | 18.9799 | 18.8696 | 18.7411 | 18.5912 | 18.4277 | 18.0955 | 18.0831 | 17.5008 | 16.7186 | 18.8816 | 18.8217 | 18.6617 | 18.503 | 18.3563 | 18.183 | 17.9831 | 17.7598 | 17.533 | 17.2853 | 16.8055 | 16.7661 | 16.153 | 15.366
| LOCHEE | ST |  |  |  | 17.2855 | 17.2754 | 17.1804 | 17.1267 | 17.0828 | 17.0121 | 16.9404 | 16.8665 | 16.7344 | 16.6105 | 16.3208 | 15.9386 | 15.4366 | 14.8789 | 19.4075 | 19.3857 | 19.319 | 19.25 | 19.1956 | 19.1114 | 19.0251 | 18.9427 | 18.79 | 18.6663 | 18.3758 | 17.7482 | 16.6658 | 15.1295 | 18.9579 | 18.9479 | 18.8733 | 18.8167 | 18.7707 | 18.7001 | 18.6237 | 18.551 | 18.4049 | 18.2805 | 17.9888 | 17.5924 | 17.0298 | 16.4102
| LOCHEE | FS |  |  |  | 17.2792 | 17.27 | 17.1972 | 17.1514 | 17.1121 | 17.0453 | 16.9904 | 16.94 | 16.8478 | 16.7509 | 16.5459 | 16.2326 | 15.7781 | 15.5217 | 19.4036 | 19.3791 | 19.3183 | 19.2608 | 19.2084 | 19.1286 | 19.0578 | 18.9816 | 18.8653 | 18.7425 | 18.4644 | 17.7603 | 16.316 | 13.8716 | 18.9525 | 18.9436 | 18.8879 | 18.8441 | 18.8059 | 18.7419 | 18.6891 | 18.6395 | 18.5461 | 18.4509 | 18.2484 | 17.9554 | 17.524 | 17.2857
PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | NO | 16.8108 | 16.2092 | 15.5606 | 14.842 | 14.5277 | 14.0629 | 13.5917 | 13.1233 | 12.8407 | 12.5364 | 11.9249 | 12.4311 | 11.8161 | 11.2027 | 19.1596 | 18.5237 | 17.8533 | 17.1416 | 16.8854 | 16.6088 | 16.3499 | 16.1082 | 15.9023 | 15.6793 | 15.195 | 15.603 | 15.0313 | 14.3225 | 17.5447 | 17.1824 | 16.4548 | 15.6604 | 15.303 | 14.9173 | 14.5502 | 14.1965 | 13.9597 | 13.7045 | 13.1266 | 13.6322 | 12.9582 | 12.2173
| LOCHGILPHEAD | CT |  |  |  | 16.8755 | 16.3492 | 15.762 | 15.0742 | 14.7357 | 14.2672 | 13.7456 | 13.2399 | 12.9837 | 12.7213 | 12.2029 | 12.5975 | 11.954 | 11.5719 | 19.2649 | 18.7276 | 18.1307 | 17.4033 | 17.0718 | 16.765 | 16.4776 | 16.2139 | 16.0189 | 15.83 | 15.4511 | 15.6099 | 15.0811 | 14.5406 | 17.5862 | 17.2765 | 16.8301 | 15.9868 | 15.5408 | 15.0963 | 14.6665 | 14.2518 | 14.0124 | 13.8152 | 13.393 | 13.7852 | 13.1592 | 12.7543
| LOCHGILPHEAD | LW |  |  |  | 16.8108 | 16.2092 | 15.5606 | 14.842 | 14.5277 | 14.0629 | 13.5917 | 13.1233 | 12.8407 | 12.5364 | 11.9249 | 12.4311 | 11.8161 | 11.2027 | 19.1596 | 18.5237 | 17.8533 | 17.1416 | 16.8854 | 16.6088 | 16.3499 | 16.1082 | 15.9023 | 15.6793 | 15.195 | 15.603 | 15.0313 | 14.3225 | 17.5447 | 17.1824 | 16.4548 | 15.6604 | 15.303 | 14.9173 | 14.5502 | 14.1965 | 13.9597 | 13.7045 | 13.1266 | 13.6322 | 12.9582 | 12.2173
| LOCHGILPHEAD | ST |  |  |  | 16.9571 | 16.4843 | 15.9778 | 15.4462 | 15.3115 | 15.1748 | 15.0482 | 14.9391 | 14.7769 | 14.6543 | 14.356 | 13.9435 | 13.4895 | 12.9983 | 19.34 | 18.8522 | 18.3298 | 17.7719 | 17.6068 | 17.4403 | 17.2827 | 17.1443 | 16.9433 | 16.7894 | 16.4304 | 16.1612 | 15.5754 | 14.9061 | 17.5964 | 17.2936 | 16.971 | 16.6006 | 16.407 | 16.2095 | 16.0179 | 15.8388 | 15.5925 | 15.3851 | 14.9061 | 14.7901 | 14.2724 | 13.7486
| LOCHGILPHEAD | FS |  |  |  | 17.0622 | 16.7062 | 16.3191 | 15.9049 | 15.7508 | 15.6542 | 15.5237 | 15.4433 | 15.324 | 15.145 | 14.7777 | 13.9298 | 13.3521 | 13.1237 | 19.4473 | 19.0771 | 18.6754 | 18.2272 | 18.0342 | 17.8979 | 17.7268 | 17.6049 | 17.4405 | 17.2173 | 16.8421 | 16.28 | 15.7285 | 15.2157 | 17.6647 | 17.4384 | 17.1926 | 16.9272 | 16.8044 | 16.6238 | 16.4103 | 16.2423 | 16.0392 | 15.7805 | 15.3274 | 14.9897 | 14.3548 | 14.1818
CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | NO | -1.4282 | -1.4387 | -1.4488 | -1.4672 | -1.4834 | -1.5114 | -1.5422 | -1.5658 | -1.5811 | -1.6014 | -1.6413 | -1.6757 | -1.716 | -1.7516 | -0.11975 | -0.12005 | -0.12057 | -0.13177 | -0.13994 | -0.14544 | -0.16414 | -0.17405 | -0.18375 | -0.19191 | -0.2082 | -0.25138 | -0.29829 | -0.34421 | -1.4252 | -1.4264 | -1.4289 | -1.4389 | -1.448 | -1.4547 | -1.4744 | -1.4815 | -1.4976 | -1.5057 | -1.5241 | -1.5704 | -1.6178 | -1.6636
| LOCHGOILHEAD | CT |  |  |  | -1.4262 | -1.4293 | -1.4402 | -1.4582 | -1.4834 | -1.5114 | -1.5422 | -1.5658 | -1.5811 | -1.6014 | -1.6413 | -1.6757 | -1.716 | -1.7516 | -0.11973 | -0.11994 | -0.12039 | -0.12263 | -0.12619 | -0.14355 | -0.16414 | -0.17405 | -0.18281 | -0.19191 | -0.2082 | -0.23579 | -0.26793 | -0.3048 | -1.4251 | -1.4261 | -1.428 | -1.4327 | -1.439 | -1.4542 | -1.4704 | -1.4762 | -1.4864 | -1.4982 | -1.5202 | -1.5553 | -1.5934 | -1.6366
| LOCHGOILHEAD | LW |  |  |  | -1.4282 | -1.4387 | -1.4488 | -1.4672 | -1.4817 | -1.4971 | -1.5182 | -1.5409 | -1.5572 | -1.5773 | -1.6187 | -1.6273 | -1.681 | -1.7488 | -0.11975 | -0.12005 | -0.12057 | -0.12113 | -0.12182 | -0.12721 | -0.13326 | -0.13955 | -0.14486 | -0.15114 | -0.16398 | -0.16875 | -0.22397 | -0.3058 | -1.4252 | -1.4264 | -1.4289 | -1.4309 | -1.4334 | -1.4354 | -1.4395 | -1.4443 | -1.4523 | -1.4609 | -1.477 | -1.4886 | -1.5496 | -1.6341
| LOCHGOILHEAD | ST |  |  |  | -1.4239 | -1.424 | -1.4272 | -1.4409 | -1.4539 | -1.4624 | -1.4862 | -1.498 | -1.518 | -1.5369 | -1.573 | -1.6508 | -1.7028 | -1.7475 | -0.11965 | -0.11975 | -0.11991 | -0.13177 | -0.13994 | -0.14544 | -0.16377 | -0.16921 | -0.18375 | -0.19117 | -0.20809 | -0.25138 | -0.29829 | -0.34421 | -1.4251 | -1.4256 | -1.4263 | -1.4389 | -1.448 | -1.4547 | -1.4744 | -1.4815 | -1.4976 | -1.5057 | -1.5241 | -1.5704 | -1.6178 | -1.6636
| LOCHGOILHEAD | FS |  |  |  | -1.4247 | -1.4242 | -1.4243 | -1.4309 | -1.4387 | -1.4483 | -1.4532 | -1.4638 | -1.4786 | -1.4877 | -1.5138 | -1.5764 | -1.6248 | -1.6362 | -0.11967 | -0.11973 | -0.11983 | -0.12237 | -0.12495 | -0.12798 | -0.13099 | -0.13372 | -0.13902 | -0.14276 | -0.15342 | -0.16807 | -0.18127 | -0.18667 | -1.425 | -1.4254 | -1.426 | -1.4291 | -1.4325 | -1.4363 | -1.4404 | -1.4443 | -1.451 | -1.4564 | -1.4681 | -1.4852 | -1.5007 | -1.5059
GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | -0.55661 | -0.80766 | -0.86985 | -0.92676 | -1.0228 | -1.0885 | -1.1446 | -1.2041 | -1.2612 | -1.3213 | -1.4382 | -1.4584 | -1.5028 | -1.5334 | -0.5609 | -0.81652 | -0.8609 | -0.88863 | -0.95672 | -0.98673 | -1.0248 | -1.0755 | -1.1209 | -1.1691 | -1.2662 | -1.2565 | -1.2941 | -1.3284 | -0.99437 | -1.2221 | -1.2856 | -1.3445 | -1.4361 | -1.4968 | -1.5634 | -1.6345 | -1.6915 | -1.751 | -1.8799 | -1.8862 | -1.9255 | -1.9535
| LOCHINVER | CT |  |  |  | -0.5201 | -0.7417 | -0.81011 | -0.90097 | -0.99126 | -1.0621 | -1.1381 | -1.2041 | -1.2282 | -1.2801 | -1.3878 | -1.4341 | -1.5028 | -1.5334 | -0.53419 | -0.76826 | -0.82466 | -0.88299 | -0.94034 | -0.97947 | -1.0154 | -1.0554 | -1.0875 | -1.1327 | -1.2197 | -1.2498 | -1.2941 | -1.3284 | -0.95851 | -1.1608 | -1.2188 | -1.3105 | -1.408 | -1.479 | -1.5498 | -1.6102 | -1.649 | -1.7068 | -1.8244 | -1.8638 | -1.9255 | -1.9535
| LOCHINVER | LW |  |  |  | -0.55661 | -0.80766 | -0.86985 | -0.92676 | -1.0228 | -1.0885 | -1.1446 | -1.2033 | -1.2612 | -1.3213 | -1.4382 | -1.4584 | -1.4912 | -1.504 | -0.5609 | -0.81652 | -0.8609 | -0.88863 | -0.95672 | -0.98673 | -1.0248 | -1.0755 | -1.1209 | -1.1691 | -1.2662 | -1.2565 | -1.2738 | -1.2798 | -0.99437 | -1.2221 | -1.2856 | -1.3445 | -1.4361 | -1.4968 | -1.5634 | -1.6345 | -1.6915 | -1.751 | -1.8799 | -1.8862 | -1.9155 | -1.9267
| LOCHINVER | ST |  |  |  | -0.50591 | -0.72231 | -0.76556 | -0.80909 | -0.85333 | -0.89035 | -0.92381 | -0.94909 | -0.97924 | -1.0144 | -1.0977 | -1.2682 | -1.3218 | -1.3594 | -0.53264 | -0.76008 | -0.79923 | -0.83614 | -0.87468 | -0.9036 | -0.93013 | -0.94555 | -0.96447 | -0.98762 | -1.0482 | -1.1709 | -1.2141 | -1.2455 | -0.94608 | -1.1353 | -1.1719 | -1.2121 | -1.2534 | -1.2896 | -1.3215 | -1.3493 | -1.3832 | -1.4232 | -1.5146 | -1.7152 | -1.7597 | -1.7881
| LOCHINVER | FS |  |  |  | -0.44673 | -0.58618 | -0.62041 | -0.66179 | -0.70012 | -0.73317 | -0.76951 | -0.80522 | -0.84458 | -0.88382 | -0.97737 | -1.2223 | -1.3821 | -1.4076 | -0.45591 | -0.6283 | -0.6592 | -0.69354 | -0.72386 | -0.74795 | -0.77343 | -0.80024 | -0.82878 | -0.85897 | -0.93027 | -1.1133 | -1.2484 | -1.2894 | -0.88313 | -1.0257 | -1.0551 | -1.0943 | -1.1308 | -1.1619 | -1.1975 | -1.2319 | -1.2718 | -1.312 | -1.4088 | -1.6631 | -1.8184 | -1.8408
LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | NO | 7.4848 | 6.4984 | 5.5173 | 4.1145 | 3.1544 | 2.0602 | 0.81689 | -0.16766 | -1.0297 | -1.5803 | -2.7659 | -2.5584 | -3.0427 | -3.2099 | 9.8407 | 8.9894 | 8.1275 | 6.9688 | 6.2463 | 5.3497 | 4.3214 | 3.5255 | 2.8276 | 2.4718 | 1.7339 | 2.1128 | 1.8591 | 1.4161 | 9.3135 | 8.3793 | 7.4282 | 6.053 | 5.0928 | 3.9537 | 2.645 | 1.6059 | 0.72816 | 0.17484 | -0.95565 | -0.70059 | -1.153 | -1.3243
| LOCHSIDE | CT |  |  |  | 7.7466 | 6.914 | 6.0633 | 4.8495 | 4.0859 | 3.2072 | 2.2098 | 1.4694 | 0.58065 | 0.032259 | -1.1178 | -1.5433 | -2.5534 | -3.0772 | 9.991 | 9.2311 | 8.4413 | 7.4719 | 6.9389 | 6.2594 | 5.4704 | 4.9211 | 4.2375 | 3.8793 | 3.1631 | 3.0658 | 2.281 | 1.4161 | 9.5541 | 8.7628 | 7.9389 | 6.7693 | 6.0209 | 5.1316 | 4.1242 | 3.3963 | 2.5255 | 1.9661 | 0.86276 | 0.56215 | -0.33815 | -0.80928
| LOCHSIDE | LW |  |  |  | 7.4848 | 6.4984 | 5.5173 | 4.1145 | 3.1544 | 2.0602 | 0.81689 | -0.16766 | -1.0297 | -1.5803 | -2.7659 | -2.5584 | -3.0427 | -3.2099 | 9.8407 | 8.9894 | 8.1275 | 6.9688 | 6.2463 | 5.3497 | 4.3214 | 3.5255 | 2.8276 | 2.4718 | 1.7339 | 2.1128 | 1.8591 | 1.7281 | 9.3135 | 8.3793 | 7.4282 | 6.053 | 5.0928 | 3.9537 | 2.645 | 1.6059 | 0.72816 | 0.17484 | -0.95565 | -0.70059 | -1.153 | -1.3243
| LOCHSIDE | ST |  |  |  | 7.8432 | 7.0872 | 6.3596 | 5.4033 | 4.9742 | 4.6102 | 3.9435 | 3.5176 | 2.9544 | 2.7177 | 2.185 | 2.035 | 1.1953 | 0.11153 | 10.0302 | 9.3165 | 8.595 | 7.5975 | 7.1793 | 6.842 | 6.1536 | 5.711 | 5.1646 | 4.9423 | 4.432 | 4.2004 | 3.4513 | 2.3806 | 9.6392 | 8.9219 | 8.2217 | 7.2496 | 6.7989 | 6.4217 | 5.6916 | 5.2371 | 4.6693 | 4.4117 | 3.8222 | 3.6309 | 2.9042 | 1.9807
| LOCHSIDE | FS |  |  |  | 8.1221 | 7.5329 | 6.9672 | 6.2901 | 5.9336 | 5.6321 | 5.2165 | 4.8599 | 4.3443 | 3.9785 | 3.316 | 2.5284 | 1.3649 | 0.43439 | 10.3055 | 9.7517 | 9.2019 | 8.5616 | 8.2309 | 7.9546 | 7.5672 | 7.214 | 6.7233 | 6.3803 | 5.7449 | 4.8594 | 3.5099 | 1.7067 | 9.9065 | 9.3498 | 8.8065 | 8.1507 | 7.7994 | 7.4993 | 7.0882 | 6.7217 | 6.2124 | 5.8447 | 5.1652 | 4.3446 | 3.2514 | 2.4324
BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | NO | 4.3671 | 4.3368 | 4.3003 | 4.2659 | 1.2761 | 1.1946 | 1.1048 | 1.0481 | 0.98087 | 0.91014 | 0.77956 | 0.52904 | 0.045973 | -0.66105 | 3.9865 | 3.9746 | 3.9575 | 3.9225 | 1.1537 | 1.1053 | 1.0252 | 0.98994 | 0.86374 | 0.80388 | 0.67467 | 0.35422 | -0.20499 | -1.0361 | 3.9519 | 3.927 | 3.8962 | 3.8682 | 1.1056 | 1.0124 | 0.91626 | 0.86298 | 0.78197 | 0.70958 | 0.5586 | 0.2922 | -0.28344 | -1.1445
| LOGIE PERT | CT |  |  |  | 4.3887 | 4.3682 | 4.3436 | 4.2893 | 1.2841 | 1.1946 | 1.1048 | 1.0481 | 0.98087 | 0.91014 | 0.77956 | 0.56412 | 0.22669 | -0.11502 | 3.9929 | 3.9839 | 3.9715 | 3.9418 | 1.1819 | 1.1053 | 1.0252 | 0.98994 | 0.91961 | 0.84426 | 0.70474 | 0.4342 | 0.062408 | -0.35577 | 3.9674 | 3.9477 | 3.925 | 3.8774 | 1.1056 | 1.0124 | 0.91626 | 0.86298 | 0.78591 | 0.71197 | 0.56961 | 0.35715 | -0.032085 | -0.44734
| LOGIE PERT | LW |  |  |  | 4.3671 | 4.3368 | 4.3003 | 4.2659 | 1.2761 | 1.2417 | 1.1973 | 1.1504 | 1.0863 | 1.0192 | 0.89093 | 0.73247 | 0.14942 | -0.66105 | 3.9865 | 3.9746 | 3.9575 | 3.942 | 1.1989 | 1.1834 | 1.1596 | 1.1331 | 1.0666 | 0.99687 | 0.86814 | 0.66903 | -0.034578 | -1.0361 | 3.9519 | 3.927 | 3.8962 | 3.8682 | 1.111 | 1.0819 | 1.0426 | 1.0007 | 0.9268 | 0.84933 | 0.70191 | 0.57616 | -0.13814 | -1.1445
| LOGIE PERT | ST |  |  |  | 4.3964 | 4.3813 | 4.3702 | 4.3063 | 1.3115 | 1.2663 | 1.1839 | 1.1404 | 1.0273 | 0.96027 | 0.82855 | 0.52904 | 0.045973 | -0.45402 | 3.9952 | 3.9892 | 3.9839 | 3.9225 | 1.1537 | 1.1186 | 1.028 | 0.99216 | 0.86374 | 0.80388 | 0.67467 | 0.35422 | -0.20499 | -0.80236 | 3.9736 | 3.9616 | 3.9516 | 3.8818 | 1.1068 | 1.0614 | 0.96378 | 0.91824 | 0.78197 | 0.70958 | 0.5586 | 0.2922 | -0.28344 | -0.88507
| LOGIE PERT | FS |  |  |  | 4.4043 | 4.3946 | 4.3862 | 4.3594 | 1.3857 | 1.3598 | 1.3334 | 1.3072 | 1.2482 | 1.2002 | 1.1016 | 0.93687 | 0.82027 | 0.73594 | 3.9976 | 3.9934 | 3.9891 | 3.9709 | 1.2279 | 1.2077 | 1.1867 | 1.1665 | 1.1123 | 1.0708 | 0.98449 | 0.87894 | 0.78217 | 0.6905 | 3.9796 | 3.9713 | 3.9639 | 3.9386 | 1.1903 | 1.164 | 1.1372 | 1.1106 | 1.0474 | 0.99705 | 0.89303 | 0.81804 | 0.6977 | 0.61026
MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | NO | 12.413 | 11.6279 | 10.6625 | 9.0281 | 7.4156 | 5.1316 | 3.0836 | 1.5368 | 0.76777 | -0.057423 | -1.8894 | -2.1201 | -2.9505 | -3.6447 | 15.6826 | 15.0415 | 14.2466 | 12.9808 | 11.7053 | 9.7412 | 8.0035 | 6.8427 | 6.3493 | 5.8161 | 4.5864 | 4.6843 | 3.7148 | 1.8285 | 15.3 | 14.6228 | 13.7613 | 12.287 | 10.7295 | 8.3994 | 6.3036 | 4.7932 | 4.1009 | 3.3597 | 1.7021 | 1.4652 | 0.55187 | -0.3096
| LONGHAUGH | CT |  |  |  | 12.8128 | 12.1994 | 11.401 | 9.9289 | 8.48 | 6.3802 | 4.6452 | 3.4448 | 2.6324 | 1.7945 | -0.015843 | -1.1355 | -2.5536 | -3.3128 | 15.8866 | 15.318 | 14.5902 | 13.4753 | 12.3493 | 10.5401 | 9.0559 | 8.1749 | 7.6408 | 7.0954 | 5.8823 | 5.161 | 3.7148 | 1.9955 | 15.622 | 15.0844 | 14.3669 | 13.0751 | 11.7564 | 9.672 | 7.8825 | 6.7227 | 5.9878 | 5.2381 | 3.6178 | 2.6516 | 1.3266 | 0.5668
| LONGHAUGH | LW |  |  |  | 12.413 | 11.6279 | 10.6625 | 9.0281 | 7.4156 | 5.1316 | 3.0836 | 1.5368 | 0.76777 | -0.057423 | -1.8894 | -2.1201 | -2.9505 | -3.6447 | 15.6826 | 15.0415 | 14.2466 | 12.9808 | 11.7053 | 9.7412 | 8.0035 | 6.8427 | 6.3493 | 5.8161 | 4.5864 | 4.6843 | 3.9137 | 3.0509 | 15.3 | 14.6228 | 13.7613 | 12.287 | 10.7295 | 8.3994 | 6.3036 | 4.7932 | 4.1009 | 3.3597 | 1.7021 | 1.4652 | 0.55187 | -0.3096
| LONGHAUGH | ST |  |  |  | 12.9342 | 12.4285 | 11.8019 | 10.8418 | 9.972 | 8.5742 | 7.3353 | 6.6622 | 6.2763 | 5.9073 | 4.9279 | 3.8917 | 2.3473 | 0.69314 | 15.9349 | 15.4268 | 14.8083 | 13.8115 | 12.8963 | 11.481 | 10.0254 | 9.227 | 8.8754 | 8.5957 | 7.8262 | 6.8452 | 5.2127 | 3.0708 | 15.7167 | 15.2779 | 14.7297 | 13.8264 | 13.001 | 11.5121 | 10.1292 | 9.4201 | 9.0499 | 8.7259 | 7.8642 | 6.9327 | 5.4033 | 3.7621
| LONGHAUGH | FS |  |  |  | 13.2607 | 12.8758 | 12.3923 | 11.7068 | 11.0279 | 9.9483 | 9.1138 | 8.4712 | 7.9966 | 7.4273 | 6.3494 | 4.6634 | 2.5471 | 1.0278 | 16.2535 | 15.8615 | 15.3739 | 14.7024 | 14.0156 | 12.9401 | 12.0891 | 11.4393 | 10.9952 | 10.4552 | 9.4377 | 7.7182 | 5.1336 | 1.8285 | 15.9982 | 15.6638 | 15.2394 | 14.6337 | 14.023 | 13.0455 | 12.1519 | 11.4813 | 11.0241 | 10.4708 | 9.468 | 7.9703 | 6.0739 | 4.7254
ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | NO | 7.6972 | 7.5509 | 7.3447 | 6.8282 | 6.2684 | 5.5059 | 4.6357 | 3.9155 | 3.4168 | 2.8941 | 1.7921 | 1.4078 | 0.8169 | 0.58213 | 8.9393 | 8.8588 | 8.7336 | 8.3401 | 7.905 | 7.2156 | 6.4285 | 5.8481 | 5.5055 | 5.1429 | 4.4017 | 4.2377 | 3.8867 | 3.6998 | 8.1788 | 8.1233 | 7.9305 | 7.4001 | 6.8198 | 5.9874 | 5.0312 | 4.2686 | 3.7623 | 3.2294 | 2.1869 | 1.7839 | 1.2342 | 0.99574
| LOSSIEMOUTH | CT |  |  |  | 7.8128 | 7.7271 | 7.6003 | 7.2366 | 6.8468 | 6.3304 | 5.7842 | 5.3987 | 4.9373 | 4.4335 | 3.4078 | 2.7223 | 1.8694 | 1.4167 | 8.9812 | 8.9217 | 8.8308 | 8.6093 | 8.3565 | 7.9315 | 7.4763 | 7.2256 | 6.9405 | 6.6189 | 5.9887 | 5.6255 | 5.0025 | 4.3599 | 8.1788 | 8.1233 | 8.0411 | 7.8019 | 7.4179 | 6.8751 | 6.2989 | 5.9252 | 5.4816 | 4.9869 | 4.0185 | 3.3953 | 2.6477 | 2.2442
| LOSSIEMOUTH | LW |  |  |  | 7.6972 | 7.5509 | 7.3447 | 6.8282 | 6.2684 | 5.5059 | 4.6357 | 3.9155 | 3.4168 | 2.8941 | 1.7921 | 1.4078 | 0.8169 | 0.58213 | 8.9393 | 8.8588 | 8.7336 | 8.3401 | 7.905 | 7.2156 | 6.4285 | 5.8481 | 5.5055 | 5.1429 | 4.4017 | 4.2377 | 3.8867 | 3.6998 | 8.1788 | 8.1287 | 7.9305 | 7.4001 | 6.8198 | 5.9874 | 5.0312 | 4.2686 | 3.7623 | 3.2294 | 2.1869 | 1.7839 | 1.2342 | 0.99574
| LOSSIEMOUTH | ST |  |  |  | 7.8513 | 7.8071 | 7.7544 | 7.5044 | 7.3029 | 7.1285 | 6.7344 | 6.5276 | 6.3037 | 6.0623 | 5.4648 | 4.8417 | 4.1275 | 3.3579 | 8.9975 | 8.966 | 8.9273 | 8.6468 | 8.4298 | 8.2548 | 7.8134 | 7.612 | 7.4 | 7.2144 | 6.7714 | 6.2453 | 5.6137 | 4.8474 | 8.1851 | 8.1571 | 8.1231 | 7.8502 | 7.6415 | 7.4747 | 7.0422 | 6.8388 | 6.604 | 6.3894 | 5.8506 | 5.2826 | 4.5964 | 3.8547
| LOSSIEMOUTH | FS |  |  |  | 7.856 | 7.82 | 7.7754 | 7.6753 | 7.5655 | 7.4416 | 7.3092 | 7.1712 | 7.0007 | 6.8256 | 6.4235 | 5.7264 | 4.7188 | 4.0987 | 9.0007 | 8.9741 | 8.941 | 8.8478 | 8.7459 | 8.63 | 8.5053 | 8.378 | 8.2362 | 8.0909 | 7.7579 | 7.2202 | 6.1543 | 4.921 | 8.1895 | 8.1665 | 8.1393 | 8.0598 | 7.9741 | 7.8749 | 7.7679 | 7.6604 | 7.5026 | 7.3257 | 6.9268 | 6.3249 | 5.417 | 4.8326
BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | NO | 0.063803 | 0.042529 | 0.013077 | -0.054782 | -0.13737 | -0.25749 | -0.41806 | -0.49516 | -0.58111 | -0.66167 | -0.8241 | -1.1559 | -1.5821 | -1.997 | 0.25269 | 0.24275 | 0.22685 | 0.11561 | 0.022593 | -0.043134 | -0.24632 | -0.31378 | -0.47409 | -0.54405 | -0.70124 | -1.0889 | -1.5924 | -2.0995 | 0.16414 | 0.1458 | 0.11942 | 0.021737 | -0.076388 | -0.17467 | -0.35943 | -0.43754 | -0.60218 | -0.68158 | -0.85927 | -1.2675 | -1.7827 | -2.2904
| LOWER OLLACH | CT |  |  |  | 0.075544 | 0.060084 | 0.036943 | -0.027645 | -0.10082 | -0.25749 | -0.41806 | -0.49516 | -0.57174 | -0.66167 | -0.8241 | -1.0528 | -1.3513 | -1.643 | 0.25642 | 0.24862 | 0.23517 | 0.193 | 0.13735 | -0.022985 | -0.19172 | -0.25166 | -0.33626 | -0.42935 | -0.59989 | -0.92132 | -1.2591 | -1.6169 | 0.17341 | 0.15995 | 0.13868 | 0.077086 | 0.0034092 | -0.17467 | -0.35943 | -0.43754 | -0.52775 | -0.63054 | -0.8173 | -1.1179 | -1.4702 | -1.8263
| LOWER OLLACH | LW |  |  |  | 0.063803 | 0.042529 | 0.013077 | -0.020028 | -0.056656 | -0.090667 | -0.13596 | -0.1878 | -0.2484 | -0.31166 | -0.4322 | -0.49054 | -0.9794 | -1.6688 | 0.25269 | 0.24275 | 0.22685 | 0.2107 | 0.19235 | 0.17583 | 0.15022 | 0.12025 | 0.066173 | 0.0090941 | -0.097838 | -0.1973 | -0.78832 | -1.644 | 0.16414 | 0.1458 | 0.11942 | 0.09059 | 0.058413 | 0.028706 | -0.012594 | -0.060194 | -0.12535 | -0.19374 | -0.32324 | -0.40794 | -1.0088 | -1.8675
| LOWER OLLACH | ST |  |  |  | 0.08228 | 0.071861 | 0.060217 | -0.054782 | -0.13737 | -0.20022 | -0.37267 | -0.43982 | -0.58111 | -0.65177 | -0.80975 | -1.1559 | -1.5821 | -1.997 | 0.25869 | 0.25389 | 0.24818 | 0.11561 | 0.022593 | -0.043134 | -0.24632 | -0.31378 | -0.47409 | -0.54405 | -0.70124 | -1.0889 | -1.5924 | -2.0995 | 0.17871 | 0.16991 | 0.1598 | 0.021737 | -0.076388 | -0.14852 | -0.35791 | -0.43359 | -0.60218 | -0.68158 | -0.85927 | -1.2675 | -1.7827 | -2.2904
| LOWER OLLACH | FS |  |  |  | 0.087515 | 0.081192 | 0.070485 | 0.038684 | 0.0047183 | -0.034118 | -0.06995 | -0.10695 | -0.17063 | -0.21928 | -0.33006 | -0.47751 | -0.59773 | -0.66114 | 0.26047 | 0.25716 | 0.25199 | 0.22068 | 0.18806 | 0.15045 | 0.11318 | 0.078013 | 0.013608 | -0.03427 | -0.13695 | -0.2476 | -0.34679 | -0.42226 | 0.18295 | 0.17748 | 0.16836 | 0.13285 | 0.095412 | 0.052378 | 0.011457 | -0.029205 | -0.10108 | -0.15541 | -0.27585 | -0.42174 | -0.5434 | -0.61375
KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | NO | 0.21924 | 0.21886 | 0.21811 | 0.21704 | 0.21577 | 0.21448 | 0.21298 | 0.21015 | 0.20685 | 0.20321 | 0.19583 | 0.2069 | 0.20675 | 0.2065 | 0.22457 | 0.22425 | 0.22341 | 0.22192 | 0.22088 | 0.21982 | 0.21867 | 0.21655 | 0.21406 | 0.2112 | 0.20538 | 0.21412 | 0.21399 | 0.21378 | 0.2224 | 0.222 | 0.2212 | 0.22009 | 0.21883 | 0.21753 | 0.21611 | 0.21339 | 0.21021 | 0.20671 | 0.1996 | 0.20952 | 0.20937 | 0.20911
| LUBNAIG | CT |  |  |  | 0.21927 | 0.21888 | 0.21825 | 0.21704 | 0.21577 | 0.21448 | 0.21298 | 0.21132 | 0.20901 | 0.20714 | 0.20247 | 0.2072 | 0.2068 | 0.2065 | 0.2246 | 0.22428 | 0.22341 | 0.22192 | 0.22088 | 0.21982 | 0.21867 | 0.21742 | 0.21568 | 0.21425 | 0.21061 | 0.21438 | 0.21403 | 0.21378 | 0.22244 | 0.22204 | 0.22139 | 0.22009 | 0.21883 | 0.21753 | 0.21611 | 0.21451 | 0.21229 | 0.21049 | 0.20599 | 0.20983 | 0.20942 | 0.20911
| LUBNAIG | LW |  |  |  | 0.21924 | 0.21886 | 0.21811 | 0.2175 | 0.21672 | 0.21544 | 0.21309 | 0.21015 | 0.20685 | 0.20321 | 0.19583 | 0.2069 | 0.20675 | 0.20675 | 0.22457 | 0.22425 | 0.22357 | 0.22269 | 0.22166 | 0.2206 | 0.21876 | 0.21655 | 0.21406 | 0.2112 | 0.20538 | 0.21412 | 0.21399 | 0.21399 | 0.2224 | 0.222 | 0.2212 | 0.22055 | 0.21971 | 0.21848 | 0.21622 | 0.21339 | 0.21021 | 0.20671 | 0.1996 | 0.20952 | 0.20937 | 0.20937
| LUBNAIG | ST |  |  |  | 0.21929 | 0.21914 | 0.21892 | 0.21863 | 0.21824 | 0.21779 | 0.21723 | 0.21593 | 0.2142 | 0.21192 | 0.20627 | 0.20801 | 0.20714 | 0.20712 | 0.22462 | 0.22448 | 0.2243 | 0.22405 | 0.22372 | 0.22306 | 0.22214 | 0.221 | 0.21961 | 0.21789 | 0.21361 | 0.21508 | 0.21433 | 0.21431 | 0.22245 | 0.22229 | 0.22207 | 0.22176 | 0.22135 | 0.22087 | 0.22027 | 0.21897 | 0.21726 | 0.21509 | 0.20966 | 0.21067 | 0.20978 | 0.20975
| LUBNAIG | FS |  |  |  | 0.21931 | 0.21918 | 0.21901 | 0.21878 | 0.21849 | 0.21817 | 0.21778 | 0.21731 | 0.21661 | 0.21543 | 0.21244 | 0.21106 | 0.20715 | 0.20711 | 0.22463 | 0.22452 | 0.22437 | 0.22418 | 0.22392 | 0.22365 | 0.22312 | 0.2224 | 0.22157 | 0.2206 | 0.21826 | 0.2177 | 0.21434 | 0.21431 | 0.22247 | 0.22234 | 0.22215 | 0.22191 | 0.2216 | 0.22126 | 0.22085 | 0.22034 | 0.21966 | 0.21848 | 0.21559 | 0.21381 | 0.20979 | 0.20974
LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | NO | 6.5439 | 5.9771 | 5.6483 | 5.0941 | 4.4493 | 3.7536 | 2.9855 | 2.2919 | 1.8507 | 1.3845 | 0.46423 | 0.54677 | -0.39124 | -1.1094 | 7.5006 | 7.0496 | 6.852 | 6.5269 | 6.1061 | 5.5989 | 5.0168 | 4.5369 | 4.2059 | 3.8464 | 3.1267 | 4.5348 | 3.8426 | 2.8965 | 7.5286 | 6.9963 | 6.6938 | 6.1562 | 5.5268 | 4.8086 | 4.0002 | 3.2907 | 2.8376 | 2.3572 | 1.4106 | 1.5305 | 0.59532 | -0.3569
| LUNANHEAD | CT |  |  |  | 6.7728 | 6.3183 | 6.0484 | 5.5492 | 4.975 | 4.2664 | 3.551 | 3.0322 | 2.6102 | 2.1602 | 1.2515 | 0.76795 | -0.39124 | -1.0965 | 7.5921 | 7.1673 | 6.9498 | 6.6221 | 6.2948 | 5.7607 | 5.2084 | 4.9006 | 4.5983 | 4.3286 | 3.7327 | 4.6746 | 4.0027 | 2.8965 | 7.7019 | 7.3233 | 7.082 | 6.5827 | 6.039 | 5.3043 | 4.5572 | 4.0546 | 3.6283 | 3.1667 | 2.2394 | 1.7569 | 0.63674 | -0.091171
| LUNANHEAD | LW |  |  |  | 6.5439 | 5.9771 | 5.6483 | 5.0941 | 4.4493 | 3.7536 | 2.9855 | 2.2919 | 1.8507 | 1.3845 | 0.46423 | 0.54677 | -0.31352 | -1.1094 | 7.5006 | 7.0496 | 6.852 | 6.5269 | 6.1061 | 5.5989 | 5.0168 | 4.5369 | 4.2059 | 3.8464 | 3.1267 | 4.5348 | 3.8426 | 2.9565 | 7.5286 | 6.9963 | 6.6938 | 6.1562 | 5.5268 | 4.8086 | 4.0002 | 3.2907 | 2.8376 | 2.3572 | 1.4106 | 1.5305 | 0.59532 | -0.3569
| LUNANHEAD | ST |  |  |  | 6.811 | 6.442 | 6.3186 | 5.963 | 5.6604 | 5.4072 | 4.9047 | 4.6321 | 4.3044 | 4.0102 | 3.2924 | 2.8062 | 1.6748 | 0.42027 | 7.6194 | 7.2621 | 7.1559 | 6.7691 | 6.4565 | 6.2099 | 5.6597 | 5.4062 | 5.0967 | 4.8479 | 4.2431 | 4.8266 | 4.1795 | 2.9974 | 7.7103 | 7.3729 | 7.2863 | 6.9203 | 6.5999 | 6.3299 | 5.7623 | 5.4911 | 5.1615 | 4.898 | 4.1475 | 3.4759 | 2.3383 | 1.1061
| LUNANHEAD | FS |  |  |  | 6.9687 | 6.6887 | 6.5928 | 6.4248 | 6.2569 | 6.08 | 5.8836 | 5.6746 | 5.4227 | 5.1717 | 4.6255 | 3.6212 | 2.6134 | 1.8318 | 7.7738 | 7.5028 | 7.4193 | 7.2617 | 7.1059 | 6.9416 | 6.7672 | 6.5899 | 6.3956 | 6.2034 | 5.7662 | 6.0213 | 5.4063 | 3.7774 | 7.8575 | 7.602 | 7.5326 | 7.4008 | 7.2417 | 7.0422 | 6.8367 | 6.6277 | 6.3766 | 6.1251 | 5.5751 | 4.6114 | 3.6322 | 2.933
PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | NO | 0.093834 | 0.093556 | 0.092956 | 0.090849 | 0.08858 | 0.088156 | 0.088827 | 0.085969 | 0.0848 | 0.083499 | 0.080598 | 0.077684 | 0.077604 | 0.076175 | 0.10251 | 0.10231 | 0.10186 | 0.10077 | 0.099756 | 0.099416 | 0.099177 | 0.097709 | 0.096654 | 0.095513 | 0.093403 | 0.092085 | 0.092018 | 0.091654 | 0.092702 | 0.092415 | 0.091819 | 0.089871 | 0.087833 | 0.087413 | 0.087802 | 0.085233 | 0.08395 | 0.082562 | 0.079834 | 0.0771 | 0.077021 | 0.075798
| LUSSAGIVEN | CT |  |  |  | 0.093842 | 0.093633 | 0.093167 | 0.090849 | 0.090116 | 0.089602 | 0.088827 | 0.086474 | 0.08562 | 0.084446 | 0.080598 | 0.077913 | 0.077604 | 0.078678 | 0.10254 | 0.10235 | 0.10202 | 0.10077 | 0.10015 | 0.099729 | 0.099177 | 0.098169 | 0.097397 | 0.096304 | 0.093776 | 0.092276 | 0.092018 | 0.092274 | 0.092744 | 0.092492 | 0.09203 | 0.089871 | 0.089133 | 0.088611 | 0.087803 | 0.085785 | 0.084852 | 0.083534 | 0.079834 | 0.077329 | 0.077021 | 0.077974
| LUSSAGIVEN | LW |  |  |  | 0.093834 | 0.093556 | 0.092956 | 0.090952 | 0.08858 | 0.088156 | 0.088828 | 0.085969 | 0.0848 | 0.083499 | 0.080948 | 0.077684 | 0.078892 | 0.078892 | 0.10251 | 0.10231 | 0.10186 | 0.10086 | 0.099756 | 0.099416 | 0.099177 | 0.097709 | 0.096654 | 0.095513 | 0.093403 | 0.092085 | 0.09244 | 0.09244 | 0.092702 | 0.092415 | 0.091819 | 0.089972 | 0.087833 | 0.087413 | 0.087802 | 0.085233 | 0.08395 | 0.082562 | 0.080156 | 0.0771 | 0.078172 | 0.078172
| LUSSAGIVEN | ST |  |  |  | 0.09386 | 0.093768 | 0.093601 | 0.093372 | 0.093058 | 0.092709 | 0.09349 | 0.092962 | 0.092301 | 0.091488 | 0.089512 | 0.08147 | 0.077904 | 0.076175 | 0.10254 | 0.10246 | 0.10234 | 0.10218 | 0.10194 | 0.10166 | 0.10177 | 0.10135 | 0.10083 | 0.10018 | 0.098614 | 0.093904 | 0.092228 | 0.091654 | 0.092743 | 0.092626 | 0.09246 | 0.092233 | 0.091921 | 0.091575 | 0.091573 | 0.091024 | 0.090347 | 0.089515 | 0.08746 | 0.080697 | 0.077316 | 0.075798
| LUSSAGIVEN | FS |  |  |  | 0.093868 | 0.0938 | 0.093662 | 0.093481 | 0.093239 | 0.092984 | 0.092675 | 0.092308 | 0.093076 | 0.092556 | 0.089939 | 0.083804 | 0.079376 | 0.07653 | 0.10255 | 0.10248 | 0.10239 | 0.10226 | 0.10208 | 0.10188 | 0.10164 | 0.10135 | 0.10144 | 0.10103 | 0.099485 | 0.095763 | 0.092807 | 0.09176 | 0.092754 | 0.092657 | 0.09252 | 0.09234 | 0.0921 | 0.091847 | 0.091541 | 0.091176 | 0.091283 | 0.090806 | 0.088823 | 0.082935 | 0.078765 | 0.076109
LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | NO | 9.1674 | 8.8486 | 8.4649 | 8.0957 | 7.7642 | 7.3274 | 6.8049 | 6.4047 | 6.1284 | 5.8112 | 5.2259 | 5.4663 | 4.9867 | 4.4606 | 9.2453 | 8.9502 | 8.5477 | 8.2467 | 8.0018 | 7.6243 | 7.1706 | 6.8751 | 6.6851 | 6.4482 | 6.0044 | 6.3537 | 5.848 | 5.1971 | 8.2341 | 7.9438 | 7.5522 | 7.1774 | 6.8425 | 6.3747 | 5.8219 | 5.415 | 5.1464 | 4.8345 | 4.2166 | 4.4853 | 3.9258 | 3.2732
| LYNDHURST | CT |  |  |  | 9.2464 | 8.9731 | 8.6571 | 8.3416 | 8.063 | 7.7224 | 7.3293 | 7.0716 | 6.8291 | 6.5542 | 6.0521 | 6.1354 | 5.6929 | 5.3752 | 9.2719 | 9.0025 | 8.6428 | 8.4095 | 8.2253 | 7.9526 | 7.6225 | 7.4518 | 7.2944 | 7.1018 | 6.787 | 6.9105 | 6.3425 | 5.5944 | 8.2437 | 7.9716 | 7.6336 | 7.4155 | 7.1627 | 6.8133 | 6.4098 | 6.1607 | 5.9148 | 5.6406 | 5.153 | 5.2953 | 4.8436 | 4.4889
| LYNDHURST | LW |  |  |  | 9.1674 | 8.8486 | 8.4649 | 8.0957 | 7.7642 | 7.3274 | 6.8049 | 6.4047 | 6.1284 | 5.8112 | 5.2259 | 5.4663 | 4.9867 | 4.4606 | 9.2453 | 8.9502 | 8.5477 | 8.2467 | 8.0018 | 7.6243 | 7.1706 | 6.8751 | 6.6851 | 6.4482 | 6.0044 | 6.3537 | 5.848 | 5.1971 | 8.2341 | 7.9438 | 7.5522 | 7.1774 | 6.8425 | 6.3747 | 5.8219 | 5.415 | 5.1464 | 4.8345 | 4.2166 | 4.4853 | 3.9258 | 3.2732
| LYNDHURST | ST |  |  |  | 9.2785 | 9.0496 | 8.778 | 8.5442 | 8.3841 | 8.2378 | 7.938 | 7.7699 | 7.587 | 7.3745 | 6.7965 | 7.2525 | 6.6738 | 6.0686 | 9.2854 | 9.0431 | 8.7263 | 8.4695 | 8.3071 | 8.168 | 7.8563 | 7.7081 | 7.5411 | 7.3538 | 6.8604 | 7.1368 | 6.496 | 5.578 | 8.2521 | 8.0121 | 7.7311 | 7.4781 | 7.3066 | 7.155 | 6.8273 | 6.654 | 6.4118 | 6.1383 | 5.5257 | 6.2287 | 5.6194 | 4.979
| LYNDHURST | FS |  |  |  | 9.3068 | 9.1307 | 8.9379 | 8.8216 | 8.7182 | 8.6282 | 8.5058 | 8.4037 | 8.2863 | 8.1335 | 7.8486 | 7.6725 | 7.1942 | 6.7992 | 9.3204 | 9.1349 | 8.8941 | 8.7632 | 8.6585 | 8.5614 | 8.4348 | 8.3353 | 8.2233 | 8.0766 | 7.8069 | 7.6129 | 6.8634 | 5.5128 | 8.2866 | 8.1054 | 7.8948 | 7.7703 | 7.6707 | 7.5735 | 7.448 | 7.345 | 7.2325 | 7.05 | 6.6738 | 6.7673 | 6.324 | 5.9632
THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | NO | 0.56797 | 0.55209 | 0.5328 | 0.50182 | 0.4641 | 0.42182 | 0.38202 | 0.33856 | 0.32747 | 0.31613 | 0.28368 | 0.29575 | 0.26587 | 0.24928 | 0.72386 | 0.71632 | 0.70573 | 0.691 | 0.66901 | 0.64985 | 0.63149 | 0.61165 | 0.60106 | 0.5889 | 0.55542 | 0.56239 | 0.54655 | 0.5349 | 0.64386 | 0.62958 | 0.61171 | 0.58393 | 0.54882 | 0.51124 | 0.47594 | 0.43755 | 0.42495 | 0.41287 | 0.37553 | 0.38344 | 0.35823 | 0.34365
| LYNESS | CT |  |  |  | 0.58325 | 0.57038 | 0.55402 | 0.50772 | 0.4641 | 0.42182 | 0.38202 | 0.33856 | 0.32747 | 0.31613 | 0.2863 | 0.3074 | 0.26587 | 0.24928 | 0.72962 | 0.72323 | 0.7135 | 0.691 | 0.66901 | 0.64985 | 0.63149 | 0.61165 | 0.60106 | 0.5889 | 0.561 | 0.56575 | 0.54655 | 0.5349 | 0.65727 | 0.64561 | 0.6304 | 0.5885 | 0.54882 | 0.51124 | 0.47594 | 0.43755 | 0.42495 | 0.41287 | 0.38069 | 0.39394 | 0.35823 | 0.34365
| LYNESS | LW |  |  |  | 0.56797 | 0.55209 | 0.5328 | 0.50182 | 0.46734 | 0.43937 | 0.40042 | 0.36108 | 0.34548 | 0.32647 | 0.28368 | 0.29575 | 0.27457 | 0.26576 | 0.72386 | 0.71632 | 0.70573 | 0.69141 | 0.67529 | 0.66208 | 0.64195 | 0.62053 | 0.60684 | 0.5912 | 0.55542 | 0.56239 | 0.55375 | 0.55048 | 0.64386 | 0.62958 | 0.61171 | 0.58393 | 0.55312 | 0.52812 | 0.49235 | 0.45576 | 0.44011 | 0.42125 | 0.37553 | 0.38344 | 0.3651 | 0.35803
| LYNESS | ST |  |  |  | 0.58678 | 0.58102 | 0.57608 | 0.56356 | 0.54991 | 0.53719 | 0.5233 | 0.51188 | 0.49173 | 0.47479 | 0.43038 | 0.3629 | 0.32814 | 0.30458 | 0.73094 | 0.72802 | 0.72509 | 0.719 | 0.712 | 0.70507 | 0.69722 | 0.6897 | 0.67813 | 0.66684 | 0.63807 | 0.59021 | 0.57076 | 0.55784 | 0.66036 | 0.65515 | 0.6506 | 0.63932 | 0.62693 | 0.61529 | 0.60247 | 0.59167 | 0.57305 | 0.55638 | 0.51254 | 0.44369 | 0.41224 | 0.39176
| LYNESS | FS |  |  |  | 0.59064 | 0.58524 | 0.58298 | 0.57235 | 0.56355 | 0.55005 | 0.54039 | 0.52738 | 0.51725 | 0.49914 | 0.46664 | 0.37551 | 0.30969 | 0.29167 | 0.73246 | 0.72979 | 0.72803 | 0.72297 | 0.71824 | 0.71166 | 0.7062 | 0.69915 | 0.69269 | 0.68286 | 0.66325 | 0.61051 | 0.5633 | 0.55072 | 0.66203 | 0.65891 | 0.65675 | 0.64721 | 0.63918 | 0.62702 | 0.61811 | 0.60618 | 0.59669 | 0.58007 | 0.54917 | 0.46092 | 0.39597 | 0.38029
STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | NO | 0.17346 | 0.17318 | 0.16893 | 0.16847 | 0.16757 | 0.16523 | 0.1647 | 0.16047 | 0.15957 | 0.15707 | 0.15631 | 0.15636 | 0.15392 | 0.15306 | 0.19994 | 0.19972 | 0.19791 | 0.19755 | 0.19683 | 0.19575 | 0.19533 | 0.19354 | 0.19271 | 0.19096 | 0.18955 | 0.18986 | 0.1889 | 0.18834 | 0.18573 | 0.18549 | 0.183 | 0.18254 | 0.18166 | 0.17955 | 0.17903 | 0.17526 | 0.17437 | 0.17193 | 0.17062 | 0.17056 | 0.16839 | 0.16754
| MAARUIG | CT |  |  |  | 0.17349 | 0.17323 | 0.17278 | 0.17204 | 0.16757 | 0.16523 | 0.1647 | 0.16047 | 0.15957 | 0.15835 | 0.15752 | 0.15724 | 0.15512 | 0.15306 | 0.19997 | 0.19976 | 0.1994 | 0.19881 | 0.19683 | 0.19575 | 0.19533 | 0.19354 | 0.19282 | 0.19184 | 0.19051 | 0.19005 | 0.18916 | 0.18834 | 0.18573 | 0.18549 | 0.18517 | 0.1845 | 0.18166 | 0.17955 | 0.17903 | 0.17526 | 0.17437 | 0.17316 | 0.17185 | 0.17108 | 0.16927 | 0.16754
| MAARUIG | LW |  |  |  | 0.17346 | 0.17318 | 0.16893 | 0.16847 | 0.16792 | 0.16747 | 0.16472 | 0.16181 | 0.16025 | 0.15707 | 0.15631 | 0.15703 | 0.15509 | 0.15324 | 0.19994 | 0.19972 | 0.19791 | 0.19755 | 0.19711 | 0.19675 | 0.19535 | 0.19381 | 0.19271 | 0.19096 | 0.18955 | 0.18986 | 0.18913 | 0.1885 | 0.18573 | 0.18553 | 0.183 | 0.18254 | 0.182 | 0.18156 | 0.17905 | 0.17637 | 0.17487 | 0.17193 | 0.17062 | 0.17085 | 0.16924 | 0.16774
| MAARUIG | ST |  |  |  | 0.1735 | 0.17338 | 0.17323 | 0.17301 | 0.17272 | 0.1724 | 0.17014 | 0.16779 | 0.1687 | 0.1665 | 0.16279 | 0.15636 | 0.15544 | 0.15542 | 0.19997 | 0.19988 | 0.19976 | 0.19959 | 0.19936 | 0.19909 | 0.19809 | 0.19701 | 0.19707 | 0.19593 | 0.19376 | 0.19007 | 0.18939 | 0.18938 | 0.18576 | 0.18568 | 0.18557 | 0.18543 | 0.18524 | 0.18502 | 0.18399 | 0.18188 | 0.18256 | 0.18058 | 0.17707 | 0.17056 | 0.16957 | 0.16955
| MAARUIG | FS |  |  |  | 0.17351 | 0.17341 | 0.17329 | 0.17312 | 0.1729 | 0.17266 | 0.17052 | 0.16833 | 0.16944 | 0.16896 | 0.16781 | 0.15842 | 0.15392 | 0.1539 | 0.19998 | 0.19991 | 0.19981 | 0.19967 | 0.19949 | 0.1993 | 0.19839 | 0.19744 | 0.19767 | 0.19728 | 0.19636 | 0.19184 | 0.1889 | 0.18888 | 0.18577 | 0.1857 | 0.18561 | 0.18551 | 0.18537 | 0.18521 | 0.18437 | 0.18241 | 0.18334 | 0.18283 | 0.18158 | 0.17293 | 0.16839 | 0.16836
LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | NO | 13.6671 | 13.5055 | 13.1407 | 12.5532 | 12.0767 | 11.6214 | 11.0741 | 10.4535 | 9.8921 | 9.3217 | 8.1909 | 7.4526 | 6.5118 | 5.8493 | 14.6989 | 14.6348 | 14.4626 | 14.2654 | 14.0485 | 13.8466 | 13.5839 | 13.2483 | 12.9182 | 12.5978 | 11.9057 | 11.0361 | 9.943 | 8.4508 | 14.0023 | 13.9528 | 13.7921 | 13.6439 | 13.5178 | 13.374 | 13.1037 | 12.6155 | 12.139 | 11.5859 | 10.4687 | 9.767 | 8.8571 | 7.9668
| MACALPINE ROAD | CT |  |  |  | 13.8003 | 13.7579 | 13.5033 | 12.9185 | 12.4362 | 11.9737 | 11.5174 | 11.0248 | 10.4719 | 9.8605 | 8.6791 | 7.4526 | 6.5118 | 5.8493 | 14.7462 | 14.6953 | 14.5075 | 14.3074 | 14.1138 | 13.8466 | 13.5839 | 13.2957 | 12.9592 | 12.603 | 11.9057 | 11.0361 | 9.943 | 8.5406 | 14.0325 | 13.9907 | 13.8089 | 13.6439 | 13.5178 | 13.374 | 13.2356 | 13.0139 | 12.5749 | 12.0195 | 10.8743 | 9.767 | 8.8571 | 8.1578
| MACALPINE ROAD | LW |  |  |  | 13.6671 | 13.5055 | 13.1407 | 12.5532 | 12.0767 | 11.6214 | 11.0741 | 10.4535 | 9.8921 | 9.3217 | 8.1909 | 7.4933 | 6.663 | 5.8677 | 14.6989 | 14.6348 | 14.4626 | 14.2654 | 14.0485 | 13.8471 | 13.5851 | 13.2483 | 12.9182 | 12.5978 | 11.9339 | 11.6365 | 10.836 | 9.8471 | 14.0023 | 13.9528 | 13.7921 | 13.673 | 13.599 | 13.5242 | 13.1037 | 12.6155 | 12.139 | 11.5859 | 10.4687 | 9.8708 | 8.9545 | 7.9668
| MACALPINE ROAD | ST |  |  |  | 13.8027 | 13.7763 | 13.6372 | 13.4767 | 13.392 | 13.2943 | 13.1461 | 12.9716 | 12.7126 | 12.4958 | 11.9944 | 10.7904 | 9.5921 | 8.3993 | 14.7536 | 14.7264 | 14.6043 | 14.4764 | 14.3995 | 14.3206 | 14.191 | 14.0415 | 13.8133 | 13.6648 | 13.2778 | 12.1704 | 10.82 | 9.1334 | 14.0352 | 14.0094 | 13.8849 | 13.7532 | 13.6793 | 13.6056 | 13.4822 | 13.346 | 13.1314 | 12.9959 | 12.6797 | 12.446 | 11.2853 | 10.1205
| MACALPINE ROAD | FS |  |  |  | 13.849 | 13.8318 | 13.714 | 13.6137 | 13.5403 | 13.4494 | 13.3478 | 13.205 | 13.0017 | 12.805 | 12.3614 | 11.3011 | 9.9453 | 9.0146 | 14.8003 | 14.7823 | 14.6835 | 14.6063 | 14.5594 | 14.5056 | 14.4478 | 14.3448 | 14.1696 | 13.9982 | 13.6056 | 12.6221 | 10.8146 | 8.4508 | 14.082 | 14.0655 | 13.9615 | 13.8797 | 13.8373 | 13.7893 | 13.7371 | 13.6433 | 13.5276 | 13.4333 | 13.2239 | 13.0898 | 11.9097 | 11.1322
MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | NO | 13.4289 | 13.1325 | 12.6886 | 11.9486 | 11.1651 | 10.2731 | 8.9512 | 7.6189 | 6.4542 | 5.7453 | 4.2656 | 3.2052 | 1.6845 | 0.62394 | 15.4482 | 15.3892 | 15.2169 | 15.0428 | 14.8216 | 14.317 | 13.3965 | 12.5035 | 11.6785 | 11.2076 | 10.2329 | 9.8406 | 8.8573 | 7.8187 | 16.3529 | 16.1128 | 15.724 | 15.0968 | 14.4215 | 13.5834 | 12.3026 | 11.0364 | 9.9394 | 9.2502 | 7.8228 | 6.9059 | 5.5957 | 4.6058
| MACDUFF | CT |  |  |  | 13.6992 | 13.5319 | 13.2332 | 12.5547 | 11.8289 | 10.9884 | 9.8353 | 8.7777 | 7.597 | 6.7698 | 5.1367 | 3.5147 | 1.6845 | 0.62394 | 15.4482 | 15.3892 | 15.2169 | 15.0558 | 14.872 | 14.4977 | 13.7546 | 13.1066 | 12.3178 | 11.7817 | 10.7412 | 9.9247 | 8.8573 | 7.8187 | 16.5441 | 16.3984 | 16.1235 | 15.5432 | 14.9073 | 14.1394 | 13.0971 | 12.1266 | 11.0323 | 10.2402 | 8.6861 | 7.2246 | 5.5957 | 4.6058
| MACDUFF | LW |  |  |  | 13.4289 | 13.1325 | 12.6886 | 11.9486 | 11.1651 | 10.2731 | 8.9512 | 7.6189 | 6.4542 | 5.7453 | 4.2656 | 3.2052 | 1.9095 | 0.9964 | 15.4486 | 15.4032 | 15.2441 | 15.0428 | 14.8216 | 14.317 | 13.3965 | 12.5035 | 11.6785 | 11.2076 | 10.2329 | 9.8406 | 9.011 | 8.1513 | 16.3529 | 16.1128 | 15.724 | 15.0968 | 14.4215 | 13.5834 | 12.3026 | 11.0364 | 9.9394 | 9.2502 | 7.8228 | 6.9059 | 5.6548 | 4.6584
| MACDUFF | ST |  |  |  | 13.8221 | 13.7604 | 13.6054 | 13.2891 | 13.0087 | 12.7573 | 11.9945 | 11.3651 | 10.5765 | 10.2158 | 9.4187 | 8.0517 | 6.4739 | 4.6788 | 15.4611 | 15.437 | 15.3355 | 15.0474 | 14.825 | 14.6473 | 13.8982 | 13.3381 | 12.5448 | 12.2995 | 11.7633 | 11.0796 | 9.9043 | 8.5623 | 16.6291 | 16.5705 | 16.432 | 16.0757 | 15.7686 | 15.5018 | 14.7172 | 14.1241 | 13.3849 | 13.0101 | 12.1658 | 10.65 | 9.2368 | 7.7481
| MACDUFF | FS |  |  |  | 13.8391 | 13.7875 | 13.6711 | 13.5027 | 13.3162 | 13.1138 | 12.7402 | 12.2563 | 11.6301 | 11.2961 | 10.5736 | 9.0064 | 7.1819 | 5.8575 | 15.4652 | 15.4464 | 15.3693 | 15.2842 | 15.1889 | 15.0795 | 14.7918 | 14.3972 | 13.8503 | 13.6763 | 13.2857 | 12.4741 | 10.8582 | 9.3579 | 16.6433 | 16.5948 | 16.4893 | 16.3271 | 16.1447 | 15.9459 | 15.6009 | 15.1623 | 14.6109 | 14.2966 | 13.6055 | 12.1078 | 10.4432 | 9.4142
CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 1.4198 | 1.3961 | 1.3581 | 1.3148 | 1.2621 | 1.212 | 1.1582 | 1.1 | 1.0428 | 0.98395 | 0.87009 | 0.82571 | 0.80035 | 0.77983 | 2.1718 | 2.1576 | 2.134 | 2.1086 | 2.0738 | 2.0443 | 2.0128 | 1.9775 | 1.939 | 1.8988 | 1.8209 | 1.8004 | 1.7706 | 1.7434 | 1.2998 | 1.28 | 1.2541 | 1.2211 | 1.1886 | 1.1535 | 1.1099 | 1.0712 | 1.0481 | 1.022 | 0.97026 | 1.0371 | 1.0123 | 0.99332
| MACHRIE | CT |  |  |  | 1.431 | 1.4119 | 1.3882 | 1.3266 | 1.2621 | 1.212 | 1.1582 | 1.1107 | 1.068 | 1.0108 | 0.90197 | 0.84282 | 0.80035 | 0.77983 | 2.1776 | 2.1657 | 2.1498 | 2.1127 | 2.0738 | 2.0443 | 2.0128 | 1.9841 | 1.955 | 1.9159 | 1.8411 | 1.8027 | 1.7706 | 1.7434 | 1.3119 | 1.295 | 1.2798 | 1.235 | 1.1936 | 1.1535 | 1.1099 | 1.0712 | 1.0512 | 1.0352 | 0.99794 | 1.052 | 1.0123 | 0.99332
| MACHRIE | LW |  |  |  | 1.4198 | 1.3961 | 1.3581 | 1.3148 | 1.2689 | 1.2282 | 1.167 | 1.1 | 1.0428 | 0.98395 | 0.87009 | 0.82571 | 0.80448 | 0.79976 | 2.1718 | 2.1576 | 2.134 | 2.1086 | 2.0812 | 2.0573 | 2.0195 | 1.9775 | 1.939 | 1.8988 | 1.8209 | 1.8004 | 1.7891 | 1.787 | 1.2998 | 1.28 | 1.2541 | 1.2211 | 1.1886 | 1.1559 | 1.116 | 1.0743 | 1.0481 | 1.022 | 0.97026 | 1.0371 | 1.0171 | 1.0125
| MACHRIE | ST |  |  |  | 1.4465 | 1.4421 | 1.4345 | 1.4216 | 1.4089 | 1.3963 | 1.3751 | 1.3539 | 1.3223 | 1.2858 | 1.2028 | 1.0111 | 0.98144 | 0.96595 | 2.1852 | 2.1816 | 2.176 | 2.1674 | 2.1582 | 2.1486 | 2.1342 | 2.119 | 2.0979 | 2.0732 | 2.0159 | 1.8813 | 1.848 | 1.8267 | 1.3271 | 1.3231 | 1.3175 | 1.3081 | 1.3007 | 1.2936 | 1.2803 | 1.2683 | 1.2504 | 1.2308 | 1.1888 | 1.2132 | 1.1867 | 1.1717
| MACHRIE | FS |  |  |  | 1.4471 | 1.4409 | 1.4333 | 1.422 | 1.4082 | 1.3939 | 1.376 | 1.3545 | 1.3349 | 1.3098 | 1.2498 | 1.0643 | 0.91222 | 0.8967 | 2.1856 | 2.1812 | 2.1758 | 2.1682 | 2.159 | 2.1493 | 2.1374 | 2.1233 | 2.1094 | 2.0924 | 2.0517 | 1.9331 | 1.8189 | 1.7927 | 1.3279 | 1.322 | 1.3162 | 1.3067 | 1.2965 | 1.2857 | 1.2726 | 1.2576 | 1.2461 | 1.2316 | 1.1978 | 1.1879 | 1.1207 | 1.1067
FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 7.6812 | 7.5819 | 7.5343 | 7.4734 | 7.4138 | 7.343 | 7.2589 | 7.1823 | 7.1302 | 7.0646 | 6.9384 | 7.0466 | 6.9966 | 6.9681 | 6.993 | 6.9376 | 6.9092 | 6.8758 | 6.8351 | 6.7921 | 6.7442 | 6.7003 | 6.6556 | 6.6038 | 6.503 | 6.5941 | 6.5475 | 6.5061 | 6.7462 | 6.7329 | 6.7296 | 6.7255 | 6.7081 | 6.6429 | 6.5714 | 6.5022 | 6.4496 | 6.3852 | 6.261 | 6.3619 | 6.322 | 6.2992
| MALLAIG | CT |  |  |  | 7.6989 | 7.6175 | 7.5825 | 7.5032 | 7.4195 | 7.343 | 7.2589 | 7.1823 | 7.1316 | 7.0748 | 6.9659 | 7.0634 | 6.9966 | 6.9681 | 7.0007 | 6.9532 | 6.9308 | 6.8846 | 6.8351 | 6.7921 | 6.7442 | 6.7003 | 6.6608 | 6.6149 | 6.5258 | 6.5941 | 6.5475 | 6.5061 | 6.7468 | 6.7354 | 6.7328 | 6.7277 | 6.7081 | 6.6429 | 6.5714 | 6.5022 | 6.4557 | 6.4015 | 6.2941 | 6.3761 | 6.322 | 6.2992
| MALLAIG | LW |  |  |  | 7.6812 | 7.5819 | 7.5343 | 7.4734 | 7.4138 | 7.3584 | 7.278 | 7.1906 | 7.1302 | 7.0646 | 6.9384 | 7.0466 | 7.0094 | 6.9967 | 6.993 | 6.9376 | 6.9092 | 6.8758 | 6.8411 | 6.8096 | 6.7596 | 6.7034 | 6.6556 | 6.6038 | 6.503 | 6.5979 | 6.5803 | 6.5744 | 6.7462 | 6.7329 | 6.7296 | 6.7255 | 6.7081 | 6.6602 | 6.5882 | 6.509 | 6.4496 | 6.3852 | 6.261 | 6.3619 | 6.3328 | 6.3228
| MALLAIG | ST |  |  |  | 7.7167 | 7.6496 | 7.6362 | 7.6173 | 7.5939 | 7.5656 | 7.5275 | 7.492 | 7.4475 | 7.3956 | 7.2754 | 7.211 | 7.1558 | 7.1229 | 7.009 | 6.9716 | 6.963 | 6.9505 | 6.9345 | 6.915 | 6.8893 | 6.8632 | 6.831 | 6.7928 | 6.7022 | 6.6618 | 6.6143 | 6.5734 | 6.7481 | 6.7378 | 6.7371 | 6.7359 | 6.7344 | 6.7322 | 6.7288 | 6.726 | 6.7223 | 6.68 | 6.5515 | 6.4995 | 6.4537 | 6.4296
| MALLAIG | FS |  |  |  | 7.7179 | 7.6633 | 7.6508 | 7.6298 | 7.6045 | 7.5783 | 7.5522 | 7.5216 | 7.4895 | 7.4509 | 7.3683 | 7.2451 | 7.1072 | 7.0759 | 7.0097 | 6.9787 | 6.9708 | 6.9581 | 6.9424 | 6.9258 | 6.9083 | 6.8877 | 6.8649 | 6.8379 | 6.7775 | 6.6999 | 6.5772 | 6.5082 | 6.7481 | 6.7392 | 6.7383 | 6.7369 | 6.7352 | 6.7333 | 6.7315 | 6.7293 | 6.727 | 6.7241 | 6.6594 | 6.5449 | 6.4128 | 6.3878
KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | NO | 3.842 | 3.6984 | 3.5252 | 3.351 | 3.1648 | 2.9887 | 2.7285 | 2.4906 | 2.3118 | 2.1351 | 1.8029 | 1.6166 | 1.2157 | 0.99118 | 4.6683 | 4.6051 | 4.5193 | 4.4355 | 4.333 | 4.1796 | 4.0199 | 3.8896 | 3.7454 | 3.6035 | 3.3335 | 3.1457 | 2.8537 | 2.527 | 4.046 | 3.9196 | 3.7618 | 3.6054 | 3.4367 | 3.2457 | 2.9974 | 2.7804 | 2.5983 | 2.4115 | 2.0613 | 1.8586 | 1.4762 | 1.2417
| MARNOCH | CT |  |  |  | 3.9342 | 3.8409 | 3.7273 | 3.4877 | 3.242 | 2.9887 | 2.7285 | 2.4906 | 2.3118 | 2.1351 | 1.8029 | 1.6166 | 1.2157 | 0.99118 | 4.7025 | 4.6574 | 4.5942 | 4.468 | 4.333 | 4.1796 | 4.0199 | 3.8896 | 3.7454 | 3.6035 | 3.3335 | 3.1457 | 2.8623 | 2.6022 | 4.1241 | 4.0407 | 3.9355 | 3.7154 | 3.4866 | 3.2457 | 2.9974 | 2.7804 | 2.5983 | 2.4115 | 2.0613 | 1.8586 | 1.4762 | 1.2417
| MARNOCH | LW |  |  |  | 3.842 | 3.6984 | 3.5252 | 3.351 | 3.1648 | 2.9887 | 2.7687 | 2.5192 | 2.3233 | 2.1558 | 1.804 | 1.7213 | 1.4064 | 1.08 | 4.6683 | 4.6051 | 4.5193 | 4.4355 | 4.3429 | 4.2581 | 4.1365 | 3.9885 | 3.833 | 3.702 | 3.4355 | 3.4049 | 3.1298 | 2.783 | 4.046 | 3.9196 | 3.7618 | 3.6054 | 3.4367 | 3.279 | 3.0736 | 2.8384 | 2.6382 | 2.4622 | 2.109 | 2.0332 | 1.6965 | 1.3177
| MARNOCH | ST |  |  |  | 3.983 | 3.921 | 3.8545 | 3.7309 | 3.61 | 3.4925 | 3.3255 | 3.1871 | 2.9884 | 2.8396 | 2.4994 | 1.8886 | 1.4381 | 1.1094 | 4.7208 | 4.6924 | 4.6599 | 4.5709 | 4.4899 | 4.4158 | 4.2836 | 4.1873 | 4.0284 | 3.9224 | 3.6762 | 3.2161 | 2.8537 | 2.527 | 4.1647 | 4.1103 | 4.0511 | 3.9275 | 3.8093 | 3.6968 | 3.5242 | 3.3898 | 3.1885 | 3.0398 | 2.6982 | 2.0703 | 1.6237 | 1.2926
| MARNOCH | FS |  |  |  | 4.0153 | 3.9701 | 3.925 | 3.8456 | 3.7579 | 3.6692 | 3.5732 | 3.469 | 3.3219 | 3.1921 | 2.9205 | 2.2318 | 1.7369 | 1.5665 | 4.7326 | 4.7109 | 4.6871 | 4.6425 | 4.5922 | 4.5394 | 4.4813 | 4.4132 | 4.3106 | 4.2279 | 4.0464 | 3.6394 | 3.2488 | 3.0177 | 4.192 | 4.1521 | 4.1115 | 4.0381 | 3.9566 | 3.8734 | 3.7829 | 3.6841 | 3.5428 | 3.4185 | 3.155 | 2.5024 | 2.0317 | 1.8809
BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 3.0838 | 3.0346 | 2.9789 | 2.9153 | 2.8338 | 2.6559 | 2.4692 | 2.254 | 2.1416 | 2.0121 | 1.7618 | 1.5116 | 1.0955 | 0.67515 | 3.417 | 3.3969 | 3.3737 | 3.2912 | 3.1986 | 3.1263 | 2.9322 | 2.8337 | 2.6699 | 2.587 | 2.3944 | 2.1231 | 1.6384 | 1.1601 | 2.9567 | 2.9307 | 2.8979 | 2.8259 | 2.7272 | 2.6195 | 2.4223 | 2.2567 | 2.1523 | 2.0467 | 1.838 | 1.5508 | 1.0307 | 0.53207
| MARYBANK | CT |  |  |  | 3.1089 | 3.0767 | 3.0328 | 2.9402 | 2.8338 | 2.6559 | 2.4692 | 2.254 | 2.1416 | 2.0121 | 1.7618 | 1.5116 | 1.1705 | 0.87643 | 3.4244 | 3.4081 | 3.386 | 3.3404 | 3.2855 | 3.1263 | 2.9564 | 2.8451 | 2.7525 | 2.6541 | 2.4587 | 2.2472 | 1.9185 | 1.5799 | 2.9637 | 2.9417 | 2.912 | 2.8556 | 2.7902 | 2.6195 | 2.4223 | 2.2567 | 2.1523 | 2.0467 | 1.838 | 1.5932 | 1.2191 | 0.87038
| MARYBANK | LW |  |  |  | 3.0838 | 3.0346 | 2.9789 | 2.9153 | 2.8468 | 2.7839 | 2.7006 | 2.4779 | 2.3879 | 2.2888 | 2.1 | 2.0196 | 1.5343 | 0.88118 | 3.417 | 3.3969 | 3.3737 | 3.3489 | 3.3222 | 3.2955 | 3.2606 | 3.1721 | 3.1136 | 3.0433 | 2.9037 | 2.9133 | 2.357 | 1.5607 | 2.9567 | 2.9307 | 2.8979 | 2.8656 | 2.8265 | 2.7776 | 2.7187 | 2.5735 | 2.505 | 2.4294 | 2.2818 | 2.2413 | 1.6606 | 0.85437
| MARYBANK | ST |  |  |  | 3.1287 | 3.1097 | 3.0881 | 2.9662 | 2.8704 | 2.794 | 2.6103 | 2.4613 | 2.2993 | 2.2 | 1.9701 | 1.5454 | 1.0955 | 0.67515 | 3.4373 | 3.429 | 3.4196 | 3.2912 | 3.1986 | 3.1309 | 2.9322 | 2.8337 | 2.6699 | 2.587 | 2.3944 | 2.1231 | 1.6384 | 1.1601 | 2.9838 | 2.9724 | 2.9592 | 2.8259 | 2.7272 | 2.6521 | 2.4458 | 2.3354 | 2.1615 | 2.0663 | 1.8442 | 1.5508 | 1.0307 | 0.53207
| MARYBANK | FS |  |  |  | 3.1379 | 3.1239 | 3.1096 | 3.0659 | 3.0197 | 2.9694 | 2.9164 | 2.8043 | 2.7253 | 2.6541 | 2.4921 | 2.2096 | 1.9869 | 1.8982 | 3.441 | 3.435 | 3.4289 | 3.3953 | 3.3607 | 3.3214 | 3.2806 | 3.219 | 3.1535 | 3.1 | 2.9833 | 2.9263 | 2.7916 | 2.713 | 2.9882 | 2.9801 | 2.9713 | 2.9343 | 2.8958 | 2.8518 | 2.8055 | 2.7361 | 2.663 | 2.6021 | 2.4681 | 2.3577 | 2.1653 | 2.08
LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | NO | 7.0692 | 6.7174 | 6.3384 | 5.5146 | 4.6478 | 3.3145 | 1.8518 | 0.82665 | 0.15797 | -0.51908 | -1.8193 | -2.5377 | -3.7247 | -4.7342 | 9.2512 | 9.0584 | 8.8398 | 8.2787 | 7.6646 | 6.5458 | 5.2882 | 4.4844 | 3.9618 | 3.4274 | 2.4061 | 2.0318 | 1.0095 | -0.12766 | 7.7571 | 7.4389 | 7.0986 | 6.2879 | 5.4246 | 4.0399 | 2.519 | 1.4768 | 0.81531 | 0.11719 | -1.2211 | -1.9217 | -3.1986 | -4.4023
| MARYTON | CT |  |  |  | 7.3171 | 7.0913 | 6.8573 | 6.1787 | 5.4665 | 4.2955 | 3.1003 | 2.4191 | 1.7522 | 1.0552 | -0.28127 | -1.563 | -3.0311 | -3.9227 | 9.3321 | 9.1848 | 9.0263 | 8.6347 | 8.1893 | 7.2421 | 6.2639 | 5.8444 | 5.3715 | 4.8545 | 3.8648 | 3.0063 | 1.9439 | 0.89645 | 7.9747 | 7.7673 | 7.5554 | 6.9323 | 6.2631 | 5.0717 | 3.8498 | 3.2024 | 2.5604 | 1.8697 | 0.52867 | -0.72164 | -2.1091 | -3.0109
| MARYTON | LW |  |  |  | 7.0692 | 6.7174 | 6.3384 | 5.5146 | 4.6478 | 3.3145 | 1.8518 | 0.82665 | 0.15797 | -0.51908 | -1.8193 | -2.5377 | -3.7247 | -4.7342 | 9.2512 | 9.0584 | 8.8398 | 8.2787 | 7.6646 | 6.5458 | 5.2882 | 4.4844 | 3.9618 | 3.4274 | 2.4061 | 2.0318 | 1.0095 | -0.12766 | 7.7571 | 7.4389 | 7.0986 | 6.2879 | 5.4246 | 4.0399 | 2.519 | 1.4768 | 0.81531 | 0.11719 | -1.2211 | -1.9217 | -3.1986 | -4.4023
| MARYTON | ST |  |  |  | 7.4289 | 7.2915 | 7.1812 | 6.6891 | 6.3019 | 5.7559 | 4.8293 | 4.4853 | 4.0273 | 3.6896 | 2.9449 | 1.471 | -0.011004 | -1.5726 | 9.3722 | 9.2763 | 9.2033 | 8.6835 | 8.2887 | 7.7829 | 6.8061 | 6.4693 | 6.0049 | 5.6921 | 4.9866 | 3.6783 | 2.3986 | 1.0017 | 8.0736 | 7.9478 | 7.8523 | 7.2968 | 6.8701 | 6.3154 | 5.2888 | 4.9152 | 4.4068 | 4.0471 | 3.2461 | 1.7326 | 0.22564 | -1.3281
| MARYTON | FS |  |  |  | 7.4536 | 7.3518 | 7.2652 | 7.0428 | 6.8206 | 6.4117 | 6.0279 | 5.7632 | 5.415 | 5.099 | 4.4421 | 3.0834 | 1.5633 | 0.56814 | 9.3824 | 9.3072 | 9.2469 | 9.0691 | 8.884 | 8.5348 | 8.2005 | 7.9705 | 7.6819 | 7.4243 | 6.8715 | 5.8726 | 4.533 | 3.2711 | 8.0954 | 8.0026 | 7.9285 | 7.7103 | 7.4895 | 7.0879 | 6.7089 | 6.4437 | 6.0977 | 5.781 | 5.1146 | 3.8102 | 2.3951 | 1.5029
STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | NO | 4.7389 | 4.5853 | 4.4044 | 4.225 | 4.023 | 3.7486 | 3.4096 | 3.1573 | 2.9839 | 2.7886 | 2.4116 | 2.0516 | 1.4867 | 0.9382 | 5.7285 | 5.662 | 5.5755 | 5.4927 | 5.3705 | 5.1148 | 4.8679 | 4.7275 | 4.5849 | 4.424 | 4.0922 | 3.5897 | 2.9559 | 2.3432 | 5.0699 | 4.9356 | 4.7723 | 4.6123 | 4.4309 | 4.1231 | 3.7816 | 3.5474 | 3.3617 | 3.1486 | 2.7406 | 2.3206 | 1.6526 | 1.0175
| MAUD | CT |  |  |  | 4.8384 | 4.7363 | 4.617 | 4.3702 | 4.0988 | 3.7486 | 3.4096 | 3.1573 | 2.9839 | 2.7886 | 2.4116 | 2.0516 | 1.4867 | 1.1006 | 5.7648 | 5.7163 | 5.6547 | 5.5251 | 5.3705 | 5.1148 | 4.8679 | 4.7275 | 4.5849 | 4.424 | 4.0922 | 3.6622 | 3.2043 | 2.7427 | 5.154 | 5.0638 | 4.955 | 4.7273 | 4.4728 | 4.1231 | 3.7816 | 3.5474 | 3.3617 | 3.1486 | 2.7406 | 2.3206 | 1.7355 | 1.3002
| MAUD | LW |  |  |  | 4.7389 | 4.5853 | 4.4044 | 4.225 | 4.023 | 3.8158 | 3.5892 | 3.3536 | 3.1839 | 3.0134 | 2.6718 | 2.4875 | 1.891 | 1.1654 | 5.7285 | 5.662 | 5.5755 | 5.4927 | 5.3923 | 5.2868 | 5.1707 | 5.0457 | 4.9219 | 4.7937 | 4.5033 | 4.3556 | 3.745 | 2.9021 | 5.0699 | 4.9356 | 4.7723 | 4.6123 | 4.4309 | 4.2462 | 4.0371 | 3.8165 | 3.639 | 3.458 | 3.1001 | 2.911 | 2.2233 | 1.3452
| MAUD | ST |  |  |  | 4.8856 | 4.822 | 4.7524 | 4.5597 | 4.3864 | 4.2115 | 3.9537 | 3.796 | 3.5578 | 3.383 | 2.9932 | 2.1958 | 1.5068 | 0.9382 | 5.7795 | 5.7534 | 5.72 | 5.5546 | 5.4148 | 5.2861 | 5.0436 | 4.9288 | 4.7186 | 4.5902 | 4.2913 | 3.5897 | 2.9559 | 2.3432 | 5.1933 | 5.1378 | 5.0763 | 4.8709 | 4.6925 | 4.5198 | 4.2347 | 4.0754 | 3.8171 | 3.6385 | 3.2374 | 2.3899 | 1.6526 | 1.0175
| MAUD | FS |  |  |  | 4.9251 | 4.8763 | 4.826 | 4.7296 | 4.6217 | 4.4931 | 4.3825 | 4.2665 | 4.1079 | 3.9616 | 3.6509 | 2.9022 | 2.3905 | 2.1937 | 5.7906 | 5.7703 | 5.7467 | 5.6876 | 5.616 | 5.5284 | 5.4534 | 5.3773 | 5.2642 | 5.1647 | 4.9511 | 4.5086 | 4.0913 | 3.8312 | 5.2265 | 5.1838 | 5.1391 | 5.0468 | 4.9433 | 4.8199 | 4.7118 | 4.5993 | 4.441 | 4.2968 | 3.9893 | 3.278 | 2.7869 | 2.6007
MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | NO | 0.24058 | 0.21053 | 0.1703 | 0.12527 | 0.082231 | 0.03534 | -0.025198 | -0.080568 | -0.1209 | -0.14703 | -0.22536 | -0.22633 | -0.27789 | -0.30546 | -0.99835 | -1.0106 | -1.0297 | -1.0489 | -1.0721 | -1.0932 | -1.1177 | -1.1462 | -1.1737 | -1.2022 | -1.2579 | -1.2708 | -1.2962 | -1.3149 | -2.0865 | -2.1127 | -2.1477 | -2.1841 | -2.2288 | -2.2747 | -2.3296 | -2.3801 | -2.4183 | -2.4433 | -2.5135 | -2.2996 | -2.3364 | -2.3573
| MELVICH | CT |  |  |  | 0.25716 | 0.22718 | 0.1924 | 0.1367 | 0.085775 | 0.03534 | -0.025198 | -0.080568 | -0.1209 | -0.14703 | -0.22536 | -0.19929 | -0.27789 | -0.30546 | -0.99191 | -1.0015 | -1.0156 | -1.0442 | -1.0721 | -1.0932 | -1.1177 | -1.1402 | -1.1623 | -1.1898 | -1.2461 | -1.2648 | -1.2962 | -1.3149 | -2.0716 | -2.0983 | -2.1291 | -2.1826 | -2.2288 | -2.2747 | -2.3296 | -2.3801 | -2.4183 | -2.4433 | -2.5135 | -2.2791 | -2.3364 | -2.3573
| MELVICH | LW |  |  |  | 0.24058 | 0.21053 | 0.1703 | 0.12527 | 0.082231 | 0.037874 | -0.015014 | -0.073434 | -0.10878 | -0.14507 | -0.21903 | -0.22633 | -0.2623 | -0.2762 | -0.99835 | -1.0106 | -1.0297 | -1.0489 | -1.0688 | -1.0873 | -1.1148 | -1.1462 | -1.1737 | -1.2022 | -1.2579 | -1.2708 | -1.2829 | -1.287 | -2.0865 | -2.1127 | -2.1477 | -2.1841 | -2.2189 | -2.2554 | -2.3012 | -2.3522 | -2.3865 | -2.4208 | -2.4894 | -2.2996 | -2.3253 | -2.3349
| MELVICH | ST |  |  |  | 0.25984 | 0.25142 | 0.23528 | 0.21371 | 0.18825 | 0.16235 | 0.13431 | 0.099896 | 0.062361 | 0.014966 | -0.091466 | -0.13512 | -0.20583 | -0.24389 | -0.98872 | -0.9945 | -1.0018 | -1.0108 | -1.0221 | -1.0335 | -1.0462 | -1.0618 | -1.0792 | -1.1007 | -1.1476 | -1.2364 | -1.2703 | -1.289 | -2.0624 | -2.0761 | -2.0921 | -2.1117 | -2.1349 | -2.1587 | -2.1847 | -2.2165 | -2.2507 | -2.2919 | -2.3804 | -2.2263 | -2.2809 | -2.3069
| MELVICH | FS |  |  |  | 0.2603 | 0.25817 | 0.2504 | 0.23293 | 0.21241 | 0.19257 | 0.16981 | 0.14663 | 0.11654 | 0.084516 | 0.011708 | -0.11559 | -0.23072 | -0.26676 | -0.98695 | -0.99083 | -0.996 | -1.0041 | -1.0134 | -1.0221 | -1.0323 | -1.0431 | -1.0571 | -1.0725 | -1.1077 | -1.1991 | -1.2795 | -1.301 | -2.0574 | -2.066 | -2.0761 | -2.0938 | -2.1129 | -2.1311 | -2.152 | -2.1734 | -2.2011 | -2.2307 | -2.2974 | -2.234 | -2.2994 | -2.3244
CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | NO | 8.7398 | 8.4082 | 7.9504 | 7.155 | 6.1896 | 5.2083 | 4.3597 | 3.443 | 2.6172 | 1.7857 | 0.12889 | 0.54012 | -0.82421 | -1.6988 | 10.2292 | 10.1374 | 9.9858 | 9.7961 | 9.3748 | 8.8705 | 8.6438 | 8.2983 | 7.8404 | 7.4213 | 6.5419 | 5.8391 | 4.1337 | 0.024105 | 13.9166 | 13.6898 | 13.2697 | 12.5855 | 11.7204 | 10.8474 | 10.0593 | 9.1945 | 8.3704 | 7.5312 | 5.8611 | 6.497 | 5.2529 | 4.3885
| MENZIESHILL | CT |  |  |  | 8.9825 | 8.7743 | 8.4762 | 7.6683 | 6.6876 | 5.7172 | 5.0246 | 4.3509 | 3.5941 | 2.8161 | 1.2356 | 0.54012 | -0.82421 | -1.6988 | 10.2489 | 10.1374 | 9.9858 | 9.7961 | 9.3748 | 8.8705 | 8.6438 | 8.2983 | 7.8404 | 7.4213 | 6.5419 | 5.8391 | 4.1337 | 1.8667 | 13.9277 | 13.8415 | 13.7141 | 12.9935 | 12.0889 | 11.2038 | 10.5636 | 9.9525 | 9.2282 | 8.4692 | 6.9272 | 6.497 | 5.2529 | 4.3885
| MENZIESHILL | LW |  |  |  | 8.7398 | 8.4082 | 7.9504 | 7.155 | 6.1896 | 5.2083 | 4.3597 | 3.443 | 2.6172 | 1.7857 | 0.12889 | 0.68794 | -0.27057 | -1.1338 | 10.2292 | 10.1408 | 10.0081 | 9.8825 | 9.4845 | 9.0638 | 8.722 | 8.33 | 7.8848 | 7.4829 | 6.6848 | 7.0811 | 6.2225 | 5.1973 | 13.9166 | 13.6898 | 13.2697 | 12.5855 | 11.7204 | 10.8474 | 10.0593 | 9.1945 | 8.3704 | 7.5312 | 5.8611 | 6.6903 | 5.665 | 4.6164
| MENZIESHILL | ST |  |  |  | 9.0897 | 8.9774 | 8.8205 | 8.6035 | 8.2236 | 7.7905 | 7.5887 | 7.392 | 7.0368 | 6.7275 | 5.9881 | 5.2776 | 3.8866 | 2.2773 | 10.2573 | 10.1886 | 10.1062 | 9.9648 | 9.5898 | 9.1595 | 8.9919 | 8.8614 | 8.5511 | 8.3221 | 7.7309 | 7.562 | 5.6685 | 2.9593 | 13.934 | 13.8773 | 13.8038 | 13.668 | 13.349 | 13.0072 | 12.8034 | 12.5863 | 12.1959 | 11.8586 | 11.0517 | 10.338 | 8.9819 | 7.4733
| MENZIESHILL | FS |  |  |  | 9.1385 | 9.044 | 8.9158 | 8.723 | 8.416 | 8.0453 | 7.8579 | 7.6575 | 7.3364 | 7.031 | 6.384 | 5.5327 | 3.8369 | 2.5091 | 10.3382 | 10.2784 | 10.203 | 10.1115 | 9.8504 | 9.5216 | 9.4033 | 9.2761 | 9.0589 | 8.8884 | 8.5261 | 7.4831 | 5.0029 | 0.024105 | 13.9707 | 13.9213 | 13.8557 | 13.7712 | 13.5508 | 13.2928 | 13.1218 | 12.9174 | 12.5978 | 12.2917 | 11.6334 | 10.8646 | 9.2889 | 8.1873
KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | NO | 4.6577 | 4.5562 | 4.4436 | 4.326 | 4.2052 | 4.0321 | 3.807 | 3.6454 | 3.5343 | 3.4084 | 3.161 | 2.9254 | 2.5282 | 2.14 | 2.2416 | 2.2312 | 2.214 | 2.1447 | 2.0802 | 2.0308 | 1.8933 | 1.8423 | 1.7278 | 1.6701 | 1.5374 | 1.3616 | 1.027 | 0.68044 | 0.97776 | 0.97271 | 0.96233 | 0.88716 | 0.82608 | 0.65661 | 0.46199 | 0.34267 | 0.25292 | 0.15934 | -0.027177 | -0.21781 | -0.65528 | -1.0616
| METHLICK | CT |  |  |  | 4.7235 | 4.6553 | 4.5795 | 4.4162 | 4.2447 | 4.0321 | 3.807 | 3.6454 | 3.5343 | 3.4084 | 3.161 | 2.9254 | 2.5516 | 2.2982 | 2.2417 | 2.2312 | 2.214 | 2.1795 | 2.1392 | 2.0308 | 1.9154 | 1.8713 | 1.803 | 1.7329 | 1.5962 | 1.4776 | 1.2522 | 1.0022 | 0.97848 | 0.97398 | 0.96546 | 0.94063 | 0.84035 | 0.65661 | 0.46199 | 0.34267 | 0.25292 | 0.15934 | -0.027177 | -0.18477 | -0.5263 | -0.79171
| METHLICK | LW |  |  |  | 4.6577 | 4.5562 | 4.4436 | 4.326 | 4.2052 | 4.0834 | 3.9405 | 3.7915 | 3.6848 | 3.5745 | 3.3541 | 3.2291 | 2.8346 | 2.353 | 2.2416 | 2.2329 | 2.2169 | 2.2034 | 2.1877 | 2.1726 | 2.1463 | 2.1152 | 2.0638 | 2.0085 | 1.9019 | 1.9632 | 1.579 | 1.0187 | 0.97776 | 0.97271 | 0.96233 | 0.90984 | 0.83078 | 0.74908 | 0.65521 | 0.55713 | 0.48202 | 0.40391 | 0.24812 | 0.23832 | -0.19865 | -0.77955
| METHLICK | ST |  |  |  | 4.7548 | 4.7081 | 4.6625 | 4.5354 | 4.4252 | 4.3247 | 4.154 | 4.0512 | 3.8919 | 3.7766 | 3.5182 | 2.9903 | 2.5282 | 2.14 | 2.2432 | 2.239 | 2.2337 | 2.1447 | 2.0802 | 2.0326 | 1.8933 | 1.8423 | 1.7278 | 1.6701 | 1.5374 | 1.3616 | 1.027 | 0.68044 | 0.97848 | 0.97635 | 0.97328 | 0.88716 | 0.82608 | 0.78316 | 0.64957 | 0.57154 | 0.41986 | 0.3256 | 0.11621 | -0.21781 | -0.65528 | -1.0616
| METHLICK | FS |  |  |  | 4.7829 | 4.7483 | 4.717 | 4.6538 | 4.5856 | 4.5161 | 4.4421 | 4.3675 | 4.2627 | 4.1689 | 3.962 | 3.4592 | 3.126 | 2.9943 | 2.2439 | 2.2403 | 2.236 | 2.2138 | 2.1904 | 2.1632 | 2.1346 | 2.1071 | 2.0602 | 2.0226 | 1.9411 | 1.9169 | 1.8397 | 1.7641 | 0.9787 | 0.97693 | 0.97441 | 0.95433 | 0.93319 | 0.90901 | 0.88389 | 0.86061 | 0.81716 | 0.74549 | 0.58878 | 0.31373 | 0.11813 | 0.0092771
SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | NO | -0.024548 | -0.050619 | -0.07859 | -0.11705 | -0.15206 | -0.18688 | -0.22838 | -0.27367 | -0.30564 | -0.3357 | -0.39636 | -0.4127 | -0.45155 | -0.47363 | 0.3028 | 0.29898 | 0.29299 | 0.28371 | 0.27629 | 0.2699 | 0.26305 | 0.25158 | 0.23701 | 0.22112 | 0.18947 | 0.1833 | 0.15912 | 0.13958 | 0.026626 | 0.0094616 | -0.0094304 | -0.032061 | -0.053298 | -0.075834 | -0.1032 | -0.13386 | -0.15864 | -0.1834 | -0.23783 | -0.26838 | -0.29583 | -0.31463
| MID YELL | CT |  |  |  | -0.011373 | -0.027319 | -0.046831 | -0.093562 | -0.14107 | -0.18325 | -0.22521 | -0.26565 | -0.29092 | -0.31636 | -0.37532 | -0.39528 | -0.45155 | -0.47363 | 0.3028 | 0.29898 | 0.29299 | 0.28371 | 0.27629 | 0.2699 | 0.26305 | 0.25587 | 0.24537 | 0.23492 | 0.208 | 0.18709 | 0.15912 | 0.13958 | 0.033922 | 0.020589 | 0.0056862 | -0.023482 | -0.049381 | -0.075555 | -0.10156 | -0.12766 | -0.14656 | -0.16096 | -0.2118 | -0.25259 | -0.29583 | -0.31463
| MID YELL | LW |  |  |  | -0.024548 | -0.050619 | -0.07859 | -0.11705 | -0.15206 | -0.18688 | -0.22838 | -0.27367 | -0.30564 | -0.3357 | -0.39636 | -0.4127 | -0.44188 | -0.45023 | 0.3028 | 0.29954 | 0.29355 | 0.288 | 0.28156 | 0.27552 | 0.26458 | 0.25158 | 0.23701 | 0.22112 | 0.18947 | 0.1833 | 0.17191 | 0.16912 | 0.026626 | 0.0094616 | -0.0094304 | -0.032061 | -0.053298 | -0.075834 | -0.1032 | -0.13386 | -0.15864 | -0.1834 | -0.23783 | -0.26838 | -0.29031 | -0.29616
| MID YELL | ST |  |  |  | -0.0032328 | -0.0084758 | -0.019695 | -0.030782 | -0.046814 | -0.063669 | -0.080241 | -0.10054 | -0.1226 | -0.14343 | -0.20161 | -0.30995 | -0.35733 | -0.38391 | 0.3037 | 0.30245 | 0.30088 | 0.2988 | 0.29602 | 0.29212 | 0.28682 | 0.28032 | 0.27236 | 0.26265 | 0.23876 | 0.22233 | 0.19283 | 0.17502 | 0.039284 | 0.03449 | 0.02712 | 0.018799 | 0.0083092 | -0.0036967 | -0.016204 | -0.031422 | -0.047877 | -0.064954 | -0.11042 | -0.18744 | -0.23033 | -0.2494
| MID YELL | FS |  |  |  | 0.0043696 | -0.0023706 | -0.0092699 | -0.024957 | -0.034779 | -0.053423 | -0.064432 | -0.083579 | -0.10418 | -0.12417 | -0.16808 | -0.2995 | -0.39435 | -0.41759 | 0.30389 | 0.30287 | 0.30156 | 0.29991 | 0.29784 | 0.29555 | 0.29237 | 0.2881 | 0.2831 | 0.27733 | 0.26352 | 0.25073 | 0.17976 | 0.15954 | 0.043238 | 0.037924 | 0.033193 | 0.023256 | 0.015767 | 0.0040724 | -0.0047896 | -0.017714 | -0.031634 | -0.045654 | -0.076888 | -0.14668 | -0.25462 | -0.27143
KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | NO | 0.55158 | 0.46131 | 0.36068 | 0.25164 | -1.0427 | -1.2232 | -1.4309 | -1.5975 | -1.6998 | -1.8045 | -2.0133 | -2.1196 | -2.5299 | -2.8266 | -0.81098 | -0.86385 | -0.93266 | -1.001 | -2.2015 | -2.3714 | -2.5486 | -2.6696 | -2.7818 | -2.9111 | -3.1601 | -3.3912 | -3.8533 | -4.3266 | 0.35956 | 0.26398 | 0.15369 | 0.042043 | -1.1672 | -1.39 | -1.624 | -1.805 | -1.9335 | -2.0527 | -2.3033 | -2.1253 | -2.5145 | -2.9367
| MIDMAR | CT |  |  |  | 0.61016 | 0.55022 | 0.46874 | 0.31631 | -1.0205 | -1.2232 | -1.4309 | -1.5975 | -1.6998 | -1.8045 | -2.0133 | -2.1196 | -2.5299 | -2.8022 | -0.78373 | -0.82231 | -0.8809 | -0.99083 | -2.2015 | -2.3714 | -2.5486 | -2.6696 | -2.7818 | -2.9111 | -3.1601 | -3.3912 | -3.7499 | -4.1173 | 0.41672 | 0.34812 | 0.25624 | 0.089463 | -1.1637 | -1.39 | -1.624 | -1.805 | -1.9335 | -2.0527 | -2.3033 | -2.1253 | -2.4989 | -2.7771
| MIDMAR | LW |  |  |  | 0.55158 | 0.46131 | 0.36068 | 0.25164 | -1.0427 | -1.155 | -1.2871 | -1.4402 | -1.5356 | -1.6383 | -1.8448 | -1.8609 | -2.2448 | -2.7135 | -0.81098 | -0.86385 | -0.93266 | -1.001 | -2.1662 | -2.2357 | -2.3321 | -2.4486 | -2.5514 | -2.662 | -2.8791 | -2.9274 | -3.3199 | -3.8549 | 0.35956 | 0.26398 | 0.15369 | 0.042043 | -1.1672 | -1.2861 | -1.4311 | -1.6003 | -1.7228 | -1.857 | -2.1272 | -1.7483 | -2.1716 | -2.7256
| MIDMAR | ST |  |  |  | 0.64618 | 0.60698 | 0.56734 | 0.4548 | -0.82647 | -0.91036 | -1.0686 | -1.1738 | -1.3215 | -1.4297 | -1.6693 | -1.9487 | -2.4241 | -2.8266 | -0.768 | -0.79301 | -0.82076 | -0.93119 | -2.1143 | -2.1907 | -2.3556 | -2.4514 | -2.6006 | -2.7018 | -2.9329 | -3.3912 | -3.8533 | -4.3266 | 0.44031 | 0.40883 | 0.36556 | 0.23437 | -0.97057 | -1.0689 | -1.2576 | -1.3797 | -1.554 | -1.6811 | -1.9695 | -2.0595 | -2.5145 | -2.9367
| MIDMAR | FS |  |  |  | 0.66572 | 0.63956 | 0.61175 | 0.55585 | -0.68109 | -0.74288 | -0.80998 | -0.87995 | -0.96918 | -1.0549 | -1.2375 | -1.5653 | -1.901 | -2.0748 | -0.75884 | -0.77787 | -0.79967 | -0.84502 | -1.9833 | -2.036 | -2.0936 | -2.1565 | -2.2379 | -2.3146 | -2.4821 | -2.8304 | -3.1681 | -3.4392 | 0.44944 | 0.4308 | 0.40867 | 0.3454 | -0.80896 | -0.87929 | -0.95565 | -1.0361 | -1.1382 | -1.2367 | -1.447 | -1.6146 | -1.8178 | -1.9596
BRIDGE OF DUN | MILL RD MONTROSE | MINIMUM HEADROOM | NO 71317 57683 | NO | NO | 5.7001 | 5.5637 | 5.4009 | 4.8165 | 4.1874 | 3.2423 | 2.2122 | 1.4263 | 1.003 | 0.55504 | -0.34593 | -0.28458 | -1.1078 | -1.7868 | 7.4776 | 7.4086 | 7.3142 | 6.8271 | 6.2884 | 5.354 | 4.3295 | 3.6323 | 3.2955 | 2.9348 | 2.2243 | 2.2848 | 1.5448 | 0.77415 | 6.3461 | 6.2912 | 6.1228 | 5.6611 | 4.9821 | 3.9083 | 2.7387 | 1.8915 | 1.4613 | 1.0056 | 0.09761 | 0.064901 | -0.84097 | -1.654
| MILL RD MONTROSE | CT |  |  |  | 5.8317 | 5.751 | 5.5875 | 5.1789 | 4.7264 | 4.09 | 3.4233 | 2.9814 | 2.6352 | 2.2898 | 1.5943 | 1.6878 | 0.70662 | 0.076084 | 7.5174 | 7.4603 | 7.3334 | 7.0751 | 6.765 | 6.2025 | 5.6059 | 5.2948 | 5.0401 | 4.783 | 4.2582 | 4.3058 | 3.347 | 2.1892 | 6.3468 | 6.2912 | 6.1228 | 5.9044 | 5.6153 | 4.9306 | 4.2105 | 3.7753 | 3.4369 | 3.1008 | 2.4258 | 2.514 | 1.5702 | 0.93116
| MILL RD MONTROSE | LW |  |  |  | 5.7001 | 5.5637 | 5.4009 | 4.8165 | 4.1874 | 3.2423 | 2.2122 | 1.4263 | 1.003 | 0.55504 | -0.34593 | -0.28458 | -1.1078 | -1.7868 | 7.4776 | 7.4086 | 7.3142 | 6.8271 | 6.2884 | 5.354 | 4.3295 | 3.6323 | 3.2955 | 2.9348 | 2.2243 | 2.2848 | 1.5448 | 0.77415 | 6.3461 | 6.304 | 6.2352 | 5.6611 | 4.9821 | 3.9083 | 2.7387 | 1.8915 | 1.4613 | 1.0056 | 0.09761 | 0.064901 | -0.84097 | -1.654
| MILL RD MONTROSE | ST |  |  |  | 5.9092 | 5.891 | 5.8703 | 5.5634 | 5.341 | 5.1673 | 4.6814 | 4.4885 | 4.27 | 4.0989 | 3.5767 | 3.6896 | 2.8925 | 1.8143 | 7.5463 | 7.5226 | 7.4935 | 7.1148 | 6.8386 | 6.6292 | 6.0366 | 5.808 | 5.5571 | 5.3775 | 4.9478 | 4.7075 | 3.7002 | 2.3003 | 6.3521 | 6.3309 | 6.3039 | 5.9293 | 5.6548 | 5.4466 | 4.8543 | 4.6205 | 4.3638 | 4.1757 | 3.7111 | 4.1419 | 3.3149 | 2.2583
| MILL RD MONTROSE | FS |  |  |  | 5.9069 | 5.8927 | 5.8786 | 5.7775 | 5.6697 | 5.5514 | 5.4213 | 5.2945 | 5.1555 | 5.0186 | 4.7058 | 4.5018 | 3.8782 | 3.2269 | 7.5469 | 7.5252 | 7.5 | 7.388 | 7.2687 | 7.133 | 6.9866 | 6.8429 | 6.6937 | 6.5478 | 6.2106 | 5.8223 | 4.7145 | 2.8446 | 6.3584 | 6.3445 | 6.3276 | 6.2349 | 6.1373 | 6.0227 | 5.9007 | 5.7823 | 5.671 | 5.566 | 5.3196 | 5.297 | 4.7311 | 4.1471
ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | NO | 0.73152 | 0.088605 | -0.69062 | -1.9586 | -3.2882 | -4.9484 | -6.9148 | -8.8544 | -10.7637 | -12.3747 | -15.1137 | -13.1399 | -14.791 | -16.252 | 4.8835 | 4.5461 | 4.0837 | 3.2175 | 2.277 | 0.93648 | -0.6762 | -2.1542 | -3.6409 | -4.869 | -7.0051 | -5.1505 | -6.5818 | -8.2091 | 3.5601 | 3.0357 | 2.3625 | 1.2004 | -0.05635 | -1.7591 | -3.7916 | -5.7147 | -7.5407 | -9.1142 | -11.8263 | -9.8468 | -11.5882 | -13.3083
| MILNATHORT | CT |  |  |  | 1.0229 | 0.54825 | -0.060479 | -1.2201 | -2.4339 | -4.0493 | -5.7679 | -7.2256 | -9.0461 | -10.6957 | -13.3777 | -12.1701 | -14.1697 | -15.369 | 4.9561 | 4.6803 | 4.2754 | 3.5711 | 2.7906 | 1.5174 | 0.14903 | -0.8306 | -2.2151 | -3.4618 | -5.4986 | -4.4178 | -5.983 | -7.563 | 3.766 | 3.3666 | 2.828 | 1.8183 | 0.73046 | -0.86901 | -2.6124 | -3.9731 | -5.6887 | -7.2817 | -9.9061 | -8.6975 | -10.5513 | -11.7577
| MILNATHORT | LW |  |  |  | 0.73152 | 0.088605 | -0.69062 | -1.9586 | -3.2882 | -4.9484 | -6.9148 | -8.8544 | -10.7637 | -12.3747 | -15.1137 | -13.1399 | -14.791 | -16.252 | 4.8835 | 4.5461 | 4.0837 | 3.2175 | 2.277 | 0.93648 | -0.6762 | -2.1542 | -3.6409 | -4.869 | -7.0051 | -5.1505 | -6.5818 | -8.2091 | 3.5601 | 3.0357 | 2.3625 | 1.2004 | -0.05635 | -1.7591 | -3.7916 | -5.7147 | -7.5407 | -9.1142 | -11.8263 | -9.8468 | -11.5882 | -13.3083
| MILNATHORT | ST |  |  |  | 1.4575 | 1.1592 | 0.84722 | -0.040687 | -0.79773 | -1.5095 | -2.8156 | -3.8033 | -5.3377 | -6.5789 | -8.8195 | -8.9055 | -11.0773 | -13.135 | 5.2193 | 5.0516 | 4.8651 | 4.0164 | 3.3292 | 2.7264 | 1.4044 | 0.56465 | -0.7488 | -1.806 | -4.2654 | -3.7978 | -5.7166 | -7.7592 | 4.1397 | 3.896 | 3.6332 | 2.6829 | 1.8954 | 1.1881 | -0.24846 | -1.2104 | -2.6535 | -3.8149 | -6.7973 | -6.3232 | -8.418 | -10.3983
| MILNATHORT | FS |  |  |  | 1.6081 | 1.3869 | 1.158 | 0.72905 | 0.29238 | -0.18971 | -0.70827 | -1.3578 | -2.4183 | -3.2376 | -4.7473 | -6.081 | -8.5374 | -10.0137 | 5.3033 | 5.173 | 5.0281 | 4.7137 | 4.3844 | 4.0121 | 3.5996 | 3.0746 | 2.2243 | 1.5911 | 0.42405 | -0.46708 | -2.6778 | -4.6606 | 4.2636 | 4.0832 | 3.8902 | 3.4917 | 3.0783 | 2.618 | 2.121 | 1.5112 | 0.55981 | -0.18505 | -1.5898 | -2.7961 | -5.1271 | -6.3902
MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | NO | 4.0322 | 3.8101 | 3.4029 | 2.7015 | 1.9992 | 1.3534 | 0.42248 | -0.51711 | -1.1909 | -1.7399 | -3.1734 | -3.4573 | -4.1445 | -4.708 | 11.09 | 10.95 | 10.6541 | 10.2041 | 9.7492 | 9.3556 | 8.6888 | 8.044 | 7.5785 | 7.219 | 6.1641 | 6.1899 | 5.1695 | 3.581 | 3.4326 | 3.2273 | 2.841 | 2.1992 | 1.5506 | 0.93647 | 0.043907 | -0.84808 | -1.5066 | -2.0536 | -3.4508 | -3.5835 | -4.2959 | -4.9513
| MILTON OF CRAIGIE | CT |  |  |  | 4.239 | 4.1187 | 3.8306 | 3.2007 | 2.5475 | 2.0016 | 1.2669 | 0.55792 | -0.098442 | -0.66501 | -2.0976 | -3.0968 | -4.1445 | -4.708 | 11.1733 | 11.0703 | 10.8169 | 10.4134 | 9.9815 | 9.6464 | 9.1196 | 8.6265 | 8.1818 | 7.8224 | 6.7924 | 6.198 | 5.1695 | 3.9385 | 3.6076 | 3.4897 | 3.2104 | 2.6337 | 2.03 | 1.5186 | 0.83144 | 0.18207 | -0.43662 | -0.97936 | -2.3358 | -3.1269 | -4.0831 | -4.647
| MILTON OF CRAIGIE | LW |  |  |  | 4.0322 | 3.8101 | 3.4029 | 2.7015 | 1.9992 | 1.3534 | 0.42248 | -0.51711 | -1.1909 | -1.7399 | -3.1734 | -3.4573 | -4.1216 | -4.6511 | 11.09 | 10.95 | 10.6541 | 10.2041 | 9.7492 | 9.3556 | 8.6888 | 8.044 | 7.5785 | 7.219 | 6.1641 | 6.1899 | 5.5906 | 4.9342 | 3.4326 | 3.2273 | 2.841 | 2.1992 | 1.5506 | 0.93647 | 0.043907 | -0.84808 | -1.5066 | -2.0536 | -3.4508 | -3.5835 | -4.2959 | -4.9513
| MILTON OF CRAIGIE | ST |  |  |  | 4.2929 | 4.2239 | 4.027 | 3.791 | 3.5542 | 3.4373 | 3.0674 | 2.7101 | 2.364 | 2.1481 | 1.3301 | 0.5926 | -0.53679 | -1.7874 | 11.1959 | 11.1249 | 10.9363 | 10.6726 | 10.4027 | 10.2776 | 9.8665 | 9.4856 | 9.156 | 8.9723 | 8.1286 | 7.481 | 6.3003 | 4.7404 | 3.6536 | 3.5852 | 3.3967 | 3.1564 | 2.9182 | 2.7903 | 2.4091 | 2.0548 | 1.6993 | 1.4698 | 0.64573 | -0.048484 | -1.1434 | -2.3141
| MILTON OF CRAIGIE | FS |  |  |  | 4.322 | 4.2728 | 4.1127 | 3.9391 | 3.7431 | 3.634 | 3.3978 | 3.1106 | 2.8002 | 2.5551 | 1.8838 | 0.8724 | -0.61062 | -1.7256 | 11.2284 | 11.1723 | 11.0192 | 10.8451 | 10.6405 | 10.5323 | 10.2831 | 9.9883 | 9.7045 | 9.4768 | 8.8339 | 7.7785 | 5.9568 | 3.581 | 3.6809 | 3.6316 | 3.4791 | 3.3134 | 3.125 | 3.0132 | 2.7841 | 2.506 | 2.2061 | 1.9671 | 1.3164 | 0.39248 | -0.97425 | -1.9233
STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | NO | 8.4491 | 8.2357 | 7.9829 | 7.576 | 7.2177 | 6.8666 | 6.3472 | 5.7876 | 5.2877 | 4.925 | 4.1717 | 3.6019 | 2.7743 | 1.9488 | 9.4635 | 9.363 | 9.2325 | 9.0094 | 8.8355 | 8.6435 | 8.3188 | 7.9988 | 7.6255 | 7.3538 | 6.8062 | 6.2791 | 5.5973 | 4.7417 | 9.5464 | 9.3555 | 9.1201 | 8.7534 | 8.4296 | 8.117 | 7.6376 | 7.1127 | 6.614 | 6.2377 | 5.4838 | 4.9198 | 4.0435 | 3.0482
| MINTLAW | CT |  |  |  | 8.6 | 8.4637 | 8.2921 | 7.83 | 7.4146 | 7.014 | 6.512 | 6.0128 | 5.538 | 5.1418 | 4.3781 | 3.6362 | 2.7743 | 2.188 | 9.5213 | 9.4492 | 9.3493 | 9.0842 | 8.8621 | 8.6435 | 8.3188 | 8.0206 | 7.6703 | 7.3859 | 6.8225 | 6.2791 | 5.5973 | 4.897 | 9.6749 | 9.5504 | 9.3873 | 8.9599 | 8.5722 | 8.2022 | 7.7398 | 7.2861 | 6.8219 | 6.4161 | 5.6434 | 4.9198 | 4.0754 | 3.4585
| MINTLAW | LW |  |  |  | 8.4491 | 8.2357 | 7.9829 | 7.576 | 7.2177 | 6.8666 | 6.3472 | 5.7876 | 5.2877 | 4.925 | 4.1717 | 3.6019 | 2.7919 | 1.9488 | 9.4635 | 9.363 | 9.2325 | 9.0094 | 8.8355 | 8.6687 | 8.3454 | 7.9988 | 7.6255 | 7.3538 | 6.8062 | 6.4338 | 5.6833 | 4.7417 | 9.5464 | 9.3555 | 9.1201 | 8.7534 | 8.4296 | 8.117 | 7.6376 | 7.1127 | 6.614 | 6.2377 | 5.4838 | 4.9307 | 4.0435 | 3.0482
| MINTLAW | ST |  |  |  | 8.6864 | 8.6134 | 8.5368 | 8.3307 | 8.1855 | 8.0396 | 7.7507 | 7.4716 | 7.0753 | 6.8409 | 6.3179 | 5.123 | 4.1685 | 3.2423 | 9.5553 | 9.5173 | 9.4743 | 9.3191 | 9.2219 | 9.1269 | 8.8817 | 8.6667 | 8.3272 | 8.1499 | 7.7386 | 6.8202 | 5.9647 | 5.044 | 9.7472 | 9.6813 | 9.6107 | 9.4119 | 9.2701 | 9.1291 | 8.8466 | 8.5777 | 8.1756 | 7.9341 | 7.39 | 6.2136 | 5.2326 | 4.2752
| MINTLAW | FS |  |  |  | 8.7212 | 8.6733 | 8.6098 | 8.4569 | 8.3313 | 8.2117 | 8.0185 | 7.7979 | 7.4998 | 7.2843 | 6.8372 | 5.6628 | 4.6372 | 4.1434 | 9.5723 | 9.5452 | 9.5086 | 9.4043 | 9.3281 | 9.2554 | 9.11 | 8.9459 | 8.7137 | 8.5589 | 8.2351 | 7.4253 | 6.5444 | 5.8404 | 9.7774 | 9.7335 | 9.6751 | 9.5333 | 9.4159 | 9.3032 | 9.1229 | 8.9143 | 8.6262 | 8.415 | 7.9718 | 6.8483 | 5.8865 | 5.4411
BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | NO | 1.6376 | -0.90742 | -3.5298 | -5.9949 | -7.2532 | -8.2595 | -9.0458 | -9.6326 | -10.1406 | -10.7069 | -11.8289 | -12.0049 | -13.2863 | -14.2144 | 2.61 | -0.13759 | -2.995 | -5.4861 | -6.527 | -7.331 | -7.8346 | -8.0722 | -8.2784 | -8.4994 | -8.9338 | -9.188 | -10.2702 | -11.3725 | 2.1773 | -0.24427 | -2.7569 | -5.141 | -6.3439 | -7.3208 | -8.0756 | -8.6127 | -9.0759 | -9.5951 | -10.6207 | -10.879 | -12.1566 | -13.4705
| MONTROSE NORTH | CT |  |  |  | 2.1148 | -0.14332 | -2.5294 | -4.837 | -5.9049 | -6.8793 | -7.7205 | -8.3306 | -8.9502 | -9.5263 | -10.6841 | -11.9932 | -13.2863 | -14.129 | 3.0062 | 0.48751 | -2.2081 | -4.5665 | -5.371 | -6.1455 | -6.8212 | -7.2152 | -7.5434 | -7.7608 | -8.2313 | -9.188 | -10.2702 | -11.3685 | 2.6319 | 0.47803 | -1.8151 | -4.0255 | -5.0311 | -5.9937 | -6.8244 | -7.3953 | -7.9683 | -8.4998 | -9.5696 | -10.879 | -12.1566 | -13.0512
| MONTROSE NORTH | LW |  |  |  | 1.6376 | -0.90742 | -3.5298 | -5.9949 | -7.2532 | -8.2595 | -9.0458 | -9.6326 | -10.1406 | -10.7069 | -11.8289 | -12.0049 | -13.094 | -14.2144 | 2.61 | -0.13759 | -2.995 | -5.4861 | -6.527 | -7.331 | -7.8346 | -8.0722 | -8.2784 | -8.4994 | -8.9338 | -8.9771 | -10.036 | -11.3725 | 2.1773 | -0.24427 | -2.7569 | -5.141 | -6.3439 | -7.3208 | -8.0756 | -8.6127 | -9.0759 | -9.5951 | -10.6207 | -10.8676 | -12.1014 | -13.4705
| MONTROSE NORTH | ST |  |  |  | 2.1637 | -0.045812 | -2.3337 | -4.3961 | -5.1583 | -5.7548 | -6.3633 | -6.7215 | -7.1053 | -7.3359 | -7.9095 | -9.2009 | -10.5177 | -11.962 | 3.0085 | 0.50236 | -2.1436 | -4.5859 | -5.4017 | -6.0326 | -6.6894 | -7.0318 | -7.3785 | -7.5134 | -7.8745 | -8.7179 | -9.8158 | -11.1166 | 2.6773 | 0.56708 | -1.6373 | -3.6816 | -4.4435 | -5.0356 | -5.6789 | -6.0286 | -6.4109 | -6.6083 | -7.1233 | -8.3792 | -9.7644 | -11.2908
| MONTROSE NORTH | FS |  |  |  | 3.1522 | 1.4666 | -0.30652 | -1.8655 | -2.5756 | -3.0791 | -3.652 | -4.0401 | -4.5459 | -5.2348 | -6.3812 | -8.4105 | -9.5768 | -10.414 | 4.1819 | 2.2779 | 0.22903 | -1.5784 | -2.3347 | -2.8461 | -3.4553 | -3.8305 | -4.297 | -4.9838 | -6.0454 | -7.7923 | -8.4682 | -10.0012 | 3.6351 | 2.0306 | 0.32517 | -1.1824 | -1.8602 | -2.3412 | -2.8956 | -3.2672 | -3.756 | -4.4184 | -5.5142 | -7.4191 | -8.4688 | -9.2578
TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 1.0314 | 0.91453 | 0.77812 | 0.64369 | 0.49995 | 0.33034 | 0.080694 | -0.14056 | -0.27071 | -0.41704 | -0.69811 | -0.89903 | -1.2782 | -1.5562 | 1.9648 | 1.9265 | 1.8759 | 1.8244 | 1.7468 | 1.6136 | 1.4549 | 1.3221 | 1.2228 | 1.1139 | 0.90606 | 0.70291 | 0.30765 | -0.074549 | 1.6896 | 1.5853 | 1.462 | 1.3411 | 1.2114 | 1.0265 | 0.77958 | 0.57337 | 0.44227 | 0.29452 | 0.012029 | -0.21739 | -0.60027 | -0.97447
| MOSSAT | CT |  |  |  | 1.1098 | 1.0305 | 0.93692 | 0.75017 | 0.55641 | 0.33034 | 0.080694 | -0.14056 | -0.27071 | -0.41704 | -0.69811 | -0.89903 | -1.2782 | -1.5088 | 1.9827 | 1.949 | 1.9037 | 1.8244 | 1.7468 | 1.6136 | 1.4549 | 1.3221 | 1.2228 | 1.1139 | 0.90606 | 0.7043 | 0.40046 | 0.11887 | 1.7585 | 1.6874 | 1.602 | 1.4304 | 1.2501 | 1.0265 | 0.77958 | 0.57337 | 0.44227 | 0.29452 | 0.012029 | -0.21739 | -0.60027 | -0.85653
| MOSSAT | LW |  |  |  | 1.0314 | 0.91453 | 0.77812 | 0.64369 | 0.49995 | 0.36247 | 0.17575 | -0.043695 | -0.17444 | -0.30832 | -0.56946 | -0.68254 | -1.0323 | -1.4398 | 1.9648 | 1.9265 | 1.8759 | 1.8301 | 1.7794 | 1.7282 | 1.6303 | 1.4995 | 1.4102 | 1.32 | 1.143 | 1.0861 | 0.73544 | 0.2656 | 1.6896 | 1.5853 | 1.462 | 1.3411 | 1.2114 | 1.0879 | 0.91694 | 0.71431 | 0.58669 | 0.45547 | 0.20005 | 0.085891 | -0.31209 | -0.80279
| MOSSAT | ST |  |  |  | 1.1433 | 1.0962 | 1.0437 | 0.91896 | 0.80953 | 0.70813 | 0.52608 | 0.38144 | 0.21483 | 0.085994 | -0.20031 | -0.75127 | -1.1984 | -1.5562 | 1.9924 | 1.9763 | 1.9577 | 1.8667 | 1.7943 | 1.7334 | 1.5776 | 1.4681 | 1.3362 | 1.251 | 1.0557 | 0.70291 | 0.30765 | -0.074549 | 1.7879 | 1.746 | 1.6989 | 1.5686 | 1.4576 | 1.3578 | 1.1643 | 1.0233 | 0.84993 | 0.72341 | 0.44139 | -0.11668 | -0.58438 | -0.97447
| MOSSAT | FS |  |  |  | 1.1721 | 1.1367 | 1.1008 | 1.0314 | 0.95823 | 0.88213 | 0.79682 | 0.68427 | 0.56867 | 0.45606 | 0.22981 | -0.36115 | -0.75283 | -0.90071 | 1.9995 | 1.9869 | 1.9736 | 1.9402 | 1.9048 | 1.8653 | 1.8135 | 1.7391 | 1.6706 | 1.6096 | 1.4813 | 1.1872 | 0.92039 | 0.74423 | 1.8132 | 1.7817 | 1.7495 | 1.6836 | 1.6141 | 1.5413 | 1.4595 | 1.3527 | 1.2401 | 1.1323 | 0.91458 | 0.37118 | 0.0034152 | -0.13431
THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | NO | 10.731 | 9.9822 | 9.1532 | 8.2665 | 7.2198 | 6.8911 | 6.6295 | 6.4197 | 6.1613 | 5.8938 | 5.5439 | 5.1326 | 4.4433 | 3.6265 | 12.0857 | 11.4549 | 10.7549 | 10.0365 | 9.1494 | 8.9251 | 8.7736 | 8.6718 | 8.5114 | 8.3411 | 8.0611 | 7.6139 | 7.0169 | 6.0881 | 11.2599 | 10.5559 | 9.7774 | 8.9478 | 7.9664 | 7.6668 | 7.434 | 7.2511 | 7.023 | 6.7865 | 6.4601 | 5.9939 | 5.2754 | 4.2455
| MOUNT PLEASANT | CT |  |  |  | 10.8061 | 10.1734 | 9.4826 | 8.6271 | 7.5017 | 7.1736 | 6.842 | 6.5816 | 6.3037 | 6.0379 | 5.6644 | 5.1326 | 4.4433 | 3.9732 | 12.1131 | 11.5664 | 10.9701 | 10.2791 | 9.3362 | 9.1024 | 8.8638 | 8.7042 | 8.5137 | 8.3424 | 8.0611 | 7.6139 | 7.0169 | 6.4125 | 11.3253 | 10.7284 | 10.0775 | 9.2777 | 8.2214 | 7.9102 | 7.595 | 7.3579 | 7.1057 | 6.8684 | 6.5195 | 5.9939 | 5.2928 | 4.7696
| MOUNT PLEASANT | LW |  |  |  | 10.731 | 9.9822 | 9.1532 | 8.2665 | 7.2198 | 6.8911 | 6.6295 | 6.4197 | 6.1613 | 5.8938 | 5.5439 | 5.2328 | 4.4714 | 3.6265 | 12.0857 | 11.4549 | 10.7549 | 10.0365 | 9.1494 | 8.9251 | 8.7736 | 8.6718 | 8.5114 | 8.3411 | 8.0784 | 7.8586 | 7.0917 | 6.0881 | 11.2599 | 10.5559 | 9.7774 | 8.9478 | 7.9664 | 7.6668 | 7.434 | 7.2511 | 7.023 | 6.7865 | 6.4601 | 6.1431 | 5.2754 | 4.2455
| MOUNT PLEASANT | ST |  |  |  | 10.833 | 10.2214 | 9.5704 | 8.8243 | 7.8281 | 7.6523 | 7.4246 | 7.2778 | 7.0313 | 6.8676 | 6.6003 | 5.9408 | 5.1976 | 4.4519 | 12.1233 | 11.5886 | 11.0168 | 10.3526 | 9.4486 | 9.2988 | 9.0901 | 8.9704 | 8.7544 | 8.6388 | 8.4265 | 7.8606 | 7.1082 | 6.2855 | 11.3493 | 10.7712 | 10.1559 | 9.4393 | 8.489 | 8.3214 | 8.0923 | 7.9535 | 7.7091 | 7.562 | 7.3033 | 6.6658 | 5.8602 | 5.0382
| MOUNT PLEASANT | FS |  |  |  | 10.8506 | 10.3851 | 9.9049 | 9.3517 | 8.5584 | 8.3825 | 8.1598 | 8.0175 | 7.7845 | 7.4668 | 7.1035 | 6.3287 | 5.8415 | 5.5488 | 12.1301 | 11.723 | 11.2988 | 10.818 | 10.121 | 9.975 | 9.7889 | 9.6735 | 9.4901 | 9.2265 | 8.93 | 8.3591 | 7.9002 | 7.419 | 11.3649 | 10.9253 | 10.4714 | 9.9474 | 9.1955 | 9.0299 | 8.8203 | 8.6876 | 8.4735 | 8.1824 | 7.8402 | 7.1505 | 6.7207 | 6.4471
BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 8.5528 | 8.099 | 7.5869 | 6.7653 | 5.8919 | 4.8772 | 3.7242 | 2.5721 | 1.8541 | 1.1134 | -0.33087 | -1.5451 | -2.6049 | -3.3942 | 11.1932 | 10.9815 | 10.7114 | 10.1728 | 9.5818 | 8.764 | 7.8077 | 6.9931 | 6.4736 | 5.9287 | 4.8772 | 4.1588 | 3.3345 | 2.4985 | 7.7042 | 7.3454 | 6.9127 | 6.1631 | 5.3534 | 4.3365 | 3.1546 | 2.0441 | 1.3332 | 0.59329 | -0.84344 | -1.9573 | -3.0377 | -3.9468
| MUIR OF ORD | CT |  |  |  | 8.8115 | 8.503 | 8.1615 | 7.4109 | 6.6106 | 5.7534 | 4.8676 | 4.0263 | 3.3924 | 2.6859 | 1.2964 | 0.23219 | -1.1009 | -1.7742 | 11.2843 | 11.1266 | 10.932 | 10.5305 | 10.0813 | 9.4978 | 8.8855 | 8.4396 | 8.027 | 7.538 | 6.5843 | 5.8766 | 5.038 | 4.3091 | 7.8951 | 7.6463 | 7.3525 | 6.7149 | 6.0206 | 5.2249 | 4.3975 | 3.6967 | 3.0991 | 2.4094 | 1.0613 | 0.051673 | -1.1503 | -1.8235
| MUIR OF ORD | LW |  |  |  | 8.5528 | 8.099 | 7.5869 | 6.7653 | 5.8919 | 4.8772 | 3.7242 | 2.5721 | 1.8541 | 1.1134 | -0.33087 | -1.5451 | -2.6049 | -3.3942 | 11.1932 | 10.9815 | 10.7114 | 10.1728 | 9.5818 | 8.764 | 7.8077 | 6.9931 | 6.4736 | 5.9287 | 4.8772 | 4.1588 | 3.3345 | 2.4985 | 7.7042 | 7.3454 | 6.9127 | 6.1631 | 5.3534 | 4.3365 | 3.1546 | 2.0441 | 1.3332 | 0.59329 | -0.84344 | -1.9573 | -3.0377 | -3.9468
| MUIR OF ORD | ST |  |  |  | 8.9367 | 8.7196 | 8.5046 | 8.0381 | 7.6125 | 7.27 | 6.6747 | 6.2129 | 5.7111 | 5.2337 | 4.1836 | 2.2883 | 1.0925 | 0.04794 | 11.3312 | 11.2231 | 11.1112 | 10.7199 | 10.3902 | 10.1325 | 9.5726 | 9.2402 | 8.8717 | 8.5453 | 7.8023 | 6.4471 | 5.4924 | 4.5501 | 7.9863 | 7.8159 | 7.6418 | 7.1713 | 6.7566 | 6.4232 | 5.7805 | 5.3441 | 4.8618 | 4.4132 | 3.4078 | 1.5767 | 0.4392 | -0.54476
| MUIR OF ORD | FS |  |  |  | 9.0284 | 8.8516 | 8.6834 | 8.3935 | 8.0951 | 7.8198 | 7.5312 | 7.1739 | 6.7663 | 6.3629 | 5.506 | 3.3302 | 1.8002 | 1.156 | 11.3677 | 11.2754 | 11.1827 | 11.0055 | 10.8172 | 10.6338 | 10.4378 | 10.205 | 9.9499 | 9.696 | 9.1377 | 7.8319 | 6.6462 | 5.9114 | 8.055 | 7.9164 | 7.7798 | 7.5284 | 7.2645 | 7.0123 | 6.745 | 6.4251 | 6.0656 | 5.7073 | 4.9332 | 3.0115 | 1.5809 | 1.0573
BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 4.1368 | 4.0238 | 3.9287 | 3.8036 | 3.6777 | 3.5505 | 3.396 | 3.2394 | 3.1947 | 3.143 | 3.0445 | 3.0513 | 2.8099 | 2.7011 | 4.8438 | 4.7853 | 4.7274 | 4.6645 | 4.5909 | 4.5006 | 4.4054 | 4.3229 | 4.2577 | 4.1736 | 4.0106 | 3.9272 | 3.7408 | 3.5457 | 4.2934 | 4.1866 | 4.0859 | 3.9643 | 3.8382 | 3.7128 | 3.5434 | 3.3912 | 3.3109 | 3.2124 | 3.0192 | 2.9999 | 2.7646 | 2.6513
| MUIREND | CT |  |  |  | 4.1976 | 4.1207 | 4.057 | 3.8969 | 3.7344 | 3.5691 | 3.396 | 3.2394 | 3.1947 | 3.143 | 3.0445 | 3.0618 | 2.8099 | 2.7011 | 4.8642 | 4.8191 | 4.7763 | 4.6866 | 4.5909 | 4.5006 | 4.4054 | 4.3229 | 4.2577 | 4.1736 | 4.0106 | 3.9272 | 3.7408 | 3.5506 | 4.3466 | 4.2728 | 4.2044 | 4.0427 | 3.8744 | 3.7128 | 3.5434 | 3.3912 | 3.3175 | 3.2234 | 3.0447 | 2.9999 | 2.7646 | 2.6513
| MUIREND | LW |  |  |  | 4.1368 | 4.0238 | 3.9287 | 3.8036 | 3.6777 | 3.5505 | 3.4114 | 3.2667 | 3.2127 | 3.1573 | 3.0476 | 3.0513 | 2.8879 | 2.7787 | 4.8438 | 4.7853 | 4.7274 | 4.6645 | 4.597 | 4.5339 | 4.4453 | 4.3465 | 4.2674 | 4.1827 | 4.0169 | 4.0334 | 3.9321 | 3.8367 | 4.2934 | 4.1866 | 4.0859 | 3.9643 | 3.8382 | 3.7153 | 3.5653 | 3.404 | 3.3109 | 3.2124 | 3.0192 | 3.0073 | 2.8453 | 2.7271
| MUIREND | ST |  |  |  | 4.2355 | 4.1749 | 4.1372 | 4.0795 | 4.0239 | 3.9661 | 3.8974 | 3.8372 | 3.7547 | 3.6826 | 3.5255 | 3.3013 | 3.1035 | 2.9388 | 4.8765 | 4.8421 | 4.8196 | 4.7803 | 4.7403 | 4.6991 | 4.6411 | 4.5914 | 4.524 | 4.4597 | 4.3105 | 4.024 | 3.8264 | 3.6166 | 4.3768 | 4.3213 | 4.2836 | 4.2238 | 4.164 | 4.102 | 4.0241 | 3.9544 | 3.8613 | 3.775 | 3.58 | 3.2221 | 3.0195 | 2.8619
| MUIREND | FS |  |  |  | 4.2571 | 4.2114 | 4.187 | 4.1364 | 4.0862 | 4.037 | 3.9847 | 3.9294 | 3.8644 | 3.7989 | 3.6611 | 3.2945 | 3.0621 | 2.9462 | 4.8845 | 4.8556 | 4.8376 | 4.8081 | 4.7758 | 4.7426 | 4.7057 | 4.6651 | 4.6159 | 4.5639 | 4.4469 | 4.1425 | 3.8198 | 3.5457 | 4.3926 | 4.351 | 4.3261 | 4.2762 | 4.2245 | 4.1729 | 4.1171 | 4.0568 | 3.9857 | 3.9121 | 3.753 | 3.3276 | 3.0262 | 2.929
NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | NO | 4.2074 | 3.836 | 3.1643 | 2.4508 | 1.7122 | 0.91479 | -0.033692 | -0.99245 | -1.7129 | -2.4611 | -3.9208 | -4.6988 | -6.3257 | -7.2869 | 6.4042 | 6.2129 | 5.794 | 5.4102 | 5.0064 | 4.5173 | 3.9126 | 3.3451 | 2.9207 | 2.4721 | 1.5924 | 1.5222 | 0.58802 | -0.38682 | 6.4996 | 6.2212 | 5.6362 | 4.9778 | 4.2881 | 3.5231 | 2.5959 | 1.678 | 0.9773 | 0.24455 | -1.1896 | -1.7816 | -3.0187 | -3.8504
| NAIRN CENTRAL | CT |  |  |  | 4.4576 | 4.2335 | 3.7444 | 3.1404 | 2.5068 | 1.8456 | 1.1168 | 0.40347 | -0.36272 | -1.1964 | -2.8135 | -4.4315 | -6.3257 | -7.2869 | 6.4942 | 6.3578 | 6.0217 | 5.6957 | 5.3428 | 4.9364 | 4.4908 | 4.1074 | 3.6908 | 3.2176 | 2.289 | 1.6679 | 0.58802 | -0.38682 | 6.4996 | 6.3756 | 6.0603 | 5.5662 | 4.9678 | 4.3366 | 3.6468 | 3.002 | 2.2913 | 1.4983 | -0.041972 | -1.4038 | -3.0187 | -3.8504
| NAIRN CENTRAL | LW |  |  |  | 4.2074 | 3.836 | 3.1643 | 2.4508 | 1.7122 | 0.91479 | -0.033692 | -0.99245 | -1.7129 | -2.4611 | -3.9208 | -4.6988 | -5.8686 | -6.2836 | 6.4042 | 6.2129 | 5.794 | 5.4102 | 5.0064 | 4.5173 | 3.9126 | 3.3451 | 2.9207 | 2.4721 | 1.5924 | 1.5222 | 0.99103 | 0.73392 | 6.5005 | 6.2212 | 5.6362 | 4.9778 | 4.2881 | 3.5231 | 2.5959 | 1.678 | 0.9773 | 0.24455 | -1.1896 | -1.7816 | -2.7961 | -3.1808
| NAIRN CENTRAL | ST |  |  |  | 4.5637 | 4.4139 | 4.047 | 3.8734 | 3.6923 | 3.519 | 3.2001 | 2.9245 | 2.6782 | 2.4047 | 1.7793 | 0.73943 | -0.65211 | -2.4591 | 6.5453 | 6.453 | 6.1981 | 6.02 | 5.8541 | 5.7014 | 5.3969 | 5.1764 | 4.9765 | 4.7582 | 4.247 | 3.5329 | 2.5901 | 1.3051 | 6.5556 | 6.4769 | 6.2489 | 6.0805 | 5.9311 | 5.7894 | 5.4845 | 5.2061 | 4.9486 | 4.6619 | 3.9953 | 2.9069 | 1.6746 | 0.14006
| NAIRN CENTRAL | FS |  |  |  | 4.5924 | 4.4653 | 4.1681 | 4.0344 | 3.8856 | 3.724 | 3.542 | 3.3383 | 3.0839 | 2.8145 | 2.2319 | 0.91277 | -0.8543 | -2.3393 | 6.5608 | 6.4791 | 6.2692 | 6.1713 | 6.0592 | 5.9353 | 5.7967 | 5.6428 | 5.4662 | 5.2748 | 4.8431 | 3.9042 | 2.3778 | 0.58902 | 6.5712 | 6.5022 | 6.3145 | 6.2451 | 6.1652 | 6.0718 | 5.904 | 5.7045 | 5.4607 | 5.2001 | 4.6261 | 3.3416 | 1.6676 | 0.42399
STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | NO | 6.8545 | 6.8419 | 6.8104 | 6.7115 | 6.6044 | 6.4791 | 6.3218 | 6.1915 | 6.0932 | 5.9869 | 5.7812 | 5.679 | 5.4349 | 5.2874 | 7.017 | 6.9816 | 6.9343 | 6.887 | 6.825 | 6.7274 | 6.6263 | 6.5562 | 6.4878 | 6.4121 | 6.2654 | 6.175 | 5.9849 | 5.7669 | 6.7216 | 6.6508 | 6.5648 | 6.4752 | 6.3791 | 6.2513 | 6.098 | 5.9774 | 5.8851 | 5.7869 | 5.5897 | 5.476 | 5.2368 | 5.0802
| NEW PITSLIGO | CT |  |  |  | 6.8554 | 6.8419 | 6.8167 | 6.7767 | 6.6337 | 6.4791 | 6.3218 | 6.1915 | 6.0932 | 5.9869 | 5.7812 | 5.679 | 5.4349 | 5.2874 | 7.0374 | 7.0107 | 6.9726 | 6.9018 | 6.825 | 6.7274 | 6.6263 | 6.5562 | 6.4878 | 6.4121 | 6.2654 | 6.175 | 5.9906 | 5.8205 | 6.7695 | 6.72 | 6.6556 | 6.5323 | 6.4017 | 6.2513 | 6.098 | 5.9774 | 5.8851 | 5.7869 | 5.5897 | 5.476 | 5.2368 | 5.0802
| NEW PITSLIGO | LW |  |  |  | 6.8545 | 6.8425 | 6.8104 | 6.7115 | 6.6044 | 6.5015 | 6.374 | 6.2343 | 6.1325 | 6.028 | 5.8166 | 5.7717 | 5.5555 | 5.3212 | 7.017 | 6.9816 | 6.9343 | 6.887 | 6.8351 | 6.786 | 6.7195 | 6.6453 | 6.5778 | 6.5072 | 6.3664 | 6.3651 | 6.1659 | 5.9095 | 6.7216 | 6.6508 | 6.5648 | 6.4752 | 6.3791 | 6.2867 | 6.1726 | 6.0476 | 5.9558 | 5.8611 | 5.6589 | 5.6178 | 5.3822 | 5.1084
| NEW PITSLIGO | ST |  |  |  | 6.8568 | 6.8511 | 6.8432 | 6.8049 | 6.7727 | 6.7445 | 6.6784 | 6.6019 | 6.4973 | 6.4046 | 6.2044 | 5.8553 | 5.5843 | 5.38 | 7.0476 | 7.0332 | 7.0152 | 6.9571 | 6.9061 | 6.8628 | 6.7775 | 6.7271 | 6.6459 | 6.5846 | 6.4474 | 6.2155 | 5.9849 | 5.7669 | 6.7935 | 6.7661 | 6.7331 | 6.6557 | 6.5838 | 6.5213 | 6.4149 | 6.3428 | 6.2382 | 6.1513 | 5.9638 | 5.6093 | 5.3329 | 5.1196
| NEW PITSLIGO | FS |  |  |  | 6.8579 | 6.8534 | 6.8473 | 6.8335 | 6.8179 | 6.8 | 6.7801 | 6.7595 | 6.6956 | 6.6222 | 6.4658 | 6.081 | 5.8134 | 5.7172 | 7.0549 | 7.0441 | 7.0287 | 7.0022 | 6.9726 | 6.9422 | 6.909 | 6.8749 | 6.8259 | 6.7797 | 6.6789 | 6.4738 | 6.2746 | 6.1264 | 6.8102 | 6.7906 | 6.7625 | 6.7197 | 6.6727 | 6.6264 | 6.5763 | 6.5247 | 6.4531 | 6.3847 | 6.2399 | 5.894 | 5.6414 | 5.5559
DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | NO | 0.22006 | 0.21638 | 0.20761 | 0.2031 | 0.19787 | 0.18947 | 0.18118 | 0.17474 | 0.16724 | 0.15526 | 0.13904 | 0.13138 | 0.12891 | 0.12593 | 0.26904 | 0.26699 | 0.26236 | 0.25954 | 0.25481 | 0.25047 | 0.24617 | 0.24037 | 0.23374 | 0.22548 | 0.21209 | 0.20699 | 0.20559 | 0.20306 | 0.25271 | 0.24927 | 0.24121 | 0.23694 | 0.2315 | 0.2238 | 0.21613 | 0.20895 | 0.20096 | 0.18934 | 0.17383 | 0.16687 | 0.16424 | 0.16119
| NEWTON | CT |  |  |  | 0.22303 | 0.21874 | 0.2127 | 0.20468 | 0.19787 | 0.18947 | 0.18278 | 0.17802 | 0.16724 | 0.16221 | 0.14673 | 0.13297 | 0.13047 | 0.12593 | 0.27057 | 0.26808 | 0.26468 | 0.25984 | 0.25481 | 0.25047 | 0.24657 | 0.24321 | 0.23664 | 0.23048 | 0.21759 | 0.20804 | 0.20592 | 0.20306 | 0.25577 | 0.25155 | 0.2458 | 0.23826 | 0.2315 | 0.2238 | 0.21745 | 0.21262 | 0.20223 | 0.1961 | 0.18126 | 0.16846 | 0.16582 | 0.16119
| NEWTON | LW |  |  |  | 0.22006 | 0.21638 | 0.20761 | 0.2031 | 0.19813 | 0.19006 | 0.18118 | 0.17474 | 0.16729 | 0.15526 | 0.13904 | 0.13138 | 0.12891 | 0.12754 | 0.26904 | 0.26699 | 0.26236 | 0.25954 | 0.25612 | 0.2521 | 0.24617 | 0.24037 | 0.23374 | 0.22548 | 0.21209 | 0.20699 | 0.20559 | 0.20503 | 0.25271 | 0.24927 | 0.24121 | 0.23694 | 0.23221 | 0.22484 | 0.21613 | 0.20895 | 0.20096 | 0.18934 | 0.17383 | 0.16687 | 0.16424 | 0.16287
| NEWTON | ST |  |  |  | 0.22306 | 0.22095 | 0.21973 | 0.21829 | 0.21478 | 0.21001 | 0.20729 | 0.20382 | 0.19966 | 0.19319 | 0.17808 | 0.14695 | 0.14037 | 0.13598 | 0.27057 | 0.26938 | 0.26853 | 0.26754 | 0.26535 | 0.26259 | 0.26044 | 0.25771 | 0.25444 | 0.24986 | 0.23896 | 0.21533 | 0.21054 | 0.20831 | 0.25575 | 0.25381 | 0.25261 | 0.25119 | 0.24768 | 0.24311 | 0.24046 | 0.23698 | 0.23294 | 0.22665 | 0.21192 | 0.1813 | 0.17496 | 0.17071
| NEWTON | FS |  |  |  | 0.22312 | 0.22114 | 0.22148 | 0.21897 | 0.21606 | 0.21292 | 0.20765 | 0.20713 | 0.2043 | 0.19965 | 0.19038 | 0.15944 | 0.13673 | 0.13368 | 0.27062 | 0.26951 | 0.26947 | 0.268 | 0.26627 | 0.26437 | 0.26167 | 0.26035 | 0.25812 | 0.25494 | 0.24815 | 0.22661 | 0.20914 | 0.20727 | 0.25581 | 0.25401 | 0.2542 | 0.25186 | 0.24904 | 0.24588 | 0.24107 | 0.24014 | 0.2374 | 0.23283 | 0.22383 | 0.19386 | 0.17178 | 0.16876
REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | NO | 3.1102 | 2.8262 | 2.4295 | 1.4215 | 0.32506 | -1.1648 | -3.5768 | -5.2777 | -6.7627 | -7.9259 | -9.9581 | -10.961 | -12.0442 | -12.5357 | 6.0595 | 5.9748 | 5.8392 | 5.2343 | 4.5593 | 3.3686 | 1.1949 | -0.14721 | -1.2834 | -2.1321 | -3.5424 | -4.0815 | -4.7273 | -5.0913 | 4.4051 | 4.3499 | 4.2448 | 3.2113 | 2.0813 | 0.45704 | -2.0502 | -3.7891 | -5.2198 | -6.3504 | -8.3206 | -9.2908 | -10.3148 | -10.8008
| NEWTONHILL | CT |  |  |  | 3.3548 | 3.1942 | 2.9498 | 2.2506 | 1.4728 | 0.47192 | -1.2362 | -2.2273 | -3.5932 | -4.7748 | -6.7605 | -8.4814 | -10.08 | -10.9321 | 6.0927 | 6.0099 | 5.8772 | 5.6061 | 5.3063 | 4.6253 | 3.0965 | 2.4955 | 1.651 | 0.83291 | -0.4666 | -1.4464 | -2.639 | -3.8633 | 4.409 | 4.3511 | 4.2454 | 4.0368 | 3.3047 | 2.2586 | 0.54582 | -0.40236 | -1.689 | -2.8069 | -4.6804 | -6.2332 | -7.6696 | -8.4397
| NEWTONHILL | LW |  |  |  | 3.1102 | 2.8262 | 2.4295 | 1.4215 | 0.32506 | -1.1648 | -3.5768 | -5.2777 | -6.7627 | -7.9259 | -9.9581 | -10.961 | -12.0442 | -12.5357 | 6.0595 | 5.9748 | 5.8392 | 5.2343 | 4.5593 | 3.3686 | 1.1949 | -0.14721 | -1.2834 | -2.1321 | -3.5424 | -4.0815 | -4.7273 | -5.0913 | 4.4051 | 4.3499 | 4.2448 | 3.2113 | 2.0813 | 0.45704 | -2.0502 | -3.7891 | -5.2198 | -6.3504 | -8.3206 | -9.2908 | -10.3148 | -10.8008
| NEWTONHILL | ST |  |  |  | 3.4147 | 3.3347 | 3.2254 | 2.7157 | 2.2915 | 1.9299 | 0.47984 | -0.19313 | -1.105 | -1.718 | -2.7105 | -4.3809 | -5.8726 | -7.4497 | 6.1075 | 6.0739 | 6.0299 | 5.5149 | 5.133 | 4.8418 | 3.2315 | 2.6431 | 1.8228 | 1.3523 | 0.71082 | -0.25808 | -1.4951 | -2.9905 | 4.4146 | 4.3882 | 4.3507 | 3.8451 | 3.4729 | 3.1947 | 1.6495 | 1.0901 | 0.3117 | -0.18713 | -1.1784 | -2.8939 | -4.225 | -5.5695
| NEWTONHILL | FS |  |  |  | 3.4385 | 3.3747 | 3.294 | 3.088 | 2.8617 | 2.606 | 1.9506 | 1.4626 | 0.7403 | 0.25021 | -0.62653 | -2.4142 | -4.6065 | -5.9294 | 6.1141 | 6.0874 | 6.0533 | 5.9127 | 5.7631 | 5.5894 | 4.9403 | 4.5375 | 3.9583 | 3.632 | 3.1405 | 1.9425 | -0.22933 | -2.4298 | 4.4183 | 4.3968 | 4.3666 | 4.2346 | 4.0926 | 3.9291 | 3.3192 | 2.9371 | 2.3953 | 2.0485 | 1.2088 | -0.44017 | -2.5112 | -3.626
CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | NO | 15.2726 | 14.8889 | 14.467 | 13.8891 | 12.9593 | 12.2576 | 11.777 | 11.3266 | 11.0118 | 10.5336 | 9.8744 | 9.8107 | 9.2467 | 8.6824 | 15.2595 | 14.9075 | 14.5096 | 13.9691 | 12.8671 | 12.1117 | 11.8401 | 11.6297 | 11.4463 | 11.1145 | 10.7258 | 11.1289 | 10.5841 | 9.9518 | 15.261 | 14.84 | 14.3683 | 13.7371 | 12.6527 | 11.8346 | 11.3904 | 10.9921 | 10.7301 | 10.3094 | 9.7507 | 9.6374 | 8.9942 | 8.305
| NINEWELLS | CT |  |  |  | 15.3479 | 15.0342 | 14.7008 | 14.1466 | 13.1933 | 12.5295 | 12.1051 | 11.733 | 11.4106 | 10.9366 | 10.2816 | 9.9113 | 9.3192 | 8.8741 | 15.2631 | 14.9193 | 14.5533 | 14.0333 | 12.9396 | 12.2057 | 11.9192 | 11.6862 | 11.4463 | 11.1145 | 10.7258 | 11.1289 | 10.5841 | 9.9695 | 15.3267 | 14.9761 | 14.5965 | 14.0036 | 12.9043 | 12.1314 | 11.7178 | 11.3613 | 11.0649 | 10.6403 | 10.0809 | 9.7456 | 9.1302 | 8.6509
| NINEWELLS | LW |  |  |  | 15.2726 | 14.8889 | 14.467 | 13.8891 | 12.9593 | 12.2576 | 11.777 | 11.3266 | 11.0118 | 10.5336 | 9.8744 | 9.8107 | 9.2467 | 8.6824 | 15.2595 | 14.9075 | 14.5096 | 13.9691 | 12.8671 | 12.1117 | 11.8401 | 11.6297 | 11.5219 | 11.1876 | 10.8196 | 11.1586 | 10.6161 | 9.9518 | 15.261 | 14.84 | 14.3683 | 13.7371 | 12.6527 | 11.8346 | 11.3904 | 10.9921 | 10.7301 | 10.3094 | 9.7507 | 9.6374 | 8.9942 | 8.305
| NINEWELLS | ST |  |  |  | 15.3765 | 15.0996 | 14.8211 | 14.4591 | 13.7023 | 13.1922 | 12.9141 | 12.6842 | 12.5049 | 12.2024 | 11.8473 | 11.3978 | 10.7561 | 10.0515 | 15.2667 | 14.9579 | 14.6334 | 14.1513 | 13.051 | 12.3327 | 12.0589 | 11.8424 | 11.6857 | 11.4237 | 11.111 | 11.2462 | 10.827 | 10.2838 | 15.3521 | 15.0365 | 14.7097 | 14.2886 | 13.3603 | 12.7334 | 12.4609 | 12.2439 | 12.0721 | 11.7941 | 11.4991 | 11.1159 | 10.4467 | 9.7206
| NINEWELLS | FS |  |  |  | 15.4097 | 15.193 | 14.9827 | 14.688 | 14.094 | 13.672 | 13.4036 | 13.1698 | 12.9804 | 12.6535 | 12.2744 | 11.7186 | 10.9505 | 10.4956 | 15.3028 | 15.0638 | 14.8197 | 14.4514 | 13.6245 | 13.048 | 12.7531 | 12.5113 | 12.3373 | 11.9971 | 11.6962 | 11.58 | 11.269 | 10.5299 | 15.3814 | 15.1376 | 14.8932 | 14.5609 | 13.8489 | 13.3346 | 13.0486 | 12.8111 | 12.6173 | 12.2762 | 11.915 | 11.4715 | 10.7569 | 10.3464
THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | NO | 0.18021 | 0.1789 | 0.17333 | 0.16956 | 0.16411 | 0.15626 | 0.14982 | 0.14532 | 0.14176 | 0.1365 | 0.11797 | 0.13839 | 0.13644 | 0.13492 | 0.19927 | 0.19838 | 0.19553 | 0.19115 | 0.18702 | 0.1834 | 0.17953 | 0.17561 | 0.17189 | 0.16836 | 0.15472 | 0.17199 | 0.17032 | 0.16873 | 0.18921 | 0.18781 | 0.18339 | 0.17677 | 0.17129 | 0.16467 | 0.15832 | 0.1529 | 0.14875 | 0.14377 | 0.126 | 0.14958 | 0.14786 | 0.14648
| NORTH HOY | CT |  |  |  | 0.18216 | 0.1794 | 0.17691 | 0.16956 | 0.16411 | 0.15626 | 0.14982 | 0.14532 | 0.14176 | 0.1365 | 0.12807 | 0.14123 | 0.13644 | 0.13492 | 0.20003 | 0.19861 | 0.19569 | 0.19115 | 0.18702 | 0.1834 | 0.17953 | 0.17561 | 0.17189 | 0.16836 | 0.16094 | 0.17289 | 0.17032 | 0.16873 | 0.18928 | 0.18789 | 0.18339 | 0.17677 | 0.17129 | 0.16467 | 0.15832 | 0.1529 | 0.14875 | 0.14377 | 0.13554 | 0.15213 | 0.14786 | 0.14648
| NORTH HOY | LW |  |  |  | 0.18021 | 0.1789 | 0.17333 | 0.17137 | 0.1657 | 0.16204 | 0.1548 | 0.14766 | 0.14406 | 0.13735 | 0.11797 | 0.13839 | 0.13753 | 0.13564 | 0.19927 | 0.19838 | 0.19553 | 0.19412 | 0.1912 | 0.1891 | 0.18487 | 0.17972 | 0.17431 | 0.1684 | 0.15472 | 0.17199 | 0.17149 | 0.17077 | 0.18921 | 0.18781 | 0.18364 | 0.18084 | 0.17607 | 0.17209 | 0.16473 | 0.15722 | 0.151 | 0.14443 | 0.126 | 0.14958 | 0.14882 | 0.1472
| NORTH HOY | ST |  |  |  | 0.1822 | 0.18178 | 0.1823 | 0.17822 | 0.17868 | 0.1756 | 0.17561 | 0.17283 | 0.16722 | 0.16238 | 0.1496 | 0.15428 | 0.15287 | 0.15024 | 0.20005 | 0.19971 | 0.19969 | 0.19779 | 0.19744 | 0.19578 | 0.1938 | 0.19135 | 0.18789 | 0.18411 | 0.17435 | 0.17847 | 0.17669 | 0.17495 | 0.18938 | 0.18899 | 0.18834 | 0.18684 | 0.18547 | 0.18293 | 0.18066 | 0.17762 | 0.17255 | 0.16789 | 0.15568 | 0.16378 | 0.16235 | 0.16007
| NORTH HOY | FS |  |  |  | 0.18228 | 0.18195 | 0.18119 | 0.17875 | 0.17952 | 0.17684 | 0.17553 | 0.17251 | 0.17075 | 0.1706 | 0.16195 | 0.15446 | 0.14552 | 0.14317 | 0.20011 | 0.19984 | 0.19935 | 0.1982 | 0.19815 | 0.19679 | 0.19587 | 0.19424 | 0.19273 | 0.19081 | 0.18521 | 0.18139 | 0.17387 | 0.17191 | 0.18948 | 0.18919 | 0.18881 | 0.18778 | 0.18693 | 0.18512 | 0.18324 | 0.18088 | 0.1783 | 0.17612 | 0.16778 | 0.16472 | 0.15589 | 0.15385
PERSLEY | NORTHFIELD | MINIMUM HEADROOM | NJ 90728 08364 | NO | NO | 14.55 | 14.55 | 14.55 | 14.5382 | 14.5303 | 14.525 | 14.5069 | 14.5019 | 14.4448 | 14.4246 | 14.38 | 14.2516 | 13.8828 | 13.2887 | 9.918 | 9.8301 | 9.6934 | 9.487 | 9.263 | 9.0539 | 8.7573 | 8.4208 | 8.0372 | 7.6256 | 6.8075 | 6.6345 | 5.6028 | 3.8647 | 10.0249 | 9.8819 | 9.6904 | 9.302 | 8.8951 | 8.5082 | 8.0192 | 7.4726 | 6.9588 | 6.3792 | 5.222 | 5.2012 | 4.304 | 3.66
| NORTHFIELD | CT |  |  |  | 14.55 | 14.55 | 14.55 | 14.5485 | 14.5457 | 14.5327 | 14.5187 | 14.5151 | 14.4892 | 14.4632 | 14.4159 | 14.2844 | 14.0847 | 13.8489 | 9.9715 | 9.9166 | 9.8309 | 9.5952 | 9.3404 | 9.123 | 8.898 | 8.6796 | 8.3529 | 7.9692 | 7.1908 | 6.6345 | 5.6028 | 4.3377 | 10.1619 | 10.0979 | 10.0015 | 9.6262 | 9.2229 | 8.8636 | 8.4979 | 8.1377 | 7.6776 | 7.1466 | 6.0714 | 5.2454 | 4.304 | 3.7557
| NORTHFIELD | LW |  |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.5218 | 14.4926 | 14.4414 | 14.299 | 13.8828 | 13.2887 | 9.918 | 9.8301 | 9.6934 | 9.487 | 9.263 | 9.0539 | 8.7573 | 8.4208 | 8.0372 | 7.6256 | 6.8075 | 7.0246 | 6.3968 | 5.6091 | 10.0249 | 9.8819 | 9.6904 | 9.302 | 8.8951 | 8.5082 | 8.0192 | 7.4726 | 6.9588 | 6.3792 | 5.222 | 5.2012 | 4.4753 | 3.66
| NORTHFIELD | ST |  |  |  | 14.55 | 14.55 | 14.55 | 14.5382 | 14.5303 | 14.525 | 14.5069 | 14.5019 | 14.4448 | 14.4246 | 14.38 | 14.2516 | 13.9437 | 13.6029 | 9.982 | 9.9539 | 9.9165 | 9.8481 | 9.773 | 9.6903 | 9.5767 | 9.4549 | 9.2292 | 9.0197 | 8.5184 | 7.6421 | 6.4701 | 4.9699 | 10.1827 | 10.153 | 10.1127 | 10.0426 | 9.9699 | 9.8879 | 9.7666 | 9.6307 | 9.395 | 9.174 | 8.6438 | 7.7162 | 6.6271 | 5.5849
| NORTHFIELD | FS |  |  |  | 14.55 | 14.55 | 14.55 | 14.5476 | 14.5452 | 14.5424 | 14.5396 | 14.5372 | 14.5165 | 14.5025 | 14.4745 | 14.4575 | 14.4403 | 14.4022 | 9.9867 | 9.9614 | 9.9299 | 9.8714 | 9.8018 | 9.7249 | 9.6375 | 9.5364 | 9.3739 | 9.2027 | 8.786 | 7.8849 | 6.1967 | 3.8647 | 10.1921 | 10.1659 | 10.1348 | 10.0756 | 10.0072 | 9.9322 | 9.8523 | 9.7517 | 9.5793 | 9.3951 | 8.968 | 8.1693 | 6.9606 | 6.1739
BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | NO | -1.258 | -1.3025 | -1.4628 | -1.66 | -1.7537 | -1.8569 | -1.9742 | -2.0799 | -2.1579 | -2.2197 | -2.3489 | -2.3588 | -2.4234 | -2.4701 | -0.69579 | -0.69862 | -0.85109 | -1.0598 | -1.1068 | -1.1701 | -1.2332 | -1.2838 | -1.3373 | -1.3747 | -1.4517 | -1.3972 | -1.4587 | -1.5023 | -1.1192 | -1.137 | -1.3014 | -1.49 | -1.5381 | -1.6024 | -1.6705 | -1.7308 | -1.7969 | -1.859 | -2.018 | -2.0221 | -2.0853 | -2.1271
| NOSTIE BRIDGE | CT |  |  |  | -1.2371 | -1.2677 | -1.3971 | -1.5912 | -1.714 | -1.8344 | -1.9469 | -2.0652 | -2.135 | -2.1915 | -2.3091 | -2.3223 | -2.4234 | -2.4701 | -0.69471 | -0.69685 | -0.80768 | -1.0067 | -1.0754 | -1.1394 | -1.1984 | -1.2602 | -1.3141 | -1.3491 | -1.4217 | -1.391 | -1.4587 | -1.5023 | -1.1166 | -1.1353 | -1.28 | -1.4492 | -1.5129 | -1.5776 | -1.6391 | -1.7054 | -1.7688 | -1.8151 | -1.9663 | -1.9861 | -2.0853 | -2.1271
| NOSTIE BRIDGE | LW |  |  |  | -1.258 | -1.3025 | -1.4628 | -1.66 | -1.7537 | -1.8569 | -1.9742 | -2.0799 | -2.1579 | -2.2197 | -2.3489 | -2.3588 | -2.4083 | -2.426 | -0.69579 | -0.69862 | -0.85109 | -1.0598 | -1.1068 | -1.1701 | -1.2332 | -1.2838 | -1.3373 | -1.3747 | -1.4517 | -1.3972 | -1.4222 | -1.4314 | -1.1192 | -1.137 | -1.3014 | -1.49 | -1.5381 | -1.6024 | -1.6705 | -1.7308 | -1.7969 | -1.859 | -2.018 | -2.0221 | -2.0712 | -2.0883
| NOSTIE BRIDGE | ST |  |  |  | -1.1998 | -1.2161 | -1.3235 | -1.4455 | -1.4872 | -1.5308 | -1.5781 | -1.6317 | -1.6995 | -1.7591 | -1.906 | -2.1791 | -2.2748 | -2.3238 | -0.69197 | -0.69316 | -0.76936 | -0.92749 | -0.9567 | -0.99268 | -1.0284 | -1.0675 | -1.12 | -1.1526 | -1.2302 | -1.3219 | -1.3836 | -1.4329 | -1.0528 | -1.0607 | -1.1894 | -1.3297 | -1.3618 | -1.3987 | -1.4387 | -1.4833 | -1.5414 | -1.5849 | -1.6906 | -1.8484 | -1.9448 | -1.9944
| NOSTIE BRIDGE | FS |  |  |  | -1.1925 | -1.2063 | -1.2893 | -1.3816 | -1.424 | -1.4591 | -1.5061 | -1.5426 | -1.5949 | -1.6578 | -1.7731 | -2.0889 | -2.3291 | -2.3725 | -0.69159 | -0.69263 | -0.74041 | -0.84166 | -0.88134 | -0.90973 | -0.95068 | -0.97337 | -1.0148 | -1.0673 | -1.1451 | -1.2935 | -1.4156 | -1.4734 | -1.0507 | -1.057 | -1.1547 | -1.2589 | -1.2949 | -1.3198 | -1.3597 | -1.3854 | -1.4283 | -1.4819 | -1.5684 | -1.761 | -1.9945 | -2.037
TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 8.6196 | 8.2205 | 7.5779 | 6.6966 | 5.7354 | 4.6554 | 3.3128 | 1.9481 | 0.90745 | -0.25253 | -2.9426 | 2.3705 | 1.7464 | 1.2937 | 12.496 | 12.175 | 11.729 | 11.1858 | 10.5759 | 9.8751 | 8.9444 | 7.99 | 7.1468 | 6.1535 | 3.967 | 8.4165 | 7.6363 | 6.7044 | 9.705 | 9.6802 | 9.6444 | 9.0566 | 8.171 | 7.1203 | 5.8145 | 4.3968 | 3.0899 | 1.5351 | -2.3087 | 5.2833 | 4.7223 | 4.4684
| OBAN | CT |  |  |  | 8.6223 | 8.312 | 7.8254 | 6.9789 | 5.9382 | 4.8046 | 3.6042 | 2.3765 | 1.417 | 0.36458 | -1.8797 | 2.7619 | 1.7676 | 1.2937 | 12.5632 | 12.2831 | 11.8686 | 11.2647 | 10.6123 | 9.9052 | 9.1501 | 8.3732 | 7.6137 | 6.7709 | 4.679 | 8.471 | 7.6363 | 6.7382 | 9.705 | 9.6802 | 9.6444 | 9.1108 | 8.2116 | 7.1203 | 5.9363 | 4.6106 | 3.3086 | 1.896 | -1.5008 | 5.7644 | 4.8894 | 4.4684
| OBAN | LW |  |  |  | 8.6196 | 8.2205 | 7.5779 | 6.6966 | 5.7354 | 4.6554 | 3.3128 | 1.9481 | 0.90745 | -0.25253 | -2.9426 | 2.3705 | 1.7464 | 1.6095 | 12.496 | 12.175 | 11.729 | 11.1858 | 10.5759 | 9.8751 | 8.9444 | 7.99 | 7.1468 | 6.1535 | 3.967 | 8.4165 | 8.1196 | 8.0711 | 9.7281 | 9.7127 | 9.6882 | 9.0566 | 8.171 | 7.1504 | 5.8145 | 4.3968 | 3.0899 | 1.5351 | -2.3087 | 5.2833 | 4.7223 | 4.6046
| OBAN | ST |  |  |  | 8.7801 | 8.6591 | 8.5211 | 8.2898 | 8.0143 | 7.6808 | 7.213 | 6.7161 | 6.0974 | 5.3168 | 1.7671 | 6.8924 | 6.6247 | 6.0296 | 12.704 | 12.577 | 12.4321 | 12.1789 | 11.8955 | 11.5756 | 11.121 | 10.6756 | 10.1498 | 9.5001 | 6.8685 | 9.9085 | 9.3025 | 8.4012 | 9.7592 | 9.7691 | 9.781 | 9.7268 | 9.6891 | 9.1748 | 8.3518 | 7.4324 | 6.3297 | 4.9591 | 1.463 | 8.5224 | 8.2394 | 7.9334
| OBAN | FS |  |  |  | 8.8124 | 8.725 | 8.6369 | 8.5079 | 8.3555 | 8.1681 | 7.953 | 7.6756 | 7.3296 | 6.9295 | 5.958 | 6.8316 | 5.6047 | 4.882 | 12.7252 | 12.6196 | 12.5069 | 12.3257 | 12.1197 | 11.8839 | 11.6208 | 11.335 | 11.0289 | 10.6723 | 9.7984 | 10.206 | 8.5679 | 6.7044 | 9.7531 | 9.7586 | 9.7673 | 9.7679 | 9.7668 | 9.7603 | 9.6832 | 9.2189 | 8.708 | 8.0906 | 6.528 | 8.864 | 7.6887 | 7.1517
MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | NO | 7.4568 | 7.2239 | 6.991 | 6.4367 | 5.8935 | 5.2352 | 4.4605 | 3.7571 | 3.2487 | 2.7079 | 1.6468 | 1.3605 | 0.59221 | -0.098848 | 7.989 | 7.8651 | 7.7239 | 7.3788 | 7.0236 | 6.5242 | 5.9277 | 5.4307 | 5.0611 | 4.664 | 3.8912 | 3.8791 | 3.1465 | 2.2785 | 7.6742 | 7.4817 | 7.2647 | 6.7677 | 6.2638 | 5.6197 | 4.8434 | 4.1592 | 3.6523 | 3.1106 | 2.0512 | 1.9119 | 1.0788 | 0.21143
| OLD CRAIGIE ROAD | CT |  |  |  | 7.5842 | 7.4376 | 7.2962 | 6.8589 | 6.3985 | 5.8619 | 5.3028 | 4.8673 | 4.4053 | 3.8747 | 2.8296 | 1.9886 | 1.113 | 0.50703 | 8.0418 | 7.9496 | 7.8527 | 7.5898 | 7.3116 | 6.9197 | 6.5051 | 6.2412 | 5.932 | 5.5649 | 4.8376 | 4.3474 | 3.4825 | 2.425 | 7.7829 | 7.6554 | 7.5228 | 7.1156 | 6.6945 | 6.1804 | 5.6413 | 5.2558 | 4.8265 | 4.3221 | 3.3313 | 2.6982 | 1.8889 | 1.2657
| OLD CRAIGIE ROAD | LW |  |  |  | 7.4568 | 7.2239 | 6.991 | 6.4367 | 5.8935 | 5.2352 | 4.4605 | 3.7571 | 3.2487 | 2.7079 | 1.6468 | 1.3605 | 0.59221 | -0.098848 | 7.989 | 7.8651 | 7.7239 | 7.3788 | 7.0236 | 6.5242 | 5.9277 | 5.4307 | 5.0611 | 4.664 | 3.8912 | 3.8791 | 3.1465 | 2.2785 | 7.6742 | 7.4817 | 7.2647 | 6.7677 | 6.2638 | 5.6197 | 4.8434 | 4.1592 | 3.6523 | 3.1106 | 2.0512 | 1.9119 | 1.0788 | 0.21143
| OLD CRAIGIE ROAD | ST |  |  |  | 7.6139 | 7.5135 | 7.448 | 7.2303 | 7.0671 | 6.9202 | 6.6012 | 6.4151 | 6.1875 | 5.9617 | 5.4333 | 4.5525 | 3.5341 | 2.5302 | 8.0566 | 7.9939 | 7.9477 | 7.716 | 7.5419 | 7.3965 | 7.0457 | 6.8686 | 6.6416 | 6.4398 | 5.9638 | 5.1865 | 4.1061 | 2.7912 | 7.8095 | 7.726 | 7.6672 | 7.4213 | 7.2353 | 7.0751 | 6.7051 | 6.5065 | 6.2635 | 6.0368 | 5.5053 | 4.6366 | 3.5981 | 2.5713
| OLD CRAIGIE ROAD | FS |  |  |  | 7.6225 | 7.5407 | 7.4823 | 7.3752 | 7.276 | 7.1659 | 7.0477 | 6.9166 | 6.743 | 6.5573 | 6.1415 | 5.3854 | 4.2441 | 3.4511 | 8.0612 | 8.0075 | 7.9651 | 7.8715 | 7.7794 | 7.6756 | 7.5631 | 7.4434 | 7.2921 | 7.1292 | 6.7485 | 5.9998 | 4.66 | 3.0158 | 7.8168 | 7.7496 | 7.698 | 7.5922 | 7.4892 | 7.3744 | 7.251 | 7.1163 | 6.9441 | 6.763 | 6.3565 | 5.6516 | 4.5835 | 3.9513
KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | NO | 2.0468 | 1.8461 | 1.6011 | 1.2187 | 0.73693 | 0.27271 | -0.39141 | -1.0641 | -1.7516 | -2.1471 | -2.966 | -3.1044 | -3.6419 | -4.0693 | 4.0317 | 3.9343 | 3.7995 | 3.5776 | 3.2652 | 2.9545 | 2.4633 | 1.9837 | 1.4494 | 1.176 | 0.60686 | 0.64851 | 0.20455 | -0.32989 | 2.9712 | 2.7924 | 2.5663 | 2.2081 | 1.7535 | 1.3006 | 0.64942 | 0.0024761 | -0.65398 | -1.0465 | -1.8544 | -1.9547 | -2.4663 | -2.8533
| OLDMELDRUM | CT |  |  |  | 2.1912 | 2.0563 | 1.8637 | 1.4668 | 0.96278 | 0.50657 | -0.083538 | -0.63038 | -1.294 | -1.7188 | -2.5661 | -2.846 | -3.6403 | -4.0693 | 4.0809 | 4.002 | 3.8759 | 3.6472 | 3.3221 | 3.0156 | 2.589 | 2.229 | 1.7294 | 1.4356 | 0.8555 | 0.74688 | 0.20455 | -0.32989 | 3.093 | 2.9705 | 2.7892 | 2.421 | 1.9483 | 1.5065 | 0.93946 | 0.43672 | -0.18455 | -0.59915 | -1.4199 | -1.6744 | -2.3782 | -2.7772
| OLDMELDRUM | LW |  |  |  | 2.0468 | 1.8461 | 1.6011 | 1.2187 | 0.73693 | 0.27271 | -0.39141 | -1.0641 | -1.7516 | -2.1471 | -2.966 | -3.1044 | -3.6419 | -4.0047 | 4.0317 | 3.9343 | 3.7995 | 3.5776 | 3.2652 | 2.9545 | 2.4633 | 1.9837 | 1.4494 | 1.176 | 0.60686 | 0.64851 | 0.30337 | -0.025125 | 2.9712 | 2.7924 | 2.5663 | 2.2081 | 1.7535 | 1.3006 | 0.64942 | 0.0024761 | -0.65398 | -1.0465 | -1.8544 | -1.9547 | -2.4663 | -2.8533
| OLDMELDRUM | ST |  |  |  | 2.2466 | 2.1681 | 2.0822 | 1.8776 | 1.609 | 1.4273 | 1.0186 | 0.66805 | 0.14677 | -0.11267 | -0.69539 | -1.3651 | -2.137 | -2.861 | 4.1032 | 4.0601 | 4.0096 | 3.8353 | 3.6137 | 3.4773 | 3.1058 | 2.8186 | 2.3765 | 2.1761 | 1.6126 | 1.2213 | 0.62283 | -0.044394 | 3.1399 | 3.0701 | 2.9927 | 2.7788 | 2.5129 | 2.3333 | 1.9128 | 1.5744 | 1.0759 | 0.82107 | 0.13354 | -0.43296 | -1.1558 | -1.8303
| OLDMELDRUM | FS |  |  |  | 2.2846 | 2.2274 | 2.1647 | 2.0531 | 1.8688 | 1.7294 | 1.5154 | 1.2546 | 0.84345 | 0.62119 | 0.13572 | -0.76953 | -1.7674 | -2.3171 | 4.1181 | 4.0845 | 4.0447 | 3.9687 | 3.8313 | 3.7325 | 3.5652 | 3.3561 | 3.0276 | 2.8691 | 2.5132 | 1.8928 | 1.015 | 0.24491 | 3.1723 | 3.1213 | 3.0645 | 2.9582 | 2.7842 | 2.6506 | 2.4473 | 2.2003 | 1.8174 | 1.607 | 1.1443 | 0.27959 | -0.65804 | -1.1355
THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | NO | 9.9348 | 9.7057 | 9.43 | 8.911 | 8.4366 | 7.9766 | 7.3862 | 6.6569 | 6.0471 | 5.4096 | 4.1162 | 4.1707 | 2.8972 | 2.1591 | 11.8371 | 11.7127 | 11.5361 | 11.2672 | 10.9982 | 10.7258 | 10.4327 | 10.071 | 9.6799 | 9.2644 | 8.4288 | 8.5872 | 7.6648 | 6.7626 | 10.4114 | 10.2164 | 9.955 | 9.5706 | 9.1744 | 8.7675 | 8.3201 | 7.7987 | 7.2487 | 6.6261 | 5.3697 | 5.4902 | 4.3426 | 3.5702
| ORMLIE | CT |  |  |  | 10.1207 | 9.9702 | 9.7575 | 9.1912 | 8.6716 | 8.1905 | 7.6561 | 7.0474 | 6.456 | 5.8318 | 4.5823 | 4.2495 | 2.8972 | 2.1591 | 11.9073 | 11.8075 | 11.6494 | 11.3142 | 10.9982 | 10.7258 | 10.4327 | 10.1135 | 9.7563 | 9.3666 | 8.5924 | 8.5872 | 7.6648 | 6.7626 | 10.5197 | 10.352 | 10.0889 | 9.6158 | 9.1744 | 8.7675 | 8.3201 | 7.8451 | 7.3597 | 6.8941 | 5.8085 | 5.5653 | 4.3426 | 3.62
| ORMLIE | LW |  |  |  | 9.9348 | 9.7057 | 9.43 | 8.911 | 8.4366 | 7.9766 | 7.3862 | 6.6569 | 6.0471 | 5.4096 | 4.1162 | 4.1707 | 3.1184 | 2.3656 | 11.8371 | 11.7127 | 11.5361 | 11.2672 | 11.0137 | 10.7809 | 10.4644 | 10.071 | 9.6799 | 9.2644 | 8.4288 | 8.7507 | 7.9847 | 7.1832 | 10.4114 | 10.2164 | 9.955 | 9.5706 | 9.1781 | 8.7936 | 8.3491 | 7.7987 | 7.2487 | 6.6261 | 5.3697 | 5.4902 | 4.4379 | 3.5702
| ORMLIE | ST |  |  |  | 10.2426 | 10.1904 | 10.1322 | 9.9878 | 9.8838 | 9.7656 | 9.6164 | 9.4181 | 9.1134 | 8.7652 | 7.8954 | 7.5579 | 6.4644 | 5.1779 | 11.9556 | 11.9121 | 11.8602 | 11.7456 | 11.6518 | 11.5497 | 11.4134 | 11.2444 | 10.9742 | 10.7132 | 10.0885 | 9.8003 | 8.8493 | 7.6637 | 10.5887 | 10.5194 | 10.4402 | 10.2934 | 10.1551 | 9.9953 | 9.7889 | 9.5379 | 9.1733 | 8.7949 | 7.874 | 8.2993 | 7.2539 | 6.0372
| ORMLIE | FS |  |  |  | 10.2664 | 10.2247 | 10.1811 | 10.0376 | 9.9262 | 9.8127 | 9.6812 | 9.5069 | 9.2764 | 9.0114 | 8.3909 | 7.5477 | 6.4015 | 5.5638 | 11.9767 | 11.9398 | 11.8972 | 11.7977 | 11.7156 | 11.6282 | 11.5255 | 11.3894 | 11.2018 | 11.0044 | 10.5496 | 9.99 | 8.9098 | 7.6492 | 10.6162 | 10.562 | 10.502 | 10.3769 | 10.2608 | 10.1338 | 9.9865 | 9.8053 | 9.572 | 9.3227 | 8.7483 | 8.5169 | 7.4143 | 6.6955
DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | NO | -0.17754 | -0.18785 | -0.20426 | -0.2233 | -0.24266 | -0.26145 | -0.28428 | -0.31299 | -0.33758 | -0.36525 | -0.41668 | -0.42853 | -0.44717 | -0.45737 | -0.020131 | -0.025786 | -0.036081 | -0.046465 | -0.06201 | -0.072795 | -0.084948 | -0.10223 | -0.12124 | -0.14221 | -0.18221 | -0.1911 | -0.20269 | -0.21189 | -0.2848 | -0.28728 | -0.29223 | -0.29902 | -0.30534 | -0.31004 | -0.31531 | -0.323 | -0.33713 | -0.35494 | -0.39094 | -0.33287 | -0.34787 | -0.35642
| OTTER FERRY | CT |  |  |  | -0.17011 | -0.17857 | -0.19272 | -0.21799 | -0.24266 | -0.26145 | -0.28366 | -0.30456 | -0.32194 | -0.34871 | -0.39702 | -0.42254 | -0.44717 | -0.45737 | -0.01716 | -0.022239 | -0.031175 | -0.046347 | -0.06201 | -0.072795 | -0.084948 | -0.096756 | -0.11054 | -0.13106 | -0.16904 | -0.18966 | -0.20269 | -0.21189 | -0.28459 | -0.28728 | -0.29223 | -0.29902 | -0.30534 | -0.31004 | -0.31531 | -0.323 | -0.33351 | -0.34468 | -0.36954 | -0.32737 | -0.34787 | -0.35642
| OTTER FERRY | LW |  |  |  | -0.17754 | -0.18785 | -0.20426 | -0.2233 | -0.24129 | -0.26003 | -0.28428 | -0.31299 | -0.33758 | -0.36525 | -0.41668 | -0.42853 | -0.4436 | -0.44693 | -0.020131 | -0.025786 | -0.036081 | -0.046465 | -0.057323 | -0.067429 | -0.083355 | -0.10223 | -0.12124 | -0.14221 | -0.18221 | -0.1911 | -0.19699 | -0.19806 | -0.2848 | -0.28713 | -0.29154 | -0.29521 | -0.2995 | -0.30355 | -0.31086 | -0.32156 | -0.33713 | -0.35494 | -0.39094 | -0.33287 | -0.34497 | -0.34751
| OTTER FERRY | ST |  |  |  | -0.16739 | -0.17229 | -0.17531 | -0.18091 | -0.1908 | -0.20001 | -0.2107 | -0.22444 | -0.23746 | -0.25248 | -0.29267 | -0.37816 | -0.3995 | -0.41224 | -0.016174 | -0.01893 | -0.021383 | -0.025225 | -0.031153 | -0.03712 | -0.044262 | -0.053217 | -0.062992 | -0.074745 | -0.10443 | -0.16907 | -0.1839 | -0.19197 | -0.28434 | -0.28537 | -0.28665 | -0.28842 | -0.29079 | -0.29357 | -0.29707 | -0.30133 | -0.30664 | -0.31319 | -0.33571 | -0.32069 | -0.32346 | -0.32359
| OTTER FERRY | FS |  |  |  | -0.16718 | -0.16899 | -0.17148 | -0.17883 | -0.18636 | -0.19396 | -0.20396 | -0.21099 | -0.22305 | -0.23661 | -0.26456 | -0.35006 | -0.41825 | -0.42824 | -0.016014 | -0.017499 | -0.019551 | -0.023674 | -0.02819 | -0.032846 | -0.038751 | -0.044073 | -0.051813 | -0.060643 | -0.080303 | -0.13908 | -0.19126 | -0.20028 | -0.2842 | -0.28498 | -0.28599 | -0.28732 | -0.28904 | -0.29094 | -0.29324 | -0.29595 | -0.29924 | -0.30304 | -0.31226 | -0.3112 | -0.32347 | -0.33127
GLENAGNES | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 26.5528 | 26.2716 | 26.0393 | 25.568 | 25.3448 | 25.1089 | 24.8404 | 24.6106 | 24.3321 | 24.0573 | 23.4072 | 24.3977 | 24.0011 | 23.4671 | 30.3916 | 30.1518 | 30.0117 | 29.605 | 29.4492 | 29.2352 | 28.9914 | 28.7878 | 28.605 | 28.4066 | 28.0186 | 28.4358 | 27.8508 | 26.6627 | 30.7207 | 30.461 | 30.3041 | 29.8122 | 29.6289 | 29.3728 | 29.0891 | 28.8411 | 28.6188 | 28.3777 | 27.902 | 28.3825 | 27.8944 | 27.2359
| OVERGATE | CT |  |  |  | 26.5554 | 26.2716 | 26.0393 | 25.568 | 25.3448 | 25.1089 | 24.8404 | 24.6106 | 24.3321 | 24.1125 | 23.6302 | 24.7167 | 24.4404 | 24.1852 | 30.3916 | 30.1555 | 30.0117 | 29.605 | 29.4492 | 29.2641 | 29.0571 | 28.9005 | 28.7106 | 28.5449 | 28.2027 | 28.4883 | 27.9029 | 27.0457 | 30.7326 | 30.4834 | 30.3058 | 29.8296 | 29.6481 | 29.4352 | 29.1985 | 29.0052 | 28.7819 | 28.6049 | 28.237 | 28.7882 | 28.4813 | 28.1771
| OVERGATE | LW |  |  |  | 26.5528 | 26.2924 | 26.115 | 25.5916 | 25.4132 | 25.1762 | 24.908 | 24.6637 | 24.3804 | 24.0573 | 23.4072 | 24.3977 | 24.0011 | 23.4671 | 30.3942 | 30.1518 | 30.0297 | 29.6122 | 29.4587 | 29.2352 | 28.9914 | 28.7878 | 28.605 | 28.4066 | 28.0186 | 28.4358 | 27.9583 | 27.3076 | 30.7207 | 30.461 | 30.3041 | 29.8122 | 29.6289 | 29.3728 | 29.0891 | 28.8411 | 28.6188 | 28.3777 | 27.902 | 28.3825 | 27.8944 | 27.2359
| OVERGATE | ST |  |  |  | 26.5672 | 26.3588 | 26.2673 | 25.88 | 25.7674 | 25.6307 | 25.413 | 25.2235 | 24.9678 | 24.7155 | 24.0957 | 25.0619 | 24.7142 | 24.3308 | 30.4006 | 30.1987 | 30.1229 | 29.7574 | 29.6495 | 29.5484 | 29.3645 | 29.2388 | 29.0563 | 28.906 | 28.5419 | 28.5592 | 27.8508 | 26.8795 | 30.7497 | 30.5503 | 30.4675 | 30.0731 | 29.9685 | 29.87 | 29.6842 | 29.554 | 29.3596 | 29.196 | 28.7931 | 29.0302 | 28.6127 | 28.1845
| OVERGATE | FS |  |  |  | 26.5742 | 26.4152 | 26.3469 | 26.0746 | 25.9758 | 25.8848 | 25.7621 | 25.6482 | 25.5094 | 25.3352 | 24.9693 | 25.4413 | 25.2156 | 25.0829 | 30.4013 | 30.2443 | 30.1852 | 29.9254 | 29.8347 | 29.7567 | 29.6508 | 29.5602 | 29.4464 | 29.3028 | 29.016 | 28.8133 | 27.9858 | 26.6627 | 30.7506 | 30.6018 | 30.5472 | 30.2805 | 30.1978 | 30.1267 | 30.0293 | 29.9473 | 29.8448 | 29.7137 | 29.4565 | 29.5437 | 29.2544 | 29.1344
CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | NO | 0.15746 | 0.15549 | 0.15491 | 0.15369 | 0.15269 | 0.15023 | 0.1488 | 0.14614 | 0.14343 | 0.1401 | 0.13285 | 0.14284 | 0.14273 | 0.14254 | 0.16044 | 0.15958 | 0.1591 | 0.15766 | 0.1567 | 0.15545 | 0.15438 | 0.15262 | 0.15033 | 0.1478 | 0.14233 | 0.15109 | 0.151 | 0.15085 | 0.15852 | 0.15732 | 0.15621 | 0.15391 | 0.1527 | 0.15044 | 0.14907 | 0.1466 | 0.14389 | 0.14069 | 0.13376 | 0.14482 | 0.14472 | 0.14453
| OVERSCAIG | CT |  |  |  | 0.15748 | 0.15549 | 0.15491 | 0.15369 | 0.15269 | 0.15023 | 0.1488 | 0.14614 | 0.144 | 0.14229 | 0.13857 | 0.14306 | 0.14447 | 0.14254 | 0.16046 | 0.15958 | 0.1591 | 0.15766 | 0.1567 | 0.15545 | 0.15438 | 0.15298 | 0.15135 | 0.15001 | 0.14682 | 0.15127 | 0.15166 | 0.15085 | 0.15852 | 0.15732 | 0.15621 | 0.15391 | 0.1527 | 0.15044 | 0.14907 | 0.1466 | 0.14454 | 0.1429 | 0.13926 | 0.14505 | 0.14625 | 0.14453
| OVERSCAIG | LW |  |  |  | 0.15746 | 0.15711 | 0.15642 | 0.15403 | 0.15338 | 0.15097 | 0.14914 | 0.14644 | 0.14343 | 0.1401 | 0.13285 | 0.14284 | 0.14273 | 0.14579 | 0.16044 | 0.16016 | 0.15948 | 0.15849 | 0.15759 | 0.15637 | 0.15466 | 0.15262 | 0.15033 | 0.1478 | 0.14233 | 0.15109 | 0.151 | 0.15213 | 0.15853 | 0.158 | 0.1568 | 0.15501 | 0.1538 | 0.15156 | 0.14939 | 0.1468 | 0.14389 | 0.14069 | 0.13376 | 0.14482 | 0.14472 | 0.1474
| OVERSCAIG | ST |  |  |  | 0.15751 | 0.15737 | 0.15718 | 0.15691 | 0.15656 | 0.15616 | 0.15552 | 0.15418 | 0.15248 | 0.15038 | 0.14579 | 0.15015 | 0.14779 | 0.14912 | 0.16048 | 0.16036 | 0.16021 | 0.16 | 0.1597 | 0.15905 | 0.15823 | 0.15722 | 0.15596 | 0.15438 | 0.15056 | 0.15414 | 0.15299 | 0.15348 | 0.15859 | 0.15844 | 0.15813 | 0.15771 | 0.15708 | 0.15627 | 0.15523 | 0.15394 | 0.15237 | 0.15039 | 0.14584 | 0.15127 | 0.14919 | 0.15033
| OVERSCAIG | FS |  |  |  | 0.15753 | 0.15741 | 0.15725 | 0.15705 | 0.15678 | 0.15649 | 0.15614 | 0.15572 | 0.15485 | 0.15369 | 0.1497 | 0.14763 | 0.14609 | 0.14606 | 0.16049 | 0.1604 | 0.16027 | 0.16011 | 0.1599 | 0.15963 | 0.1591 | 0.15846 | 0.15771 | 0.15685 | 0.15446 | 0.1542 | 0.15237 | 0.15234 | 0.15861 | 0.15848 | 0.15826 | 0.15795 | 0.15754 | 0.15699 | 0.15633 | 0.15553 | 0.15458 | 0.15348 | 0.14983 | 0.14939 | 0.1477 | 0.14766
KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | NO | -1.6736 | -1.7434 | -1.8338 | -2.4291 | -3.0912 | -4.3103 | -5.6287 | -6.4618 | -6.7523 | -7.0524 | -7.6214 | -8.4918 | -9.0619 | -9.543 | -0.65956 | -0.69569 | -0.74743 | -1.4162 | -2.1628 | -3.604 | -5.1489 | -6.0802 | -6.3728 | -6.6779 | -7.2377 | -8.2625 | -8.8753 | -9.4318 | -1.142 | -1.1635 | -1.2101 | -1.8992 | -2.6809 | -4.1572 | -5.7379 | -6.707 | -7.0205 | -7.3454 | -7.9766 | -9.062 | -9.7123 | -10.288
| PARK | CT |  |  |  | -1.6272 | -1.6726 | -1.7371 | -1.9419 | -2.1981 | -2.8847 | -3.612 | -3.8933 | -4.0974 | -4.318 | -4.7412 | -5.3145 | -5.7578 | -6.0395 | -0.64113 | -0.6683 | -0.71147 | -0.87539 | -1.1058 | -1.8828 | -2.7094 | -2.9698 | -3.1562 | -3.3591 | -3.7418 | -4.3792 | -4.7935 | -5.1573 | -1.1409 | -1.1635 | -1.2101 | -1.3514 | -1.5742 | -2.384 | -3.2435 | -3.5426 | -3.7465 | -3.9683 | -4.4132 | -5.111 | -5.5485 | -5.8547
| PARK | LW |  |  |  | -1.6736 | -1.7434 | -1.8338 | -2.4291 | -3.0912 | -4.3103 | -5.6287 | -6.4618 | -6.7523 | -7.0524 | -7.6214 | -8.4918 | -9.0619 | -9.543 | -0.65956 | -0.69569 | -0.74743 | -1.4162 | -2.1628 | -3.604 | -5.1489 | -6.0802 | -6.3728 | -6.6779 | -7.2377 | -8.2625 | -8.8753 | -9.4318 | -1.142 | -1.1611 | -1.197 | -1.8992 | -2.6809 | -4.1572 | -5.7379 | -6.707 | -7.0205 | -7.3454 | -7.9766 | -9.062 | -9.7123 | -10.288
| PARK | ST |  |  |  | -1.6104 | -1.6416 | -1.674 | -2.2262 | -2.6232 | -2.9069 | -3.7507 | -4.0303 | -4.3037 | -4.4519 | -4.798 | -5.5723 | -6.0897 | -6.503 | -0.63391 | -0.65155 | -0.67124 | -1.3352 | -1.7986 | -2.1183 | -3.138 | -3.4525 | -3.7539 | -3.8983 | -4.23 | -5.0144 | -5.5621 | -6.0444 | -1.138 | -1.1467 | -1.1577 | -1.8122 | -2.2639 | -2.5729 | -3.5839 | -3.8953 | -4.2072 | -4.3603 | -4.7135 | -5.5818 | -6.1428 | -6.5887
| PARK | FS |  |  |  | -1.5976 | -1.6183 | -1.6419 | -1.7797 | -1.9254 | -2.0885 | -2.2537 | -2.4074 | -2.5426 | -2.6564 | -2.9009 | -3.341 | -3.6977 | -3.8713 | -0.62848 | -0.64162 | -0.6573 | -0.8081 | -0.96381 | -1.142 | -1.3227 | -1.4859 | -1.6173 | -1.7224 | -1.9467 | -2.2726 | -2.5945 | -2.8674 | -1.1363 | -1.1429 | -1.1512 | -1.2928 | -1.437 | -1.605 | -1.776 | -1.9284 | -2.05 | -2.1664 | -2.4132 | -2.8316 | -3.153 | -3.3067
ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | YES | NO | 1.214 | 1.177 | 1.1246 | 1.0671 | 1.0032 | 0.91247 | 0.81658 | 0.73737 | 0.66231 | 0.5721 | 0.40766 | 0.22331 | -0.24363 | -0.93058 | 1.5939 | 1.5765 | 1.5495 | 1.522 | 1.4783 | 1.4143 | 1.3479 | 1.3049 | 1.2361 | 1.1518 | 0.99431 | 0.74842 | 0.24906 | -0.5719 | 0.9832 | 0.95207 | 0.90728 | 0.85829 | 0.80268 | 0.71163 | 0.61917 | 0.54868 | 0.47166 | 0.38052 | 0.2152 | -0.012771 | -0.56317 | -1.4133
| PEDDIESTON | CT |  |  |  | 1.2358 | 1.204 | 1.172 | 1.0934 | 1.0071 | 0.91247 | 0.81658 | 0.73737 | 0.66231 | 0.5721 | 0.40766 | 0.22331 | -0.092768 | -0.39428 | 1.6016 | 1.5861 | 1.5679 | 1.526 | 1.4783 | 1.4143 | 1.3479 | 1.3049 | 1.2361 | 1.1518 | 0.99431 | 0.76094 | 0.41549 | 0.019864 | 1.0015 | 0.97481 | 0.94765 | 0.87897 | 0.80268 | 0.71163 | 0.61917 | 0.54868 | 0.47166 | 0.38052 | 0.2152 | -0.012771 | -0.37221 | -0.7337
| PEDDIESTON | LW |  |  |  | 1.214 | 1.177 | 1.1246 | 1.0671 | 1.0032 | 0.95018 | 0.86921 | 0.78719 | 0.70072 | 0.60809 | 0.43075 | 0.26975 | -0.24363 | -0.93058 | 1.5939 | 1.5765 | 1.5495 | 1.522 | 1.491 | 1.4655 | 1.4232 | 1.3782 | 1.3013 | 1.2151 | 1.0543 | 0.86882 | 0.26855 | -0.5719 | 0.9832 | 0.95207 | 0.90728 | 0.85829 | 0.80377 | 0.75849 | 0.68873 | 0.61825 | 0.53126 | 0.43849 | 0.26294 | 0.058574 | -0.56317 | -1.4133
| PEDDIESTON | ST |  |  |  | 1.2434 | 1.228 | 1.2087 | 1.1602 | 1.1176 | 1.0807 | 1.0168 | 0.96859 | 0.85776 | 0.78564 | 0.62696 | 0.28626 | -0.13895 | -0.56832 | 1.6045 | 1.5967 | 1.5868 | 1.5458 | 1.5123 | 1.485 | 1.425 | 1.3914 | 1.2805 | 1.2214 | 1.0808 | 0.74842 | 0.24906 | -0.2932 | 1.0083 | 0.99572 | 0.97959 | 0.92991 | 0.88804 | 0.85279 | 0.78517 | 0.74051 | 0.61897 | 0.548 | 0.39148 | 0.030129 | -0.46975 | -0.98622
| PEDDIESTON | FS |  |  |  | 1.2497 | 1.2386 | 1.2232 | 1.197 | 1.1697 | 1.1378 | 1.1071 | 1.0709 | 1.0115 | 0.95736 | 0.84422 | 0.60683 | 0.42566 | 0.34312 | 1.6067 | 1.6006 | 1.5923 | 1.5757 | 1.5579 | 1.5376 | 1.5168 | 1.4938 | 1.443 | 1.4002 | 1.3083 | 1.1386 | 0.96294 | 0.80729 | 1.0134 | 1.0043 | 0.99143 | 0.96772 | 0.94316 | 0.91409 | 0.88624 | 0.85379 | 0.79353 | 0.74067 | 0.6307 | 0.41385 | 0.24798 | 0.1625
PETERHEAD GRANGE | PETERHEAD GRANGE 11kV | MINIMUM HEADROOM | NK 11738 46516 | NO | NO | 10.0305 | 9.655 | 9.1648 | 8.1714 | 7.1161 | 5.9844 | 4.1664 | 2.5931 | 1.3875 | 0.20256 | -2.2032 | -3.4972 | -5.8199 | -7.54 | 13.488 | 13.2971 | 13.0079 | 12.4911 | 11.9234 | 11.2668 | 10.0004 | 8.9747 | 8.2066 | 7.4728 | 5.987 | 5.7406 | 4.1009 | 2.2849 | 13.4406 | 13.1038 | 12.6576 | 11.7479 | 10.7783 | 9.714 | 7.9966 | 6.5243 | 5.4155 | 4.3505 | 2.1901 | 1.0108 | -0.97599 | -2.5662
| PETERHEAD GRANGE 11kV | CT |  |  |  | 10.4162 | 10.2355 | 9.9452 | 9.0375 | 8.0698 | 7.1346 | 5.6976 | 4.5683 | 3.3517 | 2.1115 | -0.33386 | -2.9205 | -5.8199 | -7.54 | 13.6248 | 13.505 | 13.2935 | 12.7928 | 12.243 | 11.6821 | 10.6708 | 9.9669 | 9.2487 | 8.5075 | 7.0518 | 5.9133 | 4.1009 | 2.2849 | 13.779 | 13.6134 | 13.3463 | 12.5291 | 11.6587 | 10.7826 | 9.4237 | 8.3829 | 7.2791 | 6.1634 | 3.9659 | 1.6393 | -0.97599 | -2.5662
| PETERHEAD GRANGE 11kV | LW |  |  |  | 10.0305 | 9.655 | 9.1648 | 8.1714 | 7.1161 | 5.9844 | 4.1664 | 2.5931 | 1.3875 | 0.20256 | -2.2032 | -3.4972 | -5.3393 | -6.494 | 13.488 | 13.2971 | 13.0079 | 12.4911 | 11.9234 | 11.2668 | 10.0004 | 8.9747 | 8.2066 | 7.4728 | 5.987 | 5.7406 | 4.6103 | 3.5834 | 13.4406 | 13.1038 | 12.6576 | 11.7479 | 10.7783 | 9.714 | 7.9966 | 6.5243 | 5.4155 | 4.3505 | 2.1901 | 1.0108 | -0.77283 | -2.0052
| PETERHEAD GRANGE 11kV | ST |  |  |  | 10.4957 | 10.4035 | 10.2839 | 10.0126 | 9.7329 | 9.4462 | 8.5579 | 7.9796 | 7.4646 | 7.0132 | 5.9808 | 4.0025 | 1.6506 | -1.2064 | 13.6553 | 13.593 | 13.5089 | 13.2662 | 13.0355 | 12.8127 | 12.0045 | 11.5139 | 11.0718 | 10.6987 | 9.8443 | 8.4264 | 6.6282 | 4.3022 | 13.8492 | 13.7668 | 13.6606 | 13.3855 | 13.1223 | 12.8617 | 11.9941 | 11.456 | 10.9784 | 10.5757 | 9.6582 | 7.8947 | 5.7327 | 3.0151
| PETERHEAD GRANGE 11kV | FS |  |  |  | 10.5262 | 10.455 | 10.3659 | 10.1827 | 9.9738 | 9.7405 | 9.2202 | 8.767 | 8.292 | 7.8472 | 6.8997 | 4.6837 | 1.9091 | -0.19197 | 13.6689 | 13.6178 | 13.5505 | 13.4152 | 13.2598 | 13.0866 | 12.6499 | 12.2705 | 11.9094 | 11.5711 | 10.8302 | 9.1715 | 6.5787 | 3.6037 | 13.8761 | 13.8127 | 13.7339 | 13.5647 | 13.3789 | 13.1715 | 12.6905 | 12.2738 | 11.8435 | 11.444 | 10.5984 | 8.6745 | 6.2118 | 4.2921
PETERHEAD GRANGE | PHEAD NORTH ST | MINIMUM HEADROOM | NK 13470 46450 | NO | NO | 9.5789 | 9.5199 | 9.4357 | 9.2602 | 9.0634 | 8.9036 | 8.73 | 8.5522 | 8.3762 | 8.2065 | 7.7257 | 8.1251 | 7.4399 | 6.777 | 14.2088 | 14.1641 | 14.0295 | 13.8806 | 13.7208 | 13.6009 | 13.4695 | 13.3293 | 13.1786 | 13.0377 | 12.7385 | 13.7198 | 13.1732 | 12.4665 | 12.8865 | 12.8727 | 12.8437 | 12.7622 | 12.4997 | 12.2811 | 12.0436 | 11.7955 | 11.5436 | 11.317 | 10.6429 | 12.0165 | 11.3794 | 10.6233
| PHEAD NORTH ST | CT |  |  |  | 9.6132 | 9.5681 | 9.4459 | 9.2602 | 9.0634 | 8.9036 | 8.73 | 8.5522 | 8.3762 | 8.2065 | 7.86 | 8.2126 | 7.4399 | 6.8581 | 14.2094 | 14.1641 | 14.0295 | 13.8806 | 13.7208 | 13.6009 | 13.4695 | 13.3293 | 13.1786 | 13.0377 | 12.7472 | 13.7429 | 13.1732 | 12.4665 | 12.8872 | 12.8743 | 12.8437 | 12.7622 | 12.4997 | 12.2811 | 12.0436 | 11.7955 | 11.5436 | 11.317 | 10.834 | 12.0755 | 11.452 | 10.8896
| PHEAD NORTH ST | LW |  |  |  | 9.5789 | 9.5199 | 9.4357 | 9.3175 | 9.1905 | 9.0553 | 8.8778 | 8.6782 | 8.4575 | 8.2218 | 7.7257 | 8.1251 | 7.4434 | 6.777 | 14.2088 | 14.1702 | 14.105 | 14.0466 | 13.9764 | 13.8994 | 13.7784 | 13.6327 | 13.4318 | 13.2083 | 12.7385 | 13.7198 | 13.221 | 12.523 | 12.8865 | 12.8727 | 12.8466 | 12.8234 | 12.7278 | 12.5501 | 12.3051 | 12.0253 | 11.7089 | 11.3646 | 10.6429 | 12.0165 | 11.3794 | 10.6233
| PHEAD NORTH ST | ST |  |  |  | 9.6335 | 9.6169 | 9.593 | 9.5572 | 9.5128 | 9.4589 | 9.3879 | 9.3102 | 9.171 | 9.0476 | 8.6941 | 9.0213 | 8.5536 | 7.9373 | 14.2147 | 14.1958 | 14.1715 | 14.1318 | 14.0848 | 14.0288 | 13.9515 | 13.8664 | 13.7033 | 13.5575 | 13.1912 | 13.721 | 13.3221 | 12.6642 | 12.8882 | 12.8818 | 12.8729 | 12.8543 | 12.8342 | 12.813 | 12.7801 | 12.7504 | 12.5803 | 12.3789 | 11.8647 | 12.3232 | 11.943 | 11.5411
| PHEAD NORTH ST | FS |  |  |  | 9.6372 | 9.6262 | 9.6118 | 9.5834 | 9.5521 | 9.5141 | 9.471 | 9.4211 | 9.3441 | 9.2635 | 9.076 | 9.1774 | 8.9412 | 8.7006 | 14.2197 | 14.2065 | 14.1899 | 14.1664 | 14.1378 | 14.1038 | 14.0628 | 14.015 | 13.9379 | 13.8587 | 13.6677 | 13.965 | 13.723 | 12.8549 | 12.8893 | 12.8843 | 12.8773 | 12.867 | 12.8541 | 12.8397 | 12.8227 | 12.8037 | 12.7607 | 12.7224 | 12.4549 | 12.5947 | 12.4898 | 12.3706
FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 5.5422 | 5.4641 | 5.2921 | 5.1164 | 4.7106 | 4.1795 | 3.5526 | 2.9752 | 2.5541 | 2.2062 | 1.7457 | 1.8468 | 1.5045 | 1.306 | 6.8782 | 6.7771 | 6.5983 | 6.4365 | 6.1878 | 5.8969 | 5.5892 | 5.3191 | 5.0936 | 4.8638 | 4.4782 | 4.3987 | 4.0665 | 3.6422 | 6.1098 | 5.9444 | 5.6847 | 5.4063 | 4.9991 | 4.5716 | 4.0633 | 3.5839 | 3.2151 | 2.8957 | 2.4024 | 2.5054 | 2.2157 | 2.024
| PINEGROVE | CT |  |  |  | 5.5471 | 5.4736 | 5.3415 | 5.153 | 4.7988 | 4.2177 | 3.6121 | 3.0538 | 2.6877 | 2.3148 | 1.8054 | 1.8468 | 1.5045 | 1.306 | 6.9042 | 6.8205 | 6.6775 | 6.4725 | 6.1922 | 5.8969 | 5.5892 | 5.3191 | 5.1038 | 4.8783 | 4.497 | 4.3987 | 4.0665 | 3.6422 | 6.1854 | 6.0609 | 5.8577 | 5.5148 | 5.0564 | 4.5716 | 4.0633 | 3.5954 | 3.301 | 2.9701 | 2.4973 | 2.5054 | 2.2157 | 2.024
| PINEGROVE | LW |  |  |  | 5.5422 | 5.4641 | 5.2921 | 5.1164 | 4.7106 | 4.1795 | 3.5526 | 2.9752 | 2.5541 | 2.2062 | 1.7457 | 1.9639 | 1.6966 | 1.4847 | 6.8782 | 6.7771 | 6.5983 | 6.4365 | 6.1878 | 5.9341 | 5.6239 | 5.3336 | 5.0936 | 4.8638 | 4.4782 | 4.6811 | 4.4978 | 4.2986 | 6.1098 | 5.9444 | 5.6847 | 5.4063 | 4.9991 | 4.5722 | 4.0689 | 3.5839 | 3.2151 | 2.8957 | 2.4024 | 2.6373 | 2.387 | 2.1605
| PINEGROVE | ST |  |  |  | 5.5892 | 5.5513 | 5.4595 | 5.3917 | 5.2631 | 5.1333 | 4.9779 | 4.8623 | 4.6335 | 4.3694 | 3.9341 | 3.5034 | 3.3261 | 3.0979 | 6.9362 | 6.8857 | 6.7897 | 6.6942 | 6.549 | 6.4019 | 6.2184 | 6.0687 | 5.8805 | 5.7016 | 5.364 | 4.9069 | 4.5768 | 4.156 | 6.2733 | 6.2044 | 6.0666 | 5.9432 | 5.7428 | 5.5388 | 5.2975 | 5.097 | 4.8499 | 4.6117 | 4.1851 | 3.6986 | 3.4928 | 3.282
| PINEGROVE | FS |  |  |  | 5.5878 | 5.5517 | 5.4699 | 5.4155 | 5.3013 | 5.18 | 5.0496 | 4.9451 | 4.7816 | 4.5801 | 4.2533 | 3.6657 | 3.2329 | 3.0993 | 6.9384 | 6.8913 | 6.8077 | 6.729 | 6.6023 | 6.4676 | 6.3214 | 6.189 | 6.0399 | 5.9009 | 5.6428 | 5.1389 | 4.4997 | 3.8468 | 6.2761 | 6.213 | 6.0989 | 5.9859 | 5.8058 | 5.6167 | 5.4123 | 5.2319 | 5.0385 | 4.8619 | 4.5537 | 4.0002 | 3.5408 | 3.4357
TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 2.8443 | 2.7235 | 2.5789 | 2.3027 | 4.136 | 3.7593 | 3.3501 | 2.991 | 2.7994 | 2.599 | 2.2344 | 2.2142 | 1.942 | 1.7738 | 3.5303 | 3.4993 | 3.4441 | 3.3172 | 5.609 | 5.3289 | 4.9622 | 4.6611 | 4.4751 | 4.2762 | 3.9001 | 3.9604 | 3.7894 | 3.6465 | 2.321 | 2.202 | 2.0482 | 1.7583 | 3.8837 | 3.4741 | 3.0049 | 2.5951 | 2.3483 | 2.0873 | 1.6009 | 1.5861 | 1.3212 | 1.1439
| PITLOCHRY | CT |  |  |  | 2.9361 | 2.8585 | 2.7578 | 2.5154 | 4.3826 | 4.0556 | 3.712 | 3.4464 | 3.2597 | 3.0662 | 2.7091 | 2.6321 | 2.2271 | 2.016 | 3.5331 | 3.5013 | 3.4441 | 3.3588 | 5.7059 | 5.5241 | 5.2823 | 5.1146 | 4.9619 | 4.7801 | 4.436 | 4.3815 | 4.1334 | 3.9101 | 2.4066 | 2.3262 | 2.2155 | 1.9606 | 4.1207 | 3.7734 | 3.4081 | 3.1385 | 2.9197 | 2.6721 | 2.2101 | 2.0822 | 1.7049 | 1.4948
| PITLOCHRY | LW |  |  |  | 2.8443 | 2.7235 | 2.5789 | 2.3027 | 4.136 | 3.7593 | 3.3501 | 2.991 | 2.7994 | 2.599 | 2.2344 | 2.2142 | 1.942 | 1.7738 | 3.5303 | 3.4993 | 3.449 | 3.3172 | 5.609 | 5.3289 | 4.9622 | 4.6611 | 4.4751 | 4.2762 | 3.9001 | 3.9604 | 3.7894 | 3.6465 | 2.321 | 2.202 | 2.0482 | 1.7583 | 3.8837 | 3.4741 | 3.0049 | 2.5951 | 2.3483 | 2.0873 | 1.6009 | 1.5861 | 1.3212 | 1.1439
| PITLOCHRY | ST |  |  |  | 2.9676 | 2.9552 | 2.9312 | 2.7921 | 4.7996 | 4.6951 | 4.4909 | 4.3732 | 4.2612 | 4.1504 | 3.9122 | 3.6921 | 3.3233 | 2.9253 | 3.5525 | 3.538 | 3.5181 | 3.385 | 5.7214 | 5.6367 | 5.4275 | 5.3289 | 5.2465 | 5.1636 | 4.9686 | 4.6839 | 4.4099 | 4.1293 | 2.4645 | 2.4312 | 2.3828 | 2.2157 | 4.5117 | 4.3868 | 4.1344 | 3.9887 | 3.8516 | 3.7108 | 3.3971 | 2.9896 | 2.6265 | 2.2761
| PITLOCHRY | FS |  |  |  | 2.9704 | 2.9619 | 2.9467 | 2.8878 | 4.9365 | 4.8539 | 4.7684 | 4.6784 | 4.5848 | 4.4887 | 4.2968 | 3.8934 | 3.4872 | 3.1814 | 3.5556 | 3.5445 | 3.5295 | 3.488 | 5.8833 | 5.8318 | 5.777 | 5.7214 | 5.6757 | 5.6271 | 5.5202 | 5.1683 | 4.7212 | 4.4126 | 2.4734 | 2.4478 | 2.4139 | 2.3296 | 4.6803 | 4.5856 | 4.4855 | 4.3795 | 4.2716 | 4.1585 | 3.9214 | 3.4013 | 2.8844 | 2.6241
ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | NO | 2.5135 | 2.4085 | 2.315 | 2.2101 | 2.0792 | 1.9603 | 1.8375 | 1.6957 | 1.5644 | 1.2831 | 0.86559 | 0.84917 | 0.77471 | 0.72984 | 3.01 | 2.9304 | 2.9005 | 2.8734 | 2.8376 | 2.7714 | 2.6957 | 2.6002 | 2.496 | 2.2478 | 1.8923 | 1.8736 | 1.7979 | 1.7271 | 2.0138 | 1.941 | 1.9067 | 1.834 | 1.7158 | 1.6058 | 1.493 | 1.3625 | 1.2435 | 0.97688 | 0.587 | 0.54943 | 0.47763 | 0.43627
| POLLACHAR | CT |  |  |  | 2.5425 | 2.4576 | 2.3843 | 2.2335 | 2.0792 | 1.9603 | 1.8375 | 1.7174 | 1.6215 | 1.3429 | 0.94206 | 0.87067 | 0.77471 | 0.72984 | 3.0179 | 2.9437 | 2.9126 | 2.8734 | 2.8376 | 2.7714 | 2.6957 | 2.6228 | 2.5443 | 2.2979 | 1.9503 | 1.8736 | 1.7979 | 1.7271 | 2.0185 | 1.9483 | 1.9125 | 1.8582 | 1.7158 | 1.6058 | 1.493 | 1.3833 | 1.2967 | 1.0318 | 0.65547 | 0.56692 | 0.47763 | 0.43627
| POLLACHAR | LW |  |  |  | 2.5135 | 2.4085 | 2.315 | 2.2101 | 2.0917 | 1.9961 | 1.8559 | 1.6957 | 1.5644 | 1.2831 | 0.86559 | 0.84917 | 0.79133 | 0.78078 | 3.01 | 2.9304 | 2.9005 | 2.8766 | 2.8464 | 2.8037 | 2.7093 | 2.6002 | 2.496 | 2.2478 | 1.8923 | 1.8895 | 1.8525 | 1.8478 | 2.0138 | 1.941 | 1.9067 | 1.834 | 1.7247 | 1.6367 | 1.5086 | 1.3625 | 1.2435 | 0.97688 | 0.587 | 0.54943 | 0.49501 | 0.4853
| POLLACHAR | ST |  |  |  | 2.5616 | 2.5007 | 2.466 | 2.4235 | 2.3732 | 2.3212 | 2.2656 | 2.1983 | 2.1153 | 1.8787 | 1.5049 | 1.0831 | 0.98014 | 0.94086 | 3.0211 | 2.9585 | 2.9418 | 2.9226 | 2.9019 | 2.8798 | 2.8562 | 2.8317 | 2.8015 | 2.588 | 2.3082 | 1.9824 | 1.8877 | 1.8269 | 2.0246 | 1.9699 | 1.9533 | 1.9349 | 1.9133 | 1.8905 | 1.8652 | 1.8277 | 1.7537 | 1.5291 | 1.1816 | 0.77231 | 0.67799 | 0.64199
| POLLACHAR | FS |  |  |  | 2.5766 | 2.529 | 2.5041 | 2.4623 | 2.4184 | 2.3756 | 2.3277 | 2.275 | 2.2117 | 2.0612 | 1.7971 | 1.312 | 0.92111 | 0.87464 | 3.0362 | 2.9893 | 2.9761 | 2.9593 | 2.9425 | 2.9274 | 2.9101 | 2.8903 | 2.8678 | 2.74 | 2.5454 | 2.1864 | 1.856 | 1.7581 | 2.0374 | 1.9965 | 1.9839 | 1.9681 | 1.9515 | 1.9372 | 1.9197 | 1.8993 | 1.8424 | 1.699 | 1.4502 | 0.98387 | 0.62076 | 0.57873
FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0.10241 | 0.1024 | 0.10238 | 0.10237 | 0.10236 | 0.10233 | 0.1023 | 0.10226 | 0.10221 | 0.10217 | 0.10208 | 0.10197 | 0.10186 | 0.10177 | 0.10685 | 0.10679 | 0.10673 | 0.10668 | 0.10662 | 0.10656 | 0.10649 | 0.10641 | 0.10634 | 0.10625 | 0.10606 | 0.10539 | 0.10397 | 0.10131 | 0.10503 | 0.10502 | 0.10499 | 0.10497 | 0.10494 | 0.10492 | 0.10489 | 0.10485 | 0.10481 | 0.10476 | 0.10467 | 0.10458 | 0.10448 | 0.10441
| POOR HOUSE | CT |  |  |  | 0.10241 | 0.1024 | 0.10239 | 0.10238 | 0.10236 | 0.10233 | 0.10231 | 0.10229 | 0.10225 | 0.1022 | 0.10211 | 0.10202 | 0.10192 | 0.10183 | 0.10685 | 0.1068 | 0.10674 | 0.10669 | 0.10662 | 0.10656 | 0.10649 | 0.10641 | 0.10634 | 0.10625 | 0.10606 | 0.10542 | 0.10432 | 0.10241 | 0.10504 | 0.10502 | 0.105 | 0.10497 | 0.10494 | 0.10492 | 0.1049 | 0.10487 | 0.10484 | 0.10479 | 0.10471 | 0.10462 | 0.10454 | 0.10446
| POOR HOUSE | LW |  |  |  | 0.10241 | 0.1024 | 0.10238 | 0.10237 | 0.10236 | 0.10234 | 0.1023 | 0.10226 | 0.10221 | 0.10217 | 0.10208 | 0.10197 | 0.10186 | 0.10177 | 0.10688 | 0.10687 | 0.10685 | 0.10684 | 0.10682 | 0.10681 | 0.10678 | 0.10676 | 0.10673 | 0.1067 | 0.10664 | 0.10657 | 0.1065 | 0.10645 | 0.10503 | 0.10502 | 0.10499 | 0.10497 | 0.10494 | 0.10492 | 0.10489 | 0.10485 | 0.10481 | 0.10476 | 0.10467 | 0.10458 | 0.10448 | 0.10441
| POOR HOUSE | ST |  |  |  | 0.10241 | 0.1024 | 0.10239 | 0.10238 | 0.10238 | 0.10237 | 0.10236 | 0.10234 | 0.10231 | 0.10228 | 0.10222 | 0.10204 | 0.10193 | 0.10185 | 0.10685 | 0.1068 | 0.10675 | 0.10671 | 0.10665 | 0.10659 | 0.10653 | 0.10645 | 0.10638 | 0.1063 | 0.10612 | 0.10543 | 0.10432 | 0.10242 | 0.10504 | 0.10502 | 0.10501 | 0.105 | 0.10498 | 0.10497 | 0.10495 | 0.10493 | 0.1049 | 0.10487 | 0.10481 | 0.10464 | 0.10455 | 0.10448
| POOR HOUSE | FS |  |  |  | 0.10241 | 0.1024 | 0.10239 | 0.10239 | 0.10238 | 0.10237 | 0.10236 | 0.10235 | 0.10233 | 0.10231 | 0.10227 | 0.10213 | 0.10198 | 0.10191 | 0.10685 | 0.10679 | 0.10673 | 0.10668 | 0.10663 | 0.10658 | 0.10651 | 0.10643 | 0.10637 | 0.10629 | 0.10611 | 0.10539 | 0.10397 | 0.10131 | 0.10504 | 0.10503 | 0.10501 | 0.105 | 0.10499 | 0.10498 | 0.10496 | 0.10494 | 0.10492 | 0.1049 | 0.10486 | 0.10473 | 0.10458 | 0.10453
PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | NO | 1.7084 | 1.6818 | 1.6407 | 1.5868 | 1.5374 | 1.4904 | 1.4373 | 1.385 | 1.3079 | 1.24 | 1.0529 | 1.1453 | 0.75969 | 0.24049 | 1.752 | 1.7363 | 1.7132 | 1.6868 | 1.6502 | 1.6228 | 1.5931 | 1.5623 | 1.4877 | 1.4076 | 1.2559 | 1.1306 | 0.66898 | 0.024942 | 1.7955 | 1.7674 | 1.7363 | 1.6992 | 1.6534 | 1.6076 | 1.5576 | 1.5125 | 1.4413 | 1.3499 | 1.1726 | 1.0603 | 0.58687 | -0.060125
| PORT ASKAIG | CT |  |  |  | 1.7127 | 1.6818 | 1.6407 | 1.5868 | 1.5374 | 1.4904 | 1.4373 | 1.385 | 1.3079 | 1.24 | 1.0961 | 1.2167 | 1.0006 | 0.77837 | 1.7559 | 1.7434 | 1.7222 | 1.6868 | 1.6502 | 1.6228 | 1.5931 | 1.5649 | 1.5053 | 1.4368 | 1.3076 | 1.2021 | 0.96438 | 0.6916 | 1.8065 | 1.7886 | 1.7591 | 1.7052 | 1.6534 | 1.6076 | 1.5576 | 1.5125 | 1.4488 | 1.3806 | 1.2317 | 1.144 | 0.88961 | 0.61774
| PORT ASKAIG | LW |  |  |  | 1.7084 | 1.6818 | 1.6465 | 1.6147 | 1.5801 | 1.5459 | 1.4905 | 1.4256 | 1.3377 | 1.2415 | 1.0529 | 1.1453 | 0.75969 | 0.24049 | 1.752 | 1.7363 | 1.7132 | 1.6907 | 1.6657 | 1.6443 | 1.6064 | 1.5623 | 1.4877 | 1.4076 | 1.2559 | 1.1306 | 0.66898 | 0.024942 | 1.7955 | 1.7674 | 1.7363 | 1.6992 | 1.6611 | 1.6266 | 1.5746 | 1.5155 | 1.4413 | 1.3499 | 1.1726 | 1.0603 | 0.58687 | -0.060125
| PORT ASKAIG | ST |  |  |  | 1.721 | 1.7099 | 1.6962 | 1.6776 | 1.6556 | 1.6298 | 1.598 | 1.5585 | 1.4673 | 1.3945 | 1.2195 | 1.2769 | 0.97148 | 0.65865 | 1.76 | 1.7543 | 1.7467 | 1.736 | 1.7229 | 1.7091 | 1.6923 | 1.671 | 1.5899 | 1.5394 | 1.4207 | 1.2199 | 0.85977 | 0.47709 | 1.8184 | 1.8099 | 1.7986 | 1.7818 | 1.764 | 1.7474 | 1.7276 | 1.701 | 1.6076 | 1.5333 | 1.3553 | 1.1966 | 0.82461 | 0.44021
| PORT ASKAIG | FS |  |  |  | 1.7244 | 1.7156 | 1.7061 | 1.6916 | 1.6756 | 1.6561 | 1.634 | 1.6081 | 1.5623 | 1.5188 | 1.4158 | 1.4678 | 1.3217 | 1.2683 | 1.7621 | 1.7569 | 1.7514 | 1.7426 | 1.7328 | 1.7214 | 1.7089 | 1.694 | 1.656 | 1.6236 | 1.5481 | 1.4432 | 1.3225 | 1.2616 | 1.824 | 1.8152 | 1.8085 | 1.7938 | 1.7804 | 1.763 | 1.7468 | 1.727 | 1.6822 | 1.6474 | 1.5578 | 1.4201 | 1.2733 | 1.2138
PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | NO | 1.7717 | 1.7351 | 1.6958 | 1.637 | 1.5702 | 1.5036 | 1.4296 | 1.3442 | 1.2512 | 1.1536 | 0.96672 | 1.0036 | 0.61205 | 0.090868 | 2.4281 | 2.3945 | 2.3552 | 2.3159 | 2.268 | 2.2257 | 2.1804 | 2.1257 | 2.0402 | 1.9496 | 1.7773 | 1.7597 | 1.2918 | 0.64587 | 2.0845 | 2.0497 | 2.0076 | 1.9579 | 1.8957 | 1.8391 | 1.7783 | 1.7063 | 1.6159 | 1.5212 | 1.3417 | 1.3072 | 0.82377 | 0.17376
| PORT ELLEN | CT |  |  |  | 1.7826 | 1.744 | 1.7034 | 1.6472 | 1.573 | 1.5036 | 1.4296 | 1.3546 | 1.2864 | 1.2097 | 1.0647 | 1.0731 | 0.84076 | 0.61516 | 2.4378 | 2.4082 | 2.3772 | 2.3238 | 2.268 | 2.2257 | 2.1804 | 2.134 | 2.0703 | 1.9996 | 1.864 | 1.825 | 1.5656 | 1.2718 | 2.094 | 2.0589 | 2.0211 | 1.9579 | 1.8957 | 1.8391 | 1.7783 | 1.7153 | 1.6483 | 1.5762 | 1.4355 | 1.3906 | 1.1169 | 0.83799
| PORT ELLEN | LW |  |  |  | 1.7717 | 1.7351 | 1.6958 | 1.637 | 1.5702 | 1.5116 | 1.4333 | 1.3442 | 1.2512 | 1.1536 | 0.96672 | 1.0036 | 0.61205 | 0.090868 | 2.4281 | 2.3945 | 2.3552 | 2.3159 | 2.2749 | 2.239 | 2.1865 | 2.1257 | 2.0402 | 1.9496 | 1.7773 | 1.7597 | 1.2918 | 0.64587 | 2.0845 | 2.0497 | 2.0076 | 1.962 | 1.9097 | 1.856 | 1.7858 | 1.7063 | 1.6159 | 1.5212 | 1.3417 | 1.3072 | 0.82377 | 0.17376
| PORT ELLEN | ST |  |  |  | 1.7891 | 1.7689 | 1.7486 | 1.7289 | 1.7078 | 1.6851 | 1.6578 | 1.6274 | 1.5475 | 1.491 | 1.3481 | 1.1763 | 0.86038 | 0.53935 | 2.4434 | 2.4254 | 2.407 | 2.3894 | 2.3708 | 2.3514 | 2.3279 | 2.3021 | 2.2155 | 2.161 | 2.0341 | 1.8658 | 1.4891 | 1.0814 | 2.1 | 2.0822 | 2.064 | 2.046 | 2.0266 | 2.0033 | 1.9743 | 1.9429 | 1.8497 | 1.7882 | 1.6438 | 1.4767 | 1.0905 | 0.69153
| PORT ELLEN | FS |  |  |  | 1.794 | 1.7766 | 1.7615 | 1.7443 | 1.7253 | 1.7055 | 1.6856 | 1.6621 | 1.6212 | 1.5828 | 1.481 | 1.3388 | 1.1922 | 1.1346 | 2.4473 | 2.4312 | 2.4166 | 2.4013 | 2.3837 | 2.3664 | 2.3486 | 2.3273 | 2.2845 | 2.2449 | 2.1578 | 2.0599 | 1.9218 | 1.8125 | 2.1044 | 2.0892 | 2.0758 | 2.0602 | 2.0429 | 2.0247 | 2.004 | 1.9782 | 1.9313 | 1.888 | 1.792 | 1.6655 | 1.5277 | 1.4621
DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | NO | 2.7699 | 2.3599 | 1.8204 | 1.5274 | 1.225 | 0.90351 | 0.59704 | 0.035579 | -0.10204 | -0.26778 | -0.56822 | -0.56979 | -0.96863 | -1.1704 | 4.3017 | 3.9897 | 3.5785 | 3.4195 | 3.2562 | 3.0659 | 2.8641 | 2.5931 | 2.4868 | 2.3468 | 2.0845 | 1.9701 | 1.6836 | 1.4153 | 3.92 | 3.6085 | 3.1278 | 2.8988 | 2.6633 | 2.3796 | 2.0615 | 1.5828 | 1.4505 | 1.2906 | 0.99293 | 0.91799 | 0.55579 | 0.34796
| PORTREE | CT |  |  |  | 2.8616 | 2.5284 | 2.0772 | 1.7175 | 1.3421 | 0.94855 | 0.59704 | 0.035579 | -0.10204 | -0.26778 | -0.56822 | -0.56979 | -0.96863 | -1.1704 | 4.337 | 4.0707 | 3.7196 | 3.5134 | 3.295 | 3.0659 | 2.8641 | 2.5931 | 2.4868 | 2.3468 | 2.0845 | 1.9701 | 1.6836 | 1.4153 | 3.9207 | 3.6542 | 3.3138 | 3.0263 | 2.7223 | 2.3881 | 2.0615 | 1.5828 | 1.4505 | 1.2906 | 0.99293 | 0.91799 | 0.55579 | 0.34796
| PORTREE | LW |  |  |  | 2.7699 | 2.3599 | 1.8204 | 1.5274 | 1.225 | 0.90351 | 0.62051 | 0.082492 | -0.053457 | -0.19738 | -0.46825 | -0.45339 | -0.75877 | -1.0174 | 4.3017 | 3.9897 | 3.5785 | 3.4195 | 3.2562 | 3.083 | 2.9337 | 2.6693 | 2.5553 | 2.4318 | 2.1966 | 2.2079 | 1.9695 | 1.6969 | 3.92 | 3.6085 | 3.1278 | 2.8988 | 2.6633 | 2.3796 | 2.1202 | 1.6632 | 1.5309 | 1.3905 | 1.1021 | 1.0758 | 0.76706 | 0.47246
| PORTREE | ST |  |  |  | 2.9342 | 2.6567 | 2.2683 | 2.098 | 1.9322 | 1.7768 | 1.6202 | 1.3898 | 1.2285 | 1.0673 | 0.72316 | 0.22212 | -0.11785 | -0.40818 | 4.3654 | 4.1284 | 3.8164 | 3.6862 | 3.5617 | 3.4479 | 3.3116 | 3.1479 | 3.0234 | 2.9113 | 2.6613 | 2.2343 | 1.9169 | 1.5951 | 3.9289 | 3.6844 | 3.3724 | 3.2637 | 3.1621 | 3.0502 | 2.8812 | 2.6886 | 2.5336 | 2.3901 | 2.0719 | 1.527 | 1.1729 | 0.88828
| PORTREE | FS |  |  |  | 2.9629 | 2.7503 | 2.4565 | 2.3207 | 2.1738 | 2.0272 | 1.919 | 1.7197 | 1.5948 | 1.4487 | 1.1425 | 0.41129 | -0.032095 | -0.18407 | 4.377 | 4.1942 | 3.9538 | 3.8623 | 3.7593 | 3.6574 | 3.5816 | 3.4437 | 3.3489 | 3.25 | 3.0347 | 2.5465 | 2.1306 | 1.8307 | 3.9331 | 3.7455 | 3.5024 | 3.4331 | 3.3529 | 3.2743 | 3.2012 | 3.044 | 2.9208 | 2.7943 | 2.5283 | 1.8687 | 1.389 | 1.2632
MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | NO | 3.0782 | 3.013 | 2.9367 | 2.8028 | 2.6623 | 2.5236 | 2.3631 | 2.1943 | 2.0619 | 1.9244 | 1.6501 | 1.2991 | 0.93276 | 0.71938 | 3.1895 | 3.1585 | 3.1166 | 3.0556 | 2.9898 | 2.9106 | 2.8071 | 2.7326 | 2.6419 | 2.5393 | 2.3371 | 2.1024 | 1.858 | 1.6349 | 3.4052 | 3.3695 | 3.3155 | 3.2357 | 3.1473 | 3.0226 | 2.8738 | 2.716 | 2.58 | 2.4342 | 2.1399 | 1.7497 | 1.4241 | 1.2161
| PORTSOY | CT |  |  |  | 3.1387 | 3.1047 | 3.0586 | 2.9184 | 2.7764 | 2.6165 | 2.4526 | 2.3107 | 2.1633 | 2.0046 | 1.6856 | 1.2991 | 0.93276 | 0.71938 | 3.2123 | 3.1926 | 3.1631 | 3.0886 | 3.01 | 2.9106 | 2.8071 | 2.7326 | 2.6419 | 2.5393 | 2.3371 | 2.1024 | 1.858 | 1.6349 | 3.4062 | 3.3875 | 3.3592 | 3.2761 | 3.1863 | 3.067 | 2.9125 | 2.7843 | 2.6376 | 2.4699 | 2.1399 | 1.7497 | 1.4241 | 1.2161
| PORTSOY | LW |  |  |  | 3.0782 | 3.013 | 2.9367 | 2.8028 | 2.6623 | 2.5236 | 2.3631 | 2.1943 | 2.0619 | 1.9244 | 1.6501 | 1.4342 | 1.1328 | 0.89303 | 3.1895 | 3.1585 | 3.1166 | 3.0556 | 2.9898 | 2.927 | 2.8456 | 2.7576 | 2.6742 | 2.5868 | 2.4147 | 2.3171 | 2.0897 | 1.8361 | 3.4052 | 3.3695 | 3.3155 | 3.2357 | 3.1473 | 3.0226 | 2.8738 | 2.716 | 2.58 | 2.4342 | 2.1464 | 1.9262 | 1.6315 | 1.3599
| PORTSOY | ST |  |  |  | 3.1641 | 3.1494 | 3.128 | 3.0745 | 3.0276 | 2.9792 | 2.9034 | 2.8499 | 2.7727 | 2.7105 | 2.5661 | 2.2272 | 1.8543 | 1.4434 | 3.2218 | 3.2128 | 3.2 | 3.1499 | 3.1078 | 3.0696 | 2.9934 | 2.9497 | 2.8767 | 2.8239 | 2.7002 | 2.4237 | 2.141 | 1.8234 | 3.4091 | 3.4026 | 3.3941 | 3.3489 | 3.3115 | 3.2789 | 3.2048 | 3.1531 | 3.0726 | 3.0106 | 2.8638 | 2.4691 | 2.115 | 1.7503
| PORTSOY | FS |  |  |  | 3.1726 | 3.1589 | 3.1428 | 3.1111 | 3.0746 | 3.0397 | 3.0004 | 2.9604 | 2.8965 | 2.8341 | 2.7075 | 2.3766 | 2.0323 | 1.7679 | 3.2252 | 3.217 | 3.2068 | 3.1845 | 3.159 | 3.1326 | 3.1032 | 3.073 | 3.0258 | 2.9806 | 2.8829 | 2.6531 | 2.3688 | 2.0867 | 3.4102 | 3.405 | 3.3981 | 3.3823 | 3.3644 | 3.3439 | 3.321 | 3.2879 | 3.2363 | 3.1861 | 3.0795 | 2.7335 | 2.3721 | 2.1615
WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 1.8788 | 1.4621 | 0.76404 | -0.2438 | -1.3613 | -2.6236 | -4.395 | -6.2766 | -7.9825 | -9.8522 | -13.6611 | -5.4963 | -6.3824 | -7.1847 | 5.2332 | 4.9461 | 4.4338 | 3.7407 | 2.9537 | 1.9862 | 0.60805 | -0.80485 | -2.1057 | -3.5382 | -6.4471 | -0.40333 | -2.5923 | -8.3707 | 3.6635 | 3.2646 | 2.5867 | 1.602 | 0.50459 | -0.77293 | -2.5583 | -4.4215 | -6.1013 | -7.944 | -11.6912 | -3.5668 | -4.4989 | -5.4178
| QUEENS LANE NORTH | CT |  |  |  | 2.0261 | 1.7013 | 1.2517 | 0.19797 | -0.95929 | -2.051 | -3.241 | -4.3161 | -5.5357 | -6.7693 | -9.4452 | -4.8482 | -6.1712 | -7.0119 | 5.2378 | 4.9487 | 4.5522 | 3.8023 | 2.9559 | 2.0987 | 1.1518 | 0.34728 | -0.59887 | -1.5667 | -3.6995 | -0.40333 | -2.5923 | -5.8082 | 3.7891 | 3.4717 | 3.0304 | 2.0219 | 0.90598 | -0.1767 | -1.3588 | -2.3945 | -3.5776 | -4.7753 | -7.3773 | -2.713 | -3.9441 | -4.766
| QUEENS LANE NORTH | LW |  |  |  | 1.8788 | 1.4621 | 0.76404 | -0.2438 | -1.3613 | -2.6236 | -4.395 | -6.2766 | -7.9825 | -9.8522 | -13.6611 | -5.4963 | -6.3824 | -7.1847 | 5.2332 | 4.9461 | 4.4338 | 3.7407 | 2.9537 | 1.9862 | 0.60805 | -0.80485 | -2.1057 | -3.5382 | -6.4471 | 0.28734 | -0.45335 | -1.3 | 3.6635 | 3.2646 | 2.5867 | 1.602 | 0.50459 | -0.77293 | -2.5583 | -4.4215 | -6.1013 | -7.944 | -11.6912 | -3.5668 | -4.4989 | -5.4178
| QUEENS LANE NORTH | ST |  |  |  | 2.1459 | 2.0226 | 1.8483 | 1.4886 | 1.1108 | 0.68502 | 0.0087878 | -0.62413 | -1.358 | -2.2044 | -4.279 | -1.2081 | -2.5289 | -4.0138 | 5.3078 | 5.164 | 4.9743 | 4.5702 | 4.164 | 3.7304 | 3.0179 | 2.4064 | 1.7164 | 0.94417 | -0.93649 | 0.80061 | -1.5171 | -4.9808 | 3.901 | 3.7784 | 3.6056 | 3.2117 | 2.8112 | 2.3728 | 1.6456 | 1.0033 | 0.26276 | -0.57923 | -2.6404 | 0.41785 | -0.86678 | -2.2894
| QUEENS LANE NORTH | FS |  |  |  | 2.1474 | 2.042 | 1.9005 | 1.6782 | 1.4077 | 1.0895 | 0.71775 | 0.27713 | -0.22883 | -0.80049 | -2.1501 | -0.50001 | -2.2116 | -3.5214 | 5.3101 | 5.1742 | 5.0015 | 4.7598 | 4.4719 | 4.1353 | 3.7412 | 3.2868 | 2.7837 | 2.2158 | 0.85839 | 1.1059 | -2.4651 | -8.3707 | 3.9038 | 3.7999 | 3.6599 | 3.4353 | 3.163 | 2.8422 | 2.4679 | 2.0277 | 1.5284 | 0.966 | -0.36224 | 1.3249 | -0.2603 | -1.4229
QUOICH | QUOICH PRIMARY | MINIMUM HEADROOM | NH 11700 01900 | YES | NO | 0.89021 | 0.88314 | 0.87739 | 0.87485 | 0.8686 | 0.85963 | 0.85454 | 0.84615 | 0.84341 | 0.83699 | 0.83304 | 0.83836 | 0.8344 | 0.83021 | 0.92805 | 0.92358 | 0.92046 | 0.91908 | 0.91603 | 0.91138 | 0.90891 | 0.90517 | 0.90316 | 0.89905 | 0.8938 | 0.89811 | 0.89662 | 0.8949 | 0.90962 | 0.90261 | 0.89628 | 0.89384 | 0.88758 | 0.87936 | 0.87475 | 0.8672 | 0.86457 | 0.8586 | 0.85425 | 0.85949 | 0.85599 | 0.85226
| QUOICH PRIMARY | CT |  |  |  | 0.89131 | 0.88518 | 0.88104 | 0.87604 | 0.87104 | 0.85963 | 0.85454 | 0.84762 | 0.84341 | 0.83699 | 0.83428 | 0.8406 | 0.8344 | 0.83021 | 0.92849 | 0.92431 | 0.92199 | 0.9192 | 0.91632 | 0.91138 | 0.90891 | 0.90577 | 0.9032 | 0.8994 | 0.89512 | 0.89911 | 0.89662 | 0.8949 | 0.91066 | 0.90453 | 0.90049 | 0.89522 | 0.89004 | 0.87936 | 0.87475 | 0.86852 | 0.86457 | 0.8586 | 0.85553 | 0.86151 | 0.85599 | 0.85226
| QUOICH PRIMARY | LW |  |  |  | 0.89021 | 0.88314 | 0.87739 | 0.87485 | 0.8686 | 0.8619 | 0.85587 | 0.84615 | 0.84485 | 0.83808 | 0.83304 | 0.83836 | 0.83442 | 0.83595 | 0.92805 | 0.92358 | 0.92046 | 0.91908 | 0.91603 | 0.91312 | 0.90993 | 0.90517 | 0.90316 | 0.89905 | 0.8938 | 0.89811 | 0.89662 | 0.89712 | 0.90962 | 0.90261 | 0.89628 | 0.89384 | 0.88758 | 0.88158 | 0.87603 | 0.8672 | 0.86571 | 0.8594 | 0.85425 | 0.85949 | 0.85601 | 0.85735
| QUOICH PRIMARY | ST |  |  |  | 0.89341 | 0.89127 | 0.88807 | 0.88352 | 0.88267 | 0.88036 | 0.87919 | 0.87777 | 0.86909 | 0.86528 | 0.86053 | 0.84339 | 0.83485 | 0.83078 | 0.9303 | 0.929 | 0.9273 | 0.9249 | 0.92441 | 0.92313 | 0.92243 | 0.92152 | 0.91701 | 0.91476 | 0.91062 | 0.90117 | 0.89733 | 0.8959 | 0.91274 | 0.91071 | 0.9076 | 0.90302 | 0.90227 | 0.8998 | 0.89875 | 0.89748 | 0.88815 | 0.88459 | 0.87996 | 0.8644 | 0.8565 | 0.85293
| QUOICH PRIMARY | FS |  |  |  | 0.89375 | 0.89335 | 0.89024 | 0.88838 | 0.88637 | 0.88567 | 0.88484 | 0.88128 | 0.87872 | 0.87322 | 0.8671 | 0.84789 | 0.83637 | 0.83117 | 0.93059 | 0.93031 | 0.92866 | 0.92765 | 0.92656 | 0.92615 | 0.92566 | 0.92376 | 0.92233 | 0.9193 | 0.91548 | 0.90555 | 0.89788 | 0.89608 | 0.91307 | 0.91268 | 0.90975 | 0.90794 | 0.90597 | 0.90529 | 0.90447 | 0.90106 | 0.89848 | 0.89238 | 0.8862 | 0.8687 | 0.85784 | 0.85328
FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 0.97527 | 0.97495 | 0.97398 | 0.96975 | 0.96721 | 0.9663 | 0.96315 | 0.95737 | 0.9548 | 0.9509 | 0.94358 | 0.95813 | 0.95596 | 0.95579 | 0.98234 | 0.98208 | 0.98144 | 0.97966 | 0.97828 | 0.9777 | 0.97585 | 0.97295 | 0.96998 | 0.96691 | 0.96089 | 0.97223 | 0.97139 | 0.97126 | 0.97926 | 0.97851 | 0.97663 | 0.97363 | 0.97069 | 0.96876 | 0.96578 | 0.96114 | 0.95789 | 0.95413 | 0.94704 | 0.96294 | 0.96102 | 0.96086
| RAHOY | CT |  |  |  | 0.97535 | 0.97579 | 0.97442 | 0.97171 | 0.96721 | 0.9663 | 0.96363 | 0.95737 | 0.95655 | 0.95341 | 0.94798 | 0.95871 | 0.95636 | 0.95579 | 0.98248 | 0.98274 | 0.98166 | 0.98029 | 0.97828 | 0.9777 | 0.97599 | 0.97332 | 0.97161 | 0.96965 | 0.96557 | 0.97252 | 0.97156 | 0.97126 | 0.97952 | 0.9786 | 0.97684 | 0.97406 | 0.97069 | 0.96876 | 0.96619 | 0.96114 | 0.95963 | 0.95674 | 0.95152 | 0.96347 | 0.96138 | 0.96086
| RAHOY | LW |  |  |  | 0.97527 | 0.97495 | 0.97398 | 0.96975 | 0.96913 | 0.96641 | 0.96315 | 0.95887 | 0.9548 | 0.9509 | 0.94358 | 0.95813 | 0.95596 | 0.95767 | 0.98234 | 0.98208 | 0.98144 | 0.97966 | 0.97916 | 0.97793 | 0.97585 | 0.97295 | 0.96998 | 0.96691 | 0.96089 | 0.97223 | 0.97139 | 0.97202 | 0.97926 | 0.97851 | 0.97663 | 0.97363 | 0.97224 | 0.9693 | 0.96578 | 0.96176 | 0.95789 | 0.95413 | 0.94704 | 0.96294 | 0.96102 | 0.96252
| RAHOY | ST |  |  |  | 0.97629 | 0.97614 | 0.97595 | 0.97657 | 0.976 | 0.97486 | 0.97368 | 0.97089 | 0.96939 | 0.96634 | 0.96088 | 0.96407 | 0.96274 | 0.96543 | 0.98301 | 0.9829 | 0.98275 | 0.983 | 0.98272 | 0.98229 | 0.98144 | 0.97974 | 0.97833 | 0.97638 | 0.97193 | 0.97453 | 0.97381 | 0.97469 | 0.97974 | 0.97941 | 0.97899 | 0.97846 | 0.97774 | 0.97666 | 0.97553 | 0.97283 | 0.97124 | 0.96846 | 0.96316 | 0.96822 | 0.967 | 0.96919
| RAHOY | FS |  |  |  | 0.9763 | 0.97618 | 0.97603 | 0.9761 | 0.9743 | 0.97541 | 0.97461 | 0.9729 | 0.97117 | 0.96979 | 0.96708 | 0.96448 | 0.96141 | 0.96137 | 0.98302 | 0.98293 | 0.98281 | 0.98254 | 0.9817 | 0.98199 | 0.98172 | 0.98077 | 0.98019 | 0.97916 | 0.97676 | 0.97574 | 0.97337 | 0.97334 | 0.97978 | 0.97951 | 0.97918 | 0.97858 | 0.97747 | 0.977 | 0.97622 | 0.97471 | 0.97315 | 0.97182 | 0.96912 | 0.96885 | 0.96583 | 0.9658
INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 1.7221 | -4.7303 | -15.2338 | -16.1692 | -17.1738 | -18.382 | -19.8707 | -21.4278 | -22.934 | -24.5455 | -27.814 | -22.822 | -24.0289 | -24.9709 | 4.3421 | -3.5534 | -16.4354 | -17.4205 | -18.4896 | -19.8571 | -21.4092 | -22.9063 | -24.1383 | -25.4718 | -28.1628 | -23.4603 | -24.4906 | -25.5307 | 1.6607 | -6.2666 | -19.2302 | -20.2579 | -21.3807 | -22.8078 | -24.5565 | -26.3445 | -27.8485 | -29.4754 | -32.7701 | -25.95 | -27.2548 | -28.3719
| RAIGMORE | CT |  |  |  | 5.2398 | 4.04 | 2.1734 | 1.3497 | 0.47013 | -0.45039 | -1.5127 | -2.5321 | -3.7028 | -4.7619 | -6.909 | -3.0851 | -4.3569 | -5.1385 | 8.7743 | 7.4738 | 5.4314 | 4.7149 | 3.9108 | 2.8748 | 1.5607 | 0.70061 | -0.21783 | -1.0655 | -2.7679 | 1.05 | 0.036695 | -1.0412 | 6.0598 | 4.6932 | 2.5224 | 1.6653 | 0.73027 | -0.32317 | -1.801 | -2.8405 | -3.9739 | -5.0208 | -7.1229 | -1.2608 | -2.4646 | -3.2447
| RAIGMORE | LW |  |  |  | 1.7221 | -4.7303 | -15.2338 | -16.1692 | -17.1738 | -18.382 | -19.8707 | -21.4278 | -22.934 | -24.5455 | -27.814 | -22.822 | -24.0289 | -24.9709 | 4.3421 | -3.5534 | -16.4354 | -17.4205 | -18.4896 | -19.8571 | -21.4092 | -22.9063 | -24.1383 | -25.4718 | -28.1628 | -23.4603 | -24.4906 | -25.5307 | 1.6607 | -6.2666 | -19.2302 | -20.2579 | -21.3807 | -22.8078 | -24.5565 | -26.3445 | -27.8485 | -29.4754 | -32.7701 | -25.95 | -27.2548 | -28.3719
| RAIGMORE | ST |  |  |  | 2.8542 | -0.26501 | -6.6084 | -7.4176 | -8.1834 | -8.6955 | -9.6715 | -10.3053 | -11.0513 | -11.9731 | -14.9344 | -10.5373 | -11.3994 | -12.6985 | 5.7776 | 1.9986 | -5.8072 | -6.6496 | -7.4195 | -7.8896 | -8.9056 | -9.5061 | -10.3607 | -11.3241 | -13.7203 | -10.3776 | -11.3989 | -12.764 | 3.0658 | -0.72926 | -8.552 | -9.459 | -10.3075 | -10.8811 | -12.0265 | -12.7321 | -13.5477 | -14.723 | -17.6755 | -13.0567 | -13.8301 | -14.4531
| RAIGMORE | FS |  |  |  | 5.9782 | 5.5451 | 4.9577 | 4.5494 | 4.083 | 3.7537 | 3.3919 | 3.0233 | 2.6058 | 2.1545 | 1.1632 | 2.7909 | 1.775 | 0.93032 | 9.6699 | 9.2286 | 8.5905 | 8.2052 | 7.752 | 7.446 | 7.1161 | 6.7955 | 6.4423 | 6.0631 | 4.8543 | 5.9136 | 4.8657 | 3.3916 | 6.9601 | 6.5052 | 5.8562 | 5.4306 | 4.934 | 4.5712 | 4.1707 | 3.7646 | 3.3181 | 2.8323 | 1.5574 | 3.5129 | 3.0581 | 2.8117
ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | NO | -1.8882 | -2.0064 | -2.134 | -2.2631 | -2.3937 | -2.5756 | -2.8383 | -3.0109 | -3.1699 | -3.344 | -3.6768 | -4.118 | -4.5995 | -5.0449 | -0.97443 | -1.0293 | -1.0924 | -1.1515 | -1.2606 | -1.4358 | -1.6513 | -1.7563 | -1.8846 | -2.0269 | -2.2958 | -2.7475 | -3.3469 | -3.9578 | -1.6474 | -1.745 | -1.856 | -1.968 | -2.083 | -2.3086 | -2.5812 | -2.7425 | -2.909 | -3.0948 | -3.4471 | -3.9518 | -4.4674 | -5.1083
| REDFORD | CT |  |  |  | -1.8229 | -1.9039 | -1.987 | -2.1495 | -2.3268 | -2.5756 | -2.8383 | -3.0109 | -3.1699 | -3.344 | -3.6768 | -4.118 | -4.5995 | -4.9645 | -0.95052 | -0.99164 | -1.0365 | -1.1273 | -1.233 | -1.4358 | -1.6513 | -1.7563 | -1.8846 | -2.0269 | -2.2958 | -2.7183 | -3.1533 | -3.5862 | -1.5936 | -1.6607 | -1.7338 | -1.8833 | -2.0505 | -2.3086 | -2.5812 | -2.7425 | -2.909 | -3.0948 | -3.4471 | -3.9518 | -4.457 | -4.8751
| REDFORD | LW |  |  |  | -1.8882 | -2.0064 | -2.134 | -2.2631 | -2.3937 | -2.5216 | -2.6719 | -2.8329 | -2.9663 | -3.1006 | -3.3762 | -3.5879 | -4.1515 | -4.8572 | -0.97443 | -1.0293 | -1.0924 | -1.1515 | -1.2133 | -1.2715 | -1.3491 | -1.4347 | -1.5323 | -1.6333 | -1.8315 | -1.9884 | -2.6059 | -3.4627 | -1.6474 | -1.745 | -1.856 | -1.968 | -2.083 | -2.1938 | -2.3301 | -2.4778 | -2.6149 | -2.7546 | -3.0359 | -3.2732 | -3.9351 | -4.8042
| REDFORD | ST |  |  |  | -1.7972 | -1.86 | -1.9115 | -2.062 | -2.1874 | -2.2905 | -2.5123 | -2.6217 | -2.8157 | -2.9362 | -3.2085 | -3.8441 | -4.4654 | -5.0449 | -0.94091 | -0.97163 | -0.99764 | -1.1469 | -1.2606 | -1.3473 | -1.5754 | -1.6673 | -1.8566 | -1.9573 | -2.1859 | -2.7475 | -3.3469 | -3.9578 | -1.573 | -1.6234 | -1.6665 | -1.8357 | -1.9715 | -2.0798 | -2.3326 | -2.4477 | -2.6649 | -2.7924 | -3.0816 | -3.7853 | -4.4674 | -5.1083
| REDFORD | FS |  |  |  | -1.7771 | -1.8214 | -1.8604 | -1.9303 | -1.9983 | -2.0727 | -2.1474 | -2.2233 | -2.337 | -2.4413 | -2.66 | -3.1677 | -3.5476 | -3.7608 | -0.93337 | -0.95673 | -0.97768 | -1.0267 | -1.0766 | -1.1324 | -1.1896 | -1.2458 | -1.3364 | -1.4137 | -1.5776 | -1.8781 | -2.152 | -2.3624 | -1.5565 | -1.5918 | -1.6244 | -1.6927 | -1.7603 | -1.8347 | -1.9102 | -1.9862 | -2.1033 | -2.208 | -2.4287 | -2.9157 | -3.2863 | -3.4786
BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | NO | 9.5041 | 8.5262 | 7.4067 | 6.3014 | 5.0196 | 3.6814 | 2.7301 | 1.6095 | 0.52867 | -0.54413 | -2.7754 | -4.631 | -5.4601 | -5.8447 | 10.558 | 9.6843 | 8.737 | 7.9517 | 7.0103 | 6.0394 | 5.6449 | 5.2194 | 4.5646 | 3.9467 | 2.5538 | 1.6048 | 1.0205 | 0.4126 | 9.7497 | 8.8761 | 7.8079 | 6.742 | 5.4975 | 4.2029 | 3.3273 | 2.3694 | 1.4047 | 0.44471 | -1.5638 | -3.0468 | -3.8143 | -4.2422
| REDGORTON | CT |  |  |  | 9.7079 | 8.8935 | 7.9347 | 6.8322 | 5.4867 | 4.1295 | 3.1808 | 2.1913 | 1.1629 | 0.06633 | -2.1905 | -3.8352 | -4.5878 | -5.0072 | 10.6322 | 9.8615 | 8.9891 | 8.2085 | 7.2124 | 6.206 | 5.757 | 5.3526 | 4.8212 | 4.1744 | 2.7768 | 1.6313 | 1.0205 | 0.4126 | 9.9198 | 9.1915 | 8.3053 | 7.2363 | 5.917 | 4.5892 | 3.706 | 2.817 | 1.9193 | 0.93916 | -1.086 | -2.5286 | -3.2226 | -3.6298
| REDGORTON | LW |  |  |  | 9.5041 | 8.5262 | 7.4067 | 6.3014 | 5.0196 | 3.6814 | 2.7301 | 1.6095 | 0.52867 | -0.54413 | -2.7754 | -4.631 | -5.4601 | -5.8447 | 10.558 | 9.6843 | 8.737 | 7.9517 | 7.0103 | 6.0394 | 5.6449 | 5.2194 | 4.5646 | 3.9467 | 2.5538 | 1.6048 | 1.0547 | 0.67359 | 9.7497 | 8.8761 | 7.8079 | 6.742 | 5.4975 | 4.2029 | 3.3273 | 2.3694 | 1.4047 | 0.44471 | -1.5638 | -3.0468 | -3.8143 | -4.2422
| REDGORTON | ST |  |  |  | 9.823 | 9.0941 | 8.2514 | 7.4569 | 6.4737 | 5.4966 | 4.9284 | 4.3773 | 3.7623 | 3.0483 | 1.429 | -0.6256 | -1.3249 | -1.9346 | 10.6365 | 9.8885 | 9.067 | 8.3134 | 7.3547 | 6.4088 | 5.9681 | 5.5784 | 5.1342 | 4.7699 | 3.8764 | 2.8552 | 2.2123 | 1.5061 | 10.0078 | 9.3653 | 8.5996 | 7.8048 | 6.816 | 5.8359 | 5.2847 | 4.7649 | 4.1738 | 3.6159 | 2.1678 | 0.224 | -0.45901 | -1.021
| REDGORTON | FS |  |  |  | 9.968 | 9.4103 | 8.7632 | 8.1365 | 7.3263 | 6.5356 | 6.01 | 5.4872 | 4.9083 | 4.2578 | 2.8706 | 0.16039 | -1.5763 | -2.0853 | 10.7844 | 10.2177 | 9.5865 | 9.0199 | 8.2523 | 7.5161 | 7.1154 | 6.7265 | 6.291 | 5.833 | 4.9768 | 3.5316 | 2.0984 | 1.1638 | 10.1314 | 9.6368 | 9.0581 | 8.4956 | 7.6992 | 6.9168 | 6.4194 | 5.9275 | 5.3757 | 4.7957 | 3.5711 | 1.1964 | -0.42525 | -0.84417
REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | NO | 19.0254 | 18.2828 | 17.4481 | 16.2778 | 14.7946 | 13.127 | 11.2672 | 9.671 | 8.3719 | 7.2744 | 5.4393 | 5.5808 | 4.3924 | 3.0739 | 21.4528 | 20.8241 | 20.0821 | 19.1291 | 17.9344 | 16.596 | 15.0365 | 13.7838 | 12.7468 | 11.945 | 10.4322 | 12.7091 | 11.5031 | 9.9786 | 16.1631 | 15.4933 | 14.6868 | 13.6386 | 12.3545 | 10.9145 | 9.2513 | 7.8728 | 6.7199 | 5.7562 | 3.9379 | 6.0109 | 4.664 | 3.0851
| REDMOSS | CT |  |  |  | 20.2966 | 18.5122 | 17.7276 | 16.7389 | 15.5784 | 14.2101 | 12.6932 | 11.4687 | 10.2217 | 9.1651 | 7.397 | 6.6786 | 5.3943 | 4.4679 | 22.99 | 20.9363 | 20.1877 | 19.3087 | 18.3022 | 17.1374 | 15.9412 | 15.0734 | 14.1541 | 13.5563 | 12.4041 | 13.7572 | 12.549 | 11.1711 | 17.7254 | 15.6399 | 14.8329 | 13.836 | 12.7282 | 11.4616 | 10.1359 | 9.1538 | 8.1411 | 7.4252 | 6.0434 | 7.3666 | 6.1001 | 5.1201
| REDMOSS | LW |  |  |  | 19.0254 | 18.2828 | 17.4481 | 16.2778 | 14.7946 | 13.127 | 11.2672 | 9.671 | 8.3719 | 7.2744 | 5.4393 | 5.5808 | 4.3924 | 3.0739 | 21.4528 | 20.8241 | 20.0821 | 19.1291 | 17.9344 | 16.596 | 15.0365 | 13.7838 | 12.7468 | 11.945 | 10.4322 | 12.7091 | 11.5031 | 9.9786 | 16.1631 | 15.4933 | 14.6868 | 13.6386 | 12.3545 | 10.9145 | 9.2513 | 7.8728 | 6.7199 | 5.7562 | 3.9379 | 6.0109 | 4.664 | 3.0851
| REDMOSS | ST |  |  |  | 20.319 | 18.642 | 18.071 | 17.274 | 16.3568 | 15.5025 | 14.3512 | 13.5037 | 12.5995 | 11.923 | 10.4717 | 10.312 | 8.8114 | 7.2576 | 23.0169 | 21.0677 | 20.5093 | 19.6766 | 18.7502 | 17.8855 | 16.7295 | 15.9595 | 15.1253 | 14.5774 | 13.397 | 14.5759 | 13.4008 | 11.6247 | 17.7661 | 15.8114 | 15.2434 | 14.3956 | 13.4578 | 12.5736 | 11.372 | 10.5469 | 9.6599 | 9.013 | 7.6072 | 9.2336 | 8.1995 | 7.1158
| REDMOSS | FS |  |  |  | 20.6142 | 20.1856 | 19.7211 | 18.0527 | 17.399 | 16.7359 | 16.0487 | 15.3997 | 14.7373 | 14.1277 | 13.0228 | 11.8552 | 10.2365 | 9.1523 | 23.3206 | 22.9127 | 22.4679 | 20.5221 | 19.8744 | 19.2196 | 18.5527 | 17.9264 | 17.2788 | 16.7563 | 15.8221 | 16.1323 | 14.7984 | 13.0421 | 18.0583 | 17.6513 | 17.2054 | 15.2491 | 14.5958 | 13.9301 | 13.2353 | 12.579 | 11.9004 | 11.3221 | 10.2614 | 10.7883 | 10.0303 | 9.5738
CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | NO | -0.69468 | -0.73318 | -0.77887 | -0.83719 | -0.89436 | -0.96143 | -1.0288 | -1.1073 | -1.1415 | -1.1764 | -1.2593 | -1.2302 | -1.279 | -1.3154 | -0.42893 | -0.45043 | -0.48376 | -0.51701 | -0.56817 | -0.60693 | -0.64629 | -0.69499 | -0.75052 | -0.8102 | -0.92516 | -0.91339 | -0.96056 | -1.002 | -0.73675 | -0.77285 | -0.8248 | -0.88408 | -0.95213 | -1.0209 | -1.0889 | -1.1718 | -1.2422 | -1.3175 | -1.4617 | -1.4489 | -1.4983 | -1.5341
| RHICONICH | CT |  |  |  | -0.6727 | -0.70129 | -0.74077 | -0.81511 | -0.8922 | -0.96143 | -1.0288 | -1.1073 | -1.1415 | -1.1758 | -1.2536 | -1.2038 | -1.279 | -1.3154 | -0.42152 | -0.4398 | -0.46757 | -0.51624 | -0.56817 | -0.60693 | -0.64629 | -0.68866 | -0.73195 | -0.78925 | -0.90144 | -0.91231 | -0.96056 | -1.002 | -0.71952 | -0.74635 | -0.78726 | -0.86589 | -0.95213 | -1.0209 | -1.0889 | -1.1648 | -1.2192 | -1.289 | -1.4286 | -1.4222 | -1.4983 | -1.5341
| RHICONICH | LW |  |  |  | -0.69468 | -0.73318 | -0.77887 | -0.83719 | -0.89436 | -0.94934 | -1.0176 | -1.091 | -1.1323 | -1.1764 | -1.2593 | -1.2302 | -1.2724 | -1.2862 | -0.42893 | -0.45043 | -0.48376 | -0.51701 | -0.55335 | -0.58476 | -0.63627 | -0.69499 | -0.75052 | -0.8102 | -0.92516 | -0.91339 | -0.93179 | -0.93728 | -0.73675 | -0.77285 | -0.8248 | -0.88408 | -0.94606 | -1.0019 | -1.0824 | -1.1718 | -1.2422 | -1.3175 | -1.4617 | -1.4489 | -1.4904 | -1.504
| RHICONICH | ST |  |  |  | -0.65198 | -0.66705 | -0.68322 | -0.70148 | -0.72597 | -0.75045 | -0.77804 | -0.8112 | -0.84821 | -0.89409 | -0.99103 | -1.0784 | -1.1541 | -1.1897 | -0.41519 | -0.42427 | -0.43527 | -0.44888 | -0.46715 | -0.48665 | -0.50996 | -0.53813 | -0.57155 | -0.61259 | -0.7081 | -0.84996 | -0.90621 | -0.94208 | -0.70578 | -0.72006 | -0.73663 | -0.75663 | -0.7835 | -0.81115 | -0.84344 | -0.88242 | -0.92841 | -0.98529 | -1.1122 | -1.2952 | -1.3666 | -1.3985
| RHICONICH | FS |  |  |  | -0.64706 | -0.65699 | -0.67177 | -0.69204 | -0.71027 | -0.73126 | -0.75421 | -0.77923 | -0.81181 | -0.84494 | -0.91611 | -1.0232 | -1.1987 | -1.2291 | -0.41329 | -0.4202 | -0.42995 | -0.44252 | -0.45664 | -0.47202 | -0.48989 | -0.51045 | -0.53559 | -0.56347 | -0.62789 | -0.77333 | -0.9293 | -0.97609 | -0.70192 | -0.71209 | -0.72705 | -0.74706 | -0.76774 | -0.79043 | -0.8162 | -0.84531 | -0.88285 | -0.92335 | -1.0137 | -1.2223 | -1.4138 | -1.445
DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 10.3445 | 9.9548 | 9.4686 | 8.4885 | 7.4819 | 6.4664 | 5.2844 | 4.0243 | 3.1692 | 2.2543 | 0.41766 | 0.8983 | -1.3435 | -2.4445 | 14.8375 | 14.6421 | 14.3703 | 13.9364 | 13.4067 | 12.8279 | 12.2205 | 11.6455 | 11.0635 | 10.3883 | 8.9512 | 8.2092 | 5.0918 | -3.1732 | 13.1738 | 12.8274 | 12.386 | 11.5097 | 10.6056 | 9.696 | 8.6239 | 7.4746 | 6.6629 | 5.7941 | 3.9358 | 4.603 | 2.5374 | 1.4524
| ROSEBANK STREET | CT |  |  |  | 10.7453 | 10.5606 | 10.2937 | 9.2914 | 8.2552 | 7.2544 | 6.2352 | 5.2432 | 4.4165 | 3.547 | 1.7519 | 0.8983 | -1.3435 | -2.4445 | 14.941 | 14.7743 | 14.5373 | 13.9896 | 13.4067 | 12.8279 | 12.2205 | 11.6455 | 11.0635 | 10.3883 | 8.9512 | 8.2092 | 5.2221 | 1.1381 | 13.5231 | 13.3553 | 13.1077 | 12.1986 | 11.2555 | 10.3391 | 9.4016 | 8.5014 | 7.726 | 6.9125 | 5.2353 | 4.603 | 2.5374 | 1.4524
| ROSEBANK STREET | LW |  |  |  | 10.3445 | 9.9548 | 9.4686 | 8.4885 | 7.4819 | 6.4664 | 5.2844 | 4.0243 | 3.1692 | 2.2543 | 0.41766 | 1.4631 | 0.40718 | -0.47383 | 14.8375 | 14.6421 | 14.3703 | 13.9364 | 13.4804 | 13.0214 | 12.4314 | 11.7817 | 11.171 | 10.4777 | 9.0886 | 10.6533 | 9.748 | 8.7003 | 13.1738 | 12.8274 | 12.386 | 11.5097 | 10.6056 | 9.696 | 8.6239 | 7.4746 | 6.6629 | 5.7941 | 3.9358 | 5.184 | 4.0555 | 2.9841
| ROSEBANK STREET | ST |  |  |  | 10.9413 | 10.913 | 10.8584 | 10.7768 | 10.6829 | 10.5711 | 10.3836 | 10.2141 | 9.9065 | 9.5913 | 8.8144 | 8.4661 | 6.5853 | 4.0123 | 15.0198 | 14.9374 | 14.8307 | 14.669 | 14.4963 | 14.3064 | 14.0245 | 13.7446 | 13.3042 | 12.8683 | 11.8152 | 10.7375 | 7.7687 | 3.0696 | 13.6966 | 13.6724 | 13.6236 | 13.5279 | 13.4243 | 13.3069 | 13.1009 | 12.8757 | 12.4905 | 12.1066 | 11.17 | 10.9271 | 9.1878 | 6.9562
| ROSEBANK STREET | FS |  |  |  | 10.9364 | 10.8932 | 10.8414 | 10.716 | 10.5843 | 10.4342 | 10.2666 | 10.0787 | 9.7795 | 9.4671 | 8.7556 | 7.8938 | 5.6869 | 3.4912 | 15.0185 | 14.9219 | 14.8079 | 14.6454 | 14.4636 | 14.2566 | 14.0175 | 13.7478 | 13.3805 | 12.9654 | 11.9555 | 9.9165 | 5.0918 | -3.1732 | 13.6891 | 13.654 | 13.6096 | 13.4924 | 13.366 | 13.2217 | 13.0597 | 12.8782 | 12.5891 | 12.2789 | 11.5184 | 10.8735 | 8.9126 | 6.9695
KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | NO | 1.8865 | 1.7805 | 1.6435 | 0.33969 | -1.1264 | -3.8116 | -6.6758 | -8.4208 | -8.9248 | -9.4573 | -10.425 | -12.062 | -12.6699 | -12.8838 | 2.992 | 2.9383 | 2.8361 | 1.3701 | -0.30455 | -3.5373 | -6.9946 | -9.0494 | -9.6316 | -10.2447 | -11.361 | -12.6886 | -13.3233 | -13.5495 | 1.5997 | 1.5038 | 1.3756 | -0.17299 | -1.9147 | -5.2112 | -8.7289 | -10.8448 | -11.4458 | -12.0796 | -13.2335 | -14.6724 | -15.3657 | -15.6101
| ROTHES | CT |  |  |  | 1.9611 | 1.8788 | 1.7706 | 1.397 | 0.91553 | -0.43826 | -1.867 | -2.3792 | -2.6627 | -2.9602 | -3.5273 | -4.1904 | -4.6511 | -4.8394 | 3.0113 | 2.9383 | 2.8361 | 2.5277 | 2.0964 | 0.53554 | -1.1272 | -1.641 | -1.9478 | -2.2319 | -2.8034 | -2.8929 | -3.1942 | -3.3099 | 1.6564 | 1.5605 | 1.4366 | 1.0548 | 0.55268 | -1.0792 | -2.8097 | -3.394 | -3.7268 | -4.0373 | -4.6595 | -4.864 | -5.2979 | -5.4683
| ROTHES | LW |  |  |  | 1.8865 | 1.7805 | 1.6435 | 0.33969 | -1.1264 | -3.8116 | -6.6758 | -8.4208 | -8.9248 | -9.4573 | -10.425 | -12.062 | -12.6699 | -12.8838 | 2.992 | 2.9384 | 2.8532 | 1.3701 | -0.30455 | -3.5373 | -6.9946 | -9.0494 | -9.6316 | -10.2447 | -11.361 | -12.6886 | -13.3233 | -13.5495 | 1.5997 | 1.5038 | 1.3756 | -0.17299 | -1.9147 | -5.2112 | -8.7289 | -10.8448 | -11.4458 | -12.0796 | -13.2335 | -14.6724 | -15.3657 | -15.6101
| ROTHES | ST |  |  |  | 1.9983 | 1.9538 | 1.9008 | 0.77298 | -0.023441 | -0.55511 | -2.2397 | -2.7691 | -3.1891 | -3.4127 | -4.0103 | -4.8626 | -5.3871 | -5.7199 | 3.0254 | 2.9937 | 2.9569 | 1.5987 | 0.65358 | 0.016374 | -2.0584 | -2.6949 | -3.1937 | -3.45 | -4.0439 | -4.3682 | -4.7561 | -4.9351 | 1.6884 | 1.6439 | 1.5917 | 0.21322 | -0.75117 | -1.4054 | -3.4996 | -4.1533 | -4.6684 | -4.9409 | -5.6018 | -6.0238 | -6.5298 | -6.8281
| ROTHES | FS |  |  |  | 2.0518 | 2.0135 | 1.976 | 1.6952 | 1.4077 | 1.098 | 0.78363 | 0.50291 | 0.29628 | 0.12519 | -0.24373 | -0.73869 | -1.1423 | -1.3533 | 3.0674 | 3.041 | 3.013 | 2.7069 | 2.3954 | 2.0408 | 1.6799 | 1.3573 | 1.1449 | 0.97228 | 0.59691 | 0.76001 | 0.64534 | 0.57853 | 1.7391 | 1.7017 | 1.6644 | 1.3413 | 1.0116 | 0.63946 | 0.26133 | -0.076744 | -0.3133 | -0.50822 | -0.92983 | -0.95588 | -1.1834 | -1.3502
DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | NO | 18.5468 | 18.393 | 18.2009 | 17.8046 | 17.3899 | 16.984 | 16.5063 | 15.9936 | 15.5957 | 15.1771 | 14.3366 | 14.1734 | 12.6268 | 11.7802 | 20.713 | 20.6381 | 20.5367 | 20.3604 | 20.1693 | 19.9837 | 19.7335 | 19.4527 | 19.1979 | 18.9236 | 18.3714 | 18.647 | 17.8357 | 17.1351 | 19.7837 | 19.6444 | 19.4617 | 19.1174 | 18.7533 | 18.3979 | 17.9621 | 17.4875 | 17.099 | 16.6869 | 15.8588 | 16.0119 | 14.7603 | 14.0166
| ROTHESAY | CT |  |  |  | 18.6944 | 18.6256 | 18.5288 | 18.1692 | 17.7737 | 17.4142 | 17.0554 | 16.6858 | 16.3239 | 15.9403 | 15.1612 | 14.2316 | 12.6268 | 11.7802 | 20.7748 | 20.7286 | 20.6566 | 20.458 | 20.2462 | 20.0696 | 19.8889 | 19.7006 | 19.4903 | 19.2588 | 18.7764 | 18.647 | 17.8357 | 17.1351 | 19.9226 | 19.8527 | 19.7558 | 19.4107 | 19.0507 | 18.7332 | 18.4143 | 18.0851 | 17.7491 | 17.3878 | 16.6499 | 16.0678 | 14.7603 | 14.0166
| ROTHESAY | LW |  |  |  | 18.5468 | 18.393 | 18.2009 | 17.8046 | 17.3899 | 16.984 | 16.5063 | 15.9936 | 15.5957 | 15.1771 | 14.3366 | 14.1734 | 13.3134 | 13.1114 | 20.713 | 20.6381 | 20.5367 | 20.3604 | 20.1693 | 19.9837 | 19.7335 | 19.4527 | 19.1979 | 18.9236 | 18.3714 | 18.8207 | 18.5056 | 18.4307 | 19.7837 | 19.6444 | 19.4617 | 19.1174 | 18.7533 | 18.3979 | 17.9621 | 17.4875 | 17.099 | 16.6869 | 15.8588 | 16.0119 | 15.3408 | 15.1835
| ROTHESAY | ST |  |  |  | 18.7298 | 18.7084 | 18.6758 | 18.6329 | 18.5758 | 18.5133 | 18.4335 | 18.3383 | 18.2222 | 18.0807 | 17.7458 | 17.4181 | 16.5717 | 15.1997 | 20.7952 | 20.7779 | 20.7532 | 20.7161 | 20.668 | 20.6136 | 20.5458 | 20.4649 | 20.3674 | 20.2495 | 19.9672 | 19.7684 | 19.216 | 18.3697 | 19.9594 | 19.9374 | 19.9048 | 19.8617 | 19.8049 | 19.7435 | 19.6649 | 19.5721 | 19.4592 | 19.3221 | 18.9985 | 18.6855 | 17.9315 | 16.8291
| ROTHESAY | FS |  |  |  | 18.7372 | 18.7159 | 18.6913 | 18.6406 | 18.5831 | 18.5217 | 18.4498 | 18.3674 | 18.2377 | 18.0966 | 17.78 | 17.1003 | 16.0612 | 15.0858 | 20.7991 | 20.7815 | 20.7611 | 20.7223 | 20.6755 | 20.6243 | 20.5639 | 20.4942 | 20.3942 | 20.2829 | 20.0261 | 19.5994 | 18.6786 | 17.4754 | 19.9667 | 19.9451 | 19.9205 | 19.8679 | 19.8087 | 19.746 | 19.6733 | 19.5904 | 19.4572 | 19.3133 | 18.9955 | 18.4368 | 17.5169 | 16.7245
THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | NO | 0.54945 | 0.54647 | 0.53329 | 0.51556 | 0.49339 | 0.4721 | 0.45048 | 0.43018 | 0.39652 | 0.3526 | 0.26898 | 0.15817 | -0.21039 | -0.72986 | 0.65926 | 0.65517 | 0.64642 | 0.63448 | 0.62035 | 0.60898 | 0.59731 | 0.58584 | 0.54384 | 0.49513 | 0.40543 | 0.25633 | -0.19877 | -0.84317 | 0.7287 | 0.72341 | 0.71205 | 0.69698 | 0.68122 | 0.66373 | 0.64585 | 0.62886 | 0.59417 | 0.54539 | 0.45568 | 0.29393 | -0.16402 | -0.81049
| ROUSAY | CT |  |  |  | 0.54959 | 0.54647 | 0.53896 | 0.51569 | 0.49339 | 0.4721 | 0.45048 | 0.43018 | 0.39763 | 0.36482 | 0.29745 | 0.21635 | 0.030339 | -0.17934 | 0.66107 | 0.65624 | 0.64939 | 0.63448 | 0.62035 | 0.60898 | 0.59731 | 0.58584 | 0.55029 | 0.51233 | 0.43988 | 0.32272 | 0.099251 | -0.1648 | 0.73264 | 0.7245 | 0.71788 | 0.69698 | 0.68122 | 0.66373 | 0.64585 | 0.62886 | 0.59545 | 0.56542 | 0.49157 | 0.36535 | 0.13971 | -0.1208
| ROUSAY | LW |  |  |  | 0.54945 | 0.54676 | 0.53329 | 0.51556 | 0.50031 | 0.48423 | 0.46298 | 0.43736 | 0.39652 | 0.3526 | 0.26898 | 0.15817 | -0.21039 | -0.72986 | 0.65926 | 0.65517 | 0.64642 | 0.63718 | 0.62812 | 0.61937 | 0.60592 | 0.58981 | 0.54384 | 0.49513 | 0.40543 | 0.25633 | -0.19877 | -0.84317 | 0.7287 | 0.72341 | 0.71205 | 0.69787 | 0.68621 | 0.67283 | 0.65647 | 0.63655 | 0.59417 | 0.54539 | 0.45568 | 0.29393 | -0.16402 | -0.81049
| ROUSAY | ST |  |  |  | 0.54995 | 0.54875 | 0.54722 | 0.54506 | 0.54233 | 0.53898 | 0.5348 | 0.52974 | 0.4798 | 0.45654 | 0.38738 | 0.26568 | -0.0073462 | -0.31215 | 0.66414 | 0.66185 | 0.66028 | 0.65757 | 0.65421 | 0.65001 | 0.64442 | 0.63941 | 0.57695 | 0.54781 | 0.48294 | 0.331 | -0.0082182 | -0.38627 | 0.73409 | 0.73325 | 0.73207 | 0.73045 | 0.72824 | 0.72578 | 0.72056 | 0.7164 | 0.6533 | 0.6234 | 0.55881 | 0.39456 | 0.0554 | -0.32155
| ROUSAY | FS |  |  |  | 0.55019 | 0.5493 | 0.54816 | 0.54665 | 0.54479 | 0.54263 | 0.54004 | 0.53324 | 0.51121 | 0.49188 | 0.45594 | 0.40065 | 0.34678 | 0.30577 | 0.66369 | 0.66226 | 0.66054 | 0.65752 | 0.65466 | 0.65133 | 0.64712 | 0.64101 | 0.61615 | 0.59637 | 0.55621 | 0.50713 | 0.45487 | 0.40235 | 0.73419 | 0.73351 | 0.73255 | 0.73129 | 0.72961 | 0.72577 | 0.72045 | 0.71203 | 0.68651 | 0.66573 | 0.62538 | 0.56486 | 0.51175 | 0.46433
CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | NO | 14.3752 | 14.0829 | 13.6519 | 12.7464 | 11.7799 | 10.6308 | 9.234 | 7.8463 | 6.7578 | 5.5942 | 3.1085 | 5.7361 | 4.8487 | 4.1245 | 17.7261 | 17.5427 | 17.2364 | 16.6383 | 15.9769 | 15.0844 | 13.9594 | 12.9521 | 12.1495 | 11.239 | 9.4059 | 12.0085 | 10.6974 | 7.5146 | 16.1355 | 15.8517 | 15.4133 | 14.5214 | 13.5569 | 12.3633 | 10.8881 | 9.4856 | 8.3534 | 7.1353 | 4.6742 | 7.6069 | 6.6912 | 5.8575
| RUTHRIESTON | CT |  |  |  | 14.6 | 14.4241 | 14.1685 | 13.3776 | 12.5322 | 11.6174 | 10.6313 | 9.8074 | 8.9181 | 7.9836 | 6.0528 | 6.7767 | 5.3591 | 4.5409 | 17.7816 | 17.6211 | 17.3893 | 16.8746 | 16.2979 | 15.6024 | 14.8496 | 14.299 | 13.6879 | 13.0293 | 11.5614 | 12.3598 | 10.6974 | 8.4984 | 16.3218 | 16.1381 | 15.868 | 15.1018 | 14.2685 | 13.3416 | 12.3518 | 11.5568 | 10.6794 | 9.747 | 7.8124 | 8.9316 | 7.66 | 6.8766
| RUTHRIESTON | LW |  |  |  | 14.3752 | 14.0829 | 13.6519 | 12.7464 | 11.7799 | 10.6308 | 9.234 | 7.8463 | 6.7578 | 5.5942 | 3.1085 | 5.7361 | 4.8487 | 4.1245 | 17.7261 | 17.5427 | 17.2364 | 16.6383 | 15.9769 | 15.0844 | 13.9594 | 12.9521 | 12.1495 | 11.239 | 9.4059 | 12.0085 | 11.2836 | 10.4976 | 16.1355 | 15.8517 | 15.4133 | 14.5214 | 13.5569 | 12.3633 | 10.8881 | 9.4856 | 8.3534 | 7.1353 | 4.6742 | 7.6069 | 6.6912 | 5.8575
| RUTHRIESTON | ST |  |  |  | 14.6715 | 14.5954 | 14.5021 | 14.1897 | 13.9042 | 13.6338 | 13.1115 | 12.7181 | 12.2866 | 11.7998 | 10.5843 | 11.0329 | 9.5342 | 7.9925 | 17.819 | 17.7354 | 17.6299 | 17.2647 | 16.9407 | 16.639 | 16.0371 | 15.6401 | 15.2286 | 14.7854 | 13.6751 | 13.7357 | 11.8948 | 9.3504 | 16.3872 | 16.3067 | 16.2051 | 15.8369 | 15.5064 | 15.1978 | 14.5824 | 14.1307 | 13.6547 | 13.1256 | 11.8479 | 12.3997 | 11.0145 | 9.6255
| RUTHRIESTON | FS |  |  |  | 14.6806 | 14.6215 | 14.544 | 14.3856 | 14.2025 | 13.9989 | 13.766 | 13.5073 | 13.1877 | 12.8128 | 11.9544 | 11.801 | 9.9687 | 8.5253 | 17.8238 | 17.7476 | 17.6513 | 17.4794 | 17.2812 | 17.0553 | 16.7967 | 16.5115 | 16.194 | 15.8424 | 15.0129 | 14.3522 | 11.6112 | 7.5146 | 16.3967 | 16.3336 | 16.25 | 16.0788 | 15.8804 | 15.6574 | 15.4024 | 15.12 | 14.7785 | 14.3908 | 13.4961 | 13.4941 | 11.7975 | 10.565
FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | NO | YES | 1.2536 | 1.1742 | 1.099 | 1.0442 | 0.97439 | 0.90183 | 0.82011 | 0.74355 | 0.66812 | 0.58144 | 0.41286 | 0.48262 | 0.43756 | 0.4052 | 1.7455 | 1.7028 | 1.6576 | 1.625 | 1.569 | 1.5264 | 1.4791 | 1.4335 | 1.373 | 1.3048 | 1.171 | 1.2281 | 1.1844 | 1.143 | -2.5195 | -2.5892 | -2.6595 | -2.7132 | -2.7843 | -2.8552 | -2.9349 | -3.0099 | -3.0832 | -3.1688 | -3.3356 | -3.2619 | -3.3062 | -3.3396
| SALEN | CT |  |  |  | 1.2715 | 1.2079 | 1.1443 | 1.0632 | 0.97439 | 0.90183 | 0.82011 | 0.74355 | 0.68303 | 0.60225 | 0.45207 | 0.50038 | 0.43756 | 0.4052 | 1.7528 | 1.7169 | 1.6769 | 1.6256 | 1.569 | 1.5264 | 1.4791 | 1.4335 | 1.3859 | 1.3227 | 1.2029 | 1.2281 | 1.1844 | 1.143 | -2.502 | -2.5576 | -2.617 | -2.6971 | -2.7843 | -2.8552 | -2.9349 | -3.0099 | -3.0699 | -3.1492 | -3.2975 | -3.2439 | -3.3062 | -3.3396
| SALEN | LW |  |  |  | 1.2536 | 1.1742 | 1.099 | 1.0442 | 0.98189 | 0.92646 | 0.8424 | 0.74753 | 0.66812 | 0.58144 | 0.41286 | 0.48262 | 0.45378 | 0.44198 | 1.7455 | 1.7028 | 1.6576 | 1.625 | 1.5873 | 1.5545 | 1.4993 | 1.4356 | 1.373 | 1.3048 | 1.171 | 1.2312 | 1.218 | 1.2135 | -2.5195 | -2.5892 | -2.6595 | -2.7132 | -2.7744 | -2.8291 | -2.9116 | -3.0049 | -3.0832 | -3.1688 | -3.3356 | -3.2619 | -3.2916 | -3.3035
| SALEN | ST |  |  |  | 1.2875 | 1.2381 | 1.2055 | 1.1874 | 1.1614 | 1.1298 | 1.0929 | 1.0523 | 1.0055 | 0.94806 | 0.81521 | 0.6674 | 0.61642 | 0.58959 | 1.7589 | 1.732 | 1.7126 | 1.6997 | 1.6815 | 1.6596 | 1.6334 | 1.6035 | 1.5684 | 1.5255 | 1.4235 | 1.303 | 1.2553 | 1.2205 | -2.487 | -2.5287 | -2.5579 | -2.5762 | -2.6019 | -2.6329 | -2.6688 | -2.7088 | -2.755 | -2.8117 | -2.9435 | -3.0847 | -3.1386 | -3.1674
| SALEN | FS |  |  |  | 1.301 | 1.2543 | 1.2242 | 1.2022 | 1.1767 | 1.1525 | 1.1233 | 1.091 | 1.0585 | 1.0157 | 0.92657 | 0.74207 | 0.55963 | 0.53167 | 1.7655 | 1.7399 | 1.7221 | 1.7084 | 1.6921 | 1.6757 | 1.6561 | 1.6339 | 1.6098 | 1.5801 | 1.5137 | 1.3815 | 1.2281 | 1.1793 | -2.4753 | -2.514 | -2.5404 | -2.5616 | -2.5865 | -2.6103 | -2.6391 | -2.671 | -2.7031 | -2.7452 | -2.8337 | -3.0114 | -3.1895 | -3.2174
TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | YES | -1.8221 | -1.8598 | -1.9096 | -1.9721 | -2.0451 | -2.1234 | -2.2008 | -2.2776 | -2.3376 | -2.4071 | -2.5397 | -2.5468 | -2.5976 | -2.6321 | -1.1869 | -1.207 | -1.2379 | -1.2712 | -1.3213 | -1.3623 | -1.4038 | -1.4483 | -1.4986 | -1.5537 | -1.6595 | -1.6577 | -1.6957 | -1.7278 | -1.2207 | -1.2553 | -1.3023 | -1.3598 | -1.4294 | -1.5011 | -1.5722 | -1.6427 | -1.7047 | -1.7734 | -1.9047 | -1.9116 | -1.9566 | -1.988
| SALEN 2 | CT |  |  |  | -1.8013 | -1.8259 | -1.8672 | -1.9558 | -2.0451 | -2.1234 | -2.2008 | -2.2776 | -2.3262 | -2.3905 | -2.5131 | -2.5169 | -2.5976 | -2.6321 | -1.1788 | -1.1944 | -1.2204 | -1.2702 | -1.3213 | -1.3623 | -1.4038 | -1.4451 | -1.4844 | -1.5371 | -1.6379 | -1.6513 | -1.6957 | -1.7278 | -1.2023 | -1.2254 | -1.2642 | -1.3464 | -1.4294 | -1.5011 | -1.5722 | -1.6427 | -1.6909 | -1.7549 | -1.8769 | -1.8842 | -1.9566 | -1.988
| SALEN 2 | LW |  |  |  | -1.8221 | -1.8598 | -1.9096 | -1.9721 | -2.0376 | -2.0986 | -2.1835 | -2.2749 | -2.3376 | -2.4071 | -2.5397 | -2.5468 | -2.5845 | -2.5999 | -1.1869 | -1.207 | -1.2379 | -1.2712 | -1.3075 | -1.3398 | -1.391 | -1.4483 | -1.4986 | -1.5537 | -1.6595 | -1.6577 | -1.6741 | -1.68 | -1.2207 | -1.2553 | -1.3023 | -1.3598 | -1.4204 | -1.4765 | -1.5561 | -1.6425 | -1.7047 | -1.7734 | -1.9047 | -1.9116 | -1.9452 | -1.9586
| SALEN 2 | ST |  |  |  | -1.7867 | -1.8045 | -1.8201 | -1.8446 | -1.872 | -1.9013 | -1.9352 | -1.9753 | -2.0215 | -2.0755 | -2.2001 | -2.3935 | -2.4655 | -2.505 | -1.1733 | -1.1828 | -1.1926 | -1.2069 | -1.2242 | -1.2431 | -1.2656 | -1.2925 | -1.3245 | -1.3628 | -1.4534 | -1.5935 | -1.6425 | -1.6723 | -1.1894 | -1.2057 | -1.2204 | -1.2431 | -1.269 | -1.2966 | -1.3288 | -1.367 | -1.4113 | -1.4633 | -1.5838 | -1.7726 | -1.8395 | -1.8742
| SALEN 2 | FS |  |  |  | -1.7829 | -1.7934 | -1.8057 | -1.8306 | -1.8515 | -1.8775 | -1.9032 | -1.9334 | -1.9677 | -2.0096 | -2.0985 | -2.3213 | -2.5105 | -2.5451 | -1.1717 | -1.178 | -1.186 | -1.1993 | -1.2125 | -1.2281 | -1.2447 | -1.2643 | -1.287 | -1.3142 | -1.3752 | -1.5187 | -1.6612 | -1.6957 | -1.1861 | -1.1958 | -1.2073 | -1.2302 | -1.2498 | -1.2741 | -1.2984 | -1.3269 | -1.3595 | -1.3992 | -1.4842 | -1.696 | -1.8788 | -1.9094
THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | NO | 0.3555 | 0.32363 | 0.28407 | 0.24042 | 0.18871 | 0.12997 | 0.070982 | 0.0081529 | -0.038932 | -0.091548 | -0.20085 | -0.10044 | -0.1394 | -0.16454 | 0.58591 | 0.56948 | 0.54574 | 0.52126 | 0.48519 | 0.45378 | 0.42066 | 0.38675 | 0.35179 | 0.3078 | 0.21532 | 0.30483 | 0.27876 | 0.25778 | 0.46856 | 0.43949 | 0.40257 | 0.36253 | 0.31303 | 0.25927 | 0.20488 | 0.14727 | 0.099479 | 0.044115 | -0.06805 | 0.030293 | -0.0040314 | -0.026563
| SANDAY | CT |  |  |  | 0.37359 | 0.34641 | 0.31594 | 0.25129 | 0.18871 | 0.12997 | 0.070982 | 0.0081529 | -0.030264 | -0.077557 | -0.16894 | -0.082264 | -0.1394 | -0.16454 | 0.59261 | 0.57744 | 0.55749 | 0.52126 | 0.48519 | 0.45378 | 0.42066 | 0.38675 | 0.35734 | 0.31979 | 0.24437 | 0.30859 | 0.27876 | 0.25778 | 0.48447 | 0.45947 | 0.43072 | 0.37105 | 0.31303 | 0.25927 | 0.20488 | 0.14727 | 0.10993 | 0.060695 | -0.035482 | 0.046825 | -0.0040314 | -0.026563
| SANDAY | LW |  |  |  | 0.3555 | 0.32363 | 0.28407 | 0.24042 | 0.19183 | 0.14428 | 0.084983 | 0.012633 | -0.038932 | -0.091548 | -0.20085 | -0.10044 | -0.13281 | -0.14572 | 0.58591 | 0.56948 | 0.54574 | 0.52232 | 0.49581 | 0.47078 | 0.4344 | 0.39054 | 0.35179 | 0.3078 | 0.21532 | 0.30483 | 0.29122 | 0.28595 | 0.46856 | 0.43949 | 0.40257 | 0.36253 | 0.31785 | 0.27439 | 0.21881 | 0.15112 | 0.099479 | 0.044115 | -0.06805 | 0.030293 | 0.0017502 | -0.0093902
| SANDAY | ST |  |  |  | 0.38143 | 0.36998 | 0.35677 | 0.33576 | 0.31494 | 0.29129 | 0.26083 | 0.22748 | 0.18593 | 0.13926 | 0.031059 | 8.0328e-05 | -0.053386 | -0.086339 | 0.59594 | 0.58937 | 0.58136 | 0.56945 | 0.55625 | 0.54096 | 0.52155 | 0.4992 | 0.47003 | 0.42665 | 0.31836 | 0.34321 | 0.30898 | 0.28698 | 0.48994 | 0.4809 | 0.46864 | 0.44931 | 0.4298 | 0.40758 | 0.37886 | 0.34619 | 0.30176 | 0.24807 | 0.11652 | 0.12031 | 0.071177 | 0.042332
| SANDAY | FS |  |  |  | 0.38735 | 0.37742 | 0.36948 | 0.34893 | 0.33337 | 0.31333 | 0.28933 | 0.26306 | 0.23573 | 0.20372 | 0.13298 | 0.037628 | -0.079346 | -0.11117 | 0.59841 | 0.59284 | 0.5874 | 0.57675 | 0.56706 | 0.55521 | 0.541 | 0.52493 | 0.50733 | 0.48676 | 0.43941 | 0.38673 | 0.3007 | 0.27368 | 0.49097 | 0.48691 | 0.48013 | 0.46145 | 0.44693 | 0.42837 | 0.40611 | 0.38161 | 0.35543 | 0.32454 | 0.25531 | 0.16119 | 0.048991 | 0.020708
DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | NO | 4.4007 | 4.3287 | 4.2331 | 4.1121 | 3.9859 | 3.86 | 3.698 | 3.5136 | 3.351 | 3.1806 | 2.8401 | 2.7203 | 2.469 | 2.3352 | 5.159 | 5.1159 | 5.0579 | 4.9892 | 4.9079 | 4.8086 | 4.7049 | 4.6209 | 4.528 | 4.4098 | 4.1811 | 4.0326 | 3.8318 | 3.6583 | 4.2518 | 4.2266 | 4.1907 | 4.1085 | 4.0285 | 3.9334 | 3.8114 | 3.6388 | 3.4931 | 3.3422 | 3.0135 | 2.8707 | 2.5828 | 2.427
| SANDBANK | CT |  |  |  | 4.4416 | 4.3913 | 4.3228 | 4.1708 | 4.0064 | 3.86 | 3.7082 | 3.5724 | 3.4381 | 3.2631 | 2.9267 | 2.7203 | 2.469 | 2.3352 | 5.179 | 5.1459 | 5.102 | 5.0093 | 4.9079 | 4.8086 | 4.7049 | 4.6209 | 4.5283 | 4.4098 | 4.1811 | 4.0326 | 3.8318 | 3.6583 | 4.2594 | 4.2369 | 4.2134 | 4.1557 | 4.0558 | 3.9458 | 3.8183 | 3.6821 | 3.5552 | 3.3948 | 3.0773 | 2.8707 | 2.5828 | 2.427
| SANDBANK | LW |  |  |  | 4.4007 | 4.3287 | 4.2331 | 4.1121 | 3.9859 | 3.8651 | 3.698 | 3.5136 | 3.351 | 3.1806 | 2.8401 | 2.7816 | 2.5886 | 2.4385 | 5.159 | 5.1159 | 5.0579 | 4.9892 | 4.9161 | 4.8473 | 4.7471 | 4.6351 | 4.528 | 4.4148 | 4.19 | 4.1762 | 4.0146 | 3.8466 | 4.2518 | 4.2266 | 4.1907 | 4.1085 | 4.0285 | 3.9334 | 3.8114 | 3.6388 | 3.4931 | 3.3422 | 3.0135 | 2.9603 | 2.7352 | 2.5499
| SANDBANK | ST |  |  |  | 4.4719 | 4.4513 | 4.4254 | 4.3755 | 4.3167 | 4.2648 | 4.1824 | 4.1069 | 4.0105 | 3.9091 | 3.6725 | 3.1981 | 2.9648 | 2.7555 | 5.1957 | 5.1816 | 5.1644 | 5.1206 | 5.0754 | 5.0357 | 4.9644 | 4.91 | 4.8334 | 4.7619 | 4.5941 | 4.2618 | 4.0471 | 3.8245 | 4.2779 | 4.2735 | 4.268 | 4.2388 | 4.2119 | 4.1914 | 4.142 | 4.113 | 4.0643 | 3.9987 | 3.7626 | 3.287 | 3.0487 | 2.8385
| SANDBANK | FS |  |  |  | 4.4781 | 4.4629 | 4.4427 | 4.4063 | 4.3626 | 4.3168 | 4.267 | 4.2107 | 4.1368 | 4.0621 | 3.8924 | 3.4326 | 3.0236 | 2.9017 | 5.1991 | 5.1881 | 5.1739 | 5.1485 | 5.1184 | 5.0862 | 5.051 | 5.0118 | 4.9594 | 4.9068 | 4.7869 | 4.4886 | 4.178 | 3.9947 | 4.2798 | 4.2775 | 4.2737 | 4.2627 | 4.2498 | 4.2351 | 4.2193 | 4.2017 | 4.1747 | 4.1391 | 4.0044 | 3.5639 | 3.1685 | 3.0584
SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | NO | 4.72 | 4.72 | 4.72 | 4.7074 | 4.6989 | 4.6933 | 4.674 | 4.6686 | 4.6106 | 4.5901 | 4.5448 | 4.4143 | 4.0476 | 3.4481 | 3.2162 | 3.2088 | 3.1936 | 3.1762 | 3.1498 | 3.1187 | 3.0858 | 3.0667 | 3.0074 | 2.9397 | 2.8119 | 2.5694 | 2.088 | 1.3386 | 3.2423 | 3.2333 | 3.2144 | 3.1942 | 3.1626 | 3.1286 | 3.0925 | 3.0704 | 3.007 | 2.9296 | 2.7865 | 2.5392 | 2.046 | 1.2967
| SANDWICK | CT |  |  |  | 4.72 | 4.72 | 4.72 | 4.7184 | 4.7155 | 4.7015 | 4.6866 | 4.6828 | 4.6564 | 4.63 | 4.5819 | 4.4484 | 4.2466 | 4.0087 | 3.2172 | 3.2108 | 3.1989 | 3.1762 | 3.1498 | 3.1187 | 3.0858 | 3.0667 | 3.0089 | 2.9397 | 2.8119 | 2.5938 | 2.328 | 2.0151 | 3.2438 | 3.2361 | 3.2216 | 3.1942 | 3.1626 | 3.1286 | 3.0925 | 3.0704 | 3.007 | 2.9296 | 2.7865 | 2.5594 | 2.2963 | 1.9603
| SANDWICK | LW |  |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.6916 | 4.6622 | 4.6108 | 4.4676 | 4.0476 | 3.4481 | 3.2162 | 3.2088 | 3.1936 | 3.1806 | 3.1649 | 3.153 | 3.1286 | 3.0998 | 3.031 | 2.9585 | 2.8248 | 2.6161 | 2.088 | 1.3386 | 3.2423 | 3.2333 | 3.2144 | 3.1983 | 3.179 | 3.1643 | 3.1341 | 3.0985 | 3.0218 | 2.9408 | 2.7908 | 2.5749 | 2.046 | 1.2967
| SANDWICK | ST |  |  |  | 4.72 | 4.72 | 4.72 | 4.7074 | 4.6989 | 4.6933 | 4.674 | 4.6686 | 4.6106 | 4.5901 | 4.5448 | 4.4143 | 4.1034 | 3.7595 | 3.217 | 3.2139 | 3.2092 | 3.1872 | 3.168 | 3.1521 | 3.1168 | 3.0966 | 3.0074 | 2.9614 | 2.8556 | 2.5694 | 2.1568 | 1.7176 | 3.2436 | 3.2398 | 3.2344 | 3.2111 | 3.1901 | 3.1723 | 3.1346 | 3.1115 | 3.0187 | 2.9682 | 2.8516 | 2.5392 | 2.127 | 1.6965
| SANDWICK | FS |  |  |  | 4.72 | 4.72 | 4.72 | 4.7174 | 4.7149 | 4.7119 | 4.7089 | 4.7063 | 4.6853 | 4.6711 | 4.6426 | 4.6253 | 4.6079 | 4.5695 | 3.2173 | 3.2146 | 3.2107 | 3.2024 | 3.1925 | 3.1821 | 3.1702 | 3.1574 | 3.1196 | 3.0885 | 3.021 | 2.8988 | 2.7843 | 2.7213 | 3.244 | 3.2408 | 3.2363 | 3.227 | 3.2157 | 3.204 | 3.1905 | 3.1757 | 3.1356 | 3.1018 | 3.0277 | 2.8857 | 2.7581 | 2.7092
SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | NO | -3.3548 | -3.4354 | -3.5419 | -3.6819 | -3.8276 | -3.9749 | -4.1428 | -4.3278 | -4.477 | -4.6264 | -4.9249 | -5.0571 | -5.502 | -6.0415 | -1.6519 | -1.6744 | -1.7086 | -1.7436 | -1.7882 | -1.8273 | -1.8692 | -1.9299 | -2.0188 | -2.1123 | -2.2919 | -2.4154 | -2.903 | -3.5544 | -4.1763 | -4.2531 | -4.3644 | -4.4968 | -4.6414 | -4.7904 | -4.9471 | -5.1493 | -5.3407 | -5.5378 | -5.9246 | -6.1191 | -6.6446 | -7.3074
| SCALLOWAY | CT |  |  |  | -3.3076 | -3.3621 | -3.4384 | -3.6239 | -3.8155 | -3.9749 | -4.1428 | -4.3075 | -4.4193 | -4.5517 | -4.8183 | -4.9436 | -5.2716 | -5.5476 | -1.6435 | -1.6648 | -1.6933 | -1.7436 | -1.7882 | -1.8273 | -1.869 | -1.9115 | -1.9782 | -2.0436 | -2.1801 | -2.374 | -2.7208 | -3.1263 | -4.1364 | -4.19 | -4.2702 | -4.4512 | -4.6414 | -4.7904 | -4.9471 | -5.1014 | -5.244 | -5.4226 | -5.7724 | -5.9916 | -6.345 | -6.6714
| SCALLOWAY | LW |  |  |  | -3.3548 | -3.4354 | -3.5419 | -3.6819 | -3.8276 | -3.9601 | -4.1365 | -4.3278 | -4.477 | -4.6264 | -4.9249 | -5.0571 | -5.502 | -6.0415 | -1.6519 | -1.6744 | -1.7086 | -1.7431 | -1.7809 | -1.8158 | -1.8692 | -1.9299 | -2.0188 | -2.1123 | -2.2919 | -2.4154 | -2.903 | -3.5544 | -4.1763 | -4.2531 | -4.3644 | -4.4968 | -4.6383 | -4.764 | -4.9467 | -5.1493 | -5.3407 | -5.5378 | -5.9246 | -6.1191 | -6.6446 | -7.3074
| SCALLOWAY | ST |  |  |  | -3.2543 | -3.271 | -3.2968 | -3.3309 | -3.3733 | -3.4157 | -3.4661 | -3.5245 | -3.6417 | -3.7428 | -3.9752 | -4.4552 | -4.8212 | -5.17 | -1.6365 | -1.6451 | -1.6561 | -1.6708 | -1.6889 | -1.7081 | -1.7314 | -1.759 | -1.846 | -1.904 | -2.0393 | -2.1729 | -2.6327 | -3.1436 | -4.0952 | -4.1158 | -4.1445 | -4.1827 | -4.2311 | -4.2812 | -4.3412 | -4.4117 | -4.554 | -4.6773 | -4.9643 | -5.5712 | -6.0149 | -6.4511
| SCALLOWAY | FS |  |  |  | -3.2549 | -3.2716 | -3.2906 | -3.335 | -3.3816 | -3.4264 | -3.4791 | -3.5364 | -3.6126 | -3.6906 | -3.8536 | -4.2889 | -4.6331 | -4.7319 | -1.6358 | -1.6432 | -1.6521 | -1.6666 | -1.6828 | -1.699 | -1.7182 | -1.7397 | -1.7826 | -1.8218 | -1.9075 | -1.9132 | -2.3089 | -2.5882 | -4.0959 | -4.1143 | -4.1363 | -4.1804 | -4.2291 | -4.277 | -4.3335 | -4.3963 | -4.4846 | -4.5753 | -4.7716 | -5.2865 | -5.715 | -5.8102
TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0.047369 | 0.045586 | 0.042977 | 0.043546 | 0.040539 | 0.037962 | 0.036838 | 0.030815 | 0.029414 | 0.028905 | 0.024121 | 0.021152 | 0.020333 | 0.018566 | 0.064683 | 0.063671 | 0.0623 | 0.062287 | 0.060496 | 0.059214 | 0.058364 | 0.055886 | 0.053914 | 0.052426 | 0.048676 | 0.046943 | 0.046315 | 0.045446 | 0.057555 | 0.055757 | 0.053282 | 0.053781 | 0.050863 | 0.048551 | 0.047462 | 0.0421 | 0.040487 | 0.039342 | 0.034717 | 0.031926 | 0.031023 | 0.029218
| SCAMMADALE | CT |  |  |  | 0.047387 | 0.047112 | 0.047541 | 0.044797 | 0.040539 | 0.037962 | 0.037167 | 0.030815 | 0.029414 | 0.030432 | 0.025895 | 0.021152 | 0.020391 | 0.018566 | 0.064733 | 0.064451 | 0.064439 | 0.062802 | 0.060496 | 0.059214 | 0.058478 | 0.055886 | 0.054732 | 0.053699 | 0.050078 | 0.046943 | 0.04636 | 0.045446 | 0.057633 | 0.057224 | 0.057507 | 0.054938 | 0.050863 | 0.048551 | 0.047728 | 0.0421 | 0.040707 | 0.04088 | 0.03645 | 0.031926 | 0.031079 | 0.029218
| SCAMMADALE | LW |  |  |  | 0.047369 | 0.045586 | 0.042977 | 0.043546 | 0.042355 | 0.040075 | 0.036838 | 0.035186 | 0.029592 | 0.028905 | 0.024121 | 0.022078 | 0.020333 | 0.020333 | 0.064683 | 0.063671 | 0.0623 | 0.062287 | 0.061417 | 0.060226 | 0.058364 | 0.056825 | 0.053914 | 0.052426 | 0.048676 | 0.047156 | 0.046315 | 0.046315 | 0.057555 | 0.055757 | 0.053282 | 0.053781 | 0.052515 | 0.050403 | 0.047462 | 0.045559 | 0.040487 | 0.039342 | 0.034717 | 0.032828 | 0.031023 | 0.031023
| SCAMMADALE | ST |  |  |  | 0.047395 | 0.047316 | 0.04703 | 0.047854 | 0.047315 | 0.047937 | 0.045832 | 0.043568 | 0.042445 | 0.038495 | 0.036359 | 0.025152 | 0.0249 | 0.026079 | 0.064729 | 0.064595 | 0.064403 | 0.064687 | 0.064264 | 0.064248 | 0.063112 | 0.061852 | 0.06097 | 0.058862 | 0.056683 | 0.049017 | 0.048333 | 0.048754 | 0.057624 | 0.057426 | 0.057141 | 0.057818 | 0.057281 | 0.057755 | 0.055823 | 0.053692 | 0.052603 | 0.048824 | 0.046643 | 0.03575 | 0.035291 | 0.036326
| SCAMMADALE | FS |  |  |  | 0.047403 | 0.047343 | 0.047132 | 0.048035 | 0.04625 | 0.045659 | 0.045132 | 0.044504 | 0.043738 | 0.042846 | 0.037967 | 0.028373 | 0.022319 | 0.023641 | 0.064742 | 0.06463 | 0.064472 | 0.064825 | 0.063865 | 0.063452 | 0.063078 | 0.062587 | 0.061986 | 0.061287 | 0.058491 | 0.052037 | 0.047327 | 0.047849 | 0.057642 | 0.057478 | 0.057243 | 0.057998 | 0.056384 | 0.055721 | 0.055209 | 0.054601 | 0.053859 | 0.052994 | 0.048258 | 0.038848 | 0.032894 | 0.03418
ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | NO | 9.7728 | 9.5503 | 9.2789 | 8.7055 | 8.072 | 7.3735 | 6.5828 | 5.8258 | 5.2382 | 4.603 | 3.3231 | 2.2034 | 1.5351 | 1.3214 | 10.76 | 10.6371 | 10.4661 | 10.1305 | 9.7439 | 9.2813 | 8.7235 | 8.2269 | 7.8504 | 7.4515 | 6.6541 | 6.3117 | 5.9982 | 5.6834 | 10.1605 | 9.9641 | 9.7051 | 9.1839 | 8.6012 | 7.938 | 7.1571 | 6.4235 | 5.8508 | 5.2492 | 4.0432 | 3.2132 | 2.6487 | 2.449
| SCONE | CT |  |  |  | 9.9575 | 9.8266 | 9.6494 | 9.1576 | 8.631 | 8.0599 | 7.482 | 6.9666 | 6.3723 | 5.7132 | 4.3709 | 3.0683 | 2.1047 | 1.5851 | 10.8312 | 10.7383 | 10.6029 | 10.3168 | 9.9984 | 9.6287 | 9.2513 | 8.9656 | 8.6313 | 8.2398 | 7.45 | 6.8745 | 6.2812 | 5.6834 | 10.307 | 10.1869 | 10.0113 | 9.56 | 9.0685 | 8.5329 | 7.9867 | 7.5264 | 6.9847 | 6.375 | 5.1453 | 4.0884 | 3.2928 | 2.8578
| SCONE | LW |  |  |  | 9.7728 | 9.5503 | 9.2789 | 8.7055 | 8.072 | 7.3735 | 6.5828 | 5.8258 | 5.2382 | 4.603 | 3.3231 | 2.2034 | 1.5351 | 1.3214 | 10.76 | 10.6371 | 10.4661 | 10.1305 | 9.7439 | 9.2813 | 8.7235 | 8.2269 | 7.8504 | 7.4515 | 6.6541 | 6.3117 | 5.9982 | 5.8552 | 10.1605 | 9.9641 | 9.7051 | 9.1839 | 8.6012 | 7.938 | 7.1571 | 6.4235 | 5.8508 | 5.2492 | 4.0432 | 3.2132 | 2.6487 | 2.449
| SCONE | ST |  |  |  | 10.028 | 9.9474 | 9.8487 | 9.6359 | 9.4361 | 9.2486 | 8.9462 | 8.7142 | 8.4766 | 8.211 | 7.5895 | 6.4796 | 5.684 | 4.7796 | 10.8574 | 10.7957 | 10.7211 | 10.5161 | 10.3325 | 10.1683 | 9.8725 | 9.6863 | 9.5092 | 9.3134 | 8.8484 | 8.0533 | 7.4576 | 6.7121 | 10.3568 | 10.2837 | 10.1929 | 9.9653 | 9.755 | 9.5613 | 9.2334 | 9.0112 | 8.7917 | 8.5464 | 7.9685 | 6.9352 | 6.2465 | 5.4532
| SCONE | FS |  |  |  | 10.0969 | 10.0301 | 9.9469 | 9.8043 | 9.6537 | 9.4937 | 9.3266 | 9.1419 | 8.918 | 8.6795 | 8.1492 | 6.854 | 5.5253 | 4.7262 | 10.9157 | 10.8627 | 10.7962 | 10.6878 | 10.5711 | 10.4443 | 10.3082 | 10.1636 | 10.0082 | 9.8399 | 9.4532 | 8.5221 | 7.3657 | 6.2597 | 10.4153 | 10.3548 | 10.2781 | 10.1454 | 10.0018 | 9.8478 | 9.6835 | 9.5085 | 9.313 | 9.1033 | 8.6304 | 7.488 | 6.281 | 5.5858
THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | NO | 0.69707 | 0.68683 | 0.67466 | 0.66198 | 0.64375 | 0.6168 | 0.59366 | 0.57314 | 0.53986 | 0.49806 | 0.42502 | 0.28085 | -0.13031 | -0.70453 | 0.75251 | 0.74753 | 0.7406 | 0.73385 | 0.72007 | 0.6996 | 0.67994 | 0.66766 | 0.61721 | 0.58669 | 0.51113 | 0.33051 | -0.16501 | -0.87976 | 0.59368 | 0.58543 | 0.57756 | 0.56831 | 0.55264 | 0.5243 | 0.49901 | 0.47821 | 0.44039 | 0.39971 | 0.32633 | 0.21415 | -0.29644 | -1.0132
| SHAPINSAY | CT |  |  |  | 0.70071 | 0.69651 | 0.6854 | 0.66696 | 0.64375 | 0.6168 | 0.59366 | 0.57314 | 0.53986 | 0.49806 | 0.42502 | 0.29018 | 0.080219 | -0.15434 | 0.75403 | 0.7514 | 0.74524 | 0.73408 | 0.72007 | 0.6996 | 0.67994 | 0.66766 | 0.63008 | 0.5876 | 0.51113 | 0.34763 | 0.098816 | -0.19101 | 0.59724 | 0.59464 | 0.58681 | 0.5724 | 0.55264 | 0.5243 | 0.49901 | 0.47821 | 0.44039 | 0.39971 | 0.32633 | 0.22163 | -0.034105 | -0.3231
| SHAPINSAY | LW |  |  |  | 0.69707 | 0.68683 | 0.67466 | 0.66198 | 0.64699 | 0.63187 | 0.61587 | 0.59402 | 0.5537 | 0.50864 | 0.42938 | 0.28085 | -0.13031 | -0.70453 | 0.75251 | 0.74753 | 0.7406 | 0.73385 | 0.72585 | 0.71828 | 0.70846 | 0.69579 | 0.65131 | 0.60379 | 0.51972 | 0.34001 | -0.16501 | -0.87976 | 0.59368 | 0.58543 | 0.57756 | 0.56831 | 0.5561 | 0.54158 | 0.52758 | 0.50825 | 0.46305 | 0.41365 | 0.32642 | 0.21415 | -0.29644 | -1.0132
| SHAPINSAY | ST |  |  |  | 0.70349 | 0.70232 | 0.69892 | 0.68507 | 0.67325 | 0.66554 | 0.6437 | 0.63475 | 0.5705 | 0.54182 | 0.47425 | 0.30162 | -0.0081067 | -0.34466 | 0.75504 | 0.75408 | 0.75206 | 0.73858 | 0.7279 | 0.72026 | 0.69908 | 0.69045 | 0.61721 | 0.58669 | 0.51714 | 0.33051 | -0.048057 | -0.46329 | 0.60039 | 0.60057 | 0.5984 | 0.58407 | 0.5736 | 0.56602 | 0.54138 | 0.53154 | 0.45489 | 0.42204 | 0.34576 | 0.22037 | -0.16005 | -0.57906
| SHAPINSAY | FS |  |  |  | 0.70362 | 0.70246 | 0.70232 | 0.69548 | 0.68802 | 0.67901 | 0.67223 | 0.66355 | 0.63533 | 0.61531 | 0.57159 | 0.49851 | 0.43739 | 0.39319 | 0.75514 | 0.75423 | 0.75354 | 0.74868 | 0.74333 | 0.73713 | 0.73155 | 0.72525 | 0.696 | 0.67494 | 0.63056 | 0.57475 | 0.52293 | 0.4706 | 0.60043 | 0.60003 | 0.60116 | 0.59508 | 0.58891 | 0.58151 | 0.57561 | 0.56665 | 0.53429 | 0.51197 | 0.46312 | 0.44168 | 0.40459 | 0.35124
BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | NO | 0.29332 | 0.27747 | 0.25162 | 0.22717 | 0.19967 | 0.17149 | 0.13503 | 0.10343 | 0.079022 | 0.056764 | 0.0114 | -0.016993 | -0.042804 | -0.059796 | 0.57426 | 0.56433 | 0.54768 | 0.53306 | 0.51068 | 0.49314 | 0.47453 | 0.44848 | 0.42026 | 0.39089 | 0.33409 | 0.31606 | 0.29447 | 0.27559 | 0.25758 | 0.25361 | 0.24798 | 0.23052 | 0.20631 | 0.18087 | 0.14742 | 0.11794 | 0.087125 | 0.05096 | -0.018872 | -0.040396 | -0.066817 | -0.0847
| SHIELDAIG | CT |  |  |  | 0.29392 | 0.29044 | 0.28042 | 0.24197 | 0.20712 | 0.17448 | 0.13932 | 0.10601 | 0.08838 | 0.069972 | 0.032335 | -0.0060408 | -0.042804 | -0.059796 | 0.57799 | 0.56999 | 0.55815 | 0.5346 | 0.51068 | 0.49314 | 0.47453 | 0.45637 | 0.43534 | 0.40661 | 0.3517 | 0.31679 | 0.29447 | 0.27559 | 0.25758 | 0.25361 | 0.24798 | 0.23902 | 0.21219 | 0.18274 | 0.15105 | 0.12097 | 0.10401 | 0.072025 | 0.0066231 | -0.028932 | -0.066817 | -0.0847
| SHIELDAIG | LW |  |  |  | 0.29332 | 0.27747 | 0.25162 | 0.22717 | 0.19967 | 0.17149 | 0.13503 | 0.10343 | 0.079022 | 0.056764 | 0.0114 | -0.016993 | -0.036778 | -0.041761 | 0.57426 | 0.56433 | 0.54768 | 0.53306 | 0.51596 | 0.50091 | 0.4755 | 0.44848 | 0.42026 | 0.39089 | 0.33409 | 0.31606 | 0.30763 | 0.30581 | 0.2578 | 0.25453 | 0.24805 | 0.23052 | 0.20631 | 0.18087 | 0.14742 | 0.11794 | 0.087125 | 0.05096 | -0.018872 | -0.040396 | -0.061014 | -0.066386
| SHIELDAIG | ST |  |  |  | 0.29388 | 0.29226 | 0.28995 | 0.28682 | 0.27419 | 0.26131 | 0.24915 | 0.23353 | 0.21471 | 0.1955 | 0.14695 | 0.042978 | 0.0053512 | -0.010837 | 0.57944 | 0.57435 | 0.57068 | 0.56332 | 0.55426 | 0.54496 | 0.53445 | 0.52148 | 0.50557 | 0.48709 | 0.44178 | 0.34122 | 0.31372 | 0.29793 | 0.25867 | 0.2571 | 0.25562 | 0.25358 | 0.25039 | 0.24702 | 0.24276 | 0.23581 | 0.21828 | 0.20018 | 0.14652 | 0.019166 | -0.020453 | -0.038011
| SHIELDAIG | FS |  |  |  | 0.29404 | 0.29269 | 0.29078 | 0.28828 | 0.28494 | 0.27455 | 0.26787 | 0.25094 | 0.23681 | 0.21993 | 0.18467 | 0.085065 | -0.01308 | -0.027792 | 0.58064 | 0.57735 | 0.57322 | 0.56774 | 0.56063 | 0.55266 | 0.54556 | 0.53478 | 0.52346 | 0.51019 | 0.47968 | 0.38649 | 0.30565 | 0.2861 | 0.25862 | 0.25775 | 0.25653 | 0.25519 | 0.25285 | 0.25027 | 0.24791 | 0.24413 | 0.23882 | 0.2233 | 0.19047 | 0.061556 | -0.037912 | -0.053347
SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 2.8691 | 2.8454 | 2.8108 | 2.7743 | 2.7361 | 2.7018 | 2.6562 | 2.6081 | 2.5823 | 2.549 | 2.4931 | 2.4575 | 2.412 | 2.389 | 3.0058 | 2.9983 | 2.9867 | 2.9754 | 2.9564 | 2.9374 | 2.9146 | 2.8864 | 2.8641 | 2.8385 | 2.7917 | 2.7718 | 2.7468 | 2.7288 | 2.8207 | 2.8067 | 2.7859 | 2.7596 | 2.7316 | 2.7054 | 2.673 | 2.6395 | 2.6273 | 2.6099 | 2.5697 | 2.5325 | 2.495 | 2.4748
| SHIN | CT |  |  |  | 2.8894 | 2.8702 | 2.8492 | 2.7997 | 2.7518 | 2.7101 | 2.6667 | 2.6212 | 2.5994 | 2.5724 | 2.5113 | 2.4791 | 2.412 | 2.389 | 3.0104 | 3.003 | 2.9943 | 2.9784 | 2.957 | 2.9374 | 2.917 | 2.8958 | 2.8778 | 2.8542 | 2.8062 | 2.7775 | 2.7468 | 2.7288 | 2.8317 | 2.8187 | 2.8045 | 2.7755 | 2.7464 | 2.7145 | 2.6814 | 2.6464 | 2.6339 | 2.6254 | 2.5899 | 2.5508 | 2.495 | 2.4748
| SHIN | LW |  |  |  | 2.8691 | 2.8454 | 2.8108 | 2.7743 | 2.7361 | 2.7018 | 2.6562 | 2.6081 | 2.5823 | 2.549 | 2.4931 | 2.4575 | 2.4234 | 2.4131 | 3.0058 | 2.9983 | 2.9867 | 2.9754 | 2.9564 | 2.9401 | 2.9146 | 2.8864 | 2.8641 | 2.8385 | 2.7917 | 2.7718 | 2.7587 | 2.7549 | 2.8207 | 2.8067 | 2.7859 | 2.7596 | 2.7316 | 2.7054 | 2.673 | 2.6395 | 2.6273 | 2.6099 | 2.5697 | 2.5325 | 2.5041 | 2.4957
| SHIN | ST |  |  |  | 2.8951 | 2.8838 | 2.871 | 2.8522 | 2.8356 | 2.8184 | 2.7998 | 2.7729 | 2.7505 | 2.7224 | 2.6601 | 2.5353 | 2.4739 | 2.441 | 3.0119 | 3.0084 | 3.0041 | 2.9983 | 2.9925 | 2.986 | 2.9786 | 2.9658 | 2.9513 | 2.9335 | 2.8923 | 2.8035 | 2.7707 | 2.7515 | 2.8348 | 2.828 | 2.8199 | 2.8088 | 2.7985 | 2.7874 | 2.7751 | 2.7583 | 2.7434 | 2.7254 | 2.6845 | 2.5976 | 2.5463 | 2.5192
| SHIN | FS |  |  |  | 2.9047 | 2.8952 | 2.885 | 2.872 | 2.8563 | 2.8386 | 2.8217 | 2.8023 | 2.7819 | 2.7577 | 2.7075 | 2.5511 | 2.4491 | 2.4195 | 3.014 | 3.011 | 3.0077 | 3.0034 | 2.9984 | 2.9926 | 2.9866 | 2.9797 | 2.9694 | 2.9557 | 2.9255 | 2.8341 | 2.7599 | 2.7372 | 2.8396 | 2.8338 | 2.8275 | 2.8193 | 2.8101 | 2.7994 | 2.7885 | 2.7764 | 2.764 | 2.7493 | 2.7183 | 2.6243 | 2.5266 | 2.5024
FORT WILLIAM | SHONA BEAG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513
| SHONA BEAG | CT |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513
| SHONA BEAG | LW |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513
| SHONA BEAG | ST |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513
| SHONA BEAG | FS |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.10218 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513 | 0.099513
KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | NO | 15.6403 | 15.3093 | 14.8262 | 14.0935 | 13.2809 | 12.5129 | 11.5574 | 10.5157 | 9.5433 | 8.5369 | 6.5257 | 6.482 | 4.6984 | 3.6551 | 18.5461 | 18.4165 | 18.217 | 17.9535 | 17.531 | 17.1524 | 16.6187 | 16.0253 | 15.4211 | 14.769 | 13.4228 | 13.4587 | 12.1709 | 10.7904 | 16.395 | 16.1812 | 15.8196 | 15.4507 | 15.0126 | 14.5828 | 13.9626 | 13.0786 | 12.2109 | 11.3107 | 9.5139 | 9.4161 | 7.7692 | 6.8055
| SKENE | CT |  |  |  | 15.9223 | 15.7078 | 15.3961 | 14.662 | 13.8908 | 13.161 | 12.3996 | 11.6799 | 10.7476 | 9.7464 | 7.7287 | 6.482 | 4.6984 | 3.6551 | 18.5539 | 18.4165 | 18.217 | 17.9877 | 17.6343 | 17.1988 | 16.7366 | 16.3267 | 15.7731 | 15.1577 | 13.8697 | 13.4587 | 12.1709 | 10.7904 | 16.4829 | 16.2576 | 15.9465 | 15.4718 | 15.0457 | 14.5828 | 14.0787 | 13.6252 | 12.9967 | 12.3292 | 10.5122 | 9.4161 | 7.7692 | 6.8055
| SKENE | LW |  |  |  | 15.6403 | 15.3093 | 14.8262 | 14.0935 | 13.2809 | 12.5129 | 11.5574 | 10.5157 | 9.5433 | 8.5369 | 6.5257 | 6.7053 | 5.5039 | 4.7868 | 18.5461 | 18.4432 | 18.237 | 17.9535 | 17.531 | 17.1524 | 16.6187 | 16.0253 | 15.4211 | 14.769 | 13.4228 | 14.201 | 13.5249 | 12.9381 | 16.395 | 16.1812 | 15.8196 | 15.4507 | 15.0126 | 14.6077 | 13.9626 | 13.0786 | 12.2109 | 11.3107 | 9.5139 | 9.7432 | 8.5982 | 7.8544
| SKENE | ST |  |  |  | 15.9871 | 15.8679 | 15.6998 | 15.4594 | 15.1976 | 14.9341 | 14.5805 | 14.2454 | 13.8346 | 13.4014 | 12.3831 | 11.3116 | 9.6507 | 7.768 | 18.5682 | 18.4955 | 18.3935 | 18.2441 | 18.0875 | 17.9406 | 17.698 | 17.496 | 17.2066 | 16.8598 | 15.984 | 15.1324 | 13.8175 | 12.159 | 16.5221 | 16.4177 | 16.2756 | 16.067 | 15.8411 | 15.6093 | 15.2662 | 14.9454 | 14.5265 | 14.083 | 13.0007 | 13.796 | 12.2772 | 10.508
| SKENE | FS |  |  |  | 16.0775 | 15.9833 | 15.8516 | 15.6765 | 15.4778 | 15.2678 | 15.0274 | 14.7743 | 14.415 | 14.0416 | 13.2051 | 11.8657 | 9.859 | 8.3875 | 18.6387 | 18.5776 | 18.4945 | 18.4157 | 18.3227 | 18.2163 | 18.0952 | 17.9615 | 17.7334 | 17.4515 | 16.798 | 15.7772 | 13.8256 | 11.6332 | 16.5983 | 16.514 | 16.402 | 16.2739 | 16.1264 | 15.9588 | 15.7661 | 15.5532 | 15.2794 | 14.9863 | 14.3021 | 14.3797 | 12.6114 | 11.2719
BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | NO | -1.6844 | -1.8093 | -1.9564 | -2.059 | 4.2665 | 4.1602 | 4.0129 | 3.8589 | 3.7429 | 3.6232 | 3.4113 | 3.3336 | 3.247 | 3.2 | -0.77788 | -0.84056 | -0.92017 | -0.97312 | 4.8303 | 4.7675 | 4.6938 | 4.6086 | 4.5262 | 4.4395 | 4.2811 | 4.2134 | 4.138 | 4.0687 | -1.4017 | -1.5076 | -1.6329 | -1.7252 | 4.0439 | 3.9455 | 3.8124 | 3.6771 | 3.5789 | 3.4757 | 3.2923 | 3.2122 | 3.1276 | 3.0842
| SKULAMUS | CT |  |  |  | -1.6543 | -1.7534 | -1.8701 | -2.0082 | 4.2843 | 4.1602 | 4.0129 | 3.8636 | 3.7722 | 3.6525 | 3.4535 | 3.3564 | 3.247 | 3.2 | -0.76658 | -0.81831 | -0.88278 | -0.95806 | 4.8303 | 4.7675 | 4.6938 | 4.6195 | 4.5547 | 4.4669 | 4.3123 | 4.2134 | 4.138 | 4.0687 | -1.3737 | -1.4563 | -1.5545 | -1.6797 | 4.0586 | 3.9455 | 3.8124 | 3.6771 | 3.5984 | 3.4945 | 3.3224 | 3.2299 | 3.1276 | 3.0842
| SKULAMUS | LW |  |  |  | -1.6844 | -1.8093 | -1.9564 | -2.059 | 4.2665 | 4.1667 | 4.0185 | 3.8589 | 3.7429 | 3.6232 | 3.4113 | 3.3336 | 3.2819 | 3.2658 | -0.77788 | -0.84056 | -0.92017 | -0.97312 | 4.836 | 4.7852 | 4.7015 | 4.6086 | 4.5262 | 4.4395 | 4.2811 | 4.2257 | 4.2032 | 4.197 | -1.4017 | -1.5076 | -1.6329 | -1.7252 | 4.0439 | 3.9534 | 3.8212 | 3.679 | 3.5789 | 3.4757 | 3.2923 | 3.2122 | 3.1639 | 3.1488
| SKULAMUS | ST |  |  |  | -1.6385 | -1.7179 | -1.8024 | -1.84 | 4.5485 | 4.4993 | 4.4309 | 4.3565 | 4.2758 | 4.1879 | 4.0026 | 3.6124 | 3.5086 | 3.4545 | -0.76065 | -0.80106 | -0.84486 | -0.86647 | 4.9734 | 4.9434 | 4.9024 | 4.8565 | 4.8052 | 4.747 | 4.6186 | 4.33 | 4.2462 | 4.1814 | -1.3585 | -1.4238 | -1.4937 | -1.5266 | 4.3003 | 4.2575 | 4.199 | 4.135 | 4.066 | 3.991 | 3.8314 | 3.4788 | 3.3839 | 3.333
| SKULAMUS | FS |  |  |  | -1.6316 | -1.6962 | -1.7676 | -1.8064 | 4.5859 | 4.5403 | 4.4841 | 4.4262 | 4.3638 | 4.2945 | 4.1538 | 3.7586 | 3.4625 | 3.4144 | -0.75789 | -0.79198 | -0.83012 | -0.85134 | 4.9913 | 4.9647 | 4.9321 | 4.8972 | 4.8583 | 4.8145 | 4.7214 | 4.4524 | 4.212 | 4.1225 | -1.3525 | -1.4049 | -1.4631 | -1.4973 | 4.3335 | 4.2939 | 4.2451 | 4.1951 | 4.1412 | 4.0813 | 3.9585 | 3.6007 | 3.3387 | 3.2953
WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 4.2065 | 3.8498 | 3.3475 | 2.2976 | 1.0602 | -0.36187 | -2.0024 | -3.4342 | -4.422 | -5.469 | -7.5918 | -7.2042 | -8.3224 | -9.2281 | 10.4419 | 10.2492 | 9.9302 | 9.1926 | 8.2818 | 7.086 | 5.6845 | 4.576 | 3.8538 | 3.0779 | 1.5238 | 2.3096 | 1.3566 | -0.67094 | 9.8934 | 9.5761 | 9.1163 | 8.0735 | 6.8423 | 5.3365 | 3.6051 | 2.1568 | 1.2009 | 0.18526 | -1.9316 | -1.4128 | -2.5823 | -3.6259
| SPRINGHILL | CT |  |  |  | 4.4823 | 4.2067 | 3.8664 | 3.0469 | 2.1436 | 1.0811 | -0.023346 | -0.87346 | -1.7588 | -2.6981 | -4.6351 | -5.1309 | -6.6203 | -7.5165 | 10.5283 | 10.3249 | 10.061 | 9.5523 | 8.9559 | 8.1195 | 7.2344 | 6.6736 | 6.0687 | 5.4057 | 4.0135 | 3.7719 | 2.0273 | -0.3013 | 10.1341 | 9.8843 | 9.5701 | 8.81 | 7.9608 | 6.8811 | 5.7532 | 4.9501 | 4.1187 | 3.2332 | 1.4085 | 1.0595 | -0.32976 | -1.2099
| SPRINGHILL | LW |  |  |  | 4.2065 | 3.8498 | 3.3475 | 2.2976 | 1.0602 | -0.36187 | -2.0024 | -3.4342 | -4.422 | -5.469 | -7.5918 | -7.2042 | -8.3224 | -9.2281 | 10.4419 | 10.2492 | 9.9302 | 9.1926 | 8.2818 | 7.086 | 5.6845 | 4.576 | 3.8538 | 3.0779 | 1.5238 | 2.3096 | 1.3566 | 0.36729 | 9.8934 | 9.5761 | 9.1163 | 8.0735 | 6.8423 | 5.3365 | 3.6051 | 2.1568 | 1.2009 | 0.18526 | -1.9316 | -1.4128 | -2.5823 | -3.6259
| SPRINGHILL | ST |  |  |  | 4.5907 | 4.4018 | 4.1973 | 3.6743 | 3.1948 | 2.8152 | 2.0606 | 1.6188 | 1.151 | 0.69865 | -0.3809 | -1.149 | -2.825 | -4.4263 | 10.5949 | 10.4527 | 10.2923 | 9.7354 | 9.2568 | 8.8864 | 8.0549 | 7.6213 | 7.1637 | 6.7436 | 5.7322 | 4.8415 | 2.8737 | 0.27832 | 10.2353 | 10.0682 | 9.8851 | 9.3033 | 8.794 | 8.3999 | 7.5447 | 7.0897 | 6.6038 | 6.1376 | 5.0218 | 4.3149 | 2.75 | 1.263
| SPRINGHILL | FS |  |  |  | 4.8614 | 4.6951 | 4.5255 | 4.2651 | 3.9947 | 3.6953 | 3.3799 | 3.0454 | 2.6546 | 2.2534 | 1.3511 | 0.26103 | -1.6739 | -3.1392 | 10.7937 | 10.6579 | 10.5117 | 10.277 | 10.0253 | 9.7429 | 9.4368 | 9.1152 | 8.7646 | 8.3983 | 7.5396 | 6.2631 | 3.4761 | -0.67094 | 10.4804 | 10.3363 | 10.186 | 9.9323 | 9.6664 | 9.3701 | 9.0575 | 8.7297 | 8.3583 | 7.9793 | 7.1007 | 6.1771 | 4.4163 | 3.1455
BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | NO | 6.2387 | 6.132 | 6.0063 | 5.8719 | 5.731 | 5.5364 | 5.2728 | 5.0704 | 4.928 | 4.7645 | 4.4392 | 4.332 | 3.7615 | 2.9749 | 6.4871 | 6.4358 | 6.369 | 6.3021 | 6.1864 | 6.0569 | 5.8754 | 5.7579 | 5.6337 | 5.4845 | 5.198 | 5.011 | 4.4588 | 3.559 | 5.7078 | 5.6124 | 5.4963 | 5.3747 | 5.2365 | 5.0413 | 4.7894 | 4.6035 | 4.4507 | 4.2796 | 3.9402 | 3.782 | 3.1445 | 2.1867
| ST CYRUS | CT |  |  |  | 6.3056 | 6.2262 | 6.1311 | 5.94 | 5.7392 | 5.5364 | 5.2728 | 5.0704 | 4.928 | 4.7645 | 4.4392 | 4.332 | 3.8708 | 3.4826 | 6.5105 | 6.4685 | 6.4104 | 6.3035 | 6.1864 | 6.0569 | 5.8754 | 5.7579 | 5.6337 | 5.4845 | 5.198 | 5.011 | 4.5595 | 4.0611 | 5.7646 | 5.6927 | 5.6032 | 5.4255 | 5.2365 | 5.0413 | 4.7894 | 4.6035 | 4.4507 | 4.2796 | 3.9402 | 3.782 | 3.2893 | 2.8423
| ST CYRUS | LW |  |  |  | 6.2387 | 6.132 | 6.0063 | 5.8719 | 5.731 | 5.5902 | 5.3613 | 5.1544 | 4.9898 | 4.8091 | 4.4514 | 4.3734 | 3.7615 | 2.9749 | 6.4871 | 6.4358 | 6.369 | 6.3021 | 6.2288 | 6.1584 | 6.0109 | 5.8831 | 5.7383 | 5.5817 | 5.2775 | 5.1793 | 4.4968 | 3.559 | 5.7078 | 5.6124 | 5.4963 | 5.3747 | 5.2458 | 5.119 | 4.9046 | 4.7085 | 4.5362 | 4.3531 | 3.975 | 3.8678 | 3.1445 | 2.1867
| ST CYRUS | ST |  |  |  | 6.3587 | 6.3209 | 6.2781 | 6.1921 | 6.1053 | 6.0241 | 5.8487 | 5.7422 | 5.5692 | 5.4334 | 5.1304 | 4.624 | 4.0529 | 3.5139 | 6.5316 | 6.5117 | 6.4882 | 6.4184 | 6.3541 | 6.2965 | 6.1439 | 6.0622 | 5.8992 | 5.7911 | 5.537 | 5.0829 | 4.4588 | 3.797 | 5.8095 | 5.7754 | 5.7365 | 5.6473 | 5.56 | 5.4799 | 5.3006 | 5.1951 | 5.005 | 4.8688 | 4.5574 | 4.0198 | 3.3728 | 2.746
| ST CYRUS | FS |  |  |  | 6.3738 | 6.3462 | 6.3154 | 6.2586 | 6.1959 | 6.1322 | 6.026 | 5.9471 | 5.8375 | 5.7333 | 5.5103 | 5.042 | 4.6605 | 4.5123 | 6.5378 | 6.5225 | 6.5044 | 6.4697 | 6.4305 | 6.3889 | 6.3144 | 6.2567 | 6.1694 | 6.0892 | 5.9156 | 5.5939 | 5.2395 | 4.961 | 5.8225 | 5.7976 | 5.7694 | 5.7159 | 5.6565 | 5.5955 | 5.4955 | 5.4193 | 5.3073 | 5.2021 | 4.9813 | 4.5365 | 4.1647 | 4.0195
ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 09165377 | NO | YES | 32.2213 | 32.1746 | 32.1152 | 29.9903 | 27.6238 | 22.9597 | 17.9995 | 15.0984 | 14.3164 | 13.5134 | 12.0778 | 8.6323 | 7.3786 | 6.6811 | 32.0353 | 32.0294 | 32.0175 | 29.476 | 26.6382 | 20.9221 | 14.8609 | 11.3675 | 10.4661 | 9.533 | 7.8823 | 3.6912 | 2.2338 | 1.3917 | 32.0347 | 32.0275 | 32.0131 | 29.4695 | 26.6061 | 20.8127 | 14.6555 | 11.0706 | 10.1284 | 9.1571 | 7.4292 | 3.1645 | 1.6508 | 0.79538
| ST FERGUS GAS TERM | CT |  |  |  | 32.2655 | 32.2371 | 32.2039 | 31.8585 | 31.3244 | 29.147 | 26.8325 | 26.1703 | 25.7808 | 25.3858 | 24.6375 | 23.0277 | 22.3495 | 21.987 | 32.0359 | 32.0306 | 32.0209 | 31.7001 | 31.1413 | 28.5259 | 25.7371 | 25.0206 | 24.6587 | 24.2477 | 23.4786 | 21.6631 | 20.9853 | 20.5737 | 32.0355 | 32.0291 | 32.0175 | 31.6933 | 31.1309 | 28.5012 | 25.6412 | 24.8487 | 24.4 | 23.942 | 23.0832 | 21.1558 | 20.399 | 19.9859
| ST FERGUS GAS TERM | LW |  |  |  | 32.2213 | 32.1746 | 32.1152 | 29.9903 | 27.6238 | 22.9597 | 17.9995 | 15.0984 | 14.3164 | 13.5134 | 12.0778 | 8.6323 | 7.3786 | 6.6811 | 32.0353 | 32.0294 | 32.0175 | 29.476 | 26.6382 | 20.9221 | 14.8609 | 11.3675 | 10.4661 | 9.533 | 7.8823 | 3.6912 | 2.2338 | 1.3917 | 32.0347 | 32.0275 | 32.0131 | 29.4695 | 26.6061 | 20.8127 | 14.6555 | 11.0706 | 10.1284 | 9.1571 | 7.4292 | 3.1645 | 1.6508 | 0.79538
| ST FERGUS GAS TERM | ST |  |  |  | 32.2756 | 32.265 | 32.2446 | 30.3508 | 29.0565 | 28.1921 | 25.2807 | 24.4473 | 23.8029 | 23.5421 | 22.9647 | 21.418 | 20.5726 | 19.9717 | 32.0361 | 32.0333 | 32.0293 | 29.6819 | 28.0912 | 27.0372 | 23.4321 | 22.4208 | 21.6534 | 21.3701 | 20.7434 | 18.9853 | 18.1147 | 17.5182 | 32.0357 | 32.0325 | 32.0278 | 29.6796 | 28.0876 | 27.0323 | 23.4255 | 22.4121 | 21.642 | 21.3555 | 20.7208 | 18.8569 | 17.8778 | 17.2191
| ST FERGUS GAS TERM | FS |  |  |  | 32.2801 | 32.2705 | 32.259 | 31.8562 | 31.4492 | 30.9791 | 30.5015 | 30.0921 | 29.8341 | 29.6417 | 29.2472 | 28.8373 | 28.5067 | 28.2751 | 32.0363 | 32.034 | 32.0306 | 31.5474 | 31.0629 | 30.4987 | 29.9334 | 29.4464 | 29.164 | 28.9683 | 28.5728 | 28.2928 | 28.0508 | 27.8362 | 32.036 | 32.0333 | 32.0295 | 31.5456 | 31.0603 | 30.4951 | 29.9286 | 29.4402 | 29.1562 | 28.9587 | 28.5587 | 28.1533 | 27.8202 | 27.61
ST FILLANS | ST FILLANS P S | MINIMUM HEADROOM | NN 69422464 | YES | NO | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
| ST FILLANS P S | CT |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
| ST FILLANS P S | LW |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
| ST FILLANS P S | ST |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
| ST FILLANS P S | FS |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 14.6979 | 14.3456 | 13.9047 | 12.8958 | 11.8227 | 10.4693 | 8.9252 | 7.5564 | 6.752 | 5.8946 | 4.1692 | 5.5439 | 4.7196 | 4.1058 | 16.4465 | 16.2619 | 15.9771 | 15.3187 | 14.5886 | 13.5073 | 12.2133 | 11.1501 | 10.4546 | 9.6996 | 8.1936 | 10.2258 | 8.0806 | 1.4061 | 15.1761 | 14.8781 | 14.4625 | 13.5546 | 12.5667 | 11.2287 | 9.6496 | 8.2867 | 7.4176 | 6.48 | 4.6 | 6.5699 | 5.6977 | 4.9772
| ST MACHAR | CT |  |  |  | 15.0334 | 14.843 | 14.6205 | 13.803 | 12.9282 | 11.9103 | 10.855 | 10.0045 | 9.3391 | 8.651 | 7.2142 | 7.0646 | 5.3589 | 4.5978 | 16.4968 | 16.3228 | 16.0967 | 15.5972 | 15.0251 | 14.261 | 13.4464 | 12.8805 | 12.3345 | 11.7545 | 10.4918 | 10.5748 | 8.3262 | 4.9965 | 15.3925 | 15.2102 | 14.979 | 14.2866 | 13.5202 | 12.5842 | 11.6038 | 10.8771 | 10.2424 | 9.5761 | 8.1639 | 8.5654 | 7.025 | 6.3
| ST MACHAR | LW |  |  |  | 14.6979 | 14.3456 | 13.9047 | 12.8958 | 11.8227 | 10.4693 | 8.9252 | 7.5564 | 6.752 | 5.8946 | 4.1692 | 5.5439 | 4.7196 | 4.1058 | 16.4465 | 16.2619 | 15.9771 | 15.3187 | 14.5886 | 13.5073 | 12.2133 | 11.1501 | 10.4546 | 9.6996 | 8.1936 | 10.2258 | 9.5539 | 8.867 | 15.1761 | 14.8781 | 14.4625 | 13.5546 | 12.5667 | 11.2287 | 9.6496 | 8.2867 | 7.4176 | 6.48 | 4.6 | 6.5699 | 5.6977 | 4.9772
| ST MACHAR | ST |  |  |  | 15.134 | 15.0428 | 14.9343 | 14.5564 | 14.2324 | 13.9365 | 13.345 | 12.9867 | 12.6295 | 12.2753 | 11.4516 | 11.1042 | 9.5184 | 7.7111 | 16.539 | 16.4328 | 16.3016 | 15.8494 | 15.4635 | 15.1178 | 14.4034 | 13.9799 | 13.5524 | 13.1318 | 12.1314 | 11.4786 | 9.1129 | 5.5995 | 15.4704 | 15.3825 | 15.2725 | 14.8349 | 14.4659 | 14.1433 | 13.4541 | 13.0581 | 12.6593 | 12.2685 | 11.3491 | 11.3783 | 10.1291 | 8.4453
| ST MACHAR | FS |  |  |  | 15.1826 | 15.1141 | 15.0339 | 14.8405 | 14.6371 | 14.4041 | 14.1509 | 13.8839 | 13.5579 | 13.2236 | 12.4826 | 11.6427 | 9.9222 | 8.3922 | 16.5524 | 16.4473 | 16.3198 | 16.0996 | 15.8542 | 15.5751 | 15.2616 | 14.9229 | 14.561 | 14.1698 | 13.2486 | 11.806 | 8.0806 | 1.4061 | 15.505 | 15.4362 | 15.3511 | 15.1575 | 14.947 | 14.7102 | 14.4516 | 14.1769 | 13.8669 | 13.5448 | 12.8175 | 12.463 | 11.1031 | 9.9464
THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | NO | -1.5866 | -1.6638 | -1.763 | -1.8949 | 2.1265 | 1.9551 | 1.7827 | 1.6064 | 1.5303 | 1.4229 | 1.1841 | 1.2097 | 1.1083 | 1.038 | -0.85749 | -0.88495 | -0.92591 | -0.97689 | 3.1764 | 3.137 | 3.0938 | 3.0482 | 2.9917 | 2.9289 | 2.7666 | 2.9771 | 2.9287 | 2.8823 | -1.1513 | -1.2065 | -1.2664 | -1.3605 | 2.7223 | 2.5918 | 2.4605 | 2.3247 | 2.2996 | 2.2539 | 2.0913 | 2.0448 | 1.9668 | 1.9081
| ST MARYS | CT |  |  |  | -1.5479 | -1.6031 | -1.679 | -1.8716 | 2.1265 | 1.9551 | 1.7827 | 1.6064 | 1.5303 | 1.4229 | 1.2166 | 1.2594 | 1.1083 | 1.038 | -0.85749 | -0.88495 | -0.92591 | -0.97689 | 3.1764 | 3.137 | 3.0938 | 3.0482 | 2.9917 | 2.9388 | 2.8225 | 2.9896 | 2.9287 | 2.8823 | -1.1196 | -1.1605 | -1.2072 | -1.3427 | 2.7223 | 2.5918 | 2.4605 | 2.3247 | 2.2996 | 2.2539 | 2.1242 | 2.0863 | 1.9668 | 1.9081
| ST MARYS | LW |  |  |  | -1.5866 | -1.6638 | -1.763 | -1.8949 | 2.1628 | 2.028 | 1.8552 | 1.6635 | 1.5542 | 1.4261 | 1.1841 | 1.2097 | 1.1265 | 1.0914 | -0.85721 | -0.87831 | -0.9114 | -0.9384 | 3.2302 | 3.199 | 3.1452 | 3.0811 | 3.0086 | 2.9289 | 2.7666 | 2.9771 | 2.9486 | 2.9373 | -1.1513 | -1.2065 | -1.2664 | -1.3605 | 2.7416 | 2.6419 | 2.5331 | 2.4155 | 2.3675 | 2.2795 | 2.0913 | 2.0448 | 1.9787 | 1.9521
| ST MARYS | ST |  |  |  | -1.5187 | -1.5432 | -1.5755 | -1.6174 | 2.5321 | 2.4757 | 2.4165 | 2.3464 | 2.258 | 2.1598 | 1.9274 | 1.5641 | 1.4236 | 1.343 | -0.85203 | -0.86126 | -0.87248 | -0.88759 | 3.2929 | 3.269 | 3.2394 | 3.2031 | 3.1579 | 3.1028 | 2.9657 | 3.0828 | 3.0071 | 2.9652 | -1.09 | -1.1055 | -1.1253 | -1.1495 | 3.0226 | 2.9905 | 2.9592 | 2.9221 | 2.877 | 2.8009 | 2.6107 | 2.319 | 2.1983 | 2.1333
| ST MARYS | FS |  |  |  | -1.5073 | -1.5259 | -1.5547 | -1.5938 | 2.5615 | 2.5106 | 2.4618 | 2.4035 | 2.3355 | 2.2631 | 2.0969 | 1.6692 | 1.3205 | 1.2532 | -0.85019 | -0.85698 | -0.86533 | -0.87641 | 3.3099 | 3.2939 | 3.2749 | 3.2525 | 3.2257 | 3.1947 | 3.1197 | 3.1943 | 2.9854 | 2.9425 | -1.0814 | -1.0929 | -1.1116 | -1.136 | 3.0373 | 3.0054 | 2.9775 | 2.9437 | 2.9065 | 2.868 | 2.766 | 2.4245 | 2.1268 | 2.0757
WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | YES | 16.9504 | 16.8759 | 16.7063 | 16.5908 | 16.3952 | 16.2016 | 15.935 | 15.6259 | 15.3374 | 15.024 | 14.3863 | 15.4579 | 15.0301 | 14.4787 | 18.0446 | 17.9755 | 17.8354 | 17.7075 | 17.5677 | 17.443 | 17.3036 | 17.153 | 16.9693 | 16.733 | 16.2189 | 15.8075 | 13.3881 | 8.9049 | 17.3291 | 17.2832 | 17.1567 | 17.0482 | 16.8853 | 16.713 | 16.4777 | 16.2055 | 15.9447 | 15.6619 | 15.0889 | 15.9834 | 15.4744 | 14.8033
| ST NICHOLAS | CT |  |  |  | 16.9715 | 16.9133 | 16.7516 | 16.6339 | 16.4537 | 16.2547 | 16.0335 | 15.7977 | 15.5835 | 15.361 | 14.9023 | 15.4579 | 15.0337 | 14.7069 | 18.0446 | 17.9755 | 17.8354 | 17.7075 | 17.5677 | 17.443 | 17.3036 | 17.153 | 16.9693 | 16.733 | 16.2189 | 15.9975 | 14.5103 | 12.1593 | 17.3291 | 17.2832 | 17.1567 | 17.0832 | 16.9286 | 16.7511 | 16.5555 | 16.3477 | 16.1532 | 15.9516 | 15.5374 | 15.9951 | 15.5565 | 15.1953
| ST NICHOLAS | LW |  |  |  | 16.9504 | 16.8759 | 16.7063 | 16.5908 | 16.3952 | 16.2016 | 15.935 | 15.6259 | 15.3374 | 15.024 | 14.3863 | 15.4619 | 15.0301 | 14.4787 | 18.0494 | 17.9911 | 17.8671 | 17.7906 | 17.7084 | 17.6259 | 17.5106 | 17.3764 | 17.2255 | 16.9907 | 16.4884 | 17.1727 | 16.6934 | 16.0358 | 17.332 | 17.2845 | 17.1678 | 17.0482 | 16.8853 | 16.713 | 16.4777 | 16.2055 | 15.9447 | 15.6619 | 15.0889 | 15.9834 | 15.4744 | 14.8033
| ST NICHOLAS | ST |  |  |  | 17.0004 | 16.9701 | 16.8665 | 16.8574 | 16.8424 | 16.8146 | 16.7664 | 16.706 | 16.5992 | 16.5076 | 16.1836 | 16.4458 | 16.0304 | 15.4863 | 18.0631 | 18.0154 | 17.9173 | 17.8751 | 17.8238 | 17.7621 | 17.6861 | 17.5952 | 17.4465 | 17.3172 | 16.878 | 16.3592 | 14.7846 | 12.2773 | 17.3375 | 17.3078 | 17.2297 | 17.2147 | 17.1937 | 17.1651 | 17.1242 | 17.0711 | 16.9599 | 16.8708 | 16.6557 | 16.8981 | 16.4426 | 15.8518
| ST NICHOLAS | FS |  |  |  | 17.0035 | 16.9748 | 16.8915 | 16.8763 | 16.8551 | 16.8316 | 16.804 | 16.7752 | 16.7239 | 16.6569 | 16.4309 | 16.5484 | 16.2078 | 15.9183 | 18.0631 | 18.0111 | 17.9218 | 17.8664 | 17.8005 | 17.7273 | 17.6414 | 17.5464 | 17.4202 | 17.2865 | 16.8258 | 15.8075 | 13.3881 | 8.9049 | 17.3415 | 17.3143 | 17.2432 | 17.23 | 17.2137 | 17.1922 | 17.1674 | 17.1394 | 17.0876 | 17.0369 | 16.9183 | 17.0226 | 16.7191 | 16.446
ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | NO | -0.030827 | -0.049063 | -0.090899 | -0.1231 | -0.15983 | -0.19877 | -0.24004 | -0.27968 | -0.30404 | -0.33241 | -0.38951 | -0.39182 | -0.41594 | -0.43569 | 0.46797 | 0.45967 | 0.43252 | 0.41731 | 0.39749 | 0.377 | 0.3556 | 0.33167 | 0.3067 | 0.28057 | 0.22921 | 0.22417 | 0.20326 | 0.18385 | 0.45004 | 0.44135 | 0.41668 | 0.40192 | 0.38929 | 0.37715 | 0.33986 | 0.3032 | 0.27188 | 0.23999 | 0.17648 | 0.16591 | 0.14567 | 0.1277
| STOCKINISH | CT |  |  |  | -0.020589 | -0.034124 | -0.064805 | -0.10945 | -0.15983 | -0.19877 | -0.24004 | -0.27968 | -0.30126 | -0.32878 | -0.38154 | -0.37808 | -0.41594 | -0.43569 | 0.46834 | 0.45967 | 0.43252 | 0.41731 | 0.39749 | 0.377 | 0.3556 | 0.33447 | 0.31533 | 0.28947 | 0.23994 | 0.22565 | 0.20326 | 0.18385 | 0.45007 | 0.44135 | 0.41668 | 0.40192 | 0.38929 | 0.37715 | 0.33986 | 0.30382 | 0.28019 | 0.24886 | 0.1892 | 0.1789 | 0.14567 | 0.1277
| STOCKINISH | LW |  |  |  | -0.030827 | -0.049063 | -0.090899 | -0.1231 | -0.15635 | -0.1895 | -0.23285 | -0.27558 | -0.30404 | -0.33241 | -0.38951 | -0.39182 | -0.40916 | -0.41536 | 0.46797 | 0.46209 | 0.43344 | 0.42165 | 0.40338 | 0.38597 | 0.3594 | 0.33167 | 0.3067 | 0.28057 | 0.22921 | 0.22417 | 0.21676 | 0.2146 | 0.45004 | 0.44446 | 0.41879 | 0.40944 | 0.40035 | 0.38653 | 0.34498 | 0.3032 | 0.27188 | 0.23999 | 0.17648 | 0.16591 | 0.15078 | 0.14566
| STOCKINISH | ST |  |  |  | -0.013335 | -0.016914 | -0.033696 | -0.048963 | -0.064178 | -0.077238 | -0.092889 | -0.11123 | -0.12743 | -0.15393 | -0.20407 | -0.2945 | -0.32534 | -0.34345 | 0.46938 | 0.46662 | 0.44702 | 0.44113 | 0.43408 | 0.42578 | 0.41631 | 0.40439 | 0.3915 | 0.37546 | 0.33664 | 0.26165 | 0.23695 | 0.22066 | 0.45097 | 0.44834 | 0.43139 | 0.42586 | 0.41903 | 0.41096 | 0.40149 | 0.38964 | 0.37634 | 0.35992 | 0.31986 | 0.2505 | 0.2198 | 0.20453
| STOCKINISH | FS |  |  |  | -0.0094608 | -0.014088 | -0.027142 | -0.03984 | -0.051641 | -0.062672 | -0.077368 | -0.092198 | -0.10643 | -0.12785 | -0.16755 | -0.27124 | -0.35927 | -0.37474 | 0.46987 | 0.46769 | 0.4529 | 0.44852 | 0.44304 | 0.43678 | 0.43011 | 0.42231 | 0.41353 | 0.40319 | 0.37576 | 0.29817 | 0.2238 | 0.20445 | 0.45136 | 0.44931 | 0.43655 | 0.43257 | 0.42731 | 0.42137 | 0.41484 | 0.40722 | 0.39842 | 0.38818 | 0.36398 | 0.28633 | 0.1931 | 0.18021
PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | NO | 0.3348 | 0.3326 | 0.33204 | 0.25333 | 0.19559 | 0.15842 | 0.024336 | -0.01292 | -0.10861 | -0.1432 | -0.21984 | -0.44084 | -0.75966 | -1.0839 | 0.34842 | 0.34749 | 0.34698 | 0.2456 | 0.17502 | 0.12872 | -0.032341 | -0.077295 | -0.19677 | -0.23963 | -0.3342 | -0.60649 | -1.0011 | -1.4047 | 0.33329 | 0.33136 | 0.33073 | 0.23104 | 0.15956 | 0.1132 | -0.051547 | -0.097338 | -0.21695 | -0.25997 | -0.35511 | -0.62958 | -1.0263 | -1.4308
| STONEFIELD | CT |  |  |  | 0.33642 | 0.33618 | 0.33546 | 0.32034 | 0.2967 | 0.20117 | 0.10104 | 0.073784 | 0.029562 | -0.013744 | -0.097127 | -0.32222 | -0.52947 | -0.75459 | 0.34913 | 0.34891 | 0.34838 | 0.33293 | 0.30704 | 0.19085 | 0.067613 | 0.035486 | -0.019398 | -0.074235 | -0.17579 | -0.45242 | -0.7111 | -0.99073 | 0.33482 | 0.33452 | 0.33377 | 0.31639 | 0.28845 | 0.17045 | 0.046154 | 0.012973 | -0.042107 | -0.096441 | -0.19927 | -0.47854 | -0.73748 | -1.018
| STONEFIELD | LW |  |  |  | 0.3348 | 0.3326 | 0.33204 | 0.33304 | 0.32501 | 0.32113 | 0.31663 | 0.31554 | 0.29726 | 0.27971 | 0.24419 | 0.1556 | -0.22831 | -0.79019 | 0.34842 | 0.34749 | 0.34698 | 0.34711 | 0.34388 | 0.34226 | 0.34019 | 0.33921 | 0.31693 | 0.29434 | 0.2527 | 0.14457 | -0.33501 | -1.0374 | 0.33329 | 0.33136 | 0.33073 | 0.33154 | 0.32443 | 0.32104 | 0.31706 | 0.31585 | 0.2933 | 0.2712 | 0.22827 | 0.11859 | -0.36119 | -1.0635
| STONEFIELD | ST |  |  |  | 0.33644 | 0.33635 | 0.33458 | 0.25333 | 0.19559 | 0.15842 | 0.024336 | -0.01292 | -0.10861 | -0.1432 | -0.21984 | -0.44084 | -0.75966 | -1.0839 | 0.34913 | 0.34903 | 0.34821 | 0.2456 | 0.17502 | 0.12872 | -0.032341 | -0.077295 | -0.19677 | -0.23963 | -0.3342 | -0.60649 | -1.0011 | -1.4047 | 0.33482 | 0.33468 | 0.33303 | 0.23104 | 0.15956 | 0.1132 | -0.051547 | -0.097338 | -0.21695 | -0.25997 | -0.35511 | -0.62958 | -1.0263 | -1.4308
| STONEFIELD | FS |  |  |  | 0.33645 | 0.33638 | 0.33464 | 0.31899 | 0.30185 | 0.28028 | 0.25694 | 0.23785 | 0.20295 | 0.17905 | 0.12773 | 0.092235 | 0.063929 | 0.026033 | 0.34914 | 0.34906 | 0.34826 | 0.32761 | 0.30635 | 0.28091 | 0.25486 | 0.2328 | 0.18938 | 0.15975 | 0.099104 | 0.059486 | 0.030083 | -0.015594 | 0.33483 | 0.33471 | 0.33309 | 0.31309 | 0.29174 | 0.26544 | 0.23761 | 0.21455 | 0.17104 | 0.1413 | 0.078732 | 0.036644 | 0.003988 | -0.042565
FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | NO | 11.148 | 10.8059 | 10.3495 | 9.4667 | 8.5178 | 7.4417 | 6.0118 | 4.5413 | 3.2826 | 2.0648 | -0.27149 | -0.42051 | -2.1533 | -3.3811 | 14.6484 | 14.4657 | 14.1768 | 13.661 | 13.0865 | 12.3604 | 11.3062 | 10.2571 | 9.3263 | 8.4789 | 6.8959 | 7.3515 | 5.8425 | 4.2152 | 14.5058 | 14.1929 | 13.7575 | 12.9265 | 12.0254 | 10.9694 | 9.5532 | 8.1211 | 6.9019 | 5.7723 | 3.6298 | 3.5626 | 2.1584 | 1.0382
| STONEHAVEN | CT |  |  |  | 11.4557 | 11.2698 | 10.9976 | 10.1955 | 9.331 | 8.3939 | 7.2578 | 6.208 | 4.9721 | 3.7517 | 1.4365 | 0.0096806 | -2.1533 | -3.3811 | 14.7419 | 14.6069 | 14.395 | 13.9191 | 13.3848 | 12.7154 | 11.8687 | 11.1725 | 10.3201 | 9.4763 | 7.9165 | 7.3515 | 5.8425 | 4.2152 | 14.764 | 14.5851 | 14.319 | 13.5766 | 12.7743 | 11.8408 | 10.7109 | 9.7251 | 8.5639 | 7.4197 | 5.2773 | 4.0582 | 2.1584 | 1.0382
| STONEHAVEN | LW |  |  |  | 11.148 | 10.8059 | 10.3495 | 9.4667 | 8.5178 | 7.4417 | 6.0118 | 4.5413 | 3.2826 | 2.0648 | -0.27149 | -0.42051 | -1.877 | -2.7539 | 14.6484 | 14.4657 | 14.1768 | 13.661 | 13.0865 | 12.3604 | 11.3062 | 10.2571 | 9.3263 | 8.4789 | 6.8959 | 7.4003 | 6.5278 | 5.7425 | 14.5058 | 14.1929 | 13.7575 | 12.9265 | 12.0254 | 10.9694 | 9.5532 | 8.1211 | 6.9019 | 5.7723 | 3.6298 | 3.5626 | 2.1927 | 1.2559
| STONEHAVEN | ST |  |  |  | 11.5652 | 11.4761 | 11.3593 | 10.9905 | 10.641 | 10.3147 | 9.5768 | 8.945 | 8.2098 | 7.5556 | 6.2447 | 4.9059 | 3.1333 | 1.1512 | 14.7896 | 14.7196 | 14.6261 | 14.2519 | 13.9277 | 13.6407 | 12.9102 | 12.3603 | 11.7062 | 11.1525 | 10.0471 | 8.9468 | 7.3807 | 5.3914 | 14.8592 | 14.7738 | 14.6615 | 14.2574 | 13.9006 | 13.5813 | 12.8039 | 12.1938 | 11.485 | 10.8748 | 9.664 | 8.4541 | 6.73 | 4.7847
| STONEHAVEN | FS |  |  |  | 11.5968 | 11.5281 | 11.4378 | 11.2475 | 11.0186 | 10.7746 | 10.4129 | 9.9549 | 9.3639 | 8.8539 | 7.8007 | 6.1191 | 3.8502 | 2.3756 | 14.8026 | 14.7429 | 14.6641 | 14.5032 | 14.3178 | 14.1134 | 13.8051 | 13.4108 | 12.9254 | 12.5127 | 11.6461 | 10.2812 | 7.9509 | 5.3382 | 14.8869 | 14.8208 | 14.7336 | 14.5446 | 14.3283 | 14.0967 | 13.7528 | 13.3181 | 12.7598 | 12.2846 | 11.3106 | 9.8021 | 7.7373 | 6.3489
STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 67734109 | YES | NO | -2.8657 | -2.8668 | -2.8682 | -2.8731 | -2.878 | -2.8818 | -2.8924 | -2.8965 | -2.9489 | -2.9691 | -3.014 | -3.1136 | -3.4975 | -4.0534 | -3.0286 | -3.0287 | -3.0288 | -3.0364 | -3.0417 | -3.0452 | -3.0571 | -3.0605 | -3.1239 | -3.1465 | -3.1996 | -3.3386 | -3.8184 | -4.5132 | -3.4475 | -3.448 | -3.4487 | -3.4558 | -3.4614 | -3.4654 | -3.4778 | -3.4819 | -3.5461 | -3.5696 | -3.6218 | -3.7573 | -4.2372 | -4.932
| STONEYHILL | CT |  |  |  | -2.8657 | -2.8668 | -2.8682 | -2.8709 | -2.8736 | -2.8818 | -2.8906 | -2.8941 | -2.9193 | -2.9441 | -2.9905 | -3.0893 | -3.275 | -3.4957 | -3.0286 | -3.0287 | -3.0288 | -3.0299 | -3.0318 | -3.0405 | -3.0498 | -3.0522 | -3.0816 | -3.1124 | -3.1695 | -3.3083 | -3.5404 | -3.8162 | -3.4475 | -3.448 | -3.4487 | -3.4507 | -3.4532 | -3.4625 | -3.4724 | -3.4755 | -3.5054 | -3.5352 | -3.5899 | -3.727 | -3.9591 | -4.2349
| STONEYHILL | LW |  |  |  | -2.8657 | -2.8665 | -2.868 | -2.8691 | -2.8704 | -2.8718 | -2.8741 | -2.877 | -2.9072 | -2.9388 | -2.995 | -3.1073 | -3.4975 | -4.0534 | -3.0286 | -3.0287 | -3.0288 | -3.0289 | -3.029 | -3.0291 | -3.0293 | -3.0295 | -3.0662 | -3.105 | -3.1741 | -3.3307 | -3.8184 | -4.5132 | -3.4475 | -3.4479 | -3.4486 | -3.4492 | -3.4499 | -3.4506 | -3.4518 | -3.4533 | -3.4887 | -3.5256 | -3.5906 | -3.7495 | -4.2372 | -4.932
| STONEYHILL | ST |  |  |  | -2.8656 | -2.8659 | -2.8664 | -2.8731 | -2.878 | -2.8817 | -2.8924 | -2.8965 | -2.9489 | -2.9691 | -3.014 | -3.1136 | -3.4003 | -3.7191 | -3.0286 | -3.0286 | -3.0287 | -3.0364 | -3.0417 | -3.0452 | -3.0571 | -3.0605 | -3.1239 | -3.1465 | -3.1996 | -3.3386 | -3.6968 | -4.0954 | -3.4474 | -3.4476 | -3.4478 | -3.4558 | -3.4614 | -3.4654 | -3.4778 | -3.4819 | -3.5461 | -3.5696 | -3.6218 | -3.7573 | -4.1156 | -4.5142
| STONEYHILL | FS |  |  |  | -2.8655 | -2.8658 | -2.8662 | -2.8679 | -2.8697 | -2.8718 | -2.874 | -2.8762 | -2.8956 | -2.9092 | -2.9371 | -2.9436 | -2.9598 | -2.9956 | -3.0286 | -3.0286 | -3.0286 | -3.0303 | -3.0319 | -3.0338 | -3.0357 | -3.0373 | -3.0603 | -3.0759 | -3.1072 | -3.1261 | -3.1463 | -3.1909 | -3.4474 | -3.4475 | -3.4477 | -3.4495 | -3.4514 | -3.4535 | -3.4558 | -3.4578 | -3.4813 | -3.4974 | -3.53 | -3.5449 | -3.5651 | -3.6097
PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | YES | NO | 11.2326 | 9.7811 | 8.2347 | 6.4857 | 4.569 | 1.6555 | -1.2483 | -3.1029 | -3.9018 | -4.5778 | -5.9158 | -6.5081 | -7.1384 | -7.5575 | 14.7162 | 13.3523 | 11.9031 | 10.2145 | 8.2748 | 5.0761 | 1.9448 | 0.086978 | -0.70988 | -1.522 | -3.1395 | -3.2539 | -3.9984 | -4.4956 | 13.7885 | 12.5594 | 11.1896 | 9.321 | 7.2524 | 3.9066 | 0.5207 | -1.5963 | -2.4299 | -3.1814 | -4.9228 | -5.6273 | -6.3951 | -6.9054
| STONEYWOOD T1&T2 | CT |  |  |  | 11.4461 | 10.1515 | 8.7523 | 7.8201 | 6.8404 | 5.0706 | 3.4095 | 2.5887 | 1.9709 | 1.4801 | 0.47868 | 0.17267 | -0.32987 | -0.62997 | 14.889 | 13.6227 | 12.2605 | 11.5492 | 10.7839 | 9.0111 | 7.3869 | 6.7464 | 6.2155 | 5.7751 | 4.7554 | 5.1233 | 4.7061 | 4.3912 | 13.9659 | 12.8783 | 11.6065 | 10.7839 | 9.8454 | 7.9308 | 6.0993 | 5.2912 | 4.7021 | 4.203 | 3.0524 | 2.7513 | 2.2278 | 1.9092
| STONEYWOOD T1&T2 | LW |  |  |  | 11.2326 | 9.7811 | 8.2347 | 6.4857 | 4.569 | 1.6555 | -1.2483 | -3.1029 | -3.9018 | -4.5778 | -5.9158 | -6.5081 | -7.1384 | -7.5575 | 14.7162 | 13.3523 | 11.9031 | 10.2145 | 8.2748 | 5.0761 | 1.9448 | 0.086978 | -0.70988 | -1.522 | -3.1395 | -3.2539 | -3.9984 | -4.4956 | 13.7885 | 12.5594 | 11.1896 | 9.321 | 7.2524 | 3.9066 | 0.5207 | -1.5963 | -2.4299 | -3.1814 | -4.9228 | -5.6273 | -6.3951 | -6.9054
| STONEYWOOD T1&T2 | ST |  |  |  | 11.4903 | 10.2427 | 8.9295 | 7.4385 | 6.2821 | 5.2913 | 3.5447 | 2.8235 | 2.247 | 1.9093 | 1.0807 | 0.44919 | -0.15695 | -0.62298 | 14.9043 | 13.6764 | 12.3797 | 10.7887 | 9.5885 | 8.5983 | 6.655 | 5.9646 | 5.4425 | 5.0746 | 4.0727 | 4.0183 | 3.4593 | 3.0342 | 14.003 | 12.9593 | 11.7541 | 10.1686 | 8.9573 | 7.9438 | 5.9202 | 5.1532 | 4.5459 | 4.095 | 2.8297 | 2.565 | 1.9035 | 1.4137
| STONEYWOOD T1&T2 | FS |  |  |  | 11.9757 | 11.0284 | 10.0188 | 9.3293 | 8.6709 | 7.9442 | 7.3378 | 6.7896 | 6.3252 | 5.946 | 5.1192 | 4.3484 | 3.7536 | 3.4115 | 15.4425 | 14.4953 | 13.4793 | 12.8442 | 12.2318 | 11.5465 | 11.0019 | 10.5154 | 10.1204 | 9.7652 | 8.9379 | 8.4696 | 8.1372 | 7.8321 | 14.4211 | 13.6264 | 12.7353 | 12.0948 | 11.4767 | 10.7832 | 10.1965 | 9.6566 | 9.2152 | 8.8461 | 8.0013 | 7.3011 | 6.7363 | 6.4275
PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 7.3536 | 6.699 | 6.003 | 5.2059 | 4.2648 | 2.8246 | 1.3921 | 0.47446 | 0.084594 | -0.24622 | -0.9004 | -1.1918 | -1.5069 | -1.7164 | 8.6943 | 8.0391 | 7.3367 | 6.4939 | 5.5425 | 3.9586 | 2.3876 | 1.4428 | 1.1064 | 0.76682 | 0.091426 | -0.36553 | -0.74178 | -0.9928 | 7.0528 | 6.4142 | 5.7132 | 4.8404 | 3.8577 | 2.2325 | 0.57837 | -0.46308 | -0.9006 | -1.3424 | -2.2259 | -1.8692 | -2.2528 | -2.508
| STONEYWOOD T3 | CT |  |  |  | 7.4309 | 6.8234 | 6.1681 | 5.8081 | 5.3907 | 4.5213 | 3.7065 | 3.3093 | 3.0081 | 2.7709 | 2.285 | 2.1502 | 1.901 | 1.7524 | 8.7753 | 8.1624 | 7.4977 | 7.1352 | 6.7478 | 5.8638 | 5.0527 | 4.7479 | 4.5416 | 4.3656 | 3.9605 | 3.7934 | 3.5371 | 3.3219 | 7.1279 | 6.5206 | 5.8507 | 5.4382 | 5.0089 | 4.0783 | 3.2018 | 2.8267 | 2.5338 | 2.2911 | 1.734 | 2.3205 | 2.0601 | 1.903
| STONEYWOOD T3 | LW |  |  |  | 7.3536 | 6.699 | 6.003 | 5.2059 | 4.2648 | 2.8246 | 1.3921 | 0.47446 | 0.084594 | -0.24622 | -0.9004 | -1.1918 | -1.5069 | -1.7164 | 8.6943 | 8.0391 | 7.3367 | 6.4939 | 5.5425 | 3.9586 | 2.3876 | 1.4428 | 1.1064 | 0.76682 | 0.091426 | -0.36553 | -0.74178 | -0.9928 | 7.0528 | 6.4142 | 5.7132 | 4.8404 | 3.8577 | 2.2325 | 0.57837 | -0.46308 | -0.9006 | -1.3424 | -2.2259 | -1.8692 | -2.2528 | -2.508
| STONEYWOOD T3 | ST |  |  |  | 7.4419 | 6.8604 | 6.25 | 5.5596 | 5.0265 | 4.5683 | 3.7334 | 3.4011 | 3.1337 | 2.971 | 2.5489 | 2.2937 | 1.9902 | 1.7493 | 8.7861 | 8.2007 | 7.5819 | 6.791 | 6.1938 | 5.701 | 4.719 | 4.3586 | 4.0767 | 3.9067 | 3.4628 | 3.3776 | 3.0508 | 2.7756 | 7.1467 | 6.5899 | 5.9998 | 5.2037 | 4.5925 | 4.0735 | 3.0484 | 2.6352 | 2.288 | 2.0427 | 1.4168 | 1.9297 | 1.6834 | 1.5294
| STONEYWOOD T3 | FS |  |  |  | 7.6814 | 7.2262 | 6.7417 | 6.4365 | 6.1429 | 5.814 | 5.5454 | 5.3034 | 5.099 | 4.9232 | 4.5323 | 4.2204 | 3.9512 | 3.7736 | 9.0404 | 8.5888 | 8.1043 | 7.7931 | 7.4914 | 7.1513 | 6.8762 | 6.6277 | 6.4236 | 6.2385 | 5.8276 | 5.6418 | 5.3629 | 5.091 | 7.3796 | 6.9497 | 6.4888 | 6.1725 | 5.8619 | 5.5072 | 5.2075 | 4.9294 | 4.6923 | 4.474 | 3.9793 | 4.183 | 4.0655 | 4.0119
CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | NO | 0.13953 | 0.13531 | 0.12692 | 0.087472 | 0.046393 | 0.0017387 | -0.045959 | -0.095471 | -0.12257 | -0.16674 | -0.28093 | -0.33682 | -0.40352 | -0.44043 | 0.54176 | 0.52093 | 0.49141 | 0.46027 | 0.42055 | 0.37815 | 0.3381 | 0.30278 | 0.26101 | 0.21316 | 0.12367 | 0.061594 | 0.012489 | -0.031574 | 0.28457 | 0.28069 | 0.27601 | 0.27048 | 0.23411 | 0.18289 | 0.1238 | 0.063486 | 0.0039216 | -0.059211 | -0.17294 | -0.23646 | -0.29709 | -0.33352
| STRACHUR | CT |  |  |  | 0.14032 | 0.13692 | 0.13254 | 0.1084 | 0.060319 | 0.004199 | -0.045959 | -0.095471 | -0.12257 | -0.15154 | -0.26803 | -0.33682 | -0.40352 | -0.44043 | 0.54783 | 0.53119 | 0.50677 | 0.46563 | 0.42055 | 0.37815 | 0.3381 | 0.30278 | 0.2638 | 0.21387 | 0.12367 | 0.061594 | 0.012489 | -0.031574 | 0.28528 | 0.28214 | 0.27809 | 0.27159 | 0.24474 | 0.18289 | 0.1238 | 0.068383 | 0.016775 | -0.048183 | -0.16377 | -0.23646 | -0.29709 | -0.33352
| STRACHUR | LW |  |  |  | 0.13953 | 0.13531 | 0.12692 | 0.087472 | 0.046393 | 0.0017387 | -0.042029 | -0.082969 | -0.10784 | -0.16674 | -0.28093 | -0.31992 | -0.36915 | -0.41023 | 0.54176 | 0.52093 | 0.49141 | 0.46027 | 0.42624 | 0.39444 | 0.35178 | 0.30629 | 0.26101 | 0.21316 | 0.12514 | 0.098729 | 0.057835 | 0.012141 | 0.28457 | 0.28069 | 0.27601 | 0.27048 | 0.23411 | 0.19393 | 0.12997 | 0.063486 | 0.0039216 | -0.059211 | -0.17294 | -0.21127 | -0.26108 | -0.30933
| STRACHUR | ST |  |  |  | 0.14138 | 0.13859 | 0.13557 | 0.12742 | 0.12047 | 0.11451 | 0.099957 | 0.081352 | 0.057572 | 0.0361 | -0.0062597 | -0.18735 | -0.25421 | -0.30148 | 0.55289 | 0.54152 | 0.52818 | 0.50689 | 0.48455 | 0.46224 | 0.43405 | 0.4102 | 0.37754 | 0.34596 | 0.27584 | 0.12061 | 0.059538 | 0.0098751 | 0.28621 | 0.28366 | 0.2809 | 0.27172 | 0.26419 | 0.25793 | 0.24546 | 0.23999 | 0.21362 | 0.17199 | 0.081233 | -0.11453 | -0.17974 | -0.22504
| STRACHUR | FS |  |  |  | 0.14172 | 0.13922 | 0.13644 | 0.13234 | 0.12804 | 0.12336 | 0.11955 | 0.10517 | 0.085761 | 0.06812 | 0.035195 | -0.091707 | -0.23438 | -0.26236 | 0.55418 | 0.54464 | 0.5328 | 0.51784 | 0.50028 | 0.48187 | 0.46515 | 0.44605 | 0.42355 | 0.40118 | 0.35349 | 0.22295 | 0.10769 | 0.073072 | 0.28652 | 0.28424 | 0.28169 | 0.27759 | 0.27329 | 0.26859 | 0.26465 | 0.26085 | 0.25537 | 0.23576 | 0.17346 | -0.003126 | -0.14312 | -0.16619
TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0.061949 | 0.015268 | -0.034729 | -0.085948 | -0.13635 | -0.26059 | -0.40554 | -0.48785 | -0.55451 | -0.62606 | -0.77955 | -1.0769 | -1.4489 | -1.7909 | 0.28871 | 0.27182 | 0.24931 | 0.18697 | 0.11454 | 0.056518 | -0.086982 | -0.14096 | -0.2609 | -0.31857 | -0.44791 | -0.78112 | -1.1594 | -1.5312 | 0.26174 | 0.22038 | 0.1722 | 0.12386 | 0.058701 | -0.080944 | -0.24137 | -0.32368 | -0.40585 | -0.49894 | -0.66694 | -1.0305 | -1.4624 | -1.8632
| STRATHDON | CT |  |  |  | 0.087463 | 0.060299 | 0.026296 | -0.044406 | -0.12462 | -0.26059 | -0.40554 | -0.48785 | -0.55451 | -0.62606 | -0.77955 | -1.0226 | -1.3031 | -1.5353 | 0.29807 | 0.28563 | 0.26936 | 0.2284 | 0.17693 | 0.056518 | -0.071755 | -0.12296 | -0.1913 | -0.26779 | -0.40769 | -0.67355 | -0.93263 | -1.1952 | 0.27908 | 0.26151 | 0.22889 | 0.15542 | 0.06982 | -0.080944 | -0.24137 | -0.32368 | -0.40585 | -0.49894 | -0.66694 | -0.95086 | -1.2623 | -1.5363
| STRATHDON | LW |  |  |  | 0.061949 | 0.015268 | -0.034729 | -0.085948 | -0.13635 | -0.18494 | -0.24763 | -0.30503 | -0.35735 | -0.41179 | -0.53339 | -0.65752 | -1.0277 | -1.5235 | 0.28871 | 0.27182 | 0.24931 | 0.22782 | 0.20501 | 0.18493 | 0.15345 | 0.12122 | 0.073723 | 0.025599 | -0.066674 | -0.17757 | -0.59582 | -1.1932 | 0.26174 | 0.22038 | 0.1722 | 0.12386 | 0.074783 | 0.029874 | -0.033148 | -0.093594 | -0.15829 | -0.22095 | -0.3458 | -0.48145 | -0.92637 | -1.5371
| STRATHDON | ST |  |  |  | 0.097366 | 0.079237 | 0.058825 | -0.034173 | -0.1131 | -0.17483 | -0.31612 | -0.37932 | -0.49592 | -0.56131 | -0.70896 | -1.0769 | -1.4489 | -1.7909 | 0.30175 | 0.29381 | 0.28444 | 0.18697 | 0.11454 | 0.062157 | -0.086982 | -0.14096 | -0.2609 | -0.31857 | -0.44791 | -0.78112 | -1.1594 | -1.5312 | 0.28045 | 0.27741 | 0.25898 | 0.14757 | 0.058701 | -0.0091483 | -0.17554 | -0.24577 | -0.38333 | -0.45828 | -0.62472 | -1.0305 | -1.4624 | -1.8632
| STRATHDON | FS |  |  |  | 0.1069 | 0.094728 | 0.080199 | 0.045288 | 0.010152 | -0.027719 | -0.068613 | -0.11134 | -0.17313 | -0.22671 | -0.34031 | -0.59691 | -0.77743 | -0.86575 | 0.30528 | 0.29959 | 0.29261 | 0.26532 | 0.23744 | 0.20625 | 0.17401 | 0.14265 | 0.090569 | 0.048724 | -0.039918 | -0.187 | -0.30153 | -0.37444 | 0.28094 | 0.2785 | 0.27547 | 0.24193 | 0.20211 | 0.15896 | 0.11425 | 0.068808 | 0.00016253 | -0.058484 | -0.18349 | -0.44226 | -0.61484 | -0.70349
STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | NO | 10.0868 | 9.9423 | 9.7762 | 9.5942 | 9.2104 | 8.9037 | 8.6036 | 8.3568 | 8.2042 | 8.0329 | 7.6967 | 7.5107 | 7.0341 | 6.7254 | 10.9996 | 10.9365 | 10.8534 | 10.7686 | 10.4802 | 10.218 | 10.0163 | 9.8848 | 9.7588 | 9.6129 | 9.3311 | 9.1005 | 8.6488 | 8.1977 | 9.8571 | 9.7308 | 9.5804 | 9.4189 | 9.0692 | 8.7495 | 8.4556 | 8.23 | 8.0694 | 7.8847 | 7.5262 | 7.2779 | 6.8064 | 6.4023
| STRICHEN | CT |  |  |  | 10.1808 | 10.0849 | 9.9647 | 9.7162 | 9.2702 | 8.9037 | 8.6036 | 8.3568 | 8.2042 | 8.0329 | 7.6967 | 7.5107 | 7.0341 | 6.7254 | 11.0332 | 10.9871 | 10.9225 | 10.7924 | 10.4802 | 10.218 | 10.0163 | 9.8848 | 9.7588 | 9.6129 | 9.3311 | 9.1005 | 8.74 | 8.4048 | 9.9366 | 9.8518 | 9.7422 | 9.5152 | 9.1011 | 8.7495 | 8.4556 | 8.23 | 8.0694 | 7.8847 | 7.5262 | 7.2779 | 6.8064 | 6.4709
| STRICHEN | LW |  |  |  | 10.0868 | 9.9423 | 9.7762 | 9.5942 | 9.2104 | 8.95 | 8.7296 | 8.4938 | 8.3322 | 8.162 | 7.8324 | 7.7839 | 7.34 | 6.8225 | 10.9996 | 10.9365 | 10.8534 | 10.7686 | 10.5041 | 10.3481 | 10.2298 | 10.0988 | 9.9744 | 9.842 | 9.5859 | 9.5577 | 9.1195 | 8.5327 | 9.8571 | 9.7308 | 9.5804 | 9.4189 | 9.0692 | 8.8377 | 8.6348 | 8.4154 | 8.2486 | 8.0722 | 7.7311 | 7.6595 | 7.1613 | 6.5451
| STRICHEN | ST |  |  |  | 10.2314 | 10.1719 | 10.11 | 9.9567 | 9.6225 | 9.423 | 9.2175 | 9.0792 | 8.8838 | 8.7301 | 8.3812 | 7.7739 | 7.2223 | 6.7661 | 11.0513 | 11.0242 | 10.9939 | 10.8702 | 10.5937 | 10.4378 | 10.2549 | 10.1571 | 9.9911 | 9.8776 | 9.6159 | 9.127 | 8.6488 | 8.1977 | 9.9787 | 9.9267 | 9.8719 | 9.7123 | 9.3912 | 9.2012 | 8.9797 | 8.8426 | 8.6354 | 8.4802 | 8.1264 | 7.4712 | 6.8912 | 6.4023
| STRICHEN | FS |  |  |  | 10.264 | 10.2194 | 10.1765 | 10.0923 | 9.8595 | 9.701 | 9.5884 | 9.4741 | 9.333 | 9.188 | 8.9084 | 8.2551 | 7.7898 | 7.5875 | 11.0632 | 11.0421 | 11.0196 | 10.9692 | 10.788 | 10.6695 | 10.5937 | 10.517 | 10.4169 | 10.3192 | 10.1286 | 9.757 | 9.4108 | 9.2087 | 10.0063 | 9.9672 | 9.9287 | 9.8494 | 9.6321 | 9.4841 | 9.3767 | 9.2677 | 9.1292 | 8.9893 | 8.7161 | 8.0946 | 7.6367 | 7.4562
THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | NO | 3.779 | -2.5168 | -12.7207 | -13.3535 | -14.1053 | -14.7419 | -15.1267 | -15.5746 | -15.9032 | -16.083 | -16.5661 | -16.5727 | -17.1559 | -17.785 | 3.9058 | -3.7615 | -16.3056 | -16.742 | -17.2998 | -17.7435 | -17.9743 | -18.2627 | -18.5797 | -18.7688 | -19.2508 | -19.3446 | -19.8915 | -20.5799 | 4.076 | -3.6857 | -16.3188 | -16.8998 | -17.6062 | -18.1977 | -18.5308 | -18.9236 | -19.2391 | -19.4063 | -19.8707 | -19.6409 | -20.2832 | -21.0193
| STROMNESS | CT |  |  |  | 7.4807 | 6.477 | 4.9638 | 4.2168 | 3.4129 | 2.6554 | 2.1818 | 1.6588 | 1.4313 | 1.2923 | 0.88935 | 1.0134 | 0.45606 | 0.050488 | 8.383 | 7.2611 | 5.5103 | 5.0902 | 4.5377 | 4.0339 | 3.792 | 3.5079 | 3.2381 | 3.0654 | 2.615 | 2.4485 | 1.9674 | 1.4428 | 8.6405 | 7.464 | 5.668 | 4.9864 | 4.2564 | 3.563 | 3.1624 | 2.7126 | 2.4406 | 2.3398 | 1.9771 | 2.2981 | 1.7484 | 1.3146
| STROMNESS | LW |  |  |  | 3.779 | -2.5168 | -12.7207 | -13.3535 | -14.1053 | -14.7419 | -15.1267 | -15.5746 | -15.9032 | -16.083 | -16.5661 | -16.5727 | -17.1559 | -17.785 | 3.9058 | -3.7615 | -16.3056 | -16.742 | -17.2998 | -17.7435 | -17.9743 | -18.2627 | -18.5797 | -18.7688 | -19.2508 | -19.3446 | -19.8915 | -20.5799 | 4.076 | -3.6857 | -16.3188 | -16.8998 | -17.6062 | -18.1977 | -18.5308 | -18.9236 | -19.2391 | -19.4063 | -19.8707 | -19.6409 | -20.2832 | -21.0193
| STROMNESS | ST |  |  |  | 5.0834 | 2.1032 | -4.0766 | -4.4117 | -4.8121 | -5.186 | -5.2769 | -5.4405 | -5.7533 | -5.9069 | -6.4101 | -7.0708 | -7.5793 | -8.1067 | 5.3566 | 1.6864 | -5.9762 | -6.3318 | -6.7532 | -7.148 | -7.2364 | -7.3872 | -7.6849 | -7.8085 | -8.2884 | -8.6875 | -9.2614 | -9.8969 | 5.6918 | 2.0095 | -5.6554 | -6.0254 | -6.4665 | -6.8828 | -7.013 | -7.1994 | -7.5414 | -7.7199 | -8.2947 | -8.366 | -8.9502 | -9.5035
| STROMNESS | FS |  |  |  | 8.4358 | 8.1172 | 7.6424 | 7.3785 | 7.0413 | 6.6993 | 6.505 | 6.2959 | 6.0004 | 5.7738 | 5.2798 | 4.2625 | 3.6185 | 3.3915 | 9.4896 | 9.1333 | 8.59 | 8.3105 | 7.9829 | 7.669 | 7.5218 | 7.352 | 7.0869 | 6.8841 | 6.4216 | 5.7272 | 5.075 | 4.6229 | 9.8122 | 9.4426 | 8.8967 | 8.5762 | 8.2058 | 7.8494 | 7.6449 | 7.4234 | 7.1107 | 6.867 | 6.3352 | 5.9522 | 5.3521 | 5.1472
THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | NO | 0.67099 | 0.66159 | 0.64874 | 0.63133 | 0.60376 | 0.56177 | 0.51397 | 0.48729 | 0.46229 | 0.43518 | 0.38491 | 0.32487 | 0.2468 | 0.16398 | 0.78725 | 0.78239 | 0.7748 | 0.75991 | 0.73924 | 0.70335 | 0.66043 | 0.64172 | 0.61778 | 0.5905 | 0.53874 | 0.44879 | 0.33468 | 0.21805 | 0.7292 | 0.72061 | 0.70863 | 0.6927 | 0.66433 | 0.61804 | 0.56601 | 0.53949 | 0.51137 | 0.47973 | 0.42215 | 0.34736 | 0.25054 | 0.13323
| STRONSAY | CT |  |  |  | 0.67948 | 0.67245 | 0.66062 | 0.63274 | 0.60376 | 0.56177 | 0.51397 | 0.48729 | 0.46229 | 0.43518 | 0.38491 | 0.32487 | 0.2468 | 0.18143 | 0.79044 | 0.78643 | 0.77925 | 0.76225 | 0.74262 | 0.70335 | 0.66043 | 0.64172 | 0.61778 | 0.5905 | 0.53874 | 0.46167 | 0.38032 | 0.29734 | 0.73541 | 0.73022 | 0.7192 | 0.6927 | 0.66433 | 0.61804 | 0.56601 | 0.53949 | 0.51137 | 0.47973 | 0.42215 | 0.34736 | 0.25874 | 0.17978
| STRONSAY | LW |  |  |  | 0.67099 | 0.66159 | 0.64874 | 0.63133 | 0.61472 | 0.59392 | 0.57545 | 0.55058 | 0.53235 | 0.50874 | 0.46156 | 0.43719 | 0.32743 | 0.17791 | 0.78725 | 0.78239 | 0.7748 | 0.76599 | 0.75698 | 0.74693 | 0.73547 | 0.7208 | 0.70338 | 0.6823 | 0.64232 | 0.61461 | 0.48625 | 0.30331 | 0.7292 | 0.72061 | 0.70863 | 0.6928 | 0.67754 | 0.65874 | 0.64133 | 0.61734 | 0.59628 | 0.57037 | 0.5212 | 0.49155 | 0.35843 | 0.17347
| STRONSAY | ST |  |  |  | 0.68475 | 0.68422 | 0.67863 | 0.65555 | 0.63841 | 0.62089 | 0.58267 | 0.56814 | 0.53048 | 0.51041 | 0.4658 | 0.35795 | 0.26256 | 0.16398 | 0.79239 | 0.79147 | 0.78842 | 0.75991 | 0.73924 | 0.72252 | 0.67737 | 0.66122 | 0.62228 | 0.60303 | 0.55842 | 0.44879 | 0.33468 | 0.21805 | 0.73569 | 0.73478 | 0.73353 | 0.70536 | 0.68473 | 0.66582 | 0.61905 | 0.60141 | 0.55798 | 0.53521 | 0.48571 | 0.36523 | 0.25054 | 0.13323
| STRONSAY | FS |  |  |  | 0.68155 | 0.68314 | 0.68121 | 0.67192 | 0.65862 | 0.64971 | 0.63837 | 0.6256 | 0.60882 | 0.59458 | 0.5651 | 0.5008 | 0.4493 | 0.42703 | 0.79126 | 0.7912 | 0.78961 | 0.78134 | 0.77129 | 0.76213 | 0.7518 | 0.74129 | 0.72493 | 0.71166 | 0.68362 | 0.63443 | 0.58978 | 0.56347 | 0.7358 | 0.73511 | 0.7342 | 0.72749 | 0.71427 | 0.70384 | 0.6913 | 0.67779 | 0.65873 | 0.64275 | 0.60934 | 0.54497 | 0.49361 | 0.47072
FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 0.072179 | 0.064849 | 0.055543 | 0.046706 | 0.036048 | 0.0062988 | -0.024918 | -0.066553 | -0.084997 | -0.10718 | -0.14945 | -0.16348 | -0.18301 | -0.19803 | 0.47344 | 0.46372 | 0.45139 | 0.43783 | 0.42094 | 0.40451 | 0.38873 | 0.36825 | 0.34626 | 0.3245 | 0.28263 | 0.26654 | 0.25055 | 0.23517 | 0.13816 | 0.12896 | 0.11798 | 0.1065 | 0.092206 | 0.078068 | 0.063837 | 0.045806 | 0.029074 | 0.014447 | -0.01409 | 0.033291 | 0.020052 | 0.008224
| STRONTIAN | CT |  |  |  | 0.074641 | 0.067189 | 0.05878 | 0.04762 | 0.036048 | 0.0062988 | -0.024918 | -0.066553 | -0.084725 | -0.10546 | -0.14437 | -0.15203 | -0.18301 | -0.19803 | 0.47738 | 0.46903 | 0.45837 | 0.44025 | 0.42094 | 0.40451 | 0.38873 | 0.36825 | 0.35343 | 0.33346 | 0.29266 | 0.26757 | 0.25055 | 0.23517 | 0.14137 | 0.13285 | 0.12273 | 0.10662 | 0.092206 | 0.078068 | 0.063837 | 0.045806 | 0.032811 | 0.023344 | 0.0027317 | 0.043096 | 0.020052 | 0.008224
| STRONTIAN | LW |  |  |  | 0.072179 | 0.064849 | 0.055543 | 0.046706 | 0.039235 | 0.019834 | -0.014982 | -0.053998 | -0.084997 | -0.10718 | -0.14945 | -0.16348 | -0.17481 | -0.1846 | 0.47344 | 0.46372 | 0.45139 | 0.43783 | 0.42509 | 0.41321 | 0.39386 | 0.37063 | 0.34626 | 0.3245 | 0.28263 | 0.26654 | 0.26199 | 0.25918 | 0.13816 | 0.12896 | 0.11798 | 0.1065 | 0.095358 | 0.084203 | 0.0677 | 0.047144 | 0.029074 | 0.014447 | -0.01409 | 0.033291 | 0.025024 | 0.018592
| STRONTIAN | ST |  |  |  | 0.076208 | 0.07126 | 0.068408 | 0.065592 | 0.062445 | 0.060303 | 0.055721 | 0.046792 | 0.037602 | 0.029577 | 0.0064033 | -0.079684 | -0.10315 | -0.11883 | 0.47873 | 0.4729 | 0.46907 | 0.46404 | 0.45802 | 0.45343 | 0.44567 | 0.43429 | 0.42017 | 0.40537 | 0.37326 | 0.29507 | 0.27592 | 0.26308 | 0.14264 | 0.13753 | 0.13369 | 0.12912 | 0.12365 | 0.11889 | 0.11154 | 0.10149 | 0.090174 | 0.078778 | 0.054682 | 0.075186 | 0.065291 | 0.058431
| STRONTIAN | FS |  |  |  | 0.076353 | 0.073174 | 0.068757 | 0.066849 | 0.064162 | 0.061659 | 0.058854 | 0.05233 | 0.044902 | 0.040173 | 0.029318 | -0.055978 | -0.11998 | -0.13698 | 0.47928 | 0.47567 | 0.47014 | 0.46599 | 0.46145 | 0.45639 | 0.45076 | 0.44195 | 0.43178 | 0.42313 | 0.39998 | 0.3298 | 0.26835 | 0.2499 | 0.14348 | 0.14014 | 0.13533 | 0.13128 | 0.1275 | 0.12262 | 0.11726 | 0.10958 | 0.10065 | 0.093695 | 0.076544 | 0.078803 | 0.063389 | 0.051975
SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | NO | -0.91803 | -0.95087 | -0.99001 | -1.0396 | -1.1109 | -1.1806 | -1.2553 | -1.3315 | -1.3992 | -1.4468 | -1.5646 | -1.2608 | -1.3015 | -1.3298 | -0.21709 | -0.23338 | -0.25772 | -0.2915 | -0.32651 | -0.36947 | -0.41648 | -0.46552 | -0.52551 | -0.5688 | -0.67541 | -0.34494 | -0.38037 | -0.40889 | -0.029329 | -0.06141 | -0.10262 | -0.1603 | -0.22551 | -0.28954 | -0.35818 | -0.4284 | -0.49265 | -0.53811 | -0.66976 | -0.59017 | -0.62044 | -0.64538
| SUMBURGH | CT |  |  |  | -0.90026 | -0.9352 | -0.97211 | -1.0396 | -1.1109 | -1.1806 | -1.2553 | -1.3315 | -1.3992 | -1.4468 | -1.5646 | -1.2367 | -1.3015 | -1.3298 | -0.21093 | -0.23315 | -0.25772 | -0.2915 | -0.32651 | -0.36947 | -0.41648 | -0.46552 | -0.52551 | -0.5688 | -0.67541 | -0.34355 | -0.38037 | -0.40889 | -0.014101 | -0.053569 | -0.096543 | -0.1603 | -0.22551 | -0.28954 | -0.35818 | -0.4284 | -0.49265 | -0.53811 | -0.66976 | -0.56818 | -0.62044 | -0.64538
| SUMBURGH | LW |  |  |  | -0.91803 | -0.95087 | -0.99001 | -1.0346 | -1.0817 | -1.1296 | -1.1894 | -1.2613 | -1.309 | -1.3603 | -1.4597 | -1.2608 | -1.296 | -1.3022 | -0.21709 | -0.23338 | -0.25527 | -0.27716 | -0.30057 | -0.32369 | -0.35571 | -0.39278 | -0.43689 | -0.48419 | -0.57525 | -0.34494 | -0.3595 | -0.36187 | -0.029329 | -0.06141 | -0.10262 | -0.145 | -0.19002 | -0.23484 | -0.29409 | -0.36058 | -0.40616 | -0.45968 | -0.56846 | -0.59017 | -0.61791 | -0.62242
| SUMBURGH | ST |  |  |  | -0.87607 | -0.88614 | -0.89347 | -0.90658 | -0.93135 | -0.95684 | -0.98952 | -1.0312 | -1.0811 | -1.1387 | -1.2765 | -1.0111 | -1.0553 | -1.09 | -0.20146 | -0.20785 | -0.21401 | -0.22326 | -0.23636 | -0.2499 | -0.27563 | -0.31183 | -0.3553 | -0.4077 | -0.53504 | -0.25604 | -0.28108 | -0.30975 | 0.0037408 | -0.0085213 | -0.019895 | -0.037036 | -0.061355 | -0.085618 | -0.11665 | -0.15613 | -0.21101 | -0.27751 | -0.43774 | -0.39751 | -0.44209 | -0.4681
| SUMBURGH | FS |  |  |  | -0.87846 | -0.88666 | -0.89037 | -0.91096 | -0.9299 | -0.95451 | -0.98783 | -1.0178 | -1.0544 | -1.0942 | -1.1855 | -1.0598 | -1.1532 | -1.1793 | -0.20192 | -0.20678 | -0.21025 | -0.22121 | -0.23235 | -0.245 | -0.26128 | -0.2766 | -0.30534 | -0.33818 | -0.41569 | -0.27928 | -0.32259 | -0.35477 | 0.0027924 | -0.0068304 | -0.013518 | -0.035514 | -0.057072 | -0.081595 | -0.11242 | -0.14059 | -0.17494 | -0.21247 | -0.30502 | -0.35683 | -0.51123 | -0.53107
ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | NO | 8.0263 | 7.6394 | 7.3334 | 6.9323 | 6.4784 | 5.8969 | 5.2837 | 4.7736 | 4.5436 | 4.2944 | 3.8119 | 4.4339 | 4.0651 | 3.7555 | 10.0095 | 9.6837 | 9.4426 | 9.137 | 8.7822 | 8.2816 | 7.7389 | 7.331 | 7.13 | 6.9129 | 6.4932 | 6.9009 | 6.5932 | 6.2721 | 8.0973 | 7.7493 | 7.4577 | 7.0751 | 6.6409 | 6.0501 | 5.4018 | 4.8811 | 4.6162 | 4.3218 | 3.6405 | 4.3419 | 3.9399 | 3.5832
| TAIN | CT |  |  |  | 8.1351 | 7.8056 | 7.5462 | 7.1593 | 6.7541 | 6.2106 | 5.6788 | 5.2967 | 5.0905 | 4.8782 | 4.4661 | 5.0932 | 4.686 | 4.4715 | 10.0683 | 9.7777 | 9.5587 | 9.3155 | 9.0514 | 8.6347 | 8.2161 | 7.9781 | 7.8089 | 7.627 | 7.2731 | 7.5917 | 7.2595 | 6.9322 | 8.1888 | 7.8761 | 7.6133 | 7.2653 | 6.9034 | 6.3693 | 5.8252 | 5.4623 | 5.2198 | 4.9813 | 4.4408 | 5.1512 | 4.7431 | 4.5012
| TAIN | LW |  |  |  | 8.0263 | 7.6394 | 7.3334 | 6.9323 | 6.4784 | 5.8969 | 5.2837 | 4.7736 | 4.5436 | 4.2944 | 3.8119 | 4.4339 | 4.0651 | 3.7555 | 10.0095 | 9.6837 | 9.4426 | 9.137 | 8.7822 | 8.2816 | 7.7389 | 7.331 | 7.13 | 6.9129 | 6.4932 | 6.9009 | 6.5932 | 6.2721 | 8.0973 | 7.7493 | 7.4577 | 7.0751 | 6.6409 | 6.0501 | 5.4018 | 4.8811 | 4.6162 | 4.3218 | 3.6405 | 4.3419 | 3.9399 | 3.5832
| TAIN | ST |  |  |  | 8.2233 | 7.9663 | 7.8064 | 7.5141 | 7.2632 | 7.0213 | 6.6406 | 6.4175 | 6.1886 | 5.9609 | 5.4392 | 5.6826 | 5.3617 | 5.062 | 10.1035 | 9.8535 | 9.6951 | 9.4071 | 9.1723 | 8.9678 | 8.5739 | 8.3816 | 8.1906 | 8.0183 | 7.4951 | 7.6555 | 7.2956 | 6.9053 | 8.2518 | 8.0139 | 7.8527 | 7.5345 | 7.2659 | 7.018 | 6.5683 | 6.2866 | 5.992 | 5.6936 | 4.9773 | 5.4836 | 5.1006 | 4.7972
| TAIN | FS |  |  |  | 8.2995 | 8.1096 | 7.9806 | 7.8148 | 7.6442 | 7.4581 | 7.2835 | 7.1089 | 6.9452 | 6.7749 | 6.4036 | 6.1778 | 5.8295 | 5.6447 | 10.1811 | 9.9928 | 9.8678 | 9.7372 | 9.603 | 9.4583 | 9.3191 | 9.1797 | 9.0488 | 8.9151 | 8.6157 | 8.4138 | 7.9918 | 7.519 | 8.3226 | 8.1458 | 8.0183 | 7.8584 | 7.6929 | 7.5128 | 7.333 | 7.1512 | 6.9772 | 6.7887 | 6.3344 | 6.3328 | 5.8682 | 5.7365
ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | NO | 2.5033 | 2.3937 | 2.2984 | 2.2282 | 2.1555 | 2.0777 | 1.993 | 1.9032 | 1.8386 | 1.772 | 1.6417 | 1.6369 | 1.5905 | 1.5569 | 2.3714 | 2.2762 | 2.2005 | 2.1647 | 2.121 | 2.0799 | 2.035 | 1.9774 | 1.9244 | 1.8681 | 1.7585 | 1.7519 | 1.7165 | 1.6841 | 2.2643 | 2.168 | 2.0886 | 2.0408 | 1.99 | 1.9386 | 1.8611 | 1.788 | 1.7299 | 1.6621 | 1.5297 | 1.5208 | 1.4843 | 1.4556
| TARBERT | CT |  |  |  | 2.5253 | 2.4311 | 2.358 | 2.2588 | 2.1576 | 2.0777 | 1.993 | 1.9113 | 1.8679 | 1.8057 | 1.6849 | 1.664 | 1.5905 | 1.5569 | 2.3782 | 2.2944 | 2.2332 | 2.1783 | 2.121 | 2.0799 | 2.0359 | 1.9954 | 1.9575 | 1.9035 | 1.7997 | 1.7558 | 1.7165 | 1.6841 | 2.2756 | 2.185 | 2.1234 | 2.0659 | 1.9947 | 1.9386 | 1.8611 | 1.788 | 1.7607 | 1.7029 | 1.5795 | 1.5453 | 1.4843 | 1.4556
| TARBERT | LW |  |  |  | 2.5033 | 2.3937 | 2.2984 | 2.2282 | 2.1555 | 2.0876 | 1.9991 | 1.9032 | 1.8386 | 1.772 | 1.6417 | 1.6369 | 1.6032 | 1.5905 | 2.3714 | 2.2762 | 2.2005 | 2.1647 | 2.1246 | 2.0876 | 2.035 | 1.9774 | 1.9244 | 1.8681 | 1.7585 | 1.7519 | 1.7395 | 1.7358 | 2.2643 | 2.168 | 2.0886 | 2.0408 | 1.99 | 1.9395 | 1.866 | 1.7884 | 1.7299 | 1.6621 | 1.5297 | 1.5208 | 1.4935 | 1.4836
| TARBERT | ST |  |  |  | 2.5425 | 2.4637 | 2.4112 | 2.3852 | 2.3524 | 2.3199 | 2.2834 | 2.2451 | 2.2068 | 2.1553 | 2.0438 | 1.8223 | 1.7541 | 1.7186 | 2.3845 | 2.3091 | 2.2617 | 2.2431 | 2.2203 | 2.1978 | 2.1715 | 2.1448 | 2.1165 | 2.0803 | 1.9967 | 1.8199 | 1.7735 | 1.7466 | 2.2844 | 2.2079 | 2.1607 | 2.1418 | 2.1197 | 2.0944 | 2.0654 | 2.0362 | 2.0066 | 1.9683 | 1.8828 | 1.6746 | 1.6138 | 1.5864
| TARBERT | FS |  |  |  | 2.5434 | 2.4867 | 2.4487 | 2.4209 | 2.3908 | 2.3622 | 2.334 | 2.2983 | 2.2655 | 2.2245 | 2.1341 | 1.8815 | 1.693 | 1.6608 | 2.3852 | 2.3284 | 2.2935 | 2.2764 | 2.2562 | 2.2378 | 2.2188 | 2.1961 | 2.1723 | 2.1441 | 2.0798 | 1.8998 | 1.7498 | 1.7143 | 2.2858 | 2.2288 | 2.194 | 2.1763 | 2.1541 | 2.1321 | 2.11 | 2.0832 | 2.0571 | 2.0256 | 1.9557 | 1.75 | 1.5661 | 1.5404
PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | NO | 0.15636 | 0.15396 | 0.14905 | 0.14594 | 0.1395 | 0.13861 | 0.13483 | 0.1271 | 0.12423 | 0.12388 | 0.11623 | 0.11101 | 0.1053 | 0.10475 | 0.16469 | 0.16354 | 0.16124 | 0.15963 | 0.15677 | 0.15553 | 0.15322 | 0.14946 | 0.14722 | 0.1455 | 0.13981 | 0.13658 | 0.13255 | 0.1296 | 0.15607 | 0.15388 | 0.14947 | 0.14657 | 0.14087 | 0.13988 | 0.13632 | 0.12933 | 0.12645 | 0.12579 | 0.11798 | 0.11329 | 0.10827 | 0.10772
| TARBERT JURA | CT |  |  |  | 0.15836 | 0.1579 | 0.15273 | 0.1491 | 0.14342 | 0.14037 | 0.13583 | 0.1271 | 0.12513 | 0.12388 | 0.11645 | 0.11153 | 0.1053 | 0.10475 | 0.16539 | 0.16494 | 0.16249 | 0.16033 | 0.15729 | 0.15553 | 0.15322 | 0.14946 | 0.14761 | 0.1455 | 0.13992 | 0.13658 | 0.13255 | 0.1296 | 0.15778 | 0.15729 | 0.15263 | 0.14925 | 0.14405 | 0.14124 | 0.13712 | 0.12933 | 0.12737 | 0.12579 | 0.1184 | 0.11381 | 0.10827 | 0.10772
| TARBERT JURA | LW |  |  |  | 0.15636 | 0.15396 | 0.14905 | 0.14594 | 0.1395 | 0.13861 | 0.13483 | 0.1288 | 0.12423 | 0.1245 | 0.11623 | 0.11101 | 0.10731 | 0.10731 | 0.16469 | 0.16354 | 0.16124 | 0.15963 | 0.15677 | 0.15597 | 0.15365 | 0.1503 | 0.14722 | 0.14569 | 0.13981 | 0.13775 | 0.13627 | 0.13627 | 0.15607 | 0.15388 | 0.14947 | 0.14657 | 0.14087 | 0.13988 | 0.13632 | 0.13077 | 0.12645 | 0.12599 | 0.11798 | 0.11329 | 0.11002 | 0.11002
| TARBERT JURA | ST |  |  |  | 0.15836 | 0.15815 | 0.15596 | 0.15333 | 0.14934 | 0.1487 | 0.14596 | 0.14303 | 0.14168 | 0.13857 | 0.13574 | 0.11555 | 0.11153 | 0.10977 | 0.16539 | 0.16514 | 0.16413 | 0.16291 | 0.16113 | 0.16049 | 0.15903 | 0.1574 | 0.15618 | 0.15412 | 0.15076 | 0.13872 | 0.13513 | 0.13195 | 0.15778 | 0.15754 | 0.15558 | 0.15322 | 0.14971 | 0.14901 | 0.14651 | 0.14382 | 0.14247 | 0.13956 | 0.13631 | 0.11751 | 0.1138 | 0.11226
| TARBERT JURA | FS |  |  |  | 0.16012 | 0.15823 | 0.15796 | 0.15728 | 0.15311 | 0.15261 | 0.15015 | 0.14942 | 0.14525 | 0.14237 | 0.13616 | 0.1207 | 0.11322 | 0.11011 | 0.16609 | 0.16519 | 0.16489 | 0.16444 | 0.16264 | 0.16217 | 0.16092 | 0.16025 | 0.15825 | 0.15664 | 0.15291 | 0.1429 | 0.13525 | 0.13052 | 0.15933 | 0.15762 | 0.15735 | 0.15671 | 0.153 | 0.1525 | 0.15028 | 0.14956 | 0.1458 | 0.14315 | 0.13743 | 0.1227 | 0.11529 | 0.11255
PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | NO | 2.5453 | 2.4749 | 2.4073 | 2.3264 | 2.2507 | 2.1261 | 1.9984 | 1.8969 | 1.823 | 1.7451 | 1.5944 | 1.6633 | 1.5016 | 1.3752 | 2.9154 | 2.8806 | 2.8462 | 2.8093 | 2.7648 | 2.6768 | 2.5844 | 2.5312 | 2.4742 | 2.414 | 2.2974 | 2.2489 | 2.0461 | 1.8343 | 1.5711 | 1.5631 | 1.5568 | 1.5153 | 1.482 | 1.4589 | 1.347 | 1.2653 | 1.1963 | 1.1239 | 0.98504 | 0.95741 | 0.7828 | 0.61885
| TARBERT LOCH FYNE | CT |  |  |  | 2.5648 | 2.5079 | 2.4557 | 2.3522 | 2.2507 | 2.1261 | 1.9984 | 1.8969 | 1.823 | 1.7451 | 1.5944 | 1.6633 | 1.5016 | 1.3752 | 2.9234 | 2.895 | 2.8686 | 2.8176 | 2.7648 | 2.6768 | 2.5844 | 2.5312 | 2.4742 | 2.414 | 2.2974 | 2.2489 | 2.0978 | 1.9281 | 1.5718 | 1.5649 | 1.5595 | 1.5453 | 1.528 | 1.4658 | 1.347 | 1.2653 | 1.1963 | 1.1239 | 0.98504 | 0.95741 | 0.7828 | 0.62661
| TARBERT LOCH FYNE | LW |  |  |  | 2.5453 | 2.4749 | 2.4073 | 2.3264 | 2.2579 | 2.1871 | 2.099 | 1.9985 | 1.9224 | 1.8404 | 1.6789 | 1.8646 | 1.6578 | 1.3894 | 2.9154 | 2.8806 | 2.8462 | 2.8093 | 2.7781 | 2.7471 | 2.7042 | 2.6548 | 2.6036 | 2.5488 | 2.4421 | 2.518 | 2.2848 | 1.9598 | 1.5711 | 1.5631 | 1.5568 | 1.5497 | 1.5449 | 1.5276 | 1.4601 | 1.3837 | 1.3198 | 1.2513 | 1.1179 | 1.2115 | 0.96042 | 0.62952
| TARBERT LOCH FYNE | ST |  |  |  | 2.5803 | 2.5597 | 2.533 | 2.4657 | 2.4207 | 2.3777 | 2.289 | 2.2389 | 2.1535 | 2.0929 | 1.9566 | 1.8642 | 1.6995 | 1.5236 | 2.9311 | 2.9111 | 2.8953 | 2.831 | 2.7865 | 2.7497 | 2.6589 | 2.6178 | 2.5398 | 2.4947 | 2.3928 | 2.2544 | 2.0461 | 1.8343 | 1.574 | 1.5689 | 1.5656 | 1.5153 | 1.482 | 1.4589 | 1.384 | 1.361 | 1.3033 | 1.2806 | 1.2127 | 1.0572 | 0.83793 | 0.61885
| TARBERT LOCH FYNE | FS |  |  |  | 2.5791 | 2.5674 | 2.541 | 2.5028 | 2.4704 | 2.4336 | 2.3961 | 2.3559 | 2.3083 | 2.2664 | 2.1704 | 2.0826 | 1.9666 | 1.9206 | 2.9336 | 2.9156 | 2.9005 | 2.8732 | 2.8495 | 2.8229 | 2.7954 | 2.7676 | 2.7295 | 2.6973 | 2.6268 | 2.5683 | 2.4823 | 2.3961 | 1.5746 | 1.5699 | 1.5665 | 1.5535 | 1.5421 | 1.5287 | 1.5153 | 1.5032 | 1.4813 | 1.4658 | 1.4341 | 1.3524 | 1.2502 | 1.2048
TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | YES | YES | 1.4531 | 1.3993 | 1.3437 | 1.2668 | 1.1906 | 1.1121 | 1.0169 | 0.92264 | 0.89128 | 0.84049 | 0.73538 | 0.74516 | 0.67309 | 0.63182 | 1.8217 | 1.7967 | 1.7682 | 1.7335 | 1.6924 | 1.6503 | 1.6074 | 1.5615 | 1.5227 | 1.48 | 1.3974 | 1.4136 | 1.3536 | 1.3044 | 1.3171 | 1.2914 | 1.2691 | 1.223 | 1.1634 | 1.097 | 1.0266 | 0.95087 | 0.90024 | 0.84423 | 0.73648 | 0.7536 | 0.69981 | 0.66605
| TAYNUILT | CT |  |  |  | 1.4832 | 1.4475 | 1.4099 | 1.3083 | 1.2069 | 1.1121 | 1.0169 | 0.92264 | 0.89512 | 0.85576 | 0.76966 | 0.77679 | 0.67309 | 0.63182 | 1.8324 | 1.8135 | 1.7923 | 1.7433 | 1.6924 | 1.6503 | 1.6074 | 1.5644 | 1.5359 | 1.4978 | 1.4231 | 1.4136 | 1.3536 | 1.3044 | 1.328 | 1.3083 | 1.2918 | 1.2471 | 1.1664 | 1.097 | 1.0266 | 0.95659 | 0.92063 | 0.87288 | 0.77892 | 0.77852 | 0.69981 | 0.66605
| TAYNUILT | LW |  |  |  | 1.4531 | 1.3993 | 1.3437 | 1.2668 | 1.1906 | 1.1153 | 1.0275 | 0.9346 | 0.89128 | 0.84049 | 0.73538 | 0.74516 | 0.69562 | 0.67698 | 1.8217 | 1.7967 | 1.7682 | 1.7335 | 1.6968 | 1.6625 | 1.6145 | 1.5615 | 1.5227 | 1.48 | 1.3974 | 1.4168 | 1.3969 | 1.39 | 1.3171 | 1.2914 | 1.2691 | 1.223 | 1.1634 | 1.1066 | 1.0318 | 0.95087 | 0.90024 | 0.84423 | 0.73648 | 0.7536 | 0.71646 | 0.70203
| TAYNUILT | ST |  |  |  | 1.5087 | 1.4884 | 1.4713 | 1.4468 | 1.416 | 1.3881 | 1.3569 | 1.3207 | 1.2783 | 1.2353 | 1.1317 | 0.9433 | 0.86234 | 0.80763 | 1.8436 | 1.8338 | 1.8244 | 1.8114 | 1.7949 | 1.7786 | 1.7596 | 1.7375 | 1.7113 | 1.6826 | 1.6131 | 1.4846 | 1.4278 | 1.3767 | 1.3443 | 1.336 | 1.3303 | 1.3217 | 1.3104 | 1.3001 | 1.2795 | 1.2481 | 1.2104 | 1.1707 | 1.0745 | 0.90258 | 0.8422 | 0.80529
| TAYNUILT | FS |  |  |  | 1.5191 | 1.5053 | 1.4906 | 1.4671 | 1.4417 | 1.4126 | 1.3851 | 1.354 | 1.3205 | 1.2824 | 1.1979 | 0.95708 | 0.78937 | 0.74119 | 1.8477 | 1.8405 | 1.8324 | 1.8205 | 1.807 | 1.7917 | 1.776 | 1.7579 | 1.7378 | 1.7149 | 1.6623 | 1.5193 | 1.3871 | 1.3167 | 1.349 | 1.3444 | 1.3396 | 1.3316 | 1.3229 | 1.3122 | 1.3027 | 1.2792 | 1.2507 | 1.2183 | 1.1451 | 0.94129 | 0.7876 | 0.75235
BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | NO | 11.585 | 11.2658 | 10.8613 | 10.0879 | 9.2694 | 8.3178 | 7.1058 | 5.906 | 5.0218 | 4.0877 | 2.1869 | 4.0733 | 2.7549 | 1.5296 | 16.7496 | 16.5887 | 16.3155 | 15.8331 | 15.3037 | 14.6389 | 13.805 | 13.0249 | 12.4341 | 11.7994 | 10.5157 | 11.7143 | 9.7435 | 5.2939 | 18.4454 | 18.1711 | 17.756 | 16.9869 | 16.1628 | 15.1856 | 13.9945 | 12.841 | 11.9997 | 11.1073 | 9.2663 | 11.2602 | 10.2352 | 9.1334
| THIMBLEROW | CT |  |  |  | 11.8159 | 11.6278 | 11.335 | 10.5832 | 9.7998 | 8.9272 | 7.9841 | 7.1199 | 6.356 | 5.5879 | 3.9676 | 4.6394 | 2.7549 | 1.5296 | 16.7602 | 16.6121 | 16.401 | 15.9182 | 15.3745 | 14.7343 | 14.054 | 13.5077 | 12.9704 | 12.4221 | 11.237 | 11.7143 | 9.7435 | 7.1275 | 18.4454 | 18.2755 | 18.0289 | 17.4683 | 16.6808 | 15.7946 | 14.8597 | 14.0577 | 13.341 | 12.6186 | 11.0947 | 11.9099 | 10.2352 | 9.1334
| THIMBLEROW | LW |  |  |  | 11.585 | 11.2658 | 10.8613 | 10.0879 | 9.2694 | 8.3178 | 7.1058 | 5.906 | 5.0218 | 4.0877 | 2.1869 | 4.0733 | 3.0956 | 2.5552 | 16.7496 | 16.5887 | 16.3155 | 15.8331 | 15.3037 | 14.6389 | 13.805 | 13.0249 | 12.4341 | 11.7994 | 10.5157 | 12.4321 | 11.907 | 11.5045 | 18.4504 | 18.1711 | 17.756 | 16.9869 | 16.1628 | 15.1856 | 13.9945 | 12.841 | 11.9997 | 11.1073 | 9.2663 | 11.2602 | 10.3539 | 9.8075
| THIMBLEROW | ST |  |  |  | 11.9539 | 11.9236 | 11.8786 | 11.6384 | 11.4101 | 11.1771 | 10.7601 | 10.4452 | 10.0985 | 9.708 | 8.5139 | 9.8061 | 8.8428 | 7.0334 | 16.7765 | 16.7168 | 16.6406 | 16.377 | 16.1424 | 15.9172 | 15.4673 | 15.1272 | 14.767 | 14.3762 | 13.1064 | 13.4934 | 11.7962 | 8.9404 | 18.4665 | 18.4064 | 18.3276 | 18.0576 | 17.8121 | 17.5712 | 17.1101 | 16.79 | 16.445 | 15.7728 | 14.0901 | 16.1209 | 15.264 | 13.8678
| THIMBLEROW | FS |  |  |  | 11.9488 | 11.9262 | 11.8911 | 11.7862 | 11.6646 | 11.4704 | 11.2602 | 11.0343 | 10.7814 | 10.5118 | 9.7999 | 9.6953 | 8.274 | 6.8799 | 16.7845 | 16.7338 | 16.672 | 16.5583 | 16.3977 | 16.1689 | 15.9127 | 15.6315 | 15.3267 | 14.9901 | 14.1878 | 13.298 | 10.3087 | 5.2939 | 18.479 | 18.4336 | 18.3767 | 18.2662 | 18.1391 | 17.9867 | 17.815 | 17.6246 | 17.4287 | 17.2106 | 16.4093 | 16.5126 | 15.2254 | 14.0018
TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0.1263 | 0.12589 | 0.11666 | 0.1137 | 0.11092 | 0.10801 | 0.10182 | 0.097418 | 0.095971 | 0.090912 | 0.082345 | 0.07799 | 0.072239 | 0.069523 | 0.13992 | 0.13952 | 0.13547 | 0.1339 | 0.13229 | 0.13076 | 0.12754 | 0.12479 | 0.12259 | 0.11904 | 0.11276 | 0.11019 | 0.10806 | 0.10678 | 0.1334 | 0.13291 | 0.12465 | 0.12192 | 0.11933 | 0.11666 | 0.11098 | 0.10682 | 0.10495 | 0.09984 | 0.091356 | 0.087243 | 0.082174 | 0.079716
| TIRORAN BRIDGE | CT |  |  |  | 0.12982 | 0.12589 | 0.12298 | 0.11563 | 0.11369 | 0.11185 | 0.1069 | 0.10236 | 0.096471 | 0.091503 | 0.086325 | 0.080301 | 0.072239 | 0.069523 | 0.14135 | 0.13952 | 0.138 | 0.1345 | 0.13295 | 0.13175 | 0.12938 | 0.12716 | 0.12394 | 0.12045 | 0.11538 | 0.11129 | 0.10806 | 0.10678 | 0.13656 | 0.13291 | 0.13024 | 0.12359 | 0.12166 | 0.11991 | 0.11542 | 0.1113 | 0.10588 | 0.101 | 0.09515 | 0.089344 | 0.082174 | 0.079716
| TIRORAN BRIDGE | LW |  |  |  | 0.1263 | 0.12725 | 0.11666 | 0.1137 | 0.11092 | 0.10801 | 0.10182 | 0.097418 | 0.095971 | 0.090912 | 0.082345 | 0.07799 | 0.073895 | 0.072184 | 0.13992 | 0.13996 | 0.13547 | 0.1339 | 0.13229 | 0.13076 | 0.12754 | 0.12479 | 0.12259 | 0.11904 | 0.11276 | 0.11019 | 0.10863 | 0.108 | 0.1334 | 0.13409 | 0.12465 | 0.12192 | 0.11933 | 0.11666 | 0.11098 | 0.10682 | 0.10495 | 0.09984 | 0.091356 | 0.087243 | 0.083616 | 0.082116
| TIRORAN BRIDGE | ST |  |  |  | 0.12981 | 0.12806 | 0.12736 | 0.12685 | 0.12245 | 0.11991 | 0.11894 | 0.11744 | 0.11412 | 0.11231 | 0.10636 | 0.08897 | 0.086033 | 0.08049 | 0.14135 | 0.14046 | 0.14004 | 0.13963 | 0.1377 | 0.13643 | 0.13565 | 0.13457 | 0.13264 | 0.13097 | 0.12643 | 0.11496 | 0.11309 | 0.11126 | 0.13655 | 0.13485 | 0.13419 | 0.13369 | 0.12975 | 0.12743 | 0.12647 | 0.12502 | 0.12188 | 0.11985 | 0.11378 | 0.097154 | 0.094356 | 0.089492
| TIRORAN BRIDGE | FS |  |  |  | 0.12984 | 0.12813 | 0.12907 | 0.12524 | 0.12285 | 0.12228 | 0.11974 | 0.11827 | 0.11727 | 0.11468 | 0.11157 | 0.090695 | 0.080272 | 0.078521 | 0.14137 | 0.14052 | 0.14083 | 0.13914 | 0.13803 | 0.13757 | 0.13633 | 0.13544 | 0.13464 | 0.13314 | 0.13044 | 0.11881 | 0.11118 | 0.11055 | 0.13658 | 0.13492 | 0.1358 | 0.1323 | 0.13015 | 0.12958 | 0.12727 | 0.12589 | 0.1249 | 0.12249 | 0.11904 | 0.099446 | 0.089308 | 0.087765
BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | NO | 0.10407 | 0.080461 | 0.049196 | 0.016291 | -0.020144 | -0.18 | -0.25036 | -0.40919 | -0.53207 | -0.6765 | -0.81478 | -0.96577 | -1.102 | -1.2008 | 0.38861 | 0.37998 | 0.36915 | 0.34202 | 0.31151 | 0.22529 | 0.16633 | 0.093425 | 0.022342 | -0.060999 | -0.16351 | -0.30983 | -0.45298 | -0.60955 | 0.1735 | 0.15162 | 0.12185 | 0.091535 | 0.051131 | -0.091243 | -0.16651 | -0.29643 | -0.40588 | -0.53438 | -0.67389 | -0.83897 | -0.98221 | -1.0973
| TOMATIN | CT |  |  |  | 0.11791 | 0.10246 | 0.082364 | 0.029805 | -0.019109 | -0.18 | -0.25036 | -0.40919 | -0.53207 | -0.6765 | -0.81478 | -0.96577 | -1.102 | -1.2008 | 0.39302 | 0.38216 | 0.36915 | 0.3493 | 0.3211 | 0.22529 | 0.16633 | 0.093425 | 0.022342 | -0.060999 | -0.16351 | -0.30983 | -0.42746 | -0.5419 | 0.18515 | 0.17023 | 0.1499 | 0.09986 | 0.051131 | -0.091243 | -0.16651 | -0.29643 | -0.40588 | -0.53438 | -0.67389 | -0.83897 | -0.98221 | -1.0973
| TOMATIN | LW |  |  |  | 0.10407 | 0.080461 | 0.049196 | 0.016291 | -0.020144 | -0.15173 | -0.19588 | -0.37377 | -0.51436 | -0.66042 | -0.75416 | -0.8124 | -0.96859 | -1.1687 | 0.38861 | 0.37998 | 0.36922 | 0.35315 | 0.3348 | 0.27767 | 0.25304 | 0.17295 | 0.099747 | 0.023262 | -0.047221 | -0.10718 | -0.27889 | -0.51984 | 0.1735 | 0.15162 | 0.12185 | 0.091535 | 0.057607 | -0.045846 | -0.088753 | -0.23385 | -0.35404 | -0.4793 | -0.57736 | -0.6449 | -0.82952 | -1.0753
| TOMATIN | ST |  |  |  | 0.12773 | 0.11417 | 0.097765 | 0.05357 | 0.015578 | -0.075314 | -0.14094 | -0.23821 | -0.34544 | -0.44241 | -0.55832 | -0.78585 | -0.94935 | -1.0914 | 0.39387 | 0.38902 | 0.38347 | 0.34202 | 0.31151 | 0.25908 | 0.19363 | 0.13576 | 0.056685 | -0.0022205 | -0.088046 | -0.28806 | -0.45298 | -0.60955 | 0.19244 | 0.18039 | 0.16562 | 0.11591 | 0.074465 | -0.0027248 | -0.077551 | -0.15986 | -0.26116 | -0.34552 | -0.4612 | -0.70706 | -0.89129 | -1.0547
| TOMATIN | FS |  |  |  | 0.14003 | 0.13154 | 0.11722 | 0.098333 | 0.078668 | 0.0063214 | -0.01935 | -0.10071 | -0.17671 | -0.25653 | -0.34782 | -0.53226 | -0.64461 | -0.68611 | 0.40213 | 0.39901 | 0.39433 | 0.38165 | 0.3693 | 0.3293 | 0.31089 | 0.26467 | 0.21562 | 0.16786 | 0.10642 | -0.012496 | -0.098514 | -0.13695 | 0.20202 | 0.19426 | 0.18179 | 0.16257 | 0.14224 | 0.083449 | 0.05776 | -0.0076979 | -0.07293 | -0.1399 | -0.22749 | -0.40426 | -0.52062 | -0.55979
LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | NO | 0.11128 | 0.11122 | 0.11109 | 0.11095 | 0.11079 | 0.11067 | 0.10867 | 0.10844 | 0.10811 | 0.10744 | 0.10667 | 0.10914 | 0.10912 | 0.10909 | 0.11415 | 0.1141 | 0.11398 | 0.11372 | 0.11354 | 0.11335 | 0.11285 | 0.11243 | 0.11195 | 0.11142 | 0.11056 | 0.11257 | 0.11255 | 0.11252 | 0.11249 | 0.11237 | 0.11217 | 0.11185 | 0.11162 | 0.11138 | 0.11014 | 0.10962 | 0.10904 | 0.10839 | 0.1076 | 0.11045 | 0.11043 | 0.11039
| TORBOLL | CT |  |  |  | 0.11129 | 0.11122 | 0.11112 | 0.11095 | 0.11079 | 0.11067 | 0.11039 | 0.10855 | 0.10836 | 0.10812 | 0.10732 | 0.10919 | 0.10913 | 0.10909 | 0.11416 | 0.11411 | 0.11398 | 0.11372 | 0.11354 | 0.11335 | 0.11314 | 0.1126 | 0.11227 | 0.112 | 0.11133 | 0.1126 | 0.11256 | 0.11252 | 0.11249 | 0.11237 | 0.11217 | 0.11185 | 0.11162 | 0.11138 | 0.11112 | 0.10984 | 0.10943 | 0.1091 | 0.10828 | 0.11049 | 0.11043 | 0.11039
| TORBOLL | LW |  |  |  | 0.11128 | 0.11122 | 0.11109 | 0.11099 | 0.11086 | 0.11076 | 0.10867 | 0.10844 | 0.10811 | 0.10744 | 0.10667 | 0.10914 | 0.10912 | 0.10912 | 0.11415 | 0.1141 | 0.114 | 0.11385 | 0.11367 | 0.11349 | 0.11285 | 0.11243 | 0.11195 | 0.11142 | 0.11056 | 0.11257 | 0.11255 | 0.11255 | 0.11249 | 0.11241 | 0.1122 | 0.11201 | 0.11178 | 0.11155 | 0.11014 | 0.10962 | 0.10904 | 0.10839 | 0.1076 | 0.11045 | 0.11043 | 0.11043
| TORBOLL | ST |  |  |  | 0.11129 | 0.11126 | 0.11123 | 0.11118 | 0.11111 | 0.11104 | 0.11094 | 0.11082 | 0.11061 | 0.11018 | 0.10937 | 0.11097 | 0.11053 | 0.11053 | 0.11416 | 0.11414 | 0.11411 | 0.11407 | 0.11402 | 0.11391 | 0.11375 | 0.11356 | 0.1133 | 0.11298 | 0.11228 | 0.1133 | 0.11309 | 0.11308 | 0.1125 | 0.11247 | 0.11243 | 0.11235 | 0.11224 | 0.11209 | 0.11189 | 0.11163 | 0.11132 | 0.11093 | 0.11011 | 0.11203 | 0.11163 | 0.11163
| TORBOLL | FS |  |  |  | 0.11129 | 0.11127 | 0.11124 | 0.1112 | 0.11115 | 0.1111 | 0.11103 | 0.11095 | 0.11086 | 0.11075 | 0.11039 | 0.11131 | 0.11084 | 0.11083 | 0.11416 | 0.11415 | 0.11412 | 0.11409 | 0.11405 | 0.11401 | 0.11392 | 0.1138 | 0.11365 | 0.11348 | 0.11309 | 0.11368 | 0.1132 | 0.11319 | 0.1125 | 0.11248 | 0.11245 | 0.11239 | 0.11232 | 0.11223 | 0.11211 | 0.11195 | 0.11176 | 0.11154 | 0.1111 | 0.11223 | 0.11189 | 0.11189
KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | NO | 13.9264 | 13.7914 | 13.4748 | 12.8182 | 11.9922 | 10.8499 | 9.5202 | 8.3306 | 6.85 | 5.5475 | 3.9838 | 3.0127 | 1.5929 | 0.7493 | 16.2154 | 16.1365 | 16.006 | 15.6909 | 15.2007 | 14.3579 | 13.3704 | 12.5261 | 11.2485 | 10.1743 | 9.2684 | 8.709 | 7.5999 | 6.475 | 14.5424 | 14.4184 | 14.2328 | 13.8284 | 13.2681 | 12.269 | 10.9603 | 9.7979 | 8.3643 | 7.1218 | 5.6439 | 4.7767 | 3.4213 | 2.5968
| TORRYBURN | CT |  |  |  | 14.007 | 13.887 | 13.681 | 13.2457 | 12.5172 | 11.3955 | 10.189 | 9.2352 | 7.7682 | 6.3483 | 4.6116 | 3.0537 | 1.5929 | 0.7493 | 16.2486 | 16.1627 | 16.0109 | 15.6909 | 15.2222 | 14.3579 | 13.395 | 12.713 | 11.5084 | 10.3985 | 9.504 | 8.709 | 7.5999 | 6.475 | 14.6135 | 14.5005 | 14.3049 | 13.8853 | 13.343 | 12.4057 | 11.3769 | 10.6249 | 9.2278 | 7.8572 | 6.2187 | 4.7813 | 3.4213 | 2.5968
| TORRYBURN | LW |  |  |  | 13.9264 | 13.7914 | 13.4748 | 12.8182 | 11.9922 | 10.8499 | 9.5202 | 8.3306 | 6.85 | 5.5475 | 3.9838 | 3.0127 | 1.8407 | 0.98683 | 16.2154 | 16.1365 | 16.006 | 15.6918 | 15.2007 | 14.3721 | 13.3704 | 12.5261 | 11.2485 | 10.1743 | 9.2684 | 9.0211 | 8.1718 | 7.3186 | 14.5424 | 14.4184 | 14.2328 | 13.8284 | 13.2681 | 12.269 | 10.9603 | 9.7979 | 8.3643 | 7.1218 | 5.6439 | 4.7767 | 3.603 | 2.6445
| TORRYBURN | ST |  |  |  | 14.0317 | 13.9692 | 13.8958 | 13.5636 | 13.1376 | 12.4662 | 11.5329 | 10.8817 | 9.6844 | 8.6135 | 7.636 | 6.0396 | 4.5324 | 3.0245 | 16.2617 | 16.2187 | 16.1674 | 15.8254 | 15.3923 | 14.7439 | 13.7872 | 13.152 | 11.949 | 10.8812 | 10.0152 | 9.6768 | 8.4171 | 6.974 | 14.636 | 14.5781 | 14.51 | 14.1427 | 13.7047 | 13.0424 | 12.0779 | 11.435 | 10.2571 | 9.2185 | 8.2603 | 7.334 | 5.8817 | 4.441
| TORRYBURN | FS |  |  |  | 14.0857 | 14.0379 | 13.9818 | 13.8144 | 13.5441 | 13.0584 | 12.559 | 12.0494 | 11.1391 | 10.4174 | 9.4799 | 7.5561 | 5.5273 | 4.4031 | 16.3084 | 16.2738 | 16.2328 | 16.0827 | 15.8204 | 15.355 | 14.8742 | 14.3782 | 13.4833 | 12.7794 | 12.0539 | 11.2972 | 9.4553 | 7.859 | 14.6869 | 14.6424 | 14.5902 | 14.4192 | 14.1519 | 13.6772 | 13.1888 | 12.6924 | 11.811 | 11.1128 | 10.321 | 9.0405 | 7.1599 | 6.1613
LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | NO | 0.62491 | 0.5975 | 0.56737 | 0.53801 | 0.49956 | 0.46796 | 0.42484 | 0.37936 | 0.35011 | 0.31545 | 0.25424 | 0.22985 | 0.19472 | 0.17256 | 0.79263 | 0.77991 | 0.76377 | 0.74888 | 0.72989 | 0.71144 | 0.69045 | 0.66438 | 0.6417 | 0.61511 | 0.56556 | 0.55641 | 0.5345 | 0.51728 | 0.69764 | 0.67323 | 0.64524 | 0.61833 | 0.5834 | 0.55479 | 0.51452 | 0.47223 | 0.44376 | 0.40871 | 0.34398 | 0.32145 | 0.2905 | 0.27056
| TRESSADY | CT |  |  |  | 0.64288 | 0.62162 | 0.60305 | 0.55805 | 0.51101 | 0.47293 | 0.42913 | 0.39401 | 0.36921 | 0.33646 | 0.2772 | 0.2511 | 0.19472 | 0.17256 | 0.79919 | 0.78857 | 0.7776 | 0.75432 | 0.73002 | 0.71144 | 0.69052 | 0.67272 | 0.65547 | 0.63035 | 0.58253 | 0.56205 | 0.5345 | 0.51728 | 0.71306 | 0.69387 | 0.67648 | 0.63533 | 0.59228 | 0.55777 | 0.51819 | 0.48621 | 0.4624 | 0.4307 | 0.36784 | 0.34062 | 0.2905 | 0.27056
| TRESSADY | LW |  |  |  | 0.62491 | 0.5975 | 0.56737 | 0.53801 | 0.49956 | 0.46796 | 0.42484 | 0.37936 | 0.35011 | 0.31545 | 0.25424 | 0.22985 | 0.2032 | 0.19554 | 0.79263 | 0.77991 | 0.76377 | 0.74888 | 0.72989 | 0.71438 | 0.69045 | 0.66438 | 0.6417 | 0.61511 | 0.56556 | 0.55641 | 0.54544 | 0.54253 | 0.69764 | 0.67323 | 0.64524 | 0.61833 | 0.5834 | 0.55479 | 0.51452 | 0.47223 | 0.44376 | 0.40871 | 0.34398 | 0.32145 | 0.29792 | 0.2913
| TRESSADY | ST |  |  |  | 0.64727 | 0.6408 | 0.62473 | 0.61058 | 0.59366 | 0.5757 | 0.55797 | 0.53694 | 0.51206 | 0.48467 | 0.42632 | 0.30751 | 0.2533 | 0.22337 | 0.80121 | 0.79764 | 0.79018 | 0.78295 | 0.774 | 0.76434 | 0.75405 | 0.74174 | 0.72697 | 0.71001 | 0.66976 | 0.58878 | 0.55867 | 0.54059 | 0.717 | 0.71106 | 0.69663 | 0.68375 | 0.66825 | 0.65177 | 0.63532 | 0.61577 | 0.59255 | 0.56668 | 0.50874 | 0.39169 | 0.34256 | 0.31636
| TRESSADY | FS |  |  |  | 0.65121 | 0.64675 | 0.63823 | 0.62194 | 0.60903 | 0.59503 | 0.57754 | 0.56071 | 0.54131 | 0.51838 | 0.46897 | 0.32946 | 0.22874 | 0.20812 | 0.80278 | 0.80012 | 0.79564 | 0.78802 | 0.78115 | 0.77372 | 0.76455 | 0.75512 | 0.74414 | 0.73124 | 0.70233 | 0.6185 | 0.54833 | 0.5308 | 0.72048 | 0.71636 | 0.70861 | 0.69395 | 0.68213 | 0.66933 | 0.65334 | 0.63782 | 0.61987 | 0.59867 | 0.55258 | 0.41742 | 0.32099 | 0.30292
SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | NO | 5.4366 | 5.3911 | 5.3363 | 5.2684 | 5.1969 | 5.0838 | 4.9682 | 4.8739 | 4.7978 | 4.7252 | 4.5771 | 4.4525 | 3.98 | 3.2768 | 6.539 | 6.5109 | 6.467 | 6.4205 | 6.3431 | 6.2524 | 6.1585 | 6.0927 | 5.9979 | 5.8826 | 5.6665 | 5.4133 | 4.9119 | 4.0449 | 5.1032 | 5.0681 | 5.0292 | 4.9741 | 4.9153 | 4.8089 | 4.701 | 4.6209 | 4.5496 | 4.4702 | 4.2914 | 4.2997 | 3.7577 | 2.8847
| TUMBLIN | CT |  |  |  | 5.4608 | 5.4257 | 5.3865 | 5.2905 | 5.1978 | 5.0838 | 4.9682 | 4.8739 | 4.7978 | 4.7252 | 4.5771 | 4.4525 | 4.1169 | 3.7995 | 6.5491 | 6.527 | 6.4949 | 6.4226 | 6.3431 | 6.2524 | 6.1585 | 6.0927 | 5.9979 | 5.8826 | 5.6665 | 5.4133 | 5.0529 | 4.6507 | 5.1226 | 5.0981 | 5.0727 | 4.995 | 4.9153 | 4.8089 | 4.701 | 4.6209 | 4.5496 | 4.4702 | 4.2914 | 4.2997 | 3.9352 | 3.5526
| TUMBLIN | LW |  |  |  | 5.4366 | 5.3911 | 5.3363 | 5.2684 | 5.1969 | 5.1281 | 5.0415 | 4.9476 | 4.861 | 4.7674 | 4.5905 | 4.5108 | 3.98 | 3.2768 | 6.539 | 6.5109 | 6.467 | 6.4205 | 6.3682 | 6.3235 | 6.2522 | 6.1715 | 6.0616 | 5.9441 | 5.7246 | 5.535 | 4.9119 | 4.0449 | 5.1032 | 5.0681 | 5.0292 | 4.9741 | 4.9169 | 4.8624 | 4.7986 | 4.7239 | 4.6277 | 4.5154 | 4.3019 | 4.4031 | 3.7577 | 2.8847
| TUMBLIN | ST |  |  |  | 5.486 | 5.4767 | 5.4638 | 5.4154 | 5.3767 | 5.3383 | 5.2705 | 5.2266 | 5.1136 | 5.0389 | 4.8714 | 4.6936 | 4.2581 | 3.8097 | 6.5601 | 6.5526 | 6.5412 | 6.4915 | 6.4496 | 6.412 | 6.336 | 6.2902 | 6.159 | 6.0779 | 5.8919 | 5.4744 | 4.9539 | 4.4018 | 5.1504 | 5.1476 | 5.1416 | 5.096 | 5.0625 | 5.0214 | 4.942 | 4.8931 | 4.7592 | 4.6751 | 4.4829 | 4.4335 | 3.9376 | 3.4051
| TUMBLIN | FS |  |  |  | 5.4874 | 5.4787 | 5.4683 | 5.4384 | 5.4055 | 5.3717 | 5.3384 | 5.2987 | 5.2403 | 5.1882 | 5.0744 | 5.0352 | 4.7732 | 4.6881 | 6.5607 | 6.5537 | 6.5442 | 6.521 | 6.4944 | 6.4663 | 6.4364 | 6.4024 | 6.3397 | 6.2841 | 6.1607 | 5.9228 | 5.6931 | 5.5646 | 5.1498 | 5.1462 | 5.1418 | 5.1188 | 5.0945 | 5.0689 | 5.0405 | 5.0024 | 4.9382 | 4.8814 | 4.7573 | 4.756 | 4.6731 | 4.5837
TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.26962 | 0.26626 | 0.25827 | 0.17577 | 0.11289 | 0.070246 | -0.068582 | -0.11126 | -0.21905 | -0.26301 | -0.36515 | -0.62608 | -0.97944 | -1.3302 | 0.40478 | 0.40035 | 0.39084 | 0.28788 | 0.20951 | 0.15644 | -0.016948 | -0.070126 | -0.20454 | -0.25913 | -0.38256 | -0.63172 | -1.0637 | -1.5013 | 0.16554 | 0.15957 | 0.14629 | 0.047085 | -0.032991 | -0.088364 | -0.26409 | -0.32071 | -0.45863 | -0.51791 | -0.65217 | -0.91397 | -1.3487 | -1.7835
| TUMMEL BRIDGE | CT |  |  |  | 0.27017 | 0.26626 | 0.25827 | 0.2373 | 0.20745 | 0.096754 | -0.024986 | -0.069674 | -0.12596 | -0.19012 | -0.31419 | -0.54138 | -0.77859 | -1.0271 | 0.40533 | 0.40035 | 0.39084 | 0.36542 | 0.32942 | 0.20004 | 0.062064 | 0.020057 | -0.04742 | -0.11434 | -0.24013 | -0.48648 | -0.77276 | -1.0807 | 0.16655 | 0.15962 | 0.14629 | 0.11557 | 0.074386 | -0.05937 | -0.20195 | -0.24898 | -0.32115 | -0.39199 | -0.527 | -0.78682 | -1.0761 | -1.3822
| TUMMEL BRIDGE | LW |  |  |  | 0.26962 | 0.26676 | 0.26113 | 0.25659 | 0.24525 | 0.23277 | 0.21287 | 0.1935 | 0.15872 | 0.11736 | 0.0408 | -0.04295 | -0.45606 | -1.0577 | 0.40478 | 0.40139 | 0.39465 | 0.3893 | 0.38071 | 0.37453 | 0.36417 | 0.35173 | 0.31503 | 0.27584 | 0.20191 | 0.14767 | -0.36507 | -1.114 | 0.16554 | 0.15957 | 0.14971 | 0.14144 | 0.12965 | 0.11991 | 0.10387 | 0.085229 | 0.042003 | -0.0042385 | -0.092816 | -0.15993 | -0.67427 | -1.4247
| TUMMEL BRIDGE | ST |  |  |  | 0.27052 | 0.26851 | 0.26606 | 0.17577 | 0.11289 | 0.070246 | -0.068582 | -0.11126 | -0.21905 | -0.26301 | -0.36515 | -0.62608 | -0.97944 | -1.3302 | 0.40585 | 0.40343 | 0.4006 | 0.28788 | 0.20951 | 0.15644 | -0.016948 | -0.070126 | -0.20454 | -0.25913 | -0.38256 | -0.63172 | -1.0637 | -1.5013 | 0.1679 | 0.16488 | 0.16092 | 0.047085 | -0.032991 | -0.088364 | -0.26409 | -0.32071 | -0.45863 | -0.51791 | -0.65217 | -0.91397 | -1.3487 | -1.7835
| TUMMEL BRIDGE | FS |  |  |  | 0.27397 | 0.27224 | 0.27028 | 0.25041 | 0.23017 | 0.20658 | 0.18262 | 0.16115 | 0.12032 | 0.090587 | 0.028869 | -0.046708 | -0.11652 | -0.16265 | 0.4099 | 0.40782 | 0.40548 | 0.38077 | 0.35564 | 0.32639 | 0.29659 | 0.26993 | 0.21914 | 0.18232 | 0.10585 | 0.090599 | 0.027667 | -0.031458 | 0.17138 | 0.16867 | 0.16578 | 0.13968 | 0.11335 | 0.082534 | 0.050947 | 0.022612 | -0.030887 | -0.070383 | -0.15285 | -0.18869 | -0.26278 | -0.31689
MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | NO | 3.8703 | 3.7574 | 3.601 | 3.4136 | 3.1713 | 2.8925 | 2.2182 | 1.2556 | 0.50556 | 0.055842 | -0.92164 | -1.2234 | -2.6078 | -3.3189 | 7.6946 | 7.5417 | 7.3288 | 7.0768 | 6.8002 | 6.4763 | 5.7994 | 4.9586 | 4.3002 | 3.9094 | 3.0539 | 2.6283 | 1.7604 | 0.99114 | 4.1455 | 3.8509 | 3.4792 | 2.9969 | 2.4802 | 1.973 | 1.0312 | -0.15775 | -1.007 | -1.5825 | -2.7961 | -3.3061 | -4.5606 | -5.2452
| TURRIFF | CT |  |  |  | 3.9318 | 3.8433 | 3.692 | 3.435 | 3.1713 | 2.8925 | 2.2182 | 1.433 | 0.8286 | 0.35912 | -0.65327 | -1.2234 | -2.6078 | -3.3189 | 7.788 | 7.6825 | 7.5149 | 7.1854 | 6.8313 | 6.4763 | 5.7994 | 5.0243 | 4.3784 | 3.9262 | 3.0539 | 2.6283 | 1.7604 | 0.99114 | 4.3685 | 4.1882 | 3.9276 | 3.3583 | 2.7585 | 2.1701 | 1.2541 | 0.22166 | -0.61715 | -1.2645 | -2.5242 | -3.3061 | -4.5606 | -5.2452
| TURRIFF | LW |  |  |  | 3.8703 | 3.7574 | 3.601 | 3.4136 | 3.208 | 2.9995 | 2.3281 | 1.2556 | 0.50556 | 0.055842 | -0.92164 | -1.1852 | -2.0867 | -2.6938 | 7.6946 | 7.5417 | 7.3288 | 7.0768 | 6.8002 | 6.5335 | 5.8547 | 4.9586 | 4.3002 | 3.9094 | 3.072 | 3.038 | 2.4723 | 1.9213 | 4.1455 | 3.8509 | 3.4792 | 2.9969 | 2.4802 | 1.973 | 1.0312 | -0.15775 | -1.007 | -1.5825 | -2.7961 | -3.1391 | -3.9945 | -4.6453
| TURRIFF | ST |  |  |  | 3.9715 | 3.927 | 3.8743 | 3.7486 | 3.6263 | 3.5057 | 2.9302 | 2.2515 | 1.6909 | 1.4272 | 0.86092 | 0.8116 | -2.7471e-05 | -1.3289 | 7.8271 | 7.7648 | 7.6911 | 7.5262 | 7.364 | 7.2078 | 6.6537 | 6.0055 | 5.4391 | 5.1345 | 4.4711 | 3.5601 | 2.6241 | 1.6229 | 4.4533 | 4.3426 | 4.219 | 3.9864 | 3.7513 | 3.5224 | 2.8891 | 2.1412 | 1.4841 | 1.0871 | 0.22751 | -1.0573 | -2.2925 | -3.4551
| TURRIFF | FS |  |  |  | 3.9893 | 3.9601 | 3.9213 | 3.8523 | 3.7763 | 3.6931 | 3.3784 | 2.8689 | 2.4659 | 2.2637 | 1.8392 | 1.4594 | 0.3508 | -0.61066 | 7.8494 | 7.804 | 7.7466 | 7.6482 | 7.5378 | 7.4208 | 7.1126 | 6.6191 | 6.1973 | 5.9442 | 5.4011 | 4.2949 | 2.9198 | 1.7838 | 4.5029 | 4.4278 | 4.3359 | 4.1785 | 4.0078 | 3.8319 | 3.46 | 2.8877 | 2.3713 | 2.0281 | 1.3012 | -0.31299 | -1.8704 | -2.6841
RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | NO | 2.4016 | 2.3807 | 2.3593 | 2.3382 | 2.3048 | 2.278 | 2.2483 | 2.2032 | 2.146 | 2.1068 | 2.006 | 2.1457 | 2.1129 | 2.0902 | 1.8883 | 1.8797 | 1.869 | 1.8576 | 1.8398 | 1.8277 | 1.8145 | 1.8013 | 1.7857 | 1.7672 | 1.7062 | 1.737 | 1.7195 | 1.7045 | 1.0014 | 0.98122 | 0.95098 | 0.91528 | 0.87491 | 0.83921 | 0.79939 | 0.7587 | 0.71364 | 0.68291 | 0.60298 | 0.86903 | 0.84093 | 0.82523
| TYNDRUM | CT |  |  |  | 2.4092 | 2.3927 | 2.3746 | 2.3436 | 2.3048 | 2.278 | 2.2483 | 2.2032 | 2.146 | 2.1068 | 2.006 | 2.1548 | 2.1129 | 2.0902 | 1.8903 | 1.8823 | 1.8728 | 1.8576 | 1.8398 | 1.8277 | 1.8145 | 1.8013 | 1.7859 | 1.768 | 1.7062 | 1.7377 | 1.7195 | 1.7045 | 1.007 | 0.98157 | 0.95098 | 0.91528 | 0.87491 | 0.83921 | 0.79939 | 0.7587 | 0.71364 | 0.68291 | 0.60298 | 0.8726 | 0.84093 | 0.82523
| TYNDRUM | LW |  |  |  | 2.4016 | 2.3807 | 2.3593 | 2.3382 | 2.3117 | 2.2883 | 2.2548 | 2.2258 | 2.2026 | 2.178 | 2.1128 | 2.1457 | 2.1166 | 2.0988 | 1.8883 | 1.8797 | 1.869 | 1.8592 | 1.8472 | 1.8371 | 1.8201 | 1.8029 | 1.7857 | 1.7672 | 1.7316 | 1.737 | 1.7273 | 1.7214 | 1.0014 | 0.98122 | 0.95911 | 0.93753 | 0.91151 | 0.88786 | 0.85127 | 0.81524 | 0.78321 | 0.74922 | 0.68357 | 0.86903 | 0.84715 | 0.83421
| TYNDRUM | ST |  |  |  | 2.4171 | 2.4084 | 2.4003 | 2.3914 | 2.3791 | 2.3656 | 2.3465 | 2.328 | 2.3054 | 2.2566 | 2.1331 | 2.2171 | 2.1832 | 2.1556 | 1.8931 | 1.8894 | 1.8857 | 1.8811 | 1.8749 | 1.8679 | 1.8587 | 1.8487 | 1.8375 | 1.825 | 1.7854 | 1.7602 | 1.7418 | 1.7271 | 1.0141 | 1.0046 | 0.99488 | 0.98323 | 0.96573 | 0.945 | 0.91759 | 0.8876 | 0.85399 | 0.81611 | 0.71815 | 0.92111 | 0.8988 | 0.87637
| TYNDRUM | FS |  |  |  | 2.4177 | 2.4154 | 2.407 | 2.3969 | 2.3864 | 2.3726 | 2.3671 | 2.3517 | 2.3367 | 2.3204 | 2.2557 | 2.2274 | 2.17 | 2.1444 | 1.8934 | 1.8918 | 1.8882 | 1.8838 | 1.8786 | 1.8725 | 1.8681 | 1.8605 | 1.8522 | 1.843 | 1.8199 | 1.7812 | 1.7357 | 1.7173 | 1.0151 | 1.0116 | 1.0034 | 0.99224 | 0.98033 | 0.96244 | 0.94882 | 0.92666 | 0.90348 | 0.87722 | 0.81205 | 0.90932 | 0.8871 | 0.86639
DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | NO | 1.5154 | 1.4671 | 1.4044 | 1.3356 | 1.2574 | 1.144 | 1.0189 | 0.92578 | 0.85495 | 0.76344 | 0.59471 | 0.46324 | 0.28241 | 0.16066 | 1.6596 | 1.6357 | 1.601 | 1.5668 | 1.506 | 1.4253 | 1.3386 | 1.2859 | 1.2245 | 1.1468 | 1.0016 | 0.85347 | 0.66783 | 0.48972 | 1.4524 | 1.4084 | 1.3529 | 1.2937 | 1.218 | 1.1075 | 0.98762 | 0.90477 | 0.83147 | 0.73719 | 0.56286 | 0.40456 | 0.22597 | 0.07137
| UIG | CT |  |  |  | 1.5413 | 1.5072 | 1.4629 | 1.3682 | 1.2588 | 1.144 | 1.0189 | 0.92578 | 0.85495 | 0.76344 | 0.59471 | 0.46324 | 0.28241 | 0.16066 | 1.6697 | 1.6507 | 1.6236 | 1.5691 | 1.506 | 1.4253 | 1.3386 | 1.2859 | 1.2245 | 1.1468 | 1.0016 | 0.85347 | 0.7093 | 0.57329 | 1.4754 | 1.4439 | 1.4024 | 1.3163 | 1.218 | 1.1075 | 0.98762 | 0.90477 | 0.83147 | 0.73719 | 0.56286 | 0.40456 | 0.22597 | 0.091514
| UIG | LW |  |  |  | 1.5154 | 1.4671 | 1.4044 | 1.3356 | 1.2574 | 1.193 | 1.0973 | 0.9951 | 0.91964 | 0.84083 | 0.68417 | 0.59484 | 0.4044 | 0.19063 | 1.6596 | 1.6357 | 1.601 | 1.5668 | 1.5272 | 1.4952 | 1.4413 | 1.3813 | 1.3203 | 1.2556 | 1.1302 | 1.0572 | 0.86718 | 0.61427 | 1.4524 | 1.4084 | 1.3529 | 1.2937 | 1.226 | 1.1707 | 1.0853 | 0.99302 | 0.91682 | 0.83675 | 0.67923 | 0.58306 | 0.36996 | 0.11028
| UIG | ST |  |  |  | 1.5528 | 1.5364 | 1.515 | 1.4583 | 1.4094 | 1.3612 | 1.2776 | 1.2208 | 1.1363 | 1.0672 | 0.90531 | 0.57378 | 0.36879 | 0.20039 | 1.6739 | 1.6649 | 1.6529 | 1.6011 | 1.5585 | 1.5212 | 1.4415 | 1.3982 | 1.3231 | 1.2694 | 1.1434 | 0.86391 | 0.66783 | 0.48972 | 1.4854 | 1.4704 | 1.4507 | 1.3888 | 1.3368 | 1.2877 | 1.1962 | 1.1402 | 1.0508 | 0.98216 | 0.82111 | 0.47536 | 0.25583 | 0.07137
| UIG | FS |  |  |  | 1.5623 | 1.5489 | 1.5335 | 1.5032 | 1.4684 | 1.4324 | 1.3962 | 1.3537 | 1.2961 | 1.2423 | 1.1207 | 0.82012 | 0.59535 | 0.53706 | 1.6776 | 1.6701 | 1.661 | 1.6402 | 1.6165 | 1.5911 | 1.5644 | 1.5355 | 1.4941 | 1.4558 | 1.3693 | 1.1761 | 1.007 | 0.95026 | 1.4938 | 1.4815 | 1.4673 | 1.4375 | 1.4033 | 1.3677 | 1.3316 | 1.2915 | 1.2359 | 1.1842 | 1.0676 | 0.78609 | 0.56935 | 0.51716
GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | YES | NO | -1.3567 | -1.4012 | -1.4533 | -1.5303 | -1.6162 | -1.7172 | -1.8196 | -1.9245 | -1.9409 | -1.9568 | -2.0002 | -1.913 | -1.9726 | -2.0201 | -0.6233 | -0.64607 | -0.68101 | -0.71907 | -0.77788 | -0.82359 | -0.87083 | -0.92396 | -0.9757 | -1.0337 | -1.1473 | -1.091 | -1.153 | -1.2434 | -0.88575 | -0.90326 | -0.92782 | -0.99368 | -1.0788 | -1.1602 | -1.2435 | -1.3285 | -1.3873 | -1.4579 | -1.596 | -1.5192 | -1.5667 | -1.6045
| ULLAPOOL | CT |  |  |  | -1.3393 | -1.3669 | -1.4031 | -1.511 | -1.6162 | -1.7172 | -1.8196 | -1.9245 | -1.9409 | -1.9568 | -2.0002 | -1.8834 | -1.9726 | -2.0201 | -0.61487 | -0.63665 | -0.66312 | -0.71907 | -0.77788 | -0.82359 | -0.87083 | -0.92396 | -0.96143 | -1.0096 | -1.1106 | -1.091 | -1.153 | -1.2232 | -0.88536 | -0.90326 | -0.92053 | -0.98174 | -1.0788 | -1.1602 | -1.2435 | -1.3285 | -1.372 | -1.4297 | -1.5482 | -1.4946 | -1.5667 | -1.6045
| ULLAPOOL | LW |  |  |  | -1.3567 | -1.4012 | -1.4533 | -1.5303 | -1.6132 | -1.6896 | -1.7747 | -1.8701 | -1.8941 | -1.9224 | -1.99 | -1.913 | -1.9676 | -1.993 | -0.6233 | -0.64607 | -0.68101 | -0.71866 | -0.76363 | -0.80075 | -0.85714 | -0.92272 | -0.9757 | -1.0337 | -1.1473 | -1.0832 | -1.1046 | -1.1143 | -0.88575 | -0.89687 | -0.92782 | -0.99368 | -1.0679 | -1.1332 | -1.2217 | -1.3234 | -1.3873 | -1.4579 | -1.596 | -1.5192 | -1.5617 | -1.5816
| ULLAPOOL | ST |  |  |  | -1.335 | -1.3418 | -1.3493 | -1.3572 | -1.3679 | -1.3907 | -1.4123 | -1.4406 | -1.4732 | -1.508 | -1.5913 | -1.6664 | -1.7345 | -1.7826 | -0.6065 | -0.61493 | -0.62666 | -0.64039 | -0.65812 | -0.67718 | -0.69843 | -0.72474 | -0.75628 | -0.79344 | -0.88335 | -1.0038 | -1.0651 | -1.1274 | -0.88119 | -0.88774 | -0.89485 | -0.90252 | -0.91284 | -0.92296 | -0.93553 | -0.95978 | -1.0016 | -1.0498 | -1.1657 | -1.3134 | -1.3689 | -1.4043
| ULLAPOOL | FS |  |  |  | -1.3262 | -1.3316 | -1.3376 | -1.3439 | -1.353 | -1.3782 | -1.405 | -1.4277 | -1.4593 | -1.491 | -1.5547 | -1.6646 | -1.818 | -1.8584 | -0.59974 | -0.60703 | -0.61653 | -0.62991 | -0.64472 | -0.66141 | -0.68055 | -0.70074 | -0.72638 | -0.75472 | -0.81973 | -0.95843 | -1.1309 | -1.2434 | -0.87269 | -0.87785 | -0.88351 | -0.88962 | -0.89695 | -0.90521 | -0.91493 | -0.93325 | -0.96817 | -1.0056 | -1.0876 | -1.2679 | -1.4394 | -1.471
SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | NO | -0.70585 | -0.72005 | -0.73447 | -0.75971 | -0.78544 | -0.81477 | -0.84543 | -0.87736 | -0.90184 | -0.9311 | -1.005 | -1.0819 | -1.4629 | -1.9811 | 0.029531 | 0.025689 | 0.010619 | -0.0088542 | -0.02959 | -0.049256 | -0.069466 | -0.093866 | -0.15271 | -0.21561 | -0.33249 | -0.39359 | -0.8542 | -1.4981 | -0.90885 | -0.91674 | -0.92427 | -0.93984 | -0.95954 | -0.97911 | -0.99845 | -1.0183 | -1.0439 | -1.0817 | -1.2047 | -1.2712 | -1.7269 | -2.3712
| UNST | CT |  |  |  | -0.69937 | -0.70992 | -0.71847 | -0.74859 | -0.78329 | -0.81477 | -0.84543 | -0.87736 | -0.90184 | -0.92754 | -0.97447 | -1.0235 | -1.2166 | -1.4433 | 0.030232 | 0.027005 | 0.014545 | -0.0088542 | -0.02959 | -0.049256 | -0.069466 | -0.09094 | -0.13668 | -0.18073 | -0.26991 | -0.32405 | -0.56036 | -0.8376 | -0.90725 | -0.91337 | -0.91839 | -0.93716 | -0.95954 | -0.97911 | -0.99845 | -1.0183 | -1.0439 | -1.0704 | -1.1433 | -1.2061 | -1.4284 | -1.6843
| UNST | LW |  |  |  | -0.70585 | -0.72005 | -0.73447 | -0.75971 | -0.78544 | -0.80795 | -0.83435 | -0.86529 | -0.89647 | -0.9311 | -1.005 | -1.0819 | -1.4629 | -1.9811 | 0.029531 | 0.025689 | 0.010619 | -0.0052176 | -0.022573 | -0.038685 | -0.064126 | -0.093866 | -0.15271 | -0.21561 | -0.33249 | -0.39359 | -0.8542 | -1.4981 | -0.90885 | -0.91674 | -0.92427 | -0.93984 | -0.95578 | -0.96973 | -0.98587 | -1.0055 | -1.0394 | -1.0817 | -1.2047 | -1.2712 | -1.7269 | -2.3712
| UNST | ST |  |  |  | -0.67639 | -0.6721 | -0.66901 | -0.66575 | -0.66185 | -0.65939 | -0.65475 | -0.65516 | -0.7015 | -0.71706 | -0.7619 | -0.82026 | -1.0923 | -1.404 | 0.037703 | 0.039586 | 0.038732 | 0.033194 | 0.026595 | 0.018121 | 0.0082871 | -0.0047606 | -0.075206 | -0.11315 | -0.20346 | -0.25223 | -0.60744 | -0.99165 | -0.88959 | -0.88455 | -0.88041 | -0.87553 | -0.87058 | -0.86625 | -0.86048 | -0.85844 | -0.91276 | -0.93011 | -0.995 | -1.0596 | -1.3621 | -1.747
| UNST | FS |  |  |  | -0.68345 | -0.67955 | -0.6797 | -0.68088 | -0.68858 | -0.69205 | -0.69567 | -0.70239 | -0.71884 | -0.73156 | -0.75715 | -0.77133 | -0.80108 | -0.84648 | 0.035549 | 0.037095 | 0.037512 | 0.033165 | 0.025382 | 0.01776 | 0.0091913 | -0.0013115 | -0.031318 | -0.056754 | -0.11152 | -0.086564 | -0.16508 | -0.22504 | -0.89478 | -0.89065 | -0.88905 | -0.88703 | -0.88979 | -0.88937 | -0.88934 | -0.89141 | -0.90906 | -0.92124 | -0.94609 | -0.95658 | -0.97223 | -1.0169
SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | NO | 6.6493 | 6.6172 | 6.5827 | 6.5178 | 6.4398 | 6.3191 | 6.1823 | 6.042 | 5.9614 | 5.8352 | 5.5678 | 5.3833 | 4.9516 | 4.4189 | 8.0908 | 8.058 | 8.0083 | 7.9487 | 7.8657 | 7.7936 | 7.7148 | 7.6352 | 7.5271 | 7.4042 | 7.1689 | 6.9948 | 6.5127 | 5.8628 | 6.6003 | 6.56 | 6.5076 | 6.424 | 6.3354 | 6.2321 | 6.1159 | 5.9972 | 5.9549 | 5.8583 | 5.6497 | 5.7295 | 5.2137 | 4.5539
| VOE | CT |  |  |  | 6.6726 | 6.6502 | 6.6274 | 6.5379 | 6.446 | 6.3191 | 6.1823 | 6.042 | 5.9737 | 5.8802 | 5.6425 | 5.4893 | 5.1803 | 4.9086 | 8.1067 | 8.0803 | 8.0431 | 7.9557 | 7.8657 | 7.7936 | 7.7148 | 7.6352 | 7.5578 | 7.4552 | 7.2429 | 7.0608 | 6.7619 | 6.4342 | 6.6208 | 6.6007 | 6.5685 | 6.4531 | 6.3405 | 6.2321 | 6.1159 | 5.9972 | 5.9549 | 5.905 | 5.7617 | 5.8423 | 5.5026 | 5.1877
| VOE | LW |  |  |  | 6.6493 | 6.6172 | 6.5827 | 6.5178 | 6.4398 | 6.3382 | 6.2062 | 6.0635 | 5.9614 | 5.8352 | 5.5678 | 5.3833 | 4.9516 | 4.4189 | 8.0908 | 8.058 | 8.0083 | 7.9487 | 7.8824 | 7.8248 | 7.7349 | 7.6352 | 7.5271 | 7.4042 | 7.1689 | 6.9948 | 6.5127 | 5.8628 | 6.6003 | 6.56 | 6.5076 | 6.424 | 6.3354 | 6.2527 | 6.1506 | 6.0424 | 5.9708 | 5.8583 | 5.6497 | 5.7295 | 5.2137 | 4.5539
| VOE | ST |  |  |  | 6.7092 | 6.7062 | 6.704 | 6.6975 | 6.6938 | 6.6845 | 6.6474 | 6.5958 | 6.4894 | 6.3981 | 6.1933 | 5.8889 | 5.4984 | 5.1308 | 8.1227 | 8.1123 | 8.0997 | 8.0809 | 8.0592 | 8.0331 | 8.0004 | 7.9636 | 7.863 | 7.7871 | 7.6172 | 7.2302 | 6.8122 | 6.3745 | 6.6528 | 6.65 | 6.6479 | 6.6401 | 6.6257 | 6.6042 | 6.58 | 6.5557 | 6.4695 | 6.3918 | 6.2075 | 6.2051 | 5.7757 | 5.3408
| VOE | FS |  |  |  | 6.7071 | 6.7047 | 6.7018 | 6.6888 | 6.676 | 6.6623 | 6.6477 | 6.6116 | 6.5487 | 6.4844 | 6.3482 | 6.1147 | 5.7306 | 5.6393 | 8.1234 | 8.1146 | 8.1035 | 8.0841 | 8.0614 | 8.038 | 8.0092 | 7.9774 | 7.9229 | 7.8692 | 7.7548 | 7.4838 | 7.2164 | 7.0922 | 6.651 | 6.6488 | 6.6461 | 6.6345 | 6.6112 | 6.5859 | 6.5589 | 6.5301 | 6.4824 | 6.4367 | 6.3336 | 6.247 | 6.1061 | 6.0107
GLENAGNES | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 18.0528 | 17.92 | 17.7752 | 16.8192 | 15.7358 | 14.051 | 12.2284 | 10.9989 | 10.4972 | 9.966 | 8.9455 | 8.6203 | 7.9317 | 7.3768 | 18.9318 | 18.8463 | 18.7416 | 17.9052 | 16.8844 | 15.0581 | 13.0066 | 11.6943 | 11.1419 | 10.5489 | 9.4134 | 9.2989 | 8.5534 | 7.8977 | 18.4999 | 18.3987 | 18.296 | 17.2723 | 16.1118 | 14.1755 | 12.0065 | 10.5772 | 10.0033 | 9.3871 | 8.194 | 7.7209 | 6.906 | 6.2282
| WALTON | CT |  |  |  | 18.1555 | 18.069 | 17.9544 | 17.4947 | 16.9311 | 16.0054 | 15.0291 | 14.5422 | 14.1916 | 13.8454 | 13.127 | 12.9587 | 12.2256 | 11.7915 | 18.9318 | 18.8463 | 18.7416 | 18.4595 | 18.0744 | 17.1302 | 16.1024 | 15.6768 | 15.3217 | 15.0135 | 14.3444 | 13.9322 | 12.6857 | 11.0192 | 18.5608 | 18.4812 | 18.369 | 17.9812 | 17.4778 | 16.4821 | 15.4267 | 14.9367 | 14.5626 | 14.1824 | 13.3943 | 13.18 | 12.4563 | 11.9964
| WALTON | LW |  |  |  | 18.0528 | 17.92 | 17.7752 | 16.8192 | 15.7358 | 14.051 | 12.2284 | 10.9989 | 10.4972 | 9.966 | 8.9455 | 8.6203 | 7.9317 | 7.3768 | 18.9363 | 18.8657 | 18.802 | 17.9052 | 16.8844 | 15.0581 | 13.0066 | 11.6943 | 11.1419 | 10.5489 | 9.4134 | 9.2989 | 8.5534 | 7.8977 | 18.4999 | 18.3987 | 18.296 | 17.2723 | 16.1118 | 14.1755 | 12.0065 | 10.5772 | 10.0033 | 9.3871 | 8.194 | 7.7209 | 6.906 | 6.2282
| WALTON | ST |  |  |  | 18.2445 | 18.231 | 18.2318 | 17.614 | 17.1178 | 16.8376 | 15.9378 | 15.6449 | 15.3569 | 15.1784 | 14.4855 | 14.5435 | 13.9093 | 13.0734 | 18.9372 | 18.8815 | 18.8471 | 18.0368 | 17.4094 | 17.0328 | 15.8856 | 15.5007 | 15.14 | 14.9264 | 14.2096 | 13.737 | 12.4594 | 10.6943 | 18.5732 | 18.5283 | 18.4996 | 17.7083 | 17.0893 | 16.7169 | 15.5727 | 15.1886 | 14.8257 | 14.6054 | 13.8346 | 14.0872 | 13.3954 | 12.6439
| WALTON | FS |  |  |  | 18.2312 | 18.2149 | 18.2124 | 18.0283 | 17.7965 | 17.6154 | 17.4193 | 17.2382 | 17.0874 | 16.9338 | 16.6209 | 16.5331 | 15.9472 | 15.3575 | 18.9462 | 18.9006 | 18.8707 | 18.6368 | 18.3687 | 18.1471 | 17.9091 | 17.6952 | 17.5205 | 17.351 | 16.9678 | 16.179 | 14.4603 | 11.1907 | 18.5825 | 18.5493 | 18.5288 | 18.3157 | 18.0628 | 17.853 | 17.6299 | 17.4299 | 17.2702 | 17.1193 | 16.8091 | 16.8304 | 16.2305 | 15.7538
INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 8.5062 | 8.0975 | 7.6217 | 7.1246 | 6.6058 | 5.8307 | 4.7346 | 3.7229 | 2.5799 | 1.6034 | -0.71164 | 5.826 | 5.2313 | 4.6557 | 10.952 | 10.6015 | 10.2077 | 9.7823 | 9.3358 | 8.6726 | 7.8548 | 7.1559 | 6.374 | 5.6899 | 3.6361 | 8.8884 | 8.3981 | 7.7385 | 11.2687 | 10.8796 | 10.4276 | 9.9485 | 9.4461 | 8.8701 | 8.1966 | 7.6347 | 6.7404 | 5.7935 | 3.388 | 9.1111 | 8.6162 | 7.9521
| WATERLOO PLACE | CT |  |  |  | 8.5067 | 8.0975 | 7.6217 | 7.1246 | 6.6058 | 5.8307 | 4.7346 | 3.7229 | 2.5799 | 1.6034 | -0.47406 | 6.5069 | 5.9362 | 5.5226 | 10.9555 | 10.6015 | 10.2077 | 9.7823 | 9.3358 | 8.6726 | 7.8548 | 7.1559 | 6.374 | 5.6983 | 4.0776 | 9.6979 | 9.4352 | 9.1152 | 11.2694 | 10.8796 | 10.4276 | 9.9485 | 9.4461 | 8.8701 | 8.1966 | 7.6347 | 6.7404 | 5.7935 | 3.7817 | 9.9577 | 9.7242 | 9.4599
| WATERLOO PLACE | LW |  |  |  | 8.5062 | 8.1585 | 7.8057 | 7.4556 | 7.0572 | 6.5489 | 5.8143 | 4.6274 | 3.3958 | 2.0413 | -0.71164 | 5.826 | 5.2313 | 4.6557 | 10.952 | 10.6492 | 10.362 | 10.028 | 9.6463 | 9.1282 | 8.4182 | 7.5052 | 6.6405 | 5.6899 | 3.6361 | 8.8884 | 8.3981 | 7.7385 | 11.2687 | 10.9388 | 10.6048 | 10.2415 | 9.8282 | 9.2771 | 8.5062 | 7.7376 | 7.0502 | 6.0646 | 3.388 | 9.1111 | 8.6162 | 7.9521
| WATERLOO PLACE | ST |  |  |  | 8.539 | 8.2972 | 8.1382 | 7.8567 | 7.5618 | 7.2287 | 6.7075 | 6.1973 | 5.3886 | 4.1937 | 1.2017 | 7.0017 | 6.6056 | 6.2125 | 10.9824 | 10.7688 | 10.6396 | 10.356 | 10.0764 | 9.776 | 9.2739 | 8.8404 | 8.1717 | 7.3458 | 5.2728 | 9.4222 | 8.9578 | 8.5021 | 11.3004 | 11.0713 | 10.9218 | 10.6213 | 10.3185 | 9.9866 | 9.4422 | 8.9462 | 8.3894 | 7.7513 | 5.351 | 9.6649 | 9.2155 | 8.8115
| WATERLOO PLACE | FS |  |  |  | 8.5821 | 8.3945 | 8.2789 | 8.1293 | 7.9553 | 7.7494 | 7.5086 | 7.2001 | 6.8872 | 6.5294 | 5.1154 | 7.7248 | 7.4789 | 7.1665 | 11.0241 | 10.8627 | 10.7709 | 10.6332 | 10.4763 | 10.2923 | 10.0782 | 9.8194 | 9.5484 | 9.2413 | 8.186 | 10.1815 | 9.9103 | 9.6311 | 11.3422 | 11.1658 | 11.0579 | 10.9086 | 10.7363 | 10.5325 | 10.2952 | 9.9979 | 9.6945 | 9.3494 | 8.514 | 10.4824 | 10.2439 | 10.0756
LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | NO | 14.316 | 14.0514 | 13.6434 | 12.9748 | 12.345 | 11.7061 | 10.9918 | 10.2709 | 9.6399 | 8.9705 | 7.6549 | 6.7306 | 5.7076 | 4.9786 | 15.7184 | 15.5767 | 15.3399 | 15.0338 | 14.7358 | 14.4462 | 14.072 | 13.6769 | 13.2624 | 12.8178 | 11.9507 | 11.26 | 10.234 | 8.992 | 14.338 | 14.1087 | 13.7589 | 13.1762 | 12.6178 | 12.0572 | 11.4112 | 10.7525 | 10.1578 | 9.5271 | 8.2898 | 7.4742 | 6.4643 | 5.7268
| WEST KIRKTON | CT |  |  |  | 14.5169 | 14.3692 | 14.0992 | 13.4659 | 12.8516 | 12.2696 | 11.7046 | 11.1708 | 10.5412 | 9.812 | 8.4036 | 6.8105 | 5.7076 | 4.9786 | 15.7845 | 15.6864 | 15.5115 | 15.1747 | 14.8365 | 14.5317 | 14.2292 | 13.9526 | 13.5694 | 13.1038 | 12.1977 | 11.26 | 10.234 | 8.992 | 14.5105 | 14.3862 | 14.1583 | 13.5958 | 13.0412 | 12.5176 | 12.0048 | 11.5238 | 10.9402 | 10.2626 | 8.953 | 7.5132 | 6.4643 | 5.7268
| WEST KIRKTON | LW |  |  |  | 14.316 | 14.0514 | 13.6434 | 12.9748 | 12.345 | 11.7061 | 10.9918 | 10.2709 | 9.6399 | 8.9705 | 7.6549 | 6.7306 | 5.8908 | 5.2008 | 15.7184 | 15.5767 | 15.3399 | 15.0338 | 14.7358 | 14.4462 | 14.072 | 13.6769 | 13.2624 | 12.8178 | 11.9507 | 11.6238 | 10.9022 | 10.0715 | 14.338 | 14.1087 | 13.7589 | 13.1762 | 12.6178 | 12.0572 | 11.4112 | 10.7525 | 10.1578 | 9.5271 | 8.2898 | 7.4742 | 6.5742 | 5.7303
| WEST KIRKTON | ST |  |  |  | 14.556 | 14.4467 | 14.2632 | 14.0994 | 13.9597 | 13.8152 | 13.6469 | 13.4936 | 13.2554 | 13.0218 | 12.4835 | 11.0786 | 9.7288 | 8.3869 | 15.7988 | 15.7298 | 15.6192 | 15.4952 | 15.3804 | 15.2609 | 15.1049 | 14.9634 | 14.7195 | 14.4938 | 13.9663 | 12.7459 | 11.4865 | 9.9563 | 14.545 | 14.4577 | 14.3128 | 14.1694 | 14.0418 | 13.9115 | 13.7475 | 13.6007 | 13.3545 | 13.1269 | 12.5972 | 11.2521 | 9.9339 | 8.6213
| WEST KIRKTON | FS |  |  |  | 14.5652 | 14.4787 | 14.3292 | 14.1832 | 14.0562 | 13.9177 | 13.79 | 13.6668 | 13.4537 | 13.2258 | 12.7361 | 11.4723 | 9.8261 | 8.6236 | 15.8032 | 15.7441 | 15.6489 | 15.5473 | 15.4489 | 15.3412 | 15.2311 | 15.117 | 14.9314 | 14.7332 | 14.2837 | 13.116 | 11.3475 | 9.2191 | 14.5528 | 14.4852 | 14.3697 | 14.249 | 14.1383 | 14.0176 | 13.9021 | 13.7862 | 13.5831 | 13.3693 | 12.9056 | 11.7424 | 10.2284 | 9.1611
KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | NO | 0.078175 | 0.062171 | 0.046483 | 0.029658 | 0.0083334 | -0.037942 | -0.092323 | -0.11941 | -0.14763 | -0.17727 | -0.22918 | -0.32351 | -0.42386 | -0.5464 | 0.09616 | 0.089479 | 0.081819 | 0.060154 | 0.035575 | 0.00912 | -0.040147 | -0.059035 | -0.10195 | -0.12335 | -0.17065 | -0.29525 | -0.4357 | -0.57891 | 0.08333 | 0.069103 | 0.054929 | 0.039831 | 0.018752 | -0.03514 | -0.09469 | -0.12178 | -0.15286 | -0.18548 | -0.24375 | -0.35436 | -0.49474 | -0.64058
| WESTER DRUMMOND | CT |  |  |  | 0.088275 | 0.075366 | 0.066265 | 0.041406 | 0.010753 | -0.037942 | -0.092323 | -0.11941 | -0.14763 | -0.17727 | -0.22918 | -0.32351 | -0.41991 | -0.50759 | 0.099749 | 0.094147 | 0.089092 | 0.074218 | 0.054639 | 0.00912 | -0.040147 | -0.059035 | -0.08562 | -0.11444 | -0.16648 | -0.27076 | -0.36973 | -0.47293 | 0.092203 | 0.080716 | 0.072407 | 0.048617 | 0.018752 | -0.03514 | -0.09469 | -0.12178 | -0.15286 | -0.18548 | -0.24375 | -0.35436 | -0.46379 | -0.5674
| WESTER DRUMMOND | LW |  |  |  | 0.078175 | 0.062171 | 0.046483 | 0.029658 | 0.0083334 | -0.0083474 | -0.035545 | -0.052913 | -0.073384 | -0.091677 | -0.12998 | -0.17803 | -0.31861 | -0.50554 | 0.09616 | 0.089479 | 0.081819 | 0.074108 | 0.064461 | 0.0569 | 0.043907 | 0.033363 | 0.015868 | -0.0012913 | -0.034375 | -0.078978 | -0.23925 | -0.46639 | 0.08333 | 0.069103 | 0.054929 | 0.039831 | 0.020716 | 0.0057623 | -0.018764 | -0.035034 | -0.056599 | -0.075912 | -0.11686 | -0.17007 | -0.33911 | -0.56994
| WESTER DRUMMOND | ST |  |  |  | 0.092295 | 0.087386 | 0.081843 | 0.049627 | 0.028934 | 0.0089068 | -0.042304 | -0.059406 | -0.098835 | -0.12288 | -0.17456 | -0.30079 | -0.42386 | -0.5464 | 0.10114 | 0.098828 | 0.096083 | 0.060154 | 0.035575 | 0.016434 | -0.039719 | -0.05814 | -0.10195 | -0.12335 | -0.17065 | -0.29525 | -0.4357 | -0.57891 | 0.095524 | 0.09115 | 0.086139 | 0.047887 | 0.022727 | 0.00046616 | -0.059798 | -0.079824 | -0.12635 | -0.1522 | -0.20819 | -0.34873 | -0.49474 | -0.64058
| WESTER DRUMMOND | FS |  |  |  | 0.093815 | 0.09277 | 0.085891 | 0.074854 | 0.061624 | 0.048847 | 0.036015 | 0.020374 | -9.3172e-06 | -0.016954 | -0.052824 | -0.12887 | -0.18331 | -0.21295 | 0.10172 | 0.10084 | 0.09766 | 0.088139 | 0.077601 | 0.066343 | 0.054763 | 0.042777 | 0.023773 | 0.0088373 | -0.022622 | -0.073757 | -0.11605 | -0.14737 | 0.096864 | 0.095837 | 0.089736 | 0.077906 | 0.064103 | 0.050353 | 0.036513 | 0.020496 | -0.0018594 | -0.020125 | -0.058642 | -0.13222 | -0.18543 | -0.2157
THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | NO | 0.30455 | 0.28727 | 0.26756 | 0.23273 | 0.19276 | 0.14308 | 0.096612 | 0.050127 | 0.046422 | 0.043228 | 0.031164 | 0.070717 | 0.048138 | 0.031817 | 0.54983 | 0.54206 | 0.53206 | 0.51713 | 0.49609 | 0.47536 | 0.45561 | 0.43564 | 0.42918 | 0.42164 | 0.37154 | 0.42973 | 0.41222 | 0.39775 | 0.42813 | 0.41267 | 0.39478 | 0.36434 | 0.32867 | 0.28592 | 0.24578 | 0.20557 | 0.20041 | 0.18423 | 0.12008 | 0.2142 | 0.19534 | 0.18107
| WESTRAY | CT |  |  |  | 0.31685 | 0.3024 | 0.29093 | 0.23919 | 0.19276 | 0.14308 | 0.096612 | 0.050127 | 0.046422 | 0.043228 | 0.031164 | 0.080971 | 0.048138 | 0.031817 | 0.55435 | 0.54744 | 0.54022 | 0.51713 | 0.49609 | 0.47536 | 0.45561 | 0.43564 | 0.42918 | 0.42164 | 0.40463 | 0.42975 | 0.41222 | 0.39775 | 0.43662 | 0.42596 | 0.41528 | 0.36951 | 0.32867 | 0.28592 | 0.24578 | 0.20557 | 0.20041 | 0.19473 | 0.16154 | 0.22331 | 0.19534 | 0.18107
| WESTRAY | LW |  |  |  | 0.30455 | 0.28727 | 0.26756 | 0.23273 | 0.19726 | 0.16393 | 0.12621 | 0.08109 | 0.070036 | 0.05974 | 0.038105 | 0.070717 | 0.050599 | 0.045218 | 0.54983 | 0.54206 | 0.53206 | 0.51717 | 0.50169 | 0.48731 | 0.46914 | 0.44748 | 0.43678 | 0.42505 | 0.37154 | 0.42973 | 0.42166 | 0.41939 | 0.42813 | 0.41267 | 0.39478 | 0.36434 | 0.33344 | 0.30454 | 0.27096 | 0.23087 | 0.21528 | 0.18423 | 0.12008 | 0.2142 | 0.19755 | 0.1932
| WESTRAY | ST |  |  |  | 0.32573 | 0.31991 | 0.31691 | 0.30986 | 0.29825 | 0.29128 | 0.28155 | 0.26931 | 0.25575 | 0.24061 | 0.20453 | 0.17763 | 0.15219 | 0.13283 | 0.5577 | 0.5548 | 0.5527 | 0.54882 | 0.54288 | 0.53838 | 0.53246 | 0.52513 | 0.51666 | 0.50455 | 0.46239 | 0.46742 | 0.45137 | 0.43651 | 0.43722 | 0.43555 | 0.43349 | 0.43063 | 0.42082 | 0.41044 | 0.39752 | 0.38103 | 0.36071 | 0.33665 | 0.27806 | 0.30253 | 0.27934 | 0.26323
| WESTRAY | FS |  |  |  | 0.32955 | 0.32402 | 0.32174 | 0.31308 | 0.30208 | 0.29256 | 0.28118 | 0.27215 | 0.261 | 0.24548 | 0.22253 | 0.16129 | 0.11403 | 0.098094 | 0.55917 | 0.55646 | 0.55475 | 0.55054 | 0.54522 | 0.5403 | 0.53446 | 0.52919 | 0.52278 | 0.51442 | 0.49959 | 0.469 | 0.43601 | 0.41928 | 0.43757 | 0.43623 | 0.43464 | 0.43246 | 0.42546 | 0.41689 | 0.40659 | 0.39584 | 0.38206 | 0.3647 | 0.33041 | 0.29561 | 0.24924 | 0.23623
TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.9629 | 2.6985 | 2.4045 | 2.0804 | 1.7476 | 1.4159 | 0.90259 | 0.50535 | 0.29862 | 0.075929 | -0.374 | -0.29937 | -0.83481 | -1.1477 | 4.6464 | 4.527 | 4.3645 | 4.2028 | 4.0082 | 3.7802 | 3.4323 | 3.2158 | 3.0284 | 2.7951 | 2.3243 | 2.2878 | 1.9202 | 1.5969 | 3.6206 | 3.4154 | 3.1597 | 2.8949 | 2.6133 | 2.3445 | 1.8909 | 1.4848 | 1.1997 | 0.89996 | 0.30159 | 0.33583 | -0.2052 | -0.51518
| WHITEHOUSE | CT |  |  |  | 3.1507 | 2.9693 | 2.7603 | 2.3407 | 1.9116 | 1.4885 | 0.92357 | 0.50535 | 0.3142 | 0.10509 | -0.31542 | -0.21283 | -0.83481 | -1.1477 | 4.7107 | 4.6217 | 4.4939 | 4.2596 | 4.0082 | 3.7802 | 3.4323 | 3.2158 | 3.0284 | 2.8 | 2.3566 | 2.2878 | 1.9202 | 1.5969 | 3.7507 | 3.6089 | 3.4308 | 3.0741 | 2.6982 | 2.3503 | 1.8909 | 1.4986 | 1.253 | 0.96792 | 0.40872 | 0.35437 | -0.2052 | -0.51518
| WHITEHOUSE | LW |  |  |  | 2.9629 | 2.6985 | 2.4045 | 2.0804 | 1.7476 | 1.4159 | 0.90259 | 0.51427 | 0.29862 | 0.075929 | -0.374 | -0.29937 | -0.61948 | -0.89588 | 4.6464 | 4.527 | 4.3645 | 4.2028 | 4.0263 | 3.8609 | 3.5108 | 3.2541 | 3.032 | 2.7951 | 2.3243 | 2.4199 | 2.2005 | 1.9676 | 3.6206 | 3.4154 | 3.1597 | 2.8949 | 2.6133 | 2.3445 | 1.8913 | 1.4848 | 1.1997 | 0.89996 | 0.30159 | 0.33583 | 0.011617 | -0.28222
| WHITEHOUSE | ST |  |  |  | 3.2694 | 3.1673 | 3.0657 | 2.8928 | 2.7268 | 2.5604 | 2.2205 | 2.0393 | 1.813 | 1.5957 | 1.1253 | 0.52592 | -0.024774 | -0.49311 | 4.7496 | 4.7 | 4.6443 | 4.5395 | 4.4336 | 4.3274 | 4.0647 | 3.9338 | 3.7602 | 3.5881 | 3.1938 | 2.5725 | 2.1615 | 1.7847 | 3.8317 | 3.7522 | 3.6679 | 3.5194 | 3.371 | 3.2226 | 2.923 | 2.7489 | 2.5292 | 2.3119 | 1.8235 | 0.94593 | 0.45599 | 0.059454
| WHITEHOUSE | FS |  |  |  | 3.3291 | 3.2587 | 3.1845 | 3.0507 | 2.9096 | 2.7653 | 2.5393 | 2.3827 | 2.1919 | 1.9982 | 1.5968 | 0.57734 | -0.1099 | -0.46383 | 4.7698 | 4.7324 | 4.6885 | 4.617 | 4.5361 | 4.4512 | 4.2935 | 4.1906 | 4.0615 | 3.926 | 3.6284 | 2.93 | 2.2539 | 1.8623 | 3.8702 | 3.8127 | 3.748 | 3.6382 | 3.5174 | 3.393 | 3.2007 | 3.0578 | 2.883 | 2.7016 | 2.3112 | 1.2743 | 0.51762 | 0.2232
PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 7.0147 | 6.4977 | 5.8367 | 4.8942 | 3.8936 | 2.914 | 1.6999 | 0.38124 | -0.90023 | -2.2317 | -4.8976 | -6.8749 | -8.3519 | -9.4713 | 8.4356 | 8.151 | 7.7702 | 7.2967 | 6.7868 | 6.296 | 5.6467 | 4.9293 | 4.1698 | 3.3724 | 1.7174 | 0.76023 | -0.5984 | -2.2598 | 7.6201 | 7.1844 | 6.6201 | 5.8022 | 4.9328 | 4.0807 | 3.0241 | 1.8758 | 0.753 | -0.46549 | -2.8927 | -4.3814 | -5.8945 | -7.2295
| WHITESTRIPES | CT |  |  |  | 7.2301 | 6.8623 | 6.379 | 5.428 | 4.4051 | 3.4206 | 2.4028 | 1.4001 | 0.20279 | -1.1378 | -3.806 | -5.8309 | -7.1288 | -8.1275 | 8.511 | 8.2897 | 8.0027 | 7.4777 | 6.9042 | 6.3328 | 5.7378 | 5.1942 | 4.4884 | 3.6807 | 2.0686 | 0.76023 | -0.5984 | -2.2598 | 7.8014 | 7.4976 | 7.1043 | 6.2754 | 5.3817 | 4.4978 | 3.5824 | 2.703 | 1.644 | 0.44658 | -1.969 | -3.7432 | -5.0357 | -6.0721
| WHITESTRIPES | LW |  |  |  | 7.0147 | 6.4977 | 5.8367 | 4.8942 | 3.8936 | 2.914 | 1.6999 | 0.38124 | -0.90023 | -2.2317 | -4.8976 | -6.8749 | -8.3519 | -9.4713 | 8.4356 | 8.151 | 7.7702 | 7.2967 | 6.7868 | 6.296 | 5.6467 | 4.9293 | 4.1698 | 3.3724 | 1.7174 | 0.94292 | -0.28362 | -1.5732 | 7.6201 | 7.1844 | 6.6201 | 5.8022 | 4.9328 | 4.0807 | 3.0241 | 1.8758 | 0.753 | -0.46549 | -2.8927 | -4.3814 | -5.8945 | -7.2295
| WHITESTRIPES | ST |  |  |  | 7.3039 | 7.0109 | 6.6745 | 6.2565 | 5.8324 | 5.3998 | 4.8641 | 4.3622 | 3.7091 | 3.0581 | 1.5811 | -0.71813 | -2.2874 | -3.7726 | 8.5396 | 8.3687 | 8.1757 | 7.8837 | 7.5955 | 7.3082 | 6.904 | 6.5617 | 6.0571 | 5.5972 | 4.5432 | 2.7135 | 1.0646 | -0.87259 | 7.864 | 7.6351 | 7.3728 | 7.0128 | 6.6579 | 6.3039 | 5.8331 | 5.409 | 4.7995 | 4.2158 | 2.8786 | 0.73056 | -0.84901 | -2.3485
| WHITESTRIPES | FS |  |  |  | 7.3515 | 7.1129 | 6.8444 | 6.5177 | 6.1607 | 5.7856 | 5.378 | 4.9454 | 4.4071 | 3.8531 | 2.6508 | 0.029728 | -2.578 | -3.8635 | 8.5635 | 8.4155 | 8.2519 | 8.0431 | 7.8125 | 7.5662 | 7.2958 | 7.0061 | 6.6265 | 6.2377 | 5.3752 | 3.4517 | 1.0264 | -1.4725 | 7.9019 | 7.7212 | 7.5205 | 7.2634 | 6.9799 | 6.6822 | 6.3569 | 6.0121 | 5.5509 | 5.0693 | 4.0146 | 1.7881 | -0.5497 | -1.678
CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 7.1133 | 7.0596 | 6.9849 | 6.8947 | 6.8002 | 6.706 | 6.5984 | 6.4681 | 6.3751 | 6.2777 | 6.0836 | 5.9934 | 5.9194 | 5.8735 | 7.3332 | 7.3035 | 7.2573 | 7.2077 | 7.1469 | 7.0907 | 7.0343 | 6.9524 | 6.8807 | 6.8045 | 6.6548 | 6.5963 | 6.5404 | 6.494 | 6.5491 | 6.4913 | 6.4156 | 6.3202 | 6.2221 | 6.1319 | 6.0156 | 5.8876 | 5.8077 | 5.7248 | 5.5576 | 5.4879 | 5.4007 | 5.3495
| WHITING BAY | CT |  |  |  | 7.1481 | 7.1075 | 7.0554 | 6.9346 | 6.8086 | 6.706 | 6.6045 | 6.5003 | 6.4275 | 6.3272 | 6.1382 | 6.0339 | 5.9194 | 5.8735 | 7.3487 | 7.3252 | 7.2916 | 7.2212 | 7.1469 | 7.0907 | 7.0343 | 6.9767 | 6.9213 | 6.8436 | 6.6967 | 6.6078 | 6.5404 | 6.494 | 6.5902 | 6.5471 | 6.4956 | 6.3705 | 6.2418 | 6.1319 | 6.0236 | 5.9123 | 5.8477 | 5.7622 | 5.5999 | 5.5299 | 5.4007 | 5.3495
| WHITING BAY | LW |  |  |  | 7.1133 | 7.0596 | 6.9849 | 6.8947 | 6.8002 | 6.7172 | 6.5984 | 6.4681 | 6.3751 | 6.2777 | 6.0836 | 5.9934 | 5.936 | 5.9214 | 7.3332 | 7.3035 | 7.2573 | 7.2077 | 7.1537 | 7.1077 | 7.0345 | 6.9524 | 6.8807 | 6.8045 | 6.6548 | 6.5963 | 6.5686 | 6.5623 | 6.5491 | 6.4913 | 6.4156 | 6.3202 | 6.2221 | 6.1341 | 6.0156 | 5.8876 | 5.8077 | 5.7248 | 5.5576 | 5.4879 | 5.4207 | 5.4028
| WHITING BAY | ST |  |  |  | 7.1778 | 7.1619 | 7.1439 | 7.1149 | 7.084 | 7.0488 | 7.009 | 6.9645 | 6.908 | 6.8363 | 6.6795 | 6.3317 | 6.2496 | 6.1994 | 7.3602 | 7.35 | 7.3375 | 7.3191 | 7.2976 | 7.2736 | 7.2455 | 7.2131 | 7.1728 | 7.1226 | 7.0076 | 6.745 | 6.678 | 6.6353 | 6.6246 | 6.6078 | 6.5894 | 6.5596 | 6.5293 | 6.4948 | 6.4568 | 6.4153 | 6.3636 | 6.2975 | 6.1571 | 5.8646 | 5.778 | 5.7147
| WHITING BAY | FS |  |  |  | 7.179 | 7.167 | 7.1536 | 7.1246 | 7.0928 | 7.059 | 7.0229 | 6.9817 | 6.9366 | 6.8855 | 6.7706 | 6.4037 | 6.1206 | 6.0746 | 7.3611 | 7.3529 | 7.343 | 7.3256 | 7.3055 | 7.2843 | 7.2607 | 7.2335 | 7.2027 | 7.1677 | 7.0869 | 6.8393 | 6.6235 | 6.5744 | 6.6259 | 6.613 | 6.5994 | 6.5683 | 6.5351 | 6.4999 | 6.4631 | 6.4218 | 6.3777 | 6.3286 | 6.22 | 5.883 | 5.6318 | 5.5784
MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | NO | 6.2744 | 5.5586 | 5.1306 | 4.3574 | 3.5809 | 2.8524 | 2.4138 | 1.9626 | 1.7324 | 1.4978 | 1.0298 | 0.43245 | -0.92573 | -1.6566 | 8.7239 | 8.2176 | 7.9658 | 7.467 | 6.9664 | 6.5055 | 6.3259 | 6.1322 | 5.9506 | 5.7932 | 5.4725 | 5.0295 | 4.0724 | 3.1168 | 6.9806 | 6.332 | 5.9497 | 5.2368 | 4.5214 | 3.8494 | 3.4631 | 3.0653 | 2.8482 | 2.6261 | 2.1849 | 1.5813 | 0.30133 | -0.58718
| WICK | CT |  |  |  | 6.5382 | 5.9687 | 5.6297 | 4.8384 | 4.0576 | 3.2797 | 2.7607 | 2.2709 | 1.9637 | 1.6905 | 1.1361 | 0.4346 | -0.92573 | -1.6566 | 8.8395 | 8.4033 | 8.1716 | 7.6562 | 7.1481 | 6.6322 | 6.3621 | 6.1322 | 5.9506 | 5.7932 | 5.4725 | 5.0295 | 4.0724 | 3.1168 | 7.2142 | 6.695 | 6.3883 | 5.6575 | 4.9346 | 4.2065 | 3.733 | 3.296 | 3.0086 | 2.753 | 2.2362 | 1.5813 | 0.30133 | -0.44154
| WICK | LW |  |  |  | 6.2744 | 5.5586 | 5.1306 | 4.3574 | 3.5809 | 2.8524 | 2.4138 | 1.9626 | 1.7324 | 1.4978 | 1.0298 | 0.43245 | -0.68319 | -1.5875 | 8.7239 | 8.2176 | 7.9658 | 7.467 | 6.9664 | 6.5055 | 6.3259 | 6.1379 | 6.0085 | 5.8742 | 5.61 | 5.3604 | 4.4968 | 3.5107 | 6.9806 | 6.332 | 5.9497 | 5.2368 | 4.5214 | 3.8494 | 3.4631 | 3.0653 | 2.8482 | 2.6261 | 2.1849 | 1.6313 | 0.4719 | -0.58718
| WICK | ST |  |  |  | 6.6265 | 6.1096 | 5.8499 | 5.3398 | 4.8625 | 4.4111 | 4.1826 | 3.9943 | 3.7653 | 3.5997 | 3.2399 | 2.5677 | 1.4373 | 0.17988 | 8.8706 | 8.4564 | 8.2668 | 7.8388 | 7.4392 | 7.0648 | 6.8933 | 6.773 | 6.5829 | 6.4702 | 6.2142 | 5.7193 | 4.7181 | 3.4611 | 7.2917 | 6.8195 | 6.5854 | 6.0936 | 5.6346 | 5.2023 | 4.9807 | 4.8081 | 4.5735 | 4.4152 | 4.0687 | 3.4272 | 2.2981 | 1.0453
| WICK | FS |  |  |  | 6.8127 | 6.4242 | 6.2234 | 5.818 | 5.4131 | 5.0398 | 4.802 | 4.6035 | 4.3477 | 4.0568 | 3.5638 | 2.4545 | 1.6805 | 0.9595 | 9.0136 | 8.6982 | 8.5493 | 8.2254 | 7.9007 | 7.6017 | 7.4347 | 7.2966 | 7.1166 | 6.9046 | 6.553 | 5.8639 | 5.0719 | 3.8271 | 7.4622 | 7.1083 | 6.9281 | 6.5459 | 6.1627 | 5.8092 | 5.5906 | 5.4098 | 5.1691 | 4.8966 | 4.4379 | 3.4564 | 2.7697 | 2.1259
WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 10.7028 | 10.3889 | 9.985 | 8.2447 | 6.3583 | 3.2318 | -0.18795 | -2.5496 | -3.5761 | -4.6496 | -6.7349 | -7.1649 | -8.2206 | -8.8542 | 12.697 | 12.5664 | 12.2663 | 10.7243 | 8.9124 | 5.5173 | 1.7773 | -0.69179 | -1.7529 | -2.8891 | -5.0716 | -4.8304 | -5.8528 | -6.5571 | 10.7069 | 10.4233 | 10.0513 | 8.1035 | 5.9773 | 2.3007 | -1.702 | -4.3688 | -5.4397 | -6.5612 | -8.7142 | -9.5105 | -10.6791 | -11.4111
| WOODHILL | CT |  |  |  | 10.9645 | 10.7625 | 10.4986 | 9.6823 | 8.7594 | 6.974 | 5.0819 | 4.1004 | 3.3238 | 2.5255 | 0.94493 | 0.57062 | -0.86015 | -1.5062 | 12.697 | 12.5664 | 12.2663 | 11.7028 | 11.0572 | 9.289 | 7.3617 | 6.5745 | 5.8788 | 5.2458 | 3.924 | 3.7513 | 1.9226 | -0.35075 | 10.9352 | 10.7481 | 10.5006 | 9.7116 | 8.7902 | 6.782 | 4.6482 | 3.6508 | 2.889 | 2.1051 | 0.55955 | 0.15738 | -1.187 | -1.8183
| WOODHILL | LW |  |  |  | 10.7028 | 10.3889 | 9.985 | 8.2447 | 6.3583 | 3.2318 | -0.18795 | -2.5496 | -3.5761 | -4.6496 | -6.7349 | -7.1649 | -8.2206 | -8.8542 | 12.7049 | 12.6097 | 12.3349 | 10.7243 | 8.9124 | 5.5173 | 1.7773 | -0.69179 | -1.7529 | -2.8891 | -5.0716 | -4.8304 | -5.8528 | -6.5571 | 10.7069 | 10.4233 | 10.0513 | 8.1035 | 5.9773 | 2.3007 | -1.702 | -4.3688 | -5.4397 | -6.5612 | -8.7142 | -9.5105 | -10.6791 | -11.4111
| WOODHILL | ST |  |  |  | 11.0412 | 10.9436 | 10.831 | 9.6638 | 8.7986 | 8.1422 | 6.3439 | 5.6336 | 5.0244 | 4.5456 | 3.4155 | 3.0491 | 1.5215 | 0.10632 | 12.7142 | 12.6607 | 12.5939 | 11.2311 | 10.189 | 9.3881 | 7.1399 | 6.2374 | 5.4362 | 4.7726 | 3.158 | 3.5074 | 1.4939 | -1.124 | 11.004 | 10.9153 | 10.8116 | 9.3998 | 8.3736 | 7.6154 | 5.4374 | 4.6316 | 3.9628 | 3.3969 | 1.4659 | 1.8648 | 0.38137 | -0.95651
| WOODHILL | FS |  |  |  | 11.0918 | 11.0139 | 10.9295 | 10.5808 | 10.2163 | 9.8094 | 9.3827 | 8.9634 | 8.5771 | 8.2006 | 7.3723 | 6.8523 | 5.3333 | 4.0277 | 12.7245 | 12.6798 | 12.627 | 12.2986 | 11.9564 | 11.5066 | 11.019 | 10.5399 | 10.1524 | 9.7664 | 8.8715 | 7.8959 | 5.0741 | 0.5053 | 11.0471 | 10.9774 | 10.9003 | 10.5123 | 10.1079 | 9.6522 | 9.1772 | 8.7194 | 8.3265 | 7.952 | 7.1294 | 6.6894 | 5.3121 | 4.1619
| TX lookup |  |  |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
| Clean Lookup |  |  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48

## Primary Headroom Gen
Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | -0.15858 | -0.26296 | -0.39707 | -0.52518 | -0.6487 | -0.76765 | -0.88202 | -0.99181 | -1.0431 | -1.0687 | -1.1191 | -1.2417 | -1.3522 | -1.4649 | -0.13237 | -0.21576 | -0.32299 | -0.42546 | -0.52426 | -0.61941 | -0.7109 | -0.79874 | -0.8399 | -0.86058 | -0.90122 | -1.0001 | -1.0894 | -1.1804 | -0.16809 | -0.2729 | -0.4077 | -0.53648 | -0.66065 | -0.78023 | -0.8952 | -1.0056 | -1.0572 | -1.083 | -1.1338 | -1.2573 | -1.3688 | -1.4823
| ABERCHALDER | CT |  |  |  | -0.15858 | -0.26296 | -0.39707 | -0.52518 | -0.6487 | -0.76765 | -0.88202 | -0.99181 | -1.0431 | -1.0687 | -1.1191 | -1.2417 | -1.3522 | -1.4649 | -0.13237 | -0.21576 | -0.32299 | -0.42546 | -0.52426 | -0.61941 | -0.7109 | -0.79874 | -0.8399 | -0.86058 | -0.90122 | -1.0001 | -1.0894 | -1.1804 | -0.16809 | -0.2729 | -0.4077 | -0.53648 | -0.66065 | -0.78023 | -0.8952 | -1.0056 | -1.0572 | -1.083 | -1.1338 | -1.2573 | -1.3688 | -1.4823
| ABERCHALDER | LW |  |  |  | -0.0097531 | -0.02612 | -0.046516 | -0.06952 | -0.094819 | -0.12218 | -0.15138 | -0.18218 | -0.21072 | -0.2401 | -0.30046 | -0.46115 | -0.61899 | -0.78552 | -0.012694 | -0.026742 | -0.043282 | -0.06196 | -0.082464 | -0.10461 | -0.12821 | -0.15308 | -0.17618 | -0.19994 | -0.24873 | -0.37849 | -0.50601 | -0.64044 | -0.017963 | -0.035524 | -0.056095 | -0.079311 | -0.10482 | -0.13239 | -0.1618 | -0.1928 | -0.22156 | -0.25116 | -0.31195 | -0.47371 | -0.63285 | -0.80071
| ABERCHALDER | ST |  |  |  | 0.019933 | 0.014463 | -0.0019651 | -0.0086999 | -0.015458 | -0.024852 | -0.033984 | -0.042853 | -0.051416 | -0.06383 | -0.087644 | -0.14196 | -0.19042 | -0.23584 | 0.0090356 | 0.0060599 | -0.0056939 | -0.012154 | -0.018496 | -0.026136 | -0.033563 | -0.040777 | -0.047758 | -0.05781 | -0.077095 | -0.12112 | -0.16042 | -0.19729 | 0.0085601 | -0.0012337 | -0.0091234 | -0.017144 | -0.025001 | -0.034489 | -0.043712 | -0.05267 | -0.061329 | -0.07384 | -0.097844 | -0.15261 | -0.20147 | -0.24727
| ABERCHALDER | FS |  |  |  | 0.014463 | -0.0019651 | -0.008881 | -0.019469 | -0.031196 | -0.042775 | -0.054197 | -0.065479 | -0.076603 | -0.08757 | -0.10903 | -0.1728 | -0.22926 | -0.28162 | 0.0061061 | -0.0054432 | -0.011834 | -0.021346 | -0.030746 | -0.040035 | -0.049198 | -0.058263 | -0.067202 | -0.076013 | -0.093253 | -0.14442 | -0.18973 | -0.23175 | -0.0012337 | -0.0088929 | -0.016905 | -0.028814 | -0.040579 | -0.052199 | -0.063661 | -0.074992 | -0.086164 | -0.097177 | -0.11873 | -0.18273 | -0.2394 | -0.29206
TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 6.7981 | 6.7961 | 6.7913 | 6.7851 | 6.7792 | 6.7732 | 6.7664 | 6.7599 | 6.7528 | 6.7456 | 6.6712 | 6.3066 | 5.7199 | 5.3709 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2464 | 7.1647 | 7.0762 | 6.9863 | 6.8221 | 6.4128 | 5.8275 | 5.4357 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5005 | 6.4071 | 6.3158 | 6.2171 | 6.1167 | 5.9417 | 5.5138 | 4.8655 | 4.4558
| ABERFELDY | CT |  |  |  | 6.7982 | 6.7965 | 6.7927 | 6.7883 | 6.784 | 6.7795 | 6.7744 | 6.7693 | 6.7636 | 6.7578 | 6.7476 | 6.5481 | 6.0454 | 5.782 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2817 | 7.2115 | 7.1388 | 7.0115 | 6.684 | 6.1929 | 5.8972 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.518 | 6.4465 | 6.3681 | 6.287 | 6.1448 | 5.7973 | 5.2476 | 4.9384
| ABERFELDY | LW |  |  |  | 6.7981 | 6.7961 | 6.7913 | 6.7851 | 6.7792 | 6.7732 | 6.7664 | 6.7599 | 6.7528 | 6.7456 | 6.6712 | 6.3066 | 5.7199 | 5.3709 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2464 | 7.1647 | 7.0762 | 6.9863 | 6.8221 | 6.4128 | 5.8275 | 5.4357 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5005 | 6.4071 | 6.3158 | 6.2171 | 6.1167 | 5.9417 | 5.5138 | 4.8655 | 4.4558
| ABERFELDY | ST |  |  |  | 6.7986 | 6.7977 | 6.7959 | 6.7933 | 6.7904 | 6.7868 | 6.7829 | 6.7789 | 6.7745 | 6.77 | 6.762 | 6.747 | 6.5657 | 6.4142 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2907 | 7.1904 | 7.0037 | 6.7403 | 6.5703 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5198 | 6.4566 | 6.3445 | 6.1362 | 5.8381 | 5.6603
| ABERFELDY | FS |  |  |  | 6.7989 | 6.7985 | 6.7981 | 6.7971 | 6.7962 | 6.7949 | 6.7934 | 6.7918 | 6.7901 | 6.7883 | 6.7852 | 6.7792 | 6.7743 | 6.7699 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2893 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5165 | 6.455
STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4707 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1906 | 4.1885 | 4.1828 | 4.1752 | 4.1669 | 4.1579 | 4.1457 | 4.1313 | 4.1157 | 4.0986 | 4.0635 | 3.8824 | 3.6979 | 3.5141
| ABERFOYLE | CT |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1906 | 4.189 | 4.1847 | 4.1793 | 4.1733 | 4.1666 | 4.1593 | 4.1517 | 4.14 | 4.127 | 4.1001 | 3.9643 | 3.8258 | 3.6874
| ABERFOYLE | LW |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4707 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1906 | 4.1885 | 4.1828 | 4.1752 | 4.1669 | 4.1579 | 4.1457 | 4.1313 | 4.1157 | 4.0986 | 4.0635 | 3.8824 | 3.6979 | 3.5141
| ABERFOYLE | ST |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1912 | 4.1903 | 4.1883 | 4.1851 | 4.1809 | 4.1708 | 4.1604 | 4.1487 | 4.132 | 4.1143 | 4.0787 | 3.9855 | 3.8942 | 3.8046
| ABERFOYLE | FS |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1915 | 4.1913 | 4.1909 | 4.1898 | 4.1885 | 4.1852 | 4.1818 | 4.1777 | 4.1736 | 4.1693 | 4.1607 | 4.13 | 4.0948 | 4.0592
KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5347 | 6.525 | 6.5194 | 6.5177 | 6.5165 | 6.5154 | 6.5143 | 6.5132 | 6.512 | 6.5108 | 6.5085 | 6.4887 | 6.4684 | 6.4485 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
| ABERLOUR | CT |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.535 | 6.5269 | 6.5199 | 6.5187 | 6.5179 | 6.517 | 6.516 | 6.5149 | 6.5139 | 6.513 | 6.5114 | 6.4952 | 6.4787 | 6.4624 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
| ABERLOUR | LW |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5347 | 6.525 | 6.5194 | 6.5177 | 6.5165 | 6.5154 | 6.5143 | 6.5132 | 6.512 | 6.5108 | 6.5085 | 6.4887 | 6.4684 | 6.4485 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
| ABERLOUR | ST |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5382 | 6.5331 | 6.5253 | 6.5206 | 6.52 | 6.5185 | 6.5169 | 6.5153 | 6.5136 | 6.512 | 6.5091 | 6.5019 | 6.4948 | 6.4877 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
| ABERLOUR | FS |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5411 | 6.5383 | 6.5351 | 6.5323 | 6.5305 | 6.5251 | 6.5207 | 6.52 | 6.5193 | 6.5186 | 6.5173 | 6.5143 | 6.5116 | 6.5089 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 2.0326 | 1.9737 | 1.8982 | 1.8307 | 1.7656 | 1.7029 | 1.6427 | 1.5848 | 1.5541 | 1.5388 | 1.5087 | 1.4395 | 0.97319 | 0.90029 | 2.0478 | 2.0217 | 1.9881 | 1.9579 | 1.9288 | 1.9007 | 1.8488 | 1.789 | 1.7525 | 1.73 | 1.6843 | 1.5732 | 1.1118 | 1.0034 | 1.7541 | 1.6883 | 1.6007 | 1.5207 | 1.4429 | 1.3673 | 1.2949 | 1.2251 | 1.1836 | 1.1589 | 1.1091 | 0.98884 | 0.4456 | 0.32698
| ABERNETHY | CT |  |  |  | 2.0326 | 1.9737 | 1.8982 | 1.8307 | 1.7656 | 1.7029 | 1.6427 | 1.5848 | 1.5541 | 1.5388 | 1.5087 | 1.4395 | 0.97319 | 0.90029 | 2.0478 | 2.0217 | 1.9881 | 1.9579 | 1.9288 | 1.9007 | 1.8488 | 1.789 | 1.7525 | 1.73 | 1.6843 | 1.5732 | 1.1118 | 1.0034 | 1.7541 | 1.6883 | 1.6007 | 1.5207 | 1.4429 | 1.3673 | 1.2949 | 1.2251 | 1.1836 | 1.1589 | 1.1091 | 0.98884 | 0.4456 | 0.32698
| ABERNETHY | LW |  |  |  | 2.1172 | 2.1074 | 2.0961 | 2.0833 | 2.0693 | 2.054 | 2.0378 | 2.0206 | 2.0025 | 1.9839 | 1.9456 | 1.8435 | 1.3339 | 1.2233 | 2.0851 | 2.0806 | 2.0753 | 2.0692 | 2.0625 | 2.0553 | 2.0476 | 2.0396 | 2.0311 | 2.0223 | 2.0044 | 1.8963 | 1.3766 | 1.2155 | 1.8447 | 1.8314 | 1.8117 | 1.7889 | 1.7646 | 1.7385 | 1.7117 | 1.684 | 1.6545 | 1.6246 | 1.5625 | 1.3882 | 0.78019 | 0.6033
| ABERNETHY | ST |  |  |  | 2.1301 | 2.1268 | 2.1222 | 2.1179 | 2.1136 | 2.1084 | 2.1033 | 2.0984 | 2.094 | 2.0875 | 2.0752 | 2.0421 | 1.8145 | 1.7842 | 2.091 | 2.0894 | 2.0873 | 2.0852 | 2.0832 | 2.0805 | 2.078 | 2.0755 | 2.0732 | 2.07 | 2.0638 | 2.0474 | 1.9171 | 1.8583 | 1.8614 | 1.8567 | 1.8498 | 1.8421 | 1.8336 | 1.8214 | 1.8097 | 1.7983 | 1.7868 | 1.7732 | 1.7461 | 1.6761 | 1.4005 | 1.3384
| ABERNETHY | FS |  |  |  | 2.1268 | 2.1222 | 2.1177 | 2.1111 | 2.1045 | 2.098 | 2.0916 | 2.0852 | 2.079 | 2.0729 | 2.0608 | 2.0251 | 1.9883 | 1.9528 | 2.0922 | 2.0876 | 2.0856 | 2.0826 | 2.0796 | 2.0766 | 2.0737 | 2.0708 | 2.0679 | 2.065 | 2.0594 | 2.043 | 2.0261 | 2.0099 | 1.9093 | 1.8545 | 1.8492 | 1.841 | 1.8327 | 1.8235 | 1.8145 | 1.805 | 1.7957 | 1.7865 | 1.7683 | 1.7165 | 1.6648 | 1.6159
TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | NO | 18.7196 | 18.7177 | 18.7123 | 18.7055 | 18.6988 | 18.6919 | 18.6851 | 18.6783 | 18.671 | 18.664 | 18.6496 | 18.5813 | 18.5126 | 18.4454 | 16.002 | 15.9972 | 15.9835 | 15.9783 | 15.975 | 15.9716 | 15.9682 | 15.9649 | 15.9613 | 15.9578 | 15.9507 | 13.6119 | 12.9514 | 12.3049 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.5088 | 12.8547
| ABOYNE | CT |  |  |  | 18.7196 | 18.7179 | 18.7137 | 18.7087 | 18.7037 | 18.6987 | 18.6935 | 18.6885 | 18.683 | 18.6778 | 18.6671 | 18.6223 | 18.5773 | 18.5334 | 16.002 | 15.9978 | 15.987 | 15.9799 | 15.9774 | 15.9749 | 15.9724 | 15.9699 | 15.9672 | 15.9647 | 15.9594 | 15.9373 | 13.5741 | 13.1514 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.7112
| ABOYNE | LW |  |  |  | 18.7196 | 18.7177 | 18.7123 | 18.7055 | 18.6988 | 18.6919 | 18.6851 | 18.6783 | 18.671 | 18.664 | 18.6496 | 18.5813 | 18.5126 | 18.4454 | 16.002 | 15.9972 | 15.9835 | 15.9783 | 15.975 | 15.9716 | 15.9682 | 15.9649 | 15.9613 | 15.9578 | 15.9507 | 13.6119 | 12.9514 | 12.3049 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.5088 | 12.8547
| ABOYNE | ST |  |  |  | 18.7203 | 18.7197 | 18.7183 | 18.7162 | 18.7136 | 18.7072 | 18.7009 | 18.6948 | 18.6881 | 18.6816 | 18.6687 | 18.6375 | 18.607 | 18.577 | 16.0037 | 16.0021 | 15.9987 | 15.9933 | 15.9868 | 15.9792 | 15.9761 | 15.973 | 15.9697 | 15.9665 | 15.9602 | 15.9448 | 15.9297 | 13.5714 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968
| ABOYNE | FS |  |  |  | 18.7205 | 18.7204 | 18.7202 | 18.7196 | 18.7188 | 18.7167 | 18.7146 | 18.712 | 18.7094 | 18.7069 | 18.7019 | 18.6899 | 18.6787 | 18.6681 | 16.0043 | 16.004 | 16.0036 | 16.002 | 16 | 15.9947 | 15.9894 | 15.9828 | 15.9802 | 15.979 | 15.9765 | 15.9706 | 15.9651 | 15.9599 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968
GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | YES | 1.0606 | 1.0605 | 1.0603 | 1.06 | 1.0597 | 1.0594 | 1.0591 | 1.0586 | 1.058 | 1.0575 | 1.0564 | 1.0514 | -0.044879 | -0.065611 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | -0.33403 | -0.41659 | 0.40439 | 0.4043 | 0.40403 | 0.40371 | 0.40339 | 0.40308 | 0.40278 | 0.40226 | 0.40164 | 0.40103 | 0.39985 | 0.39462 | -0.5228 | -0.60304
| ACHILTIBUIE | CT |  |  |  | 1.0606 | 1.0606 | 1.0604 | 1.0602 | 1.0599 | 1.0597 | 1.0595 | 1.0593 | 1.0591 | 1.0589 | 1.0585 | 1.054 | -0.030434 | -0.045446 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | -0.27651 | -0.33629 | 0.40439 | 0.40431 | 0.40411 | 0.40389 | 0.40367 | 0.40345 | 0.40324 | 0.40303 | 0.4028 | 0.40258 | 0.40214 | 0.39736 | -0.4669 | -0.525
| ACHILTIBUIE | LW |  |  |  | 1.0606 | 1.0605 | 1.0603 | 1.06 | 1.0597 | 1.0594 | 1.0591 | 1.0588 | 1.0585 | 1.0582 | 1.0576 | 1.0514 | -0.044879 | -0.065611 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | -0.33403 | -0.41659 | 0.40439 | 0.4043 | 0.40403 | 0.40371 | 0.40339 | 0.40308 | 0.40278 | 0.40248 | 0.40216 | 0.40184 | 0.40121 | 0.39462 | -0.5228 | -0.60304
| ACHILTIBUIE | ST |  |  |  | 1.0607 | 1.0606 | 1.0605 | 1.0604 | 1.0603 | 1.0597 | 1.0592 | 1.0586 | 1.058 | 1.0575 | 1.0564 | 1.0536 | 0.8534 | 0.85072 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | -0.089397 | -0.12521 | 0.40442 | 0.40438 | 0.4043 | 0.40418 | 0.40403 | 0.40343 | 0.40284 | 0.40226 | 0.40164 | 0.40103 | 0.39985 | 0.39696 | -0.2188 | -0.2536
| ACHILTIBUIE | FS |  |  |  | 1.0607 | 1.0607 | 1.0607 | 1.0606 | 1.0606 | 1.0604 | 1.0602 | 1.06 | 1.0597 | 1.0595 | 1.0591 | 1.058 | 1.057 | 1.0561 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.88046 | 0.40443 | 0.40443 | 0.40442 | 0.40439 | 0.40435 | 0.40415 | 0.40395 | 0.4037 | 0.40345 | 0.40321 | 0.40274 | 0.40163 | 0.40059 | 0.3996
BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | -0.014954 | 0.046658 | 0.04648 | 0.045975 | 0.045361 | 0.044759 | 0.04417 | 0.043333 | 0.04232 | 0.041917 | 0.041659 | 0.041607 | -0.0046756 | -0.03597 | -0.066676 | 0.05262 | 0.052534 | 0.052289 | 0.05199 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | -0.026801 | -0.057518
| AIGAS | CT |  |  |  | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.046658 | 0.04651 | 0.046131 | 0.0457 | 0.045277 | 0.044864 | 0.044458 | 0.044059 | 0.043651 | 0.043328 | 0.042692 | 0.041607 | -0.014799 | -0.036869 | 0.05262 | 0.052548 | 0.052364 | 0.052155 | 0.05195 | 0.051749 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | -0.0059169 | -0.0277
| AIGAS | LW |  |  |  | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | -0.014954 | 0.046658 | 0.04648 | 0.045975 | 0.045361 | 0.044759 | 0.04417 | 0.043624 | 0.043195 | 0.042734 | 0.042276 | 0.041951 | -0.0046756 | -0.03597 | -0.066676 | 0.05262 | 0.052534 | 0.052289 | 0.05199 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | -0.026801 | -0.057518
| AIGAS | ST |  |  |  | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.04671 | 0.046643 | 0.046489 | 0.046253 | 0.045971 | 0.044574 | 0.043333 | 0.04232 | 0.041917 | 0.041659 | 0.041607 | 0.041607 | -0.0098586 | -0.023322 | 0.052645 | 0.052613 | 0.052538 | 0.052423 | 0.052286 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | -0.0011048 | -0.014219
| AIGAS | FS |  |  |  | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.085203 | 0.046741 | 0.046731 | 0.046719 | 0.046651 | 0.046572 | 0.046114 | 0.045665 | 0.045089 | 0.04452 | 0.043963 | 0.04308 | 0.041898 | 0.041607 | 0.041607 | 0.052661 | 0.052656 | 0.05265 | 0.052617 | 0.052578 | 0.052356 | 0.052138 | 0.051858 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739 | 0.051739
ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4327 | 7.2853 | 8.7342 | 8.7311 | 8.7222 | 8.7114 | 8.7007 | 8.6902 | 8.6799 | 8.6698 | 8.6589 | 8.648 | 8.6265 | 7.1045 | 6.9504 | 6.7986 | 8.8474 | 8.8446 | 8.8365 | 8.8265 | 8.8167 | 8.8071 | 8.7977 | 8.7884 | 8.7788 | 8.7762 | 8.771 | 6.8444 | 6.6807 | 6.5195
| AIRD | CT |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4504 | 7.4504 | 8.7342 | 8.7318 | 8.7254 | 8.7181 | 8.711 | 8.7039 | 8.697 | 8.6902 | 8.6829 | 8.6756 | 8.6612 | 7.2259 | 7.1125 | 7.0008 | 8.8475 | 8.8452 | 8.8394 | 8.8327 | 8.8261 | 8.8197 | 8.8134 | 8.8072 | 8.8005 | 8.7938 | 8.7806 | 6.9734 | 6.8529 | 6.7343
| AIRD | LW |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4327 | 7.2853 | 8.7342 | 8.7311 | 8.7222 | 8.7114 | 8.7007 | 8.6902 | 8.6799 | 8.6698 | 8.6589 | 8.648 | 8.6265 | 7.1045 | 6.9504 | 6.7986 | 8.8474 | 8.8446 | 8.8365 | 8.8265 | 8.8167 | 8.8071 | 8.7977 | 8.7884 | 8.7788 | 8.7762 | 8.771 | 6.8444 | 6.6807 | 6.5195
| AIRD | ST |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.2658 | 9.2658 | 9.2658 | 8.7351 | 8.7339 | 8.7313 | 8.7272 | 8.7222 | 8.7161 | 8.7101 | 8.7042 | 8.6979 | 8.6916 | 8.6795 | 8.3844 | 7.5711 | 7.5031 | 8.8483 | 8.8472 | 8.8448 | 8.841 | 8.8365 | 8.8309 | 8.8254 | 8.82 | 8.8141 | 8.8084 | 8.7973 | 7.4786 | 7.4062 | 7.3339
| AIRD | FS |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 8.7356 | 8.7355 | 8.7353 | 8.7341 | 8.7327 | 8.7308 | 8.7288 | 8.7263 | 8.7239 | 8.7215 | 8.7168 | 8.7057 | 8.6954 | 8.6857 | 8.8487 | 8.8486 | 8.8484 | 8.8474 | 8.8461 | 8.8443 | 8.8425 | 8.8402 | 8.838 | 8.8358 | 8.8315 | 8.8214 | 8.8119 | 8.803
PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRIGH-NA-BRODAIG | CT |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRIGH-NA-BRODAIG | LW |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRIGH-NA-BRODAIG | ST |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRIGH-NA-BRODAIG | FS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 4.8166 | 6.606 | 6.6028 | 6.5966 | 6.5887 | 6.5796 | 6.569 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 4.4061 | 3.9432 | 3.4949 | 6.9553 | 6.9521 | 6.9459 | 6.9379 | 6.9287 | 6.918 | 6.9062 | 4.9314 | 4.8366 | 4.7559 | 4.6105 | 3.9175 | 3.4681 | 3.033
| ALYTH | CT |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 7.2685 | 6.606 | 6.6034 | 6.5986 | 6.5927 | 6.5856 | 6.5772 | 6.568 | 6.565 | 6.565 | 6.565 | 6.565 | 4.6783 | 4.3463 | 4.0284 | 6.9554 | 6.9527 | 6.9478 | 6.9419 | 6.9348 | 6.9263 | 6.917 | 6.9076 | 4.9893 | 4.9125 | 4.7752 | 4.1818 | 3.8595 | 3.5509
| ALYTH | LW |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 4.8166 | 6.606 | 6.6028 | 6.5966 | 6.5887 | 6.5796 | 6.569 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 4.4061 | 3.9432 | 3.4949 | 6.9553 | 6.9521 | 6.9459 | 6.9379 | 6.9287 | 6.918 | 6.9062 | 4.9314 | 4.8366 | 4.7559 | 4.6105 | 3.9175 | 3.4681 | 3.033
| ALYTH | ST |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.3747 | 7.3747 | 7.3747 | 6.6247 | 6.6051 | 6.6026 | 6.5991 | 6.5945 | 6.5874 | 6.5799 | 6.5723 | 6.5657 | 6.565 | 6.565 | 6.5041 | 4.8793 | 4.6838 | 6.961 | 6.9545 | 6.952 | 6.9484 | 6.9437 | 6.9366 | 6.929 | 6.9213 | 6.9147 | 6.9084 | 4.955 | 4.6069 | 4.4093 | 4.2194
| ALYTH | FS |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 6.628 | 6.623 | 6.6056 | 6.6041 | 6.6023 | 6.5996 | 6.5966 | 6.5934 | 6.5909 | 6.5885 | 6.5841 | 6.5754 | 6.5687 | 6.565 | 6.9615 | 6.9607 | 6.9549 | 6.9535 | 6.9516 | 6.9489 | 6.9459 | 6.9427 | 6.9401 | 6.9377 | 6.9333 | 6.9245 | 6.9177 | 6.9115
FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 9.291 | 9.2711 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7075 | 8.698 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.2967 | 7.0649 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.4012 | 7.1692 | 6.942
| ANNAT | CT |  |  |  | 9.291 | 9.2711 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7075 | 8.698 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.3696 | 7.1706 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.439 | 7.2406 | 7.0456
| ANNAT | LW |  |  |  | 9.2943 | 9.2771 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7091 | 8.7009 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.2967 | 7.0649 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.4012 | 7.1692 | 6.942
| ANNAT | ST |  |  |  | 9.2995 | 9.2933 | 9.279 | 9.2567 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7116 | 8.7086 | 8.7018 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796
| ANNAT | FS |  |  |  | 9.3024 | 9.3015 | 9.3003 | 9.2939 | 9.2863 | 9.2814 | 9.2766 | 9.2704 | 9.2643 | 9.2583 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.713 | 8.7125 | 8.712 | 8.7089 | 8.7052 | 8.7029 | 8.7006 | 8.6976 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796
NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 6.447 | 6.4454 | 6.4429 | 6.4398 | 6.4366 | 6.4331 | 6.4293 | 6.4252 | 6.4208 | 6.4163 | 6.416 | 6.416 | 6.416 | 6.416 | 5.9406 | 5.9289 | 5.91 | 5.8874 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.687 | 4.533 | 4.3839 | 5.9589 | 5.9546 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.8169 | 4.6725 | 4.5326
| ARDERSIER | CT |  |  |  | 6.4472 | 6.4461 | 6.4446 | 6.4429 | 6.441 | 6.4387 | 6.4362 | 6.4333 | 6.43 | 6.4265 | 6.4186 | 6.416 | 6.416 | 6.416 | 5.9423 | 5.934 | 5.923 | 5.9106 | 5.8959 | 5.8787 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.9832 | 4.8661 | 4.7565 | 5.9595 | 5.9565 | 5.9524 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.9848 | 4.882
| ARDERSIER | LW |  |  |  | 6.447 | 6.4454 | 6.4429 | 6.4398 | 6.4366 | 6.4331 | 6.4293 | 6.4252 | 6.4208 | 6.4163 | 6.416 | 6.416 | 6.416 | 6.416 | 5.9406 | 5.9289 | 5.91 | 5.8874 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.687 | 4.533 | 4.3839 | 5.9589 | 5.9546 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.8169 | 4.6725 | 4.5326
| ARDERSIER | ST |  |  |  | 6.455 | 6.4466 | 6.4451 | 6.4432 | 6.4408 | 6.4384 | 6.4359 | 6.4332 | 6.4301 | 6.4268 | 6.4194 | 6.416 | 6.416 | 6.416 | 6.0009 | 5.9381 | 5.927 | 5.9123 | 5.8944 | 5.8767 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.9904 | 4.9262 | 5.9813 | 5.958 | 5.9539 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518
| ARDERSIER | FS |  |  |  | 6.4557 | 6.4552 | 6.4547 | 6.4541 | 6.4533 | 6.4524 | 6.4514 | 6.4503 | 6.4491 | 6.4478 | 6.445 | 6.4383 | 6.435 | 6.433 | 6.006 | 6.0024 | 5.9987 | 5.9937 | 5.9883 | 5.9813 | 5.9739 | 5.9654 | 5.9563 | 5.9467 | 5.9258 | 5.8758 | 5.8696 | 5.8696 | 5.9832 | 5.9819 | 5.9805 | 5.9786 | 5.9766 | 5.974 | 5.9713 | 5.9681 | 5.9647 | 5.9612 | 5.9534 | 5.9518 | 5.9518 | 5.9518
FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.6801 | 3.6792 | 3.6769 | 3.674 | 3.6712 | 3.6684 | 3.6657 | 3.663 | 3.6601 | 3.6565 | 3.6484 | 3.6287 | 3.6137 | 3.6107 | 3.6745 | 3.6742 | 3.6734 | 3.6724 | 3.6715 | 3.6706 | 3.6696 | 3.6687 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668
| ARISAIG | CT |  |  |  | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.6801 | 3.6794 | 3.6776 | 3.6756 | 3.6736 | 3.6717 | 3.6698 | 3.6679 | 3.6658 | 3.6638 | 3.6598 | 3.6357 | 3.6224 | 3.6133 | 3.6745 | 3.6742 | 3.6736 | 3.673 | 3.6723 | 3.6717 | 3.671 | 3.6704 | 3.6697 | 3.669 | 3.668 | 3.668 | 3.668 | 3.668
| ARISAIG | LW |  |  |  | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.6801 | 3.6792 | 3.6769 | 3.674 | 3.6712 | 3.6684 | 3.6657 | 3.663 | 3.6601 | 3.6572 | 3.6515 | 3.6287 | 3.6137 | 3.6107 | 3.6745 | 3.6742 | 3.6734 | 3.6724 | 3.6715 | 3.6706 | 3.6696 | 3.6687 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668
| ARISAIG | ST |  |  |  | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.6803 | 3.68 | 3.6793 | 3.6782 | 3.6769 | 3.6728 | 3.6688 | 3.6649 | 3.6607 | 3.6565 | 3.6484 | 3.6374 | 3.6303 | 3.6231 | 3.6745 | 3.6744 | 3.6742 | 3.6738 | 3.6734 | 3.672 | 3.6707 | 3.6694 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668 | 3.668
| ARISAIG | FS |  |  |  | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.7437 | 3.6804 | 3.6804 | 3.6803 | 3.68 | 3.6797 | 3.6783 | 3.6769 | 3.6752 | 3.6735 | 3.6718 | 3.6685 | 3.6608 | 3.6534 | 3.6464 | 3.6746 | 3.6746 | 3.6746 | 3.6745 | 3.6743 | 3.6739 | 3.6734 | 3.6728 | 3.6723 | 3.6717 | 3.6706 | 3.668 | 3.668 | 3.668
STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | YES | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9993 | 11.999 | 11.9987 | 11.9983
| ARNISH | CT |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988 | 12 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988
| ARNISH | LW |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9993 | 11.999 | 11.9987 | 11.9983
| ARNISH | ST |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9994 | 11.9993 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9994 | 11.9993
| ARNISH | FS |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997
ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 27.6528 | 27.5923 | 27.5147 | 27.4438 | 27.3754 | 27.3096 | 27.2463 | 27.1855 | 27.1522 | 27.1356 | 27.103 | 27.0264 | 22.7252 | 22.0693 | 24.1215 | 24.0205 | 23.8749 | 23.8011 | 23.7592 | 23.7211 | 23.6845 | 23.6493 | 23.63 | 21.9058 | 21.1698 | 19.544 | 18.8095 | 18.0938 | 24.2854 | 24.2105 | 24.1102 | 24.0214 | 23.9514 | 23.8858 | 23.8228 | 23.7623 | 23.729 | 23.7125 | 21.3681 | 19.7145 | 18.9491 | 18.2015
| ASHGROVE | CT |  |  |  | 27.6528 | 27.5923 | 27.5147 | 27.4438 | 27.3754 | 27.3096 | 27.2463 | 27.1855 | 27.1522 | 27.1356 | 27.103 | 27.0264 | 26.9473 | 23.0985 | 24.1215 | 24.0205 | 23.8749 | 23.8011 | 23.7592 | 23.7211 | 23.6845 | 23.6493 | 23.63 | 22.0157 | 21.4316 | 20.5505 | 19.9844 | 19.4503 | 24.2854 | 24.2105 | 24.1102 | 24.0214 | 23.9514 | 23.8858 | 23.8228 | 23.7623 | 23.729 | 23.7125 | 21.5146 | 20.6139 | 20.0278 | 19.4724
| ASHGROVE | LW |  |  |  | 27.7397 | 27.7297 | 27.718 | 27.7049 | 27.6905 | 27.6748 | 27.6581 | 27.6405 | 27.6213 | 27.6016 | 27.561 | 27.4529 | 22.7252 | 22.0693 | 24.1906 | 24.1177 | 23.9955 | 23.9522 | 23.9415 | 23.9325 | 23.9228 | 23.9126 | 23.9015 | 21.9058 | 21.1698 | 19.544 | 18.8095 | 18.0938 | 24.3738 | 24.347 | 24.3063 | 24.2894 | 24.2745 | 24.2585 | 24.2413 | 24.2232 | 24.2036 | 24.1833 | 21.3681 | 19.7145 | 18.9491 | 18.2015
| ASHGROVE | ST |  |  |  | 27.753 | 27.7496 | 27.7449 | 27.7404 | 27.736 | 27.7307 | 27.7255 | 27.7205 | 27.7158 | 27.709 | 27.696 | 27.661 | 27.6297 | 27.596 | 24.2132 | 24.1791 | 24.1337 | 24.0861 | 24.0358 | 23.9913 | 23.9717 | 23.9609 | 23.9562 | 23.9522 | 23.9447 | 22.0688 | 21.753 | 21.457 | 24.3904 | 24.3788 | 24.3635 | 24.3476 | 24.3312 | 24.3158 | 24.3105 | 24.3053 | 24.3005 | 24.2936 | 24.2802 | 24.2443 | 21.9687 | 21.6642
| ASHGROVE | FS |  |  |  | 27.7496 | 27.7449 | 27.7403 | 27.7334 | 27.7267 | 27.72 | 27.7134 | 27.7069 | 27.7005 | 27.6942 | 27.6818 | 27.6451 | 27.607 | 27.5702 | 24.2174 | 24.1983 | 24.1806 | 24.158 | 24.1349 | 24.1119 | 24.0889 | 24.0629 | 24.0206 | 23.9757 | 23.9419 | 23.9152 | 23.8932 | 23.8719 | 24.3886 | 24.38 | 24.3717 | 24.3603 | 24.3489 | 24.3376 | 24.3264 | 24.3145 | 24.2985 | 24.2819 | 24.2657 | 24.2279 | 24.1888 | 24.151
MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | NO | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 8.9249 | 7.7076 | 6.5091 | 15.9138 | 15.8582 | 15.746 | 15.6249 | 15.5825 | 15.5597 | 15.5373 | 15.5153 | 15.4914 | 15.4676 | 9.8149 | 8.3371 | 6.8651 | 5.4159 | 16.1082 | 16.0725 | 15.9795 | 15.8679 | 15.7584 | 15.6769 | 15.6082 | 15.5406 | 15.489 | 15.489 | 15.489 | 8.8817 | 7.4527 | 6.0458
| ASHLUDIE | CT |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 9.2886 | 15.9189 | 15.8802 | 15.8002 | 15.7315 | 15.6639 | 15.6002 | 15.5873 | 15.5747 | 15.5611 | 15.5476 | 15.5206 | 15.4693 | 9.7731 | 8.7769 | 16.1115 | 16.0866 | 16.0295 | 15.9662 | 15.9038 | 15.842 | 15.781 | 15.7229 | 15.6812 | 15.6396 | 15.5571 | 15.489 | 15.489 | 9.3087
| ASHLUDIE | LW |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 8.9249 | 7.7076 | 6.5091 | 15.9138 | 15.8582 | 15.746 | 15.6249 | 15.5825 | 15.5597 | 15.5373 | 15.5153 | 15.4914 | 15.4676 | 9.8149 | 8.3371 | 6.8651 | 5.4159 | 16.1082 | 16.0725 | 15.9795 | 15.8679 | 15.7584 | 15.6769 | 15.6082 | 15.5406 | 15.489 | 15.489 | 15.489 | 8.8817 | 7.4527 | 6.0458
| ASHLUDIE | ST |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 15.9318 | 15.9093 | 15.8636 | 15.8031 | 15.7462 | 15.711 | 15.6763 | 15.6427 | 15.6065 | 15.5951 | 15.5814 | 15.5478 | 15.515 | 15.4824 | 16.1198 | 16.1053 | 16.076 | 16.0322 | 15.9797 | 15.9472 | 15.9153 | 15.8842 | 15.8509 | 15.8178 | 15.7533 | 15.6403 | 15.5399 | 15.489
| ASHLUDIE | FS |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 15.9439 | 15.9388 | 15.9344 | 15.9151 | 15.8925 | 15.8759 | 15.8597 | 15.8389 | 15.8191 | 15.805 | 15.7776 | 15.7124 | 15.6519 | 15.5998 | 16.1275 | 16.1243 | 16.1214 | 16.109 | 16.0945 | 16.0839 | 16.0734 | 16.0601 | 16.0469 | 16.0339 | 16.0087 | 15.9486 | 15.8927 | 15.8399
GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | YES | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0245 | 7.0224 | 7.0161 | 7.0085 | 7.0011 | 6.9938 | 6.9867 | 6.9727 | 6.9645 | 6.9627 | 6.9592 | 6.9422 | 6.9205 | 5.8941 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 5.9476
| AULTBEA | CT |  |  |  | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0245 | 7.0227 | 7.018 | 7.0127 | 7.0075 | 7.0024 | 6.9974 | 6.9925 | 6.9872 | 6.9819 | 6.9715 | 6.9493 | 6.9322 | 6.9154 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743
| AULTBEA | LW |  |  |  | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0245 | 7.0224 | 7.0161 | 7.0085 | 7.0011 | 6.9938 | 6.9867 | 6.9797 | 6.9722 | 6.9653 | 6.9636 | 6.9422 | 6.9205 | 5.8941 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 5.9476
| AULTBEA | ST |  |  |  | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0252 | 7.0244 | 7.0225 | 7.0195 | 7.0161 | 7.0013 | 6.9869 | 6.9727 | 6.9645 | 6.9627 | 6.9592 | 6.9507 | 6.9422 | 6.9338 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743
| AULTBEA | FS |  |  |  | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0633 | 7.0256 | 7.0255 | 7.0253 | 7.0245 | 7.0235 | 7.0182 | 7.013 | 7.0062 | 6.9996 | 6.9932 | 6.9806 | 6.9637 | 6.9603 | 6.9572 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743 | 7.0743
BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 20.9708 | 20.9624 | 20.9479 | 20.9334 | 20.9182 | 20.9024 | 20.8752 | 20.8571 | 20.8377 | 20.8199 | 20.7911 | 20.742 | 20.6919 | 20.643 | 19.7986 | 19.7932 | 19.784 | 19.7747 | 19.7651 | 19.755 | 19.7376 | 19.7261 | 19.7137 | 19.7024 | 19.684 | 19.6527 | 19.6207 | 19.5896 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
| AVIEMORE | CT |  |  |  | 20.9711 | 20.9639 | 20.9522 | 20.9415 | 20.9298 | 20.917 | 20.8944 | 20.8787 | 20.8619 | 20.8454 | 20.8185 | 20.7769 | 20.7405 | 20.7054 | 19.7988 | 19.7942 | 19.7868 | 19.7799 | 19.7725 | 19.7643 | 19.7499 | 19.7399 | 19.7292 | 19.7187 | 19.7015 | 19.675 | 19.6518 | 19.6294 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
| AVIEMORE | LW |  |  |  | 20.9708 | 20.9624 | 20.9479 | 20.9334 | 20.9182 | 20.9024 | 20.8752 | 20.8571 | 20.8377 | 20.8199 | 20.7911 | 20.742 | 20.6919 | 20.643 | 19.7986 | 19.7932 | 19.784 | 19.7747 | 19.7651 | 19.755 | 19.7376 | 19.7261 | 19.7137 | 19.7024 | 19.684 | 19.6527 | 19.6207 | 19.5896 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
| AVIEMORE | ST |  |  |  | 20.9735 | 20.9691 | 20.9627 | 20.9563 | 20.9486 | 20.94 | 20.9249 | 20.9144 | 20.903 | 20.8916 | 20.873 | 20.8455 | 20.8228 | 20.8009 | 19.8003 | 19.7975 | 19.7935 | 19.7894 | 19.7844 | 19.7789 | 19.7693 | 19.7626 | 19.7554 | 19.7481 | 19.7363 | 19.7187 | 19.7042 | 19.6903 | 19.7437 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
| AVIEMORE | FS |  |  |  | 20.9756 | 20.9733 | 20.9707 | 20.968 | 20.965 | 20.9615 | 20.9555 | 20.9512 | 20.9466 | 20.9422 | 20.9348 | 20.9233 | 20.9147 | 20.9066 | 19.8017 | 19.8002 | 19.7985 | 19.7968 | 19.7949 | 19.7927 | 19.7888 | 19.7861 | 19.7832 | 19.7803 | 19.7756 | 19.7683 | 19.7628 | 19.7577 | 19.7474 | 19.7433 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3076 | 6.3076 | 3.8319 | 5.3069 | 5.2929 | 5.258 | 5.218 | 5.1783 | 5.1396 | 5.1095 | 5.1095 | 5.1095 | 5.1095 | 3.8914 | 3.5974 | 3.3631 | 3.1328 | 5.616 | 5.6063 | 5.5848 | 5.5774 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.4847 | 3.7787 | 3.5566
| BALALDIE | CT |  |  |  | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3076 | 6.3076 | 3.8319 | 5.3069 | 5.2929 | 5.258 | 5.218 | 5.1783 | 5.1396 | 5.1095 | 5.1095 | 5.1095 | 5.1095 | 3.8914 | 3.5974 | 3.3631 | 3.1328 | 5.616 | 5.6063 | 5.5848 | 5.5774 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.4847 | 3.7787 | 3.5566
| BALALDIE | LW |  |  |  | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3076 | 6.3076 | 3.915 | 5.3106 | 5.3013 | 5.2765 | 5.2462 | 5.2161 | 5.1868 | 5.1592 | 5.1321 | 5.1095 | 5.1095 | 5.1095 | 3.7751 | 3.4997 | 3.2303 | 5.6185 | 5.6121 | 5.5949 | 5.5826 | 5.5771 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.5717 | 5.4847 | 3.9103 | 3.6507
| BALALDIE | ST |  |  |  | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3505 | 6.3505 | 6.3505 | 5.3137 | 5.3109 | 5.3054 | 5.2972 | 5.2874 | 5.2751 | 5.2636 | 5.2522 | 5.2398 | 5.2277 | 5.2045 | 5.1145 | 5.0851 | 5.0851 | 5.6206 | 5.6187 | 5.6149 | 5.6092 | 5.6024 | 5.5939 | 5.5859 | 5.5837 | 5.5814 | 5.5792 | 5.575 | 5.5282 | 5.5282 | 5.5282
| BALALDIE | FS |  |  |  | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 6.3933 | 5.3146 | 5.3138 | 5.3128 | 5.3094 | 5.3054 | 5.3012 | 5.2973 | 5.2923 | 5.2875 | 5.2827 | 5.2735 | 5.252 | 5.2312 | 5.211 | 5.6213 | 5.6207 | 5.62 | 5.6177 | 5.6149 | 5.612 | 5.6093 | 5.6059 | 5.6025 | 5.5992 | 5.5928 | 5.5837 | 5.5799 | 5.5761
ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 11.0319 | 10.9655 | 10.8804 | 10.7927 | 10.708 | 10.6266 | 10.5482 | 10.473 | 10.4252 | 10.4014 | 10.3547 | 10.2351 | 9.6726 | 9.524 | 10.0168 | 9.9784 | 9.9242 | 9.8663 | 9.8065 | 9.7486 | 9.6888 | 9.6351 | 9.5943 | 9.5754 | 9.5486 | 9.4799 | 6.8987 | 6.4187 | 9.6219 | 9.5599 | 9.4784 | 9.3934 | 9.3098 | 9.2293 | 9.1501 | 9.0756 | 9.0254 | 8.9964 | 7.4363 | 7.0537 | 6.216 | 5.8242
| BALBEGGIE | CT |  |  |  | 11.0319 | 10.9655 | 10.8804 | 10.7927 | 10.708 | 10.6266 | 10.5482 | 10.473 | 10.4252 | 10.4014 | 10.3547 | 10.2351 | 9.6726 | 9.524 | 10.0168 | 9.9784 | 9.9242 | 9.8663 | 9.8065 | 9.7486 | 9.6888 | 9.6351 | 9.5943 | 9.5754 | 9.5486 | 9.4799 | 6.8987 | 6.5484 | 9.6219 | 9.5599 | 9.4784 | 9.3934 | 9.3098 | 9.2293 | 9.1501 | 9.0756 | 9.0254 | 8.9964 | 7.4363 | 7.0537 | 6.216 | 5.8325
| BALBEGGIE | LW |  |  |  | 11.1272 | 11.1161 | 11.1034 | 11.089 | 11.0732 | 11.056 | 11.0377 | 11.0184 | 10.9937 | 10.9683 | 10.916 | 10.7767 | 10.1774 | 9.9621 | 10.0644 | 10.0524 | 10.0303 | 10.0033 | 9.9717 | 9.951 | 9.9405 | 9.9294 | 9.9152 | 9.9006 | 9.8706 | 9.7907 | 6.9394 | 6.4187 | 9.7078 | 9.6951 | 9.6771 | 9.6559 | 9.6318 | 9.6067 | 9.5787 | 9.5525 | 9.5213 | 9.4895 | 9.4266 | 7.3821 | 6.3921 | 5.8242
| BALBEGGIE | ST |  |  |  | 11.1418 | 11.138 | 11.1329 | 11.1279 | 11.1231 | 11.1173 | 11.1116 | 11.1061 | 11.1003 | 11.0919 | 11.0758 | 11.031 | 10.7746 | 10.7214 | 10.0736 | 10.0687 | 10.06 | 10.0485 | 10.0335 | 10.0149 | 9.9942 | 9.9797 | 9.9764 | 9.9716 | 9.9623 | 9.9367 | 9.7895 | 9.759 | 9.7218 | 9.717 | 9.7099 | 9.7017 | 9.6921 | 9.6803 | 9.6678 | 9.6566 | 9.6448 | 9.6302 | 9.6033 | 9.5397 | 9.2878 | 7.4388
| BALBEGGIE | FS |  |  |  | 11.138 | 11.1329 | 11.1278 | 11.1203 | 11.1129 | 11.1055 | 11.0983 | 11.0912 | 11.0842 | 11.0773 | 11.0637 | 11.0234 | 10.9797 | 10.9371 | 10.0732 | 10.0694 | 10.0652 | 10.0581 | 10.0498 | 10.0403 | 10.0298 | 10.0199 | 10.0101 | 10.0002 | 9.982 | 9.9394 | 9.9072 | 9.8828 | 9.7189 | 9.7138 | 9.7085 | 9.7004 | 9.6918 | 9.6827 | 9.6734 | 9.6643 | 9.6554 | 9.6465 | 9.6295 | 9.5838 | 9.5368 | 9.4914
MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | NO | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 22.3684 | 27.3585 | 27.3249 | 27.2351 | 27.127 | 27.025 | 26.9238 | 26.8231 | 26.7242 | 26.6965 | 26.6965 | 22.3586 | 21.3832 | 20.4413 | 19.5346 | 29.0379 | 29.0239 | 28.9865 | 28.9416 | 28.8992 | 28.8571 | 28.8152 | 28.7741 | 28.7291 | 22.7265 | 22.1324 | 21.2354 | 20.3691 | 19.5352
| BALDOVIE | CT |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 27.3585 | 27.3293 | 27.2588 | 27.1798 | 27.1055 | 27.0316 | 26.9588 | 26.887 | 26.8091 | 26.7293 | 26.6965 | 22.4666 | 21.7706 | 21.103 | 29.0379 | 29.0257 | 28.9964 | 28.9636 | 28.9326 | 28.9019 | 28.8716 | 28.8418 | 28.8094 | 28.7762 | 22.8997 | 22.2318 | 21.5916 | 20.9777
| BALDOVIE | LW |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 22.3684 | 27.3589 | 27.3249 | 27.2351 | 27.127 | 27.025 | 26.9238 | 26.8231 | 26.7242 | 26.6965 | 26.6965 | 22.3586 | 21.3832 | 20.4413 | 19.5346 | 29.038 | 29.0239 | 28.9865 | 28.9416 | 28.8992 | 28.8571 | 28.8152 | 28.7741 | 28.7291 | 22.7265 | 22.1324 | 21.2354 | 20.3691 | 19.5352
| BALDOVIE | ST |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 27.3697 | 27.3569 | 27.3301 | 27.2909 | 27.2466 | 27.2185 | 27.1908 | 27.1634 | 27.1339 | 27.103 | 27.0417 | 26.8934 | 26.7559 | 26.6965 | 29.0425 | 29.0372 | 29.0261 | 29.0097 | 28.9913 | 28.9796 | 28.9681 | 28.9567 | 28.9444 | 28.9316 | 28.9061 | 28.8444 | 28.7873 | 28.7321
| BALDOVIE | FS |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 27.3759 | 27.3727 | 27.3691 | 27.3569 | 27.344 | 27.3347 | 27.3256 | 27.3139 | 27.3021 | 27.2901 | 27.2665 | 27.2098 | 27.1594 | 27.1135 | 29.0451 | 29.0438 | 29.0423 | 29.0372 | 29.0318 | 29.028 | 29.0242 | 29.0193 | 29.0144 | 29.0094 | 28.9996 | 28.976 | 28.9551 | 28.936
TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | NO | 10.9427 | 10.9414 | 10.938 | 10.9342 | 10.9303 | 10.9265 | 10.9227 | 10.9189 | 10.9149 | 10.9109 | 10.903 | 10.8783 | 10.8474 | 10.8165 | 14.2959 | 14.286 | 14.2603 | 14.2305 | 14.2027 | 14.1758 | 14.154 | 14.1401 | 14.1251 | 14.1104 | 14.0808 | 13.9891 | 13.8742 | 11.6978 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.7481 | 11.3086
| BALLATER | CT |  |  |  | 10.9427 | 10.9414 | 10.938 | 10.9342 | 10.9303 | 10.9265 | 10.9227 | 10.9189 | 10.9149 | 10.9109 | 10.903 | 10.8783 | 10.8535 | 10.8291 | 14.2959 | 14.286 | 14.2603 | 14.2305 | 14.2027 | 14.1758 | 14.154 | 14.1401 | 14.1251 | 14.1104 | 14.0808 | 13.9891 | 13.8969 | 11.8731 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.8332 | 11.4895
| BALLATER | LW |  |  |  | 10.943 | 10.9421 | 10.9395 | 10.9363 | 10.9331 | 10.9299 | 10.9266 | 10.9235 | 10.9201 | 10.9168 | 10.9101 | 10.8788 | 10.8474 | 10.8165 | 14.2983 | 14.2913 | 14.2714 | 14.2467 | 14.222 | 14.1994 | 14.1768 | 14.157 | 14.1444 | 14.1321 | 14.1073 | 13.991 | 13.8742 | 11.6978 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.7481 | 11.3086
| BALLATER | ST |  |  |  | 10.9432 | 10.9429 | 10.9421 | 10.9408 | 10.9393 | 10.9365 | 10.9337 | 10.9309 | 10.9279 | 10.925 | 10.9193 | 10.9054 | 10.8918 | 10.8785 | 14.3003 | 14.2977 | 14.2915 | 14.2818 | 14.2702 | 14.2483 | 14.2266 | 14.2068 | 14.1858 | 14.1653 | 14.1413 | 14.0898 | 14.0395 | 13.9898 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073
| BALLATER | FS |  |  |  | 10.9434 | 10.9433 | 10.9433 | 10.9429 | 10.9425 | 10.9415 | 10.9406 | 10.9394 | 10.9382 | 10.937 | 10.9347 | 10.9293 | 10.9242 | 10.9195 | 14.3016 | 14.3011 | 14.3005 | 14.2977 | 14.2943 | 14.287 | 14.2797 | 14.2704 | 14.2613 | 14.2524 | 14.2349 | 14.1957 | 14.1598 | 14.1421 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073
CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | -0.0087012 | -0.047586 | -0.08584 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | -0.0066244 | -0.051754 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | -0.035235
| BALLIEKINE | CT |  |  |  | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | -0.029341 | -0.059468 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | -0.020641 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | -0.0087968
| BALLIEKINE | LW |  |  |  | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | -0.0087012 | -0.047586 | -0.08584 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | -0.0066244 | -0.051754 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | -0.035235
| BALLIEKINE | ST |  |  |  | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | -0.0099936 | -0.025464 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792
| BALLIEKINE | FS |  |  |  | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.31147 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792 | 0.33792
BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 15.5928 | 15.5342 | 15.459 | 15.3906 | 15.3247 | 15.2612 | 15.2002 | 15.1416 | 15.1096 | 15.0937 | 15.0625 | 14.9894 | 14.9144 | 14.8352 | 12.8673 | 12.8199 | 12.7568 | 12.6984 | 12.6419 | 12.5875 | 12.5351 | 12.4847 | 12.4547 | 12.4435 | 12.4216 | 12.3623 | 11.472 | 11.2572 | 14.3551 | 14.3022 | 14.2339 | 14.1715 | 14.1114 | 14.0534 | 13.9977 | 13.9442 | 13.9145 | 13.8991 | 13.869 | 13.7915 | 13.7121 | 13.6291
| BALLINDALLOCH | CT |  |  |  | 15.5928 | 15.5342 | 15.459 | 15.3906 | 15.3247 | 15.2612 | 15.2002 | 15.1416 | 15.1096 | 15.0937 | 15.0625 | 14.9894 | 14.9144 | 14.8352 | 12.8673 | 12.8199 | 12.7568 | 12.6984 | 12.6419 | 12.5875 | 12.5351 | 12.4847 | 12.4547 | 12.4435 | 12.4216 | 12.3623 | 11.472 | 11.2572 | 14.3551 | 14.3022 | 14.2339 | 14.1715 | 14.1114 | 14.0534 | 13.9977 | 13.9442 | 13.9145 | 13.8991 | 13.869 | 13.7915 | 13.7121 | 13.6291
| BALLINDALLOCH | LW |  |  |  | 15.677 | 15.6673 | 15.656 | 15.6433 | 15.6293 | 15.6142 | 15.598 | 15.5809 | 15.5624 | 15.5434 | 15.5044 | 15.4003 | 15.2834 | 15.1642 | 12.933 | 12.9233 | 12.9086 | 12.8915 | 12.8734 | 12.8546 | 12.8351 | 12.8151 | 12.7934 | 12.7714 | 12.7266 | 12.6096 | 12.5175 | 11.3218 | 14.4306 | 14.4214 | 14.41 | 14.3971 | 14.383 | 14.368 | 14.352 | 14.3352 | 14.3172 | 14.2986 | 14.2605 | 14.1507 | 14.0292 | 13.9058
| BALLINDALLOCH | ST |  |  |  | 15.6899 | 15.6865 | 15.6821 | 15.6777 | 15.6734 | 15.6683 | 15.6632 | 15.6583 | 15.6539 | 15.6473 | 15.6348 | 15.6011 | 15.571 | 15.5389 | 12.9436 | 12.9403 | 12.935 | 12.9288 | 12.9222 | 12.9117 | 12.9014 | 12.8913 | 12.8811 | 12.8694 | 12.8467 | 12.7892 | 12.7348 | 12.697 | 14.4423 | 14.4391 | 14.4347 | 14.4302 | 14.4256 | 14.4196 | 14.4137 | 14.408 | 14.4026 | 14.3953 | 14.3813 | 14.3444 | 14.3109 | 14.2755
| BALLINDALLOCH | FS |  |  |  | 15.6865 | 15.6821 | 15.6776 | 15.6709 | 15.6644 | 15.6579 | 15.6515 | 15.6452 | 15.639 | 15.6329 | 15.6209 | 15.5853 | 15.5485 | 15.5129 | 12.9414 | 12.9378 | 12.9341 | 12.9282 | 12.9221 | 12.9149 | 12.9077 | 12.9 | 12.8924 | 12.8849 | 12.8703 | 12.8301 | 12.7897 | 12.751 | 14.4393 | 14.4353 | 14.4312 | 14.4251 | 14.419 | 14.4128 | 14.4066 | 14.4003 | 14.3942 | 14.3881 | 14.3763 | 14.3417 | 14.3062 | 14.2719
CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 2.176 | 2.1259 | 2.0617 | 2.0011 | 1.9427 | 1.8865 | 1.217 | 1.1445 | 1.0895 | 1.052 | 0.97779 | 0.6446 | 0.41536 | 0.27741 | 2.1305 | 2.0763 | 1.9966 | 1.9174 | 1.8405 | 1.7662 | 1.197 | 1.1274 | 1.0767 | 1.04 | 0.96745 | 0.68531 | 0.48648 | 0.36117 | 2.0403 | 1.9763 | 1.8833 | 1.7914 | 1.7023 | 1.616 | 0.93498 | 0.8544 | 0.79672 | 0.75587 | 0.67519 | 0.3434 | 0.11181 | -0.031512
| BALLURE | CT |  |  |  | 2.176 | 2.1259 | 2.0617 | 2.0011 | 1.9427 | 1.8865 | 1.217 | 1.1445 | 1.0895 | 1.052 | 0.97779 | 0.6446 | 0.41536 | 0.27741 | 2.1305 | 2.0763 | 1.9966 | 1.9174 | 1.8405 | 1.7662 | 1.197 | 1.1274 | 1.0767 | 1.04 | 0.96745 | 0.68531 | 0.48648 | 0.36117 | 2.0403 | 1.9763 | 1.8833 | 1.7914 | 1.7023 | 1.616 | 0.93498 | 0.8544 | 0.79672 | 0.75587 | 0.67519 | 0.3434 | 0.11181 | -0.031512
| BALLURE | LW |  |  |  | 2.248 | 2.2396 | 2.23 | 2.2192 | 2.2072 | 2.1943 | 1.644 | 1.629 | 1.6111 | 1.5878 | 1.5401 | 1.2022 | 0.93055 | 0.74344 | 2.2008 | 2.1909 | 2.1755 | 2.1575 | 2.1387 | 2.1191 | 1.6016 | 1.5808 | 1.5575 | 1.5339 | 1.4859 | 1.1769 | 0.94161 | 0.77536 | 2.1244 | 2.1127 | 2.0951 | 2.0746 | 2.0531 | 2.0306 | 1.4097 | 1.3857 | 1.3589 | 1.3315 | 1.276 | 0.91272 | 0.63807 | 0.44627
| BALLURE | ST |  |  |  | 2.259 | 2.2561 | 2.2523 | 2.2485 | 2.2449 | 2.2405 | 1.9684 | 1.9643 | 1.9603 | 1.9545 | 1.9434 | 1.824 | 1.7527 | 1.7056 | 2.2117 | 2.2083 | 2.2028 | 2.1963 | 2.1894 | 2.1802 | 1.9226 | 1.9139 | 1.9049 | 1.8944 | 1.874 | 1.7388 | 1.6504 | 1.5978 | 2.1374 | 2.1333 | 2.127 | 2.1196 | 2.1118 | 2.1014 | 1.7926 | 1.7828 | 1.7728 | 1.7608 | 1.7378 | 1.5787 | 1.4759 | 1.4161
| BALLURE | FS |  |  |  | 2.2561 | 2.2523 | 2.2484 | 2.2428 | 2.2372 | 2.2316 | 2.2262 | 2.2208 | 2.2155 | 2.2103 | 2.2 | 2.1696 | 2.1377 | 2.1068 | 2.2094 | 2.2058 | 2.2021 | 2.196 | 2.1898 | 2.1829 | 2.1762 | 2.1691 | 2.162 | 2.1551 | 2.1415 | 2.1037 | 2.0652 | 2.0283 | 2.1346 | 2.1302 | 2.1257 | 2.1185 | 2.1112 | 2.1032 | 2.0954 | 2.0871 | 2.0789 | 2.0709 | 2.0552 | 2.0111 | 1.9661 | 1.9229
DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 10.4483 | 10.4442 | 10.4323 | 10.4178 | 10.4033 | 10.389 | 10.3749 | 10.361 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 6.9923 | 9.7841 | 9.7591 | 9.6875 | 9.5993 | 9.5119 | 9.4683 | 9.4404 | 9.413 | 9.3833 | 7.4331 | 7.0691 | 6.4538 | 5.8347 | 5.2288 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 7.1745 | 6.6006 | 6.0388
| BALMEDIE | CT |  |  |  | 10.4487 | 10.446 | 10.4389 | 10.4307 | 10.4226 | 10.4146 | 10.4065 | 10.3986 | 10.3901 | 10.3817 | 10.3649 | 10.3603 | 10.3603 | 10.3603 | 9.7867 | 9.7701 | 9.7273 | 9.6779 | 9.6287 | 9.5799 | 9.5312 | 9.4872 | 9.4703 | 9.4538 | 9.4207 | 7.4366 | 7.023 | 6.6187 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 7.3274
| BALMEDIE | LW |  |  |  | 10.4483 | 10.4442 | 10.4323 | 10.4178 | 10.4033 | 10.389 | 10.3749 | 10.361 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 6.9923 | 9.7841 | 9.7591 | 9.6875 | 9.5993 | 9.5119 | 9.4683 | 9.4404 | 9.413 | 9.3833 | 7.4331 | 7.0691 | 6.4538 | 5.8347 | 5.2288 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 7.1745 | 6.6006 | 6.0388
| BALMEDIE | ST |  |  |  | 10.4495 | 10.4479 | 10.4443 | 10.4386 | 10.4317 | 10.427 | 10.4223 | 10.4177 | 10.4127 | 10.4079 | 10.3983 | 10.375 | 10.3603 | 10.3603 | 9.7914 | 9.7819 | 9.7597 | 9.7252 | 9.6837 | 9.6551 | 9.6267 | 9.5988 | 9.5687 | 9.5395 | 9.4865 | 9.4407 | 9.3957 | 7.4169 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923
| BALMEDIE | FS |  |  |  | 10.4502 | 10.45 | 10.4497 | 10.448 | 10.446 | 10.4445 | 10.4429 | 10.441 | 10.4391 | 10.4372 | 10.4335 | 10.4247 | 10.4164 | 10.4086 | 9.7957 | 9.7943 | 9.7924 | 9.7824 | 9.7705 | 9.7611 | 9.7518 | 9.74 | 9.7283 | 9.7171 | 9.6947 | 9.6415 | 9.5912 | 9.5438 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923 | 10.1923
CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 14.1901 | 14.1111 | 14.008 | 13.9102 | 13.8152 | 13.7236 | 13.636 | 13.5519 | 13.5015 | 13.4742 | 13.4204 | 11.4978 | 11.394 | 11.2833 | 14.2472 | 14.1928 | 14.1206 | 14.0519 | 13.9848 | 13.9198 | 13.8581 | 13.7987 | 13.7618 | 13.7404 | 13.6982 | 13.5611 | 13.4172 | 13.2711 | 13.4517 | 13.3763 | 13.2773 | 13.1834 | 13.092 | 13.0038 | 12.9196 | 12.8387 | 12.7897 | 12.7626 | 12.7093 | 11.4533 | 11.3583 | 11.2571
| BALNAGASK | CT |  |  |  | 14.1901 | 14.1111 | 14.008 | 13.9102 | 13.8152 | 13.7236 | 13.636 | 13.5519 | 13.5015 | 13.4742 | 13.4204 | 11.4978 | 11.394 | 11.2833 | 14.2472 | 14.1928 | 14.1206 | 14.0519 | 13.9848 | 13.9198 | 13.8581 | 13.7987 | 13.7618 | 13.7404 | 13.6982 | 13.5611 | 13.4172 | 13.2711 | 13.4517 | 13.3763 | 13.2773 | 13.1834 | 13.092 | 13.0038 | 12.9196 | 12.8387 | 12.7897 | 12.7626 | 12.7093 | 11.4533 | 11.3583 | 11.2571
| BALNAGASK | LW |  |  |  | 14.3001 | 14.2849 | 14.2645 | 14.2414 | 14.2168 | 14.1908 | 14.1636 | 14.1353 | 14.1034 | 14.0709 | 14.003 | 13.7939 | 13.5584 | 13.3084 | 14.3207 | 14.309 | 14.2914 | 14.2716 | 14.2509 | 14.2293 | 14.2069 | 14.184 | 14.1583 | 14.1323 | 14.0772 | 13.8926 | 13.6886 | 13.4756 | 13.556 | 13.541 | 13.5201 | 13.4966 | 13.4717 | 13.4455 | 13.4181 | 13.3897 | 13.3579 | 13.3255 | 13.2575 | 13.0425 | 12.8145 | 12.5908
| BALNAGASK | ST |  |  |  | 14.3208 | 14.3153 | 14.3075 | 14.2993 | 14.2903 | 14.2759 | 14.2623 | 14.249 | 14.2355 | 14.2193 | 14.1879 | 14.1007 | 14.0175 | 13.9311 | 14.3372 | 14.3328 | 14.3262 | 14.319 | 14.3108 | 14.2959 | 14.282 | 14.2685 | 14.2544 | 14.2386 | 14.2078 | 14.1217 | 14.0386 | 13.9544 | 13.5766 | 13.5711 | 13.5632 | 13.5547 | 13.5454 | 13.5298 | 13.5151 | 13.5007 | 13.486 | 13.4688 | 13.4354 | 13.3422 | 13.2533 | 13.1832
| BALNAGASK | FS |  |  |  | 14.3194 | 14.313 | 14.3066 | 14.2968 | 14.2872 | 14.2766 | 14.2661 | 14.2552 | 14.2444 | 14.2339 | 14.2134 | 14.155 | 14.0938 | 14.0339 | 14.3384 | 14.3337 | 14.329 | 14.3216 | 14.3146 | 14.306 | 14.2976 | 14.2884 | 14.2794 | 14.2707 | 14.2537 | 14.2067 | 14.1574 | 14.1087 | 13.5761 | 13.5699 | 13.5636 | 13.554 | 13.5447 | 13.5341 | 13.5236 | 13.5125 | 13.5016 | 13.491 | 13.4704 | 13.412 | 13.3509 | 13.2908
KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3124 | 19.2555 | 19.0924 | 18.8907 | 18.7047 | 18.5667 | 18.4291 | 18.3848 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 12.8442 | 11.6536 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.0258 | 10.7876 | 9.5762
| BANCHORY | CT |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.318 | 19.2797 | 19.1806 | 19.0654 | 18.9499 | 18.8343 | 18.7245 | 18.6457 | 18.5606 | 18.4777 | 18.3865 | 18.3813 | 18.3813 | 18.3813 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.7913 | 11.9734
| BANCHORY | LW |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3124 | 19.2555 | 19.0924 | 18.8907 | 18.7047 | 18.5667 | 18.4291 | 18.3848 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 12.8442 | 11.6536 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.0258 | 10.7876 | 9.5762
| BANCHORY | ST |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3294 | 19.3085 | 19.26 | 19.1841 | 19.0924 | 19.0087 | 18.925 | 18.8429 | 18.7543 | 18.6901 | 18.5717 | 18.3839 | 18.3813 | 18.3813 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603
| BANCHORY | FS |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3388 | 19.3355 | 19.3309 | 19.3082 | 19.2811 | 19.2535 | 19.2259 | 19.1912 | 19.1569 | 19.1237 | 19.0575 | 18.8994 | 18.7498 | 18.6488 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603
TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1123 | 7.0994 | 7.0115 | 6.8309 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632
| BARCALDINE | CT |  |  |  | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1123 | 7.1002 | 7.0567 | 6.9107 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632
| BARCALDINE | LW |  |  |  | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.0994 | 7.0115 | 6.8309 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632
| BARCALDINE | ST |  |  |  | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1099 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632
| BARCALDINE | FS |  |  |  | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 7.1142 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 9.9437 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632 | 6.8632
STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 4.4205 | 4.4185 | 4.4133 | 4.4073 | 4.4014 | 4.3956 | 4.3899 | 4.3843 | 4.3783 | 4.3723 | 4.3604 | 4.3541 | 4.3541 | 4.3541 | 4.0541 | 4.0364 | 3.9905 | 3.9379 | 3.893 | 3.8628 | 3.8331 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 2.3054 | 1.9953 | 4.0619 | 4.0498 | 4.0184 | 3.9824 | 3.9471 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.3008 | 1.9937
| BARVAS | CT |  |  |  | 4.4205 | 4.4185 | 4.4133 | 4.4073 | 4.4014 | 4.3956 | 4.3899 | 4.3843 | 4.3783 | 4.3723 | 4.3604 | 4.3541 | 4.3541 | 4.3541 | 4.0541 | 4.0364 | 3.9905 | 3.9379 | 3.893 | 3.8628 | 3.8331 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 2.3054 | 1.9953 | 4.0619 | 4.0498 | 4.0184 | 3.9824 | 3.9471 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.3008 | 1.9937
| BARVAS | LW |  |  |  | 4.4213 | 4.4205 | 4.4183 | 4.4155 | 4.4128 | 4.4101 | 4.4075 | 4.405 | 4.4022 | 4.3994 | 4.394 | 4.3644 | 4.3541 | 4.3541 | 4.0613 | 4.0544 | 4.0345 | 4.0102 | 3.9864 | 3.963 | 3.9401 | 3.9176 | 3.8971 | 3.8827 | 3.8542 | 3.8238 | 3.8238 | 2.2581 | 4.0668 | 4.062 | 4.0485 | 4.0319 | 4.0155 | 3.9996 | 3.9839 | 3.9685 | 3.9518 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.254
| BARVAS | ST |  |  |  | 4.4217 | 4.4216 | 4.4214 | 4.4212 | 4.4208 | 4.4185 | 4.4162 | 4.4139 | 4.4115 | 4.4091 | 4.4045 | 4.3932 | 4.382 | 4.3709 | 4.0643 | 4.0636 | 4.0621 | 4.0597 | 4.0569 | 4.0363 | 4.0161 | 3.9964 | 3.9751 | 3.9542 | 3.9135 | 3.8503 | 3.8238 | 3.8238 | 4.0689 | 4.0684 | 4.0673 | 4.0657 | 4.0638 | 4.0497 | 4.0359 | 4.0224 | 4.0078 | 3.9935 | 3.9657 | 3.9354 | 3.9354 | 3.9354
| BARVAS | FS |  |  |  | 4.4217 | 4.4217 | 4.4217 | 4.4216 | 4.4215 | 4.4206 | 4.4198 | 4.4187 | 4.4176 | 4.4165 | 4.4145 | 4.4096 | 4.4051 | 4.4008 | 4.0646 | 4.0645 | 4.0644 | 4.0636 | 4.0627 | 4.0551 | 4.0476 | 4.038 | 4.0285 | 4.0192 | 4.0011 | 3.9584 | 3.9185 | 3.8899 | 4.0691 | 4.069 | 4.0689 | 4.0684 | 4.0678 | 4.0626 | 4.0574 | 4.0508 | 4.0443 | 4.038 | 4.0256 | 3.9964 | 3.9691 | 3.9435
STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.1113 | 21.1113 | 15.2127 | 17.9041 | 17.8587 | 17.749 | 17.6406 | 17.5946 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 13.385 | 12.2328 | 11.099 | 18.3228 | 18.3008 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 13.93 | 12.7974 | 11.6632
| BATTERY POINT | CT |  |  |  | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.1113 | 21.1113 | 21.1113 | 17.9041 | 17.8592 | 17.7633 | 17.6699 | 17.606 | 17.5876 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 14.117 | 13.2948 | 12.4858 | 18.3228 | 18.301 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 14.6429 | 13.8421 | 13.0506
| BATTERY POINT | LW |  |  |  | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.1113 | 21.1113 | 15.2127 | 17.9067 | 17.8587 | 17.749 | 17.6406 | 17.5946 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 17.5758 | 13.385 | 12.2328 | 11.099 | 18.3241 | 18.3008 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 13.93 | 12.7974 | 11.6632
| BATTERY POINT | ST |  |  |  | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.2397 | 21.2397 | 21.2397 | 17.9197 | 17.9015 | 17.8717 | 17.8275 | 17.775 | 17.7206 | 17.6789 | 17.6396 | 17.6083 | 17.5983 | 17.5794 | 17.5015 | 17.5015 | 14.6924 | 18.3304 | 18.3215 | 18.3071 | 18.2856 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.1434 | 18.1434 | 18.1434
| BATTERY POINT | FS |  |  |  | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 21.3682 | 17.9255 | 17.919 | 17.9135 | 17.8968 | 17.8774 | 17.8587 | 17.8402 | 17.8177 | 17.7957 | 17.7741 | 17.7324 | 17.657 | 17.6066 | 17.5915 | 18.3332 | 18.33 | 18.3274 | 18.3193 | 18.3098 | 18.3008 | 18.2918 | 18.2809 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713 | 18.2713
DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | NO | 0.32075 | -0.021864 | -0.12553 | -0.22391 | -0.31992 | -0.41236 | -0.50125 | -0.58657 | -0.62442 | -0.64324 | -0.68667 | -0.84822 | -0.99554 | -1.1421 | 0.36512 | 0.29784 | -0.020929 | -0.10991 | -0.19937 | -0.28677 | -0.37085 | -0.45163 | -0.48933 | -0.50963 | -0.54955 | -0.71047 | -0.86047 | -1.0093 | 0.26882 | -0.029408 | -0.12871 | -0.22428 | -0.33702 | -0.44563 | -0.55011 | -0.65046 | -0.69669 | -0.72111 | -0.76912 | -0.94585 | -1.1126 | -1.2783
| BETTYHILL | CT |  |  |  | 0.32075 | -0.021864 | -0.12553 | -0.22391 | -0.31992 | -0.41236 | -0.50125 | -0.58657 | -0.62442 | -0.64324 | -0.68667 | -0.84822 | -0.99554 | -1.1421 | 0.36512 | 0.29784 | -0.020929 | -0.10991 | -0.19937 | -0.28677 | -0.37085 | -0.45163 | -0.48933 | -0.50963 | -0.54955 | -0.71047 | -0.86047 | -1.0093 | 0.26882 | -0.029408 | -0.12871 | -0.22428 | -0.33702 | -0.44563 | -0.55011 | -0.65046 | -0.69669 | -0.72111 | -0.76912 | -0.94585 | -1.1126 | -1.2783
| BETTYHILL | LW |  |  |  | 0.44498 | 0.43047 | 0.41352 | 0.3944 | 0.37338 | 0.35065 | 0.3264 | 0.30082 | 0.27816 | 0.25483 | -0.043828 | -0.18576 | -0.40055 | -0.62551 | 0.46123 | 0.44957 | 0.43522 | 0.4189 | 0.40115 | 0.38211 | 0.36193 | 0.34074 | 0.3217 | 0.30216 | 0.26214 | -0.21244 | -0.42626 | -0.63927 | 0.39184 | 0.37747 | 0.36103 | 0.34251 | 0.3221 | 0.29999 | 0.27637 | 0.25143 | 0.22941 | -0.008242 | -0.050584 | -0.2944 | -0.53083 | -0.76699
| BETTYHILL | ST |  |  |  | 0.46405 | 0.45904 | 0.45232 | 0.44572 | 0.43925 | 0.43076 | 0.4225 | 0.41447 | 0.40671 | 0.39581 | 0.37487 | 0.32836 | 0.29294 | -0.037361 | 0.47612 | 0.47208 | 0.4665 | 0.46081 | 0.45511 | 0.44526 | 0.43566 | 0.4263 | 0.41691 | 0.40515 | 0.38246 | 0.33055 | -0.051863 | -0.12904 | 0.41108 | 0.40602 | 0.39923 | 0.3927 | 0.38648 | 0.37893 | 0.37159 | 0.36447 | 0.35767 | 0.34776 | 0.32874 | 0.28658 | -0.07521 | -0.15748
| BETTYHILL | FS |  |  |  | 0.4591 | 0.45248 | 0.44585 | 0.436 | 0.42628 | 0.41645 | 0.40675 | 0.39711 | 0.3876 | 0.37823 | 0.3599 | 0.30576 | 0.25894 | -0.032789 | 0.47237 | 0.46721 | 0.46206 | 0.45427 | 0.44655 | 0.43787 | 0.4293 | 0.42047 | 0.41177 | 0.40321 | 0.38646 | 0.33854 | 0.29664 | -0.019666 | 0.40609 | 0.3994 | 0.39271 | 0.38283 | 0.37326 | 0.36382 | 0.35451 | 0.34533 | 0.33627 | 0.32734 | 0.30987 | 0.25789 | -0.0098476 | -0.070992
ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 14.8397 | 26.1131 | 26.0962 | 26.077 | 26.0518 | 26.026 | 26.0003 | 25.9739 | 25.9443 | 25.9123 | 25.854 | 25.7542 | 25.7125 | 25.6851 | 13.3658 | 23.4407 | 23.4275 | 23.4125 | 23.3928 | 23.3727 | 23.3526 | 23.332 | 23.3089 | 23.2839 | 23.2383 | 23.1238 | 23.0135 | 22.0148 | 13.557 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 22.0716 | 21.9346
| BILBOHALL | CT |  |  |  | 14.8397 | 26.1131 | 26.0962 | 26.077 | 26.0518 | 26.026 | 26.0003 | 25.9739 | 25.9443 | 25.9123 | 25.854 | 25.7542 | 25.7125 | 25.6851 | 13.3658 | 23.4407 | 23.4275 | 23.4125 | 23.3928 | 23.3727 | 23.3526 | 23.332 | 23.3089 | 23.2839 | 23.2383 | 23.1238 | 23.0135 | 22.0148 | 13.557 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 22.0716 | 21.9346
| BILBOHALL | LW |  |  |  | 14.8427 | 26.1209 | 26.1162 | 26.1105 | 26.0978 | 26.084 | 26.069 | 26.053 | 26.0356 | 26.0172 | 25.9884 | 25.8172 | 25.7334 | 25.6937 | 13.3682 | 23.4468 | 23.4431 | 23.4386 | 23.4287 | 23.418 | 23.4063 | 23.3938 | 23.3801 | 23.3658 | 23.3433 | 23.2096 | 23.0733 | 22.0684 | 13.557 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 21.9865
| BILBOHALL | ST |  |  |  | 14.8432 | 26.1225 | 26.121 | 26.1187 | 26.1119 | 26.0919 | 26.0722 | 26.052 | 26.0294 | 26.0051 | 25.9605 | 25.8791 | 25.8037 | 25.7616 | 13.3686 | 23.448 | 23.4468 | 23.4451 | 23.4397 | 23.4242 | 23.4087 | 23.393 | 23.3754 | 23.3563 | 23.3215 | 23.258 | 23.1991 | 23.1417 | 13.557 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637
| BILBOHALL | FS |  |  |  | 14.8435 | 26.1233 | 26.1231 | 26.1224 | 26.1198 | 26.1127 | 26.1055 | 26.0967 | 26.0875 | 26.0781 | 26.061 | 26.0285 | 26.0016 | 25.9762 | 13.3688 | 23.4487 | 23.4485 | 23.448 | 23.4459 | 23.4404 | 23.4348 | 23.4279 | 23.4207 | 23.4133 | 23.4 | 23.3746 | 23.3536 | 23.3338 | 13.557 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637
RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | -0.00040083 | 0.025898 | 0.025531 | 0.024601 | 0.024377 | 0.02419 | 0.024008 | 0.02391 | 0.02391 | 0.02391 | 0.02391 | 0.02391 | -0.0094437 | -0.019522 | -0.029499 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | -0.0060417 | -0.016123 | -0.026103
| BLACKMOUNT | CT |  |  |  | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.025898 | 0.025593 | 0.024807 | 0.024482 | 0.024351 | 0.024224 | 0.024099 | 0.023977 | 0.02391 | 0.02391 | 0.02391 | -0.00035002 | -0.0074047 | -0.014388 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | -0.004002 | -0.010988
| BLACKMOUNT | LW |  |  |  | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | -0.00040083 | 0.025898 | 0.025531 | 0.024601 | 0.024377 | 0.02419 | 0.024008 | 0.02391 | 0.02391 | 0.02391 | 0.02391 | 0.02391 | -0.0094437 | -0.019522 | -0.029499 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | -0.0060417 | -0.016123 | -0.026103
| BLACKMOUNT | ST |  |  |  | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.026006 | 0.02587 | 0.025551 | 0.025055 | 0.024598 | 0.024481 | 0.024398 | 0.024317 | 0.02423 | 0.024145 | 0.023978 | 0.02391 | 0.02391 | -0.00067507 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161
| BLACKMOUNT | FS |  |  |  | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.050802 | 0.026069 | 0.026051 | 0.026029 | 0.02589 | 0.025725 | 0.025533 | 0.025343 | 0.025098 | 0.024858 | 0.024664 | 0.024522 | 0.024362 | 0.024215 | 0.02408 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161 | 0.029161
BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 9.3189 | 9.2269 | 9.1087 | 8.9959 | 7.7691 | 7.5845 | 7.405 | 7.2247 | 7.103 | 7.0069 | 6.8168 | 6.4717 | 6.1315 | 5.7933 | 9.0225 | 8.9383 | 8.815 | 8.6934 | 7.6507 | 7.4994 | 7.3517 | 7.2013 | 7.09 | 6.9959 | 6.8098 | 6.4746 | 6.1141 | 5.615 | 9.1356 | 9.0434 | 8.9251 | 8.8123 | 8.7035 | 7.769 | 7.5781 | 7.3854 | 7.2514 | 7.1429 | 6.9284 | 6.5441 | 6.1635 | 5.7856
| BLACKSTAND | CT |  |  |  | 9.3189 | 9.2269 | 9.1087 | 8.9959 | 7.7691 | 7.5845 | 7.405 | 7.2247 | 7.103 | 7.0069 | 6.8168 | 6.4717 | 6.1315 | 5.7933 | 9.0225 | 8.9383 | 8.815 | 8.6934 | 7.6507 | 7.4994 | 7.3517 | 7.2013 | 7.09 | 6.9959 | 6.8098 | 6.4746 | 6.1141 | 5.7568 | 9.1356 | 9.0434 | 8.9251 | 8.8123 | 8.7035 | 7.769 | 7.5781 | 7.3854 | 7.2514 | 7.1429 | 6.9284 | 6.5441 | 6.1635 | 5.7856
| BLACKSTAND | LW |  |  |  | 9.4513 | 9.436 | 9.4183 | 9.3983 | 9.3763 | 9.3525 | 9.3271 | 9.3002 | 7.7362 | 7.6087 | 7.3548 | 6.886 | 6.4117 | 5.9364 | 9.1282 | 9.1035 | 9.0518 | 8.9917 | 8.9307 | 8.8865 | 7.6854 | 7.5576 | 7.4307 | 7.3041 | 7.0525 | 6.6084 | 6.1143 | 5.615 | 9.2688 | 9.2531 | 9.235 | 9.215 | 9.193 | 9.1692 | 9.1437 | 9.1168 | 9.0921 | 7.7056 | 7.4178 | 6.8949 | 6.3629 | 5.8248
| BLACKSTAND | ST |  |  |  | 9.4716 | 9.4663 | 9.4593 | 9.4524 | 9.4457 | 9.4376 | 9.4297 | 9.422 | 9.4146 | 9.4038 | 9.3831 | 9.3361 | 9.2943 | 7.7 | 9.1485 | 9.1403 | 9.1245 | 9.1047 | 9.0821 | 9.0631 | 9.0444 | 9.0241 | 9.005 | 8.9834 | 8.9416 | 7.7613 | 7.5794 | 7.4009 | 9.2895 | 9.2841 | 9.2769 | 9.2699 | 9.263 | 9.2547 | 9.2467 | 9.2388 | 9.2313 | 9.2205 | 9.1998 | 9.1527 | 9.1109 | 9.072
| BLACKSTAND | FS |  |  |  | 9.4663 | 9.4593 | 9.4522 | 9.4418 | 9.4315 | 9.4213 | 9.4112 | 9.4014 | 9.3916 | 9.382 | 9.3632 | 9.3072 | 9.2577 | 9.2119 | 9.1461 | 9.1399 | 9.133 | 9.1206 | 9.1075 | 9.0952 | 9.0831 | 9.0692 | 9.0562 | 9.0434 | 9.0184 | 8.9503 | 8.8885 | 8.8303 | 9.2841 | 9.2769 | 9.2697 | 9.259 | 9.2485 | 9.2381 | 9.2279 | 9.218 | 9.2083 | 9.1987 | 9.1798 | 9.1238 | 9.0743 | 9.0284
COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.4136 | 28.4136 | 22.6299 | 26.8091 | 26.7501 | 26.6283 | 26.6135 | 26.5985 | 26.5817 | 26.5635 | 26.5445 | 26.524 | 26.5031 | 26.4658 | 22.8339 | 21.9198 | 21.0838 | 26.9953 | 26.9861 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 22.7522 | 21.8583 | 21.0407
| BLAIRGOWRIE | CT |  |  |  | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.4136 | 28.4136 | 28.4136 | 26.8091 | 26.754 | 26.632 | 26.6183 | 26.6061 | 26.592 | 26.5768 | 26.5606 | 26.5429 | 26.5245 | 26.4906 | 26.2194 | 22.7089 | 22.0599 | 26.9953 | 26.9868 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.6641 | 22.6299 | 21.9953
| BLAIRGOWRIE | LW |  |  |  | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.4136 | 28.4136 | 22.6299 | 26.8105 | 26.7501 | 26.6283 | 26.6135 | 26.5985 | 26.5817 | 26.5635 | 26.5445 | 26.524 | 26.5031 | 26.4658 | 22.8339 | 21.9198 | 21.0838 | 26.9955 | 26.9861 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 22.7522 | 21.8583 | 21.0407
| BLAIRGOWRIE | ST |  |  |  | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.5729 | 28.5729 | 28.5729 | 26.9206 | 26.8041 | 26.7572 | 26.6968 | 26.63 | 26.6199 | 26.6091 | 26.5977 | 26.585 | 26.5718 | 26.5472 | 26.4036 | 26.3683 | 26.3352 | 27.0126 | 26.9945 | 26.9872 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.8217 | 26.8217 | 26.8217
| BLAIRGOWRIE | FS |  |  |  | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 28.7321 | 26.9309 | 26.9198 | 26.9045 | 26.8798 | 26.8527 | 26.8112 | 26.7665 | 26.7136 | 26.6581 | 26.6276 | 26.6183 | 26.5975 | 26.5816 | 26.5694 | 27.0142 | 27.0124 | 27.0101 | 27.0062 | 27.002 | 26.9956 | 26.9887 | 26.9805 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792 | 26.9792
STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | -0.55255 | -0.55289 | -0.55386 | -0.55506 | -0.55623 | -0.55737 | -0.55849 | -0.55959 | -0.56077 | -0.56194 | -0.56427 | -0.57427 | -0.67058 | -0.68052 | -0.75687 | -0.75728 | -0.75847 | -0.75991 | -0.76132 | -0.76271 | -0.76406 | -0.76538 | -0.76681 | -0.76823 | -0.77103 | -0.78311 | -0.85817 | -0.87016 | -0.73128 | -0.73169 | -0.73286 | -0.73431 | -0.73572 | -0.7371 | -0.73845 | -0.73976 | -0.74119 | -0.74261 | -0.74541 | -0.75746 | -0.85479 | -0.86676
| BLAIRLINNANS | CT |  |  |  | -0.55254 | -0.55283 | -0.55356 | -0.5544 | -0.55522 | -0.55602 | -0.5568 | -0.55757 | -0.5584 | -0.55922 | -0.56085 | -0.56796 | -0.66136 | -0.66844 | -0.75687 | -0.75721 | -0.7581 | -0.75911 | -0.7601 | -0.76107 | -0.76202 | -0.76294 | -0.76394 | -0.76493 | -0.7669 | -0.77549 | -0.84703 | -0.85557 | -0.73128 | -0.73162 | -0.7325 | -0.73351 | -0.7345 | -0.73546 | -0.73641 | -0.73733 | -0.73833 | -0.73932 | -0.74128 | -0.74986 | -0.84367 | -0.8522
| BLAIRLINNANS | LW |  |  |  | -0.55255 | -0.55289 | -0.55386 | -0.55506 | -0.55623 | -0.55737 | -0.55849 | -0.55959 | -0.56077 | -0.56194 | -0.56427 | -0.57427 | -0.67058 | -0.68052 | -0.75687 | -0.75728 | -0.75847 | -0.75991 | -0.76132 | -0.76271 | -0.76406 | -0.76538 | -0.76681 | -0.76823 | -0.77103 | -0.78311 | -0.85817 | -0.87016 | -0.73128 | -0.73169 | -0.73286 | -0.73431 | -0.73572 | -0.7371 | -0.73845 | -0.73976 | -0.74119 | -0.74261 | -0.74541 | -0.75746 | -0.85479 | -0.86676
| BLAIRLINNANS | ST |  |  |  | 0.32211 | -0.55257 | -0.55287 | -0.55332 | -0.55387 | -0.5548 | -0.55571 | -0.5566 | -0.55756 | -0.5585 | -0.56033 | -0.56475 | -0.61222 | -0.61656 | 0.28999 | -0.7569 | -0.75726 | -0.75781 | -0.75848 | -0.7596 | -0.7607 | -0.76177 | -0.76293 | -0.76406 | -0.76628 | -0.77162 | -0.80831 | -0.81355 | 0.29698 | -0.73131 | -0.73166 | -0.73221 | -0.73287 | -0.734 | -0.73509 | -0.73616 | -0.73732 | -0.73845 | -0.74066 | -0.74599 | -0.79382 | -0.79905
| BLAIRLINNANS | FS |  |  |  | 0.32212 | 0.32211 | -0.55242 | -0.55255 | -0.5527 | -0.55301 | -0.55331 | -0.5537 | -0.55409 | -0.55446 | -0.55519 | -0.55692 | -0.55852 | -0.56001 | 0.29002 | 0.29001 | -0.75672 | -0.75688 | -0.75706 | -0.75743 | -0.7578 | -0.75827 | -0.75874 | -0.75919 | -0.76007 | -0.76216 | -0.7641 | -0.76589 | 0.29703 | 0.29701 | -0.73113 | -0.73128 | -0.73147 | -0.73184 | -0.7322 | -0.73267 | -0.73314 | -0.73359 | -0.73447 | -0.73655 | -0.73848 | -0.74028
BOAT OF GARTEN | BOAT OF GARTEN 11 kV | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 7.7729 | 9.5772 | 9.5624 | 9.5261 | 9.4815 | 9.4378 | 9.3947 | 9.3524 | 9.3108 | 9.2658 | 9.2211 | 9.172 | 9.1204 | 7.86 | 7.5361 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 7.809 | 7.5093
| BOAT OF GARTEN 11 kV | CT |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.579 | 9.5694 | 9.5495 | 9.5267 | 9.5041 | 9.4816 | 9.4593 | 9.4378 | 9.4145 | 9.3914 | 9.3459 | 9.1847 | 9.1317 | 9.1144 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
| BOAT OF GARTEN 11 kV | LW |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 7.7729 | 9.5772 | 9.5624 | 9.5261 | 9.4815 | 9.4378 | 9.3947 | 9.3524 | 9.3108 | 9.2658 | 9.2211 | 9.172 | 9.1204 | 7.86 | 7.5361 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 7.809 | 7.5093
| BOAT OF GARTEN 11 kV | ST |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.582 | 9.5761 | 9.5653 | 9.5485 | 9.5284 | 9.5033 | 9.4786 | 9.4546 | 9.4288 | 9.4034 | 9.354 | 9.2339 | 9.1648 | 9.1328 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
| BOAT OF GARTEN 11 kV | FS |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.5851 | 9.5835 | 9.5827 | 9.5778 | 9.5721 | 9.564 | 9.5559 | 9.5457 | 9.5355 | 9.5256 | 9.5064 | 9.4609 | 9.4179 | 9.377 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 10.5684 | 10.5654 | 10.557 | 10.5466 | 10.543 | 10.5397 | 10.5365 | 10.5333 | 10.5299 | 10.5265 | 10.5197 | 10.5049 | 10.49 | 10.4755 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
| BODDAM | CT |  |  |  | 10.5684 | 10.566 | 10.5598 | 10.5527 | 10.546 | 10.5437 | 10.5415 | 10.5393 | 10.5369 | 10.5346 | 10.5299 | 10.5192 | 10.5085 | 10.498 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
| BODDAM | LW |  |  |  | 10.5684 | 10.5654 | 10.557 | 10.5466 | 10.543 | 10.5397 | 10.5365 | 10.5333 | 10.5299 | 10.5265 | 10.5197 | 10.5049 | 10.49 | 10.4755 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
| BODDAM | ST |  |  |  | 10.5693 | 10.5682 | 10.5658 | 10.562 | 10.5575 | 10.5531 | 10.5487 | 10.5456 | 10.5441 | 10.5427 | 10.5399 | 10.533 | 10.5263 | 10.5197 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
| BODDAM | FS |  |  |  | 10.5698 | 10.5696 | 10.5694 | 10.5683 | 10.567 | 10.5655 | 10.5641 | 10.5622 | 10.5604 | 10.5587 | 10.5552 | 10.547 | 10.5439 | 10.5416 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 6.8711 | 6.7767 | 6.6383 | 6.5014 | 6.3675 | 6.2364 | 6.1219 | 6.0265 | 5.9637 | 5.9223 | 5.8436 | 5.7065 | 4.8309 | 4.5947 | 6.984 | 6.9321 | 6.8548 | 6.7776 | 6.702 | 6.6278 | 6.556 | 6.4851 | 6.4318 | 6.3905 | 6.3472 | 6.2771 | 6.209 | 4.8229 | 6.9835 | 6.9052 | 6.7977 | 6.6945 | 6.5942 | 6.4967 | 6.4027 | 6.3111 | 6.251 | 6.2114 | 6.1399 | 6.0263 | 4.8355 | 4.5802
| BONSKEID | CT |  |  |  | 6.8711 | 6.7767 | 6.6383 | 6.5014 | 6.3675 | 6.2364 | 6.1219 | 6.0265 | 5.9637 | 5.9223 | 5.8436 | 5.7065 | 4.8309 | 4.5947 | 6.984 | 6.9321 | 6.8548 | 6.7776 | 6.702 | 6.6278 | 6.556 | 6.4851 | 6.4318 | 6.3905 | 6.3472 | 6.2771 | 6.209 | 4.8229 | 6.9835 | 6.9052 | 6.7977 | 6.6945 | 6.5942 | 6.4967 | 6.4027 | 6.3111 | 6.251 | 6.2114 | 6.1399 | 6.0263 | 4.8355 | 4.5802
| BONSKEID | LW |  |  |  | 6.9919 | 6.9656 | 6.9104 | 6.842 | 6.771 | 6.6976 | 6.6229 | 6.5767 | 6.5274 | 6.4771 | 6.4096 | 6.2673 | 6.1047 | 4.7878 | 7.049 | 7.0337 | 7.0003 | 6.9588 | 6.9159 | 6.8715 | 6.8266 | 6.7806 | 6.7608 | 6.7417 | 6.7032 | 6.606 | 6.502 | 4.8254 | 7.0897 | 7.0723 | 7.0419 | 7.005 | 6.9662 | 6.9256 | 6.8838 | 6.8406 | 6.7935 | 6.753 | 6.6978 | 6.5508 | 6.3828 | 4.7205
| BONSKEID | ST |  |  |  | 7.014 | 7.0046 | 6.9854 | 6.9588 | 6.9284 | 6.8988 | 6.8699 | 6.8401 | 6.8081 | 6.772 | 6.706 | 6.5984 | 6.5221 | 6.4527 | 7.0612 | 7.0558 | 7.0443 | 7.028 | 7.0094 | 6.9914 | 6.9738 | 6.9556 | 6.936 | 6.9141 | 6.8742 | 6.7944 | 6.7643 | 6.7322 | 7.1075 | 7.1014 | 7.0904 | 7.0764 | 7.061 | 7.0452 | 7.0299 | 7.0142 | 6.9979 | 6.9785 | 6.9426 | 6.8615 | 6.7892 | 6.7423
| BONSKEID | FS |  |  |  | 7.0113 | 7.0042 | 6.9957 | 6.9795 | 6.9623 | 6.9451 | 6.9279 | 6.9091 | 6.8902 | 6.8711 | 6.8356 | 6.7482 | 6.6647 | 6.5861 | 7.06 | 7.0561 | 7.0513 | 7.042 | 7.032 | 7.022 | 7.012 | 7.001 | 6.9898 | 6.9786 | 6.9578 | 6.9074 | 6.8596 | 6.8147 | 7.1041 | 7.0982 | 7.0917 | 7.0806 | 7.0691 | 7.0576 | 7.0462 | 7.0342 | 7.0222 | 7.0102 | 6.9874 | 6.9274 | 6.8681 | 6.8115
PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | YES | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
| BOWMORE | CT |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
| BOWMORE | LW |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
| BOWMORE | ST |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
| BOWMORE | FS |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
WOODHILL | BRAE | MINIMUM HEADROOM | HU 3604068816 | YES | NO | 2.0615 | 1.9918 | 1.9024 | 1.8188 | 1.7382 | 1.6606 | 1.586 | 1.5143 | 1.4738 | 1.4537 | 1.4141 | -0.15866 | -0.26015 | -0.45653 | 1.0912 | 1.026 | 0.94117 | 0.86113 | 0.78368 | 0.70957 | 0.66765 | 0.63257 | 0.6126 | 0.60257 | 0.58285 | -0.35019 | -0.56355 | -0.78089 | 1.0664 | 0.9875 | 0.88566 | 0.79017 | 0.69799 | -0.028168 | -0.10062 | -0.17018 | -0.20954 | -0.22911 | -0.26756 | -0.51183 | -0.68341 | -0.92406
| BRAE | CT |  |  |  | 2.0615 | 1.9918 | 1.9024 | 1.8188 | 1.7382 | 1.6606 | 1.586 | 1.5143 | 1.4738 | 1.4537 | 1.4141 | -0.15866 | -0.26015 | -0.45653 | 1.0912 | 1.026 | 0.94117 | 0.86113 | 0.78368 | 0.70957 | 0.66765 | 0.63257 | 0.6126 | 0.60257 | 0.58285 | -0.35019 | -0.56355 | -0.78089 | 1.0664 | 0.9875 | 0.88566 | 0.79017 | 0.69799 | -0.028168 | -0.10062 | -0.17018 | -0.20954 | -0.22911 | -0.26756 | -0.51183 | -0.68341 | -0.92406
| BRAE | LW |  |  |  | 2.1617 | 2.1501 | 2.1367 | 2.1216 | 2.1049 | 2.0869 | 2.0676 | 2.0473 | 2.0245 | 2.0011 | 1.9529 | 1.6678 | 1.5196 | -0.078077 | 1.1835 | 1.1716 | 1.1561 | 1.138 | 1.1183 | 1.0981 | 1.0765 | 1.0539 | 1.0291 | 1.004 | 0.95274 | 0.69324 | -0.20248 | -0.49438 | 1.1793 | 1.1658 | 1.1493 | 1.1305 | 1.1099 | 1.088 | 1.0647 | 1.0402 | 1.0129 | 0.98498 | 0.92775 | -0.021125 | -0.23257 | -0.55859
| BRAE | ST |  |  |  | 2.177 | 2.173 | 2.1677 | 2.1625 | 2.1574 | 2.1512 | 2.1453 | 2.1395 | 2.134 | 2.126 | 2.1106 | 1.9908 | 1.9529 | 1.9111 | 1.198 | 1.1938 | 1.1879 | 1.1813 | 1.1745 | 1.1576 | 1.1409 | 1.1245 | 1.1078 | 1.0891 | 1.053 | 0.90252 | 0.87108 | 0.83704 | 1.1968 | 1.1921 | 1.1856 | 1.179 | 1.1724 | 1.1607 | 1.1492 | 1.138 | 1.1268 | 1.113 | 1.0863 | 0.93875 | 0.8913 | 0.83962
| BRAE | FS |  |  |  | 2.173 | 2.1677 | 2.1623 | 2.1544 | 2.1466 | 2.1389 | 2.1313 | 2.1239 | 2.1165 | 2.1092 | 2.0949 | 2.0526 | 2.0083 | 1.9655 | 1.1945 | 1.1895 | 1.1844 | 1.1766 | 1.1687 | 1.158 | 1.1473 | 1.1357 | 1.1243 | 1.1132 | 1.0915 | 1.0322 | 0.97251 | 0.91526 | 1.1924 | 1.1863 | 1.1802 | 1.1711 | 1.162 | 1.1518 | 1.1417 | 1.1312 | 1.121 | 1.1109 | 1.0912 | 1.0348 | 0.97689 | 0.92105
BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.154 | 10.6255 | 14.4598 | 14.429 | 14.3609 | 14.2815 | 14.196 | 14.1546 | 14.1233 | 14.092 | 14.0582 | 14.0241 | 13.9576 | 10.7651 | 9.5167 | 8.8963 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 10.9667 | 9.5608 | 8.9725
| BRECHIN | CT |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.3929 | 10.9858 | 14.4598 | 14.429 | 14.3609 | 14.2823 | 14.2023 | 14.159 | 14.1283 | 14.0967 | 14.0622 | 14.0272 | 13.9606 | 10.9047 | 9.7972 | 9.3193 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 11.0962 | 9.8208 | 9.3777
| BRECHIN | LW |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.154 | 10.6255 | 14.4632 | 14.4333 | 14.365 | 14.2815 | 14.196 | 14.1546 | 14.1233 | 14.092 | 14.0582 | 14.0241 | 13.9576 | 10.7651 | 9.5167 | 8.8963 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 10.9667 | 9.5608 | 8.9725
| BRECHIN | ST |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.5536 | 16.1745 | 16.1745 | 14.4964 | 14.4554 | 14.4312 | 14.3972 | 14.3571 | 14.3147 | 14.2737 | 14.2314 | 14.1875 | 14.1628 | 14.1247 | 13.8416 | 11.4279 | 11.1676 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.5477 | 14.1695 | 11.3123
| BRECHIN | FS |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 14.4993 | 14.4942 | 14.4877 | 14.4753 | 14.4611 | 14.4456 | 14.4311 | 14.4134 | 14.3954 | 14.3773 | 14.3423 | 14.2752 | 14.2171 | 14.174 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418
PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 36.7273 | 36.6207 | 36.3729 | 36.074 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.5482 | 33.4413 | 33.2249 | 32.9638 | 32.7406 | 32.5299 | 32.3233 | 32.1202 | 31.9004 | 31.6823 | 31.2453 | 30.4332 | 29.8818 | 29.4026 | 33.2353 | 33.0762 | 32.7063 | 32.3493 | 32.2024 | 32.0638 | 31.9361 | 31.8508 | 31.7585 | 31.6669 | 31.4834 | 30.951 | 30.6708 | 30.4385
| BRIDGE OF DON | CT |  |  |  | 36.7331 | 36.6513 | 36.4789 | 36.2841 | 36.1258 | 35.9748 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.5543 | 33.4684 | 33.3175 | 33.1473 | 33.009 | 32.8771 | 32.7406 | 32.6024 | 32.455 | 32.3162 | 32.0496 | 31.4389 | 30.981 | 30.5369 | 33.2441 | 33.1219 | 32.8646 | 32.5737 | 32.379 | 32.2923 | 32.2024 | 32.1114 | 32.0144 | 31.9331 | 31.8212 | 31.3733 | 31.181 | 30.9945
| BRIDGE OF DON | LW |  |  |  | 36.7273 | 36.6207 | 36.3729 | 36.074 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.5482 | 33.4413 | 33.2249 | 32.9638 | 32.7406 | 32.5299 | 32.3233 | 32.1202 | 31.9004 | 31.6823 | 31.2453 | 30.4332 | 29.8818 | 29.4026 | 33.2353 | 33.0762 | 32.7063 | 32.3493 | 32.2024 | 32.0638 | 31.9361 | 31.8508 | 31.7585 | 31.6669 | 31.4834 | 30.951 | 30.6708 | 30.4385
| BRIDGE OF DON | ST |  |  |  | 36.8185 | 36.712 | 36.6311 | 36.5183 | 36.412 | 36.3416 | 36.2674 | 36.1917 | 36.1111 | 36.0376 | 35.9008 | 35.6883 | 35.6883 | 35.6883 | 33.6738 | 33.5322 | 33.4504 | 33.3519 | 33.259 | 33.1976 | 33.1327 | 33.0665 | 32.9962 | 32.932 | 32.8124 | 32.4206 | 32.1118 | 31.8114 | 33.3714 | 33.2126 | 33.0918 | 32.9234 | 32.7646 | 32.6596 | 32.5488 | 32.4357 | 32.3706 | 32.3284 | 32.2497 | 31.9135 | 31.7516 | 31.6254
| BRIDGE OF DON | FS |  |  |  | 36.8353 | 36.8185 | 36.7367 | 36.6966 | 36.6635 | 36.6387 | 36.6138 | 36.5833 | 36.5536 | 36.5247 | 36.4688 | 36.344 | 36.221 | 36.1002 | 33.7007 | 33.6739 | 33.5581 | 33.516 | 33.4813 | 33.457 | 33.4353 | 33.4087 | 33.3827 | 33.3575 | 33.3086 | 33.1996 | 33.0922 | 32.9866 | 33.3966 | 33.3716 | 33.2494 | 33.1896 | 33.1401 | 33.103 | 33.0659 | 33.0204 | 32.9761 | 32.9329 | 32.8494 | 32.6631 | 32.4796 | 32.3643
BRIDGE OF DUN | BRIDGE OF DUN 11kV | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | -0.3359 | -0.37027 | -0.40429 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | -0.017779 | -0.45916 | -0.50024 | -0.5409 | 0.59105 | 0.59032 | 0.58843 | 0.58627 | 0.58415 | 0.58207 | 0.58003 | 0.57803 | 0.57586 | 0.57581 | 0.57581 | -0.47343 | -0.51695 | -0.56001
| BRIDGE OF DUN 11kV | CT |  |  |  | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | -0.32681 | -0.35213 | -0.37717 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | -0.017721 | -0.44829 | -0.47855 | -0.50849 | 0.59105 | 0.59032 | 0.58843 | 0.58627 | 0.58415 | 0.58207 | 0.58003 | 0.57803 | 0.57586 | 0.57581 | 0.57581 | -0.46193 | -0.49398 | -0.52568
| BRIDGE OF DUN 11kV | LW |  |  |  | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | -0.3359 | -0.37027 | -0.40429 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | -0.017779 | -0.45916 | -0.50024 | -0.5409 | 0.59117 | 0.59055 | 0.58875 | 0.58655 | 0.58439 | 0.58227 | 0.5802 | 0.57816 | 0.57596 | 0.57581 | 0.57581 | -0.47343 | -0.51695 | -0.56001
| BRIDGE OF DUN 11kV | ST |  |  |  | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.38235 | 0.38235 | -0.0066885 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | -0.13406 | -0.15296 | -0.17189 | 0.59136 | 0.59113 | 0.59061 | 0.5898 | 0.58883 | 0.5882 | 0.58759 | 0.58699 | 0.58635 | 0.58571 | 0.58448 | -0.10519 | -0.12336 | -0.14157
| BRIDGE OF DUN 11kV | FS |  |  |  | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.62869 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.40542 | 0.59146 | 0.59143 | 0.59139 | 0.59116 | 0.59089 | 0.59068 | 0.59047 | 0.59021 | 0.58995 | 0.58969 | 0.5892 | 0.58802 | 0.58693 | 0.58592
ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 17.8404 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 14.8227 | 14.4252 | 14.0806 | 16.5083 | 16.4873 | 16.4404 | 16.3833 | 16.3537 | 16.3537 | 16.3537 | 16.3537 | 14.8889 | 14.695 | 14.3274 | 13.627 | 13.1254 | 12.6906 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 14.9053 | 14.7165 | 14.3584 | 13.6762 | 13.1876 | 12.7641
| BRIDGE OF EARN | CT |  |  |  | 17.8404 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 14.9893 | 14.7518 | 16.5083 | 16.4893 | 16.4498 | 16.4043 | 16.3585 | 16.3537 | 16.3537 | 16.3537 | 16.3537 | 14.9196 | 14.5928 | 14.1584 | 13.8373 | 13.5375 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 14.9353 | 14.6169 | 14.1938 | 13.881 | 13.589
| BRIDGE OF EARN | LW |  |  |  | 17.8405 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 14.8227 | 14.4252 | 14.0806 | 16.5087 | 16.4873 | 16.4404 | 16.3833 | 16.3537 | 16.3537 | 16.3537 | 16.3537 | 14.8889 | 14.695 | 14.3274 | 13.627 | 13.1254 | 12.6906 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 14.9053 | 14.7165 | 14.3584 | 13.6762 | 13.1876 | 12.7641
| BRIDGE OF EARN | ST |  |  |  | 17.8416 | 17.8396 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 16.5139 | 16.5048 | 16.4893 | 16.4682 | 16.444 | 16.4177 | 16.389 | 16.3579 | 16.3537 | 16.3537 | 16.3537 | 14.9921 | 14.7843 | 14.5896 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 14.8035 | 14.6138
| BRIDGE OF EARN | FS |  |  |  | 17.8422 | 17.8413 | 17.8403 | 17.8385 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 17.8377 | 16.5165 | 16.5126 | 16.5077 | 16.4996 | 16.4909 | 16.4808 | 16.4699 | 16.4572 | 16.4438 | 16.4297 | 16.4028 | 16.3537 | 16.3537 | 16.3537 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197 | 16.7197
RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.21952 | 0.21889 | 0.21707 | 0.21482 | 0.21261 | 0.21045 | 0.20853 | 0.20735 | 0.20675 | 0.20641 | 0.20576 | 0.2041 | 0.20243 | 0.20153 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579
| BRIDGE OF GAUR | CT |  |  |  | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.21952 | 0.219 | 0.21763 | 0.21606 | 0.21452 | 0.213 | 0.21151 | 0.21006 | 0.20866 | 0.20752 | 0.20671 | 0.2056 | 0.20448 | 0.20338 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579
| BRIDGE OF GAUR | LW |  |  |  | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.21952 | 0.21889 | 0.21707 | 0.21482 | 0.21261 | 0.21045 | 0.20853 | 0.20735 | 0.20675 | 0.20641 | 0.20576 | 0.2041 | 0.20243 | 0.20153 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579
| BRIDGE OF GAUR | ST |  |  |  | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.2197 | 0.21947 | 0.21892 | 0.21807 | 0.21704 | 0.21598 | 0.21495 | 0.21395 | 0.21286 | 0.21179 | 0.20969 | 0.20692 | 0.2061 | 0.20538 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579
| BRIDGE OF GAUR | FS |  |  |  | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.42819 | 0.21981 | 0.21978 | 0.21974 | 0.2195 | 0.21922 | 0.21887 | 0.21853 | 0.21808 | 0.21764 | 0.21722 | 0.21638 | 0.21438 | 0.21253 | 0.21084 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579 | 0.24579
BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 6.0993 | 6.0989 | 6.0978 | 6.0965 | 6.0952 | 6.0913 | 6.09 | 6.0887 | 6.0873 | 6.0859 | 6.0832 | 6.0817 | 6.0817 | 6.0817 | 5.8544 | 5.852 | 5.8452 | 5.8371 | 5.8291 | 5.8056 | 5.7974 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 4.9446 | 5.9504 | 5.9487 | 5.9438 | 5.938 | 5.9322 | 5.9154 | 5.9095 | 5.9036 | 5.8976 | 5.8916 | 5.8797 | 5.8373 | 5.8211 | 5.8211
| BROADFORD | CT |  |  |  | 6.0993 | 6.099 | 6.0982 | 6.0973 | 6.0964 | 6.0932 | 6.0924 | 6.0915 | 6.0906 | 6.0895 | 6.0872 | 6.0817 | 6.0817 | 6.0817 | 5.8545 | 5.8526 | 5.8476 | 5.8421 | 5.8365 | 5.8171 | 5.8118 | 5.8066 | 5.8011 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.9505 | 5.9491 | 5.9456 | 5.9416 | 5.9376 | 5.9236 | 5.9199 | 5.9161 | 5.9121 | 5.9072 | 5.897 | 5.8666 | 5.8358 | 5.8211
| BROADFORD | LW |  |  |  | 6.0993 | 6.0989 | 6.0978 | 6.0965 | 6.0952 | 6.0913 | 6.09 | 6.0887 | 6.0873 | 6.0859 | 6.0832 | 6.0817 | 6.0817 | 6.0817 | 5.8544 | 5.852 | 5.8452 | 5.8371 | 5.8291 | 5.8056 | 5.7974 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 4.9446 | 5.9504 | 5.9487 | 5.9438 | 5.938 | 5.9322 | 5.9154 | 5.9095 | 5.9036 | 5.8976 | 5.8916 | 5.8797 | 5.8373 | 5.8211 | 5.8211
| BROADFORD | ST |  |  |  | 6.0996 | 6.0994 | 6.0992 | 6.0987 | 6.0982 | 6.0958 | 6.0949 | 6.094 | 6.0931 | 6.0921 | 6.0899 | 6.0855 | 6.0817 | 6.0817 | 5.8561 | 5.8553 | 5.8536 | 5.851 | 5.8478 | 5.8329 | 5.8275 | 5.8222 | 5.8165 | 5.81 | 5.7967 | 5.7944 | 5.7944 | 5.7944 | 5.9517 | 5.9511 | 5.9498 | 5.948 | 5.9457 | 5.935 | 5.9311 | 5.9273 | 5.9232 | 5.9186 | 5.909 | 5.8896 | 5.8704 | 5.8513
| BROADFORD | FS |  |  |  | 6.0998 | 6.0997 | 6.0997 | 6.0995 | 6.0994 | 6.0984 | 6.0981 | 6.0977 | 6.0973 | 6.0969 | 6.0961 | 6.0944 | 6.0928 | 6.0913 | 5.8573 | 5.8571 | 5.8569 | 5.8559 | 5.8549 | 5.8492 | 5.8473 | 5.8448 | 5.8422 | 5.8397 | 5.835 | 5.8242 | 5.8145 | 5.8053 | 5.9525 | 5.9524 | 5.9522 | 5.9515 | 5.9508 | 5.9467 | 5.9453 | 5.9435 | 5.9417 | 5.9398 | 5.9365 | 5.9287 | 5.9218 | 5.9152
CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 10.7009 | 10.6916 | 10.6803 | 10.6661 | 10.6523 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.229 | 10.2211 | 10.2114 | 10.1994 | 10.1876 | 10.1761 | 10.1647 | 10.1535 | 10.1414 | 10.1267 | 10.0926 | 9.9142 | 9.8626 | 9.8118 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
| BRODICK | CT |  |  |  | 10.7009 | 10.6931 | 10.6848 | 10.6752 | 10.6656 | 10.6556 | 10.645 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.229 | 10.2224 | 10.2153 | 10.2071 | 10.1989 | 10.1904 | 10.1814 | 10.1734 | 10.1646 | 10.1563 | 10.1396 | 9.9697 | 9.8842 | 9.8397 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
| BRODICK | LW |  |  |  | 10.7009 | 10.6916 | 10.6803 | 10.6661 | 10.6523 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.229 | 10.2211 | 10.2114 | 10.1994 | 10.1876 | 10.1761 | 10.1647 | 10.1535 | 10.1414 | 10.1294 | 10.1055 | 9.9142 | 9.8626 | 9.8118 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
| BRODICK | ST |  |  |  | 10.702 | 10.6974 | 10.6942 | 10.689 | 10.6827 | 10.6623 | 10.6417 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.6391 | 10.2299 | 10.226 | 10.2232 | 10.2188 | 10.2135 | 10.1961 | 10.1787 | 10.1621 | 10.1441 | 10.1267 | 10.0926 | 10.0101 | 9.9283 | 9.8971 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
| BRODICK | FS |  |  |  | 10.7026 | 10.7005 | 10.7003 | 10.6988 | 10.697 | 10.6902 | 10.6836 | 10.675 | 10.6666 | 10.6583 | 10.6423 | 10.6391 | 10.6391 | 10.6391 | 10.2304 | 10.2287 | 10.2285 | 10.2272 | 10.2257 | 10.2199 | 10.2142 | 10.207 | 10.1998 | 10.1928 | 10.1791 | 10.147 | 10.1169 | 10.0887 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469 | 9.5469
BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 3.8645 | 6.0024 | 5.9989 | 5.9891 | 5.977 | 4.9651 | 4.9535 | 4.9419 | 4.9306 | 4.9183 | 4.9062 | 4.897 | 4.8926 | 3.9868 | 3.7675 | 6.0231 | 6.014 | 5.9879 | 5.956 | 4.9245 | 4.8936 | 4.8632 | 4.8562 | 4.8511 | 4.8461 | 4.8361 | 4.8145 | 4.8145 | 3.9582
| BRORA | CT |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 6.0025 | 5.9997 | 5.9927 | 5.9846 | 4.9767 | 4.9689 | 4.9612 | 4.9535 | 4.9453 | 4.9371 | 4.921 | 4.8926 | 4.8926 | 4.8926 | 6.0233 | 6.0161 | 5.9974 | 5.9761 | 4.9551 | 4.9345 | 4.914 | 4.8939 | 4.8721 | 4.859 | 4.8523 | 4.825 | 4.8145 | 4.8145
| BRORA | LW |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 3.8645 | 6.0024 | 5.9989 | 5.9891 | 5.977 | 4.9651 | 4.9535 | 4.9419 | 4.9306 | 4.9183 | 4.9062 | 4.897 | 4.8926 | 3.9868 | 3.7675 | 6.0231 | 6.014 | 5.9879 | 5.956 | 4.9245 | 4.8936 | 4.8632 | 4.8562 | 4.8511 | 4.8461 | 4.8361 | 4.8145 | 4.8145 | 3.9582
| BRORA | ST |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 6.0056 | 6.0047 | 6.0029 | 6.0018 | 5.0004 | 4.9932 | 4.9862 | 4.9792 | 4.9717 | 4.9644 | 4.95 | 4.9152 | 4.8963 | 4.8926 | 6.0272 | 6.0263 | 6.0244 | 6.0214 | 5.0179 | 4.9989 | 4.9802 | 4.9618 | 4.942 | 4.9225 | 4.8846 | 4.8498 | 4.8349 | 4.8202
| BRORA | FS |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 5.4674 | 6.0061 | 6.0059 | 6.0056 | 6.0048 | 5.0038 | 5.0009 | 4.9985 | 4.9955 | 4.9925 | 4.9896 | 4.9839 | 4.9704 | 4.9575 | 4.9449 | 6.0276 | 6.0274 | 6.0272 | 6.0264 | 5.0254 | 5.0191 | 5.0128 | 5.0048 | 4.9969 | 4.9891 | 4.9741 | 4.9386 | 4.9042 | 4.8711
MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | NO | 15.1162 | 15.0935 | 15.0281 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2865 | 14.2746 | 14.2405 | 14.1986 | 14.1576 | 14.1162 | 14.0744 | 14.0334 | 13.9878 | 13.9409 | 13.847 | 13.6872 | 13.6284 | 13.6284 | 14.5071 | 14.4915 | 14.4467 | 14.3914 | 14.3376 | 14.2831 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
| BROUGHTY FERRY | CT |  |  |  | 15.1168 | 15.0989 | 15.0525 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2868 | 14.2774 | 14.2532 | 14.2254 | 14.198 | 14.1708 | 14.1445 | 14.1187 | 14.0902 | 14.0588 | 13.9948 | 13.8811 | 13.7783 | 13.6822 | 14.5076 | 14.4953 | 14.4634 | 14.4268 | 14.3907 | 14.3549 | 14.3203 | 14.2864 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
| BROUGHTY FERRY | LW |  |  |  | 15.1162 | 15.0935 | 15.0281 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2865 | 14.2746 | 14.2405 | 14.1986 | 14.1576 | 14.1162 | 14.0744 | 14.0334 | 13.9878 | 13.9409 | 13.847 | 13.6872 | 13.6284 | 13.6284 | 14.5071 | 14.4915 | 14.4467 | 14.3914 | 14.3376 | 14.2831 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
| BROUGHTY FERRY | ST |  |  |  | 15.1229 | 15.1146 | 15.0952 | 15.0651 | 15.029 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2899 | 14.2856 | 14.2755 | 14.2598 | 14.241 | 14.2279 | 14.2154 | 14.2032 | 14.1896 | 14.174 | 14.1421 | 14.0645 | 13.9966 | 13.9328 | 14.5117 | 14.506 | 14.4927 | 14.472 | 14.4472 | 14.4301 | 14.4136 | 14.3975 | 14.3796 | 14.3591 | 14.3171 | 14.2742 | 14.2742 | 14.2742
| BROUGHTY FERRY | FS |  |  |  | 15.1267 | 15.1256 | 15.1241 | 15.1156 | 15.1059 | 15.0982 | 15.0905 | 15.0805 | 15.0701 | 15.059 | 15.037 | 15.0068 | 15.0068 | 15.0068 | 14.2919 | 14.2913 | 14.2905 | 14.2862 | 14.2811 | 14.277 | 14.273 | 14.2679 | 14.2624 | 14.2566 | 14.2451 | 14.2161 | 14.1912 | 14.1693 | 14.5144 | 14.5136 | 14.5125 | 14.5067 | 14.5001 | 14.4947 | 14.4895 | 14.4826 | 14.4755 | 14.4679 | 14.4527 | 14.4145 | 14.3818 | 14.3529
DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 11.6171 | 11.5594 | 11.4853 | 11.4146 | 11.3465 | 11.2809 | 11.2179 | 11.1574 | 11.1222 | 11.1048 | 11.0705 | 9.9137 | 9.6244 | 9.3321 | 11.0952 | 11.0461 | 10.981 | 10.9182 | 10.8575 | 10.799 | 10.7427 | 10.6885 | 10.6633 | 10.6531 | 10.6331 | 9.8093 | 9.4995 | 9.1881 | 10.9121 | 10.8558 | 10.7835 | 10.7147 | 10.6483 | 10.5843 | 9.9778 | 9.9038 | 9.8573 | 9.8305 | 9.7778 | 9.4981 | 9.2091 | 8.8771
| BRUCHAG | CT |  |  |  | 11.6171 | 11.5594 | 11.4853 | 11.4146 | 11.3465 | 11.2809 | 11.2179 | 11.1574 | 11.1222 | 11.1048 | 11.0705 | 9.9137 | 9.6244 | 9.3321 | 11.0952 | 11.0461 | 10.981 | 10.9182 | 10.8575 | 10.799 | 10.7427 | 10.6885 | 10.6633 | 10.6531 | 10.6331 | 9.8093 | 9.4995 | 9.1881 | 10.9121 | 10.8558 | 10.7835 | 10.7147 | 10.6483 | 10.5843 | 9.9778 | 9.9038 | 9.8573 | 9.8305 | 9.7778 | 9.4981 | 9.2091 | 8.8771
| BRUCHAG | LW |  |  |  | 11.7002 | 11.6906 | 11.6794 | 11.6669 | 11.6531 | 11.6382 | 11.6223 | 11.6054 | 11.586 | 11.5661 | 11.5251 | 11.4158 | 9.9044 | 9.5169 | 11.1633 | 11.1535 | 11.1389 | 11.1219 | 11.1041 | 11.0854 | 11.066 | 11.046 | 11.0235 | 11.0005 | 10.9538 | 10.8344 | 9.6978 | 9.2845 | 10.993 | 10.9837 | 10.9728 | 10.9606 | 10.9472 | 10.9326 | 10.9171 | 10.9006 | 10.8818 | 10.8623 | 10.8224 | 9.9004 | 9.4915 | 9.034
| BRUCHAG | ST |  |  |  | 11.7129 | 11.7096 | 11.7052 | 11.7008 | 11.6966 | 11.6915 | 11.6866 | 11.6818 | 11.6771 | 11.6704 | 11.6574 | 11.6222 | 11.5894 | 11.5525 | 11.1743 | 11.1709 | 11.1656 | 11.1595 | 11.153 | 11.1379 | 11.1231 | 11.1087 | 11.0937 | 11.077 | 11.0448 | 10.9635 | 10.9356 | 10.9141 | 11.0054 | 11.0022 | 10.9979 | 10.9937 | 10.9896 | 10.9846 | 10.9798 | 10.9751 | 10.9706 | 10.964 | 10.9514 | 10.917 | 10.8851 | 10.8491
| BRUCHAG | FS |  |  |  | 11.7096 | 11.7052 | 11.7007 | 11.6942 | 11.6877 | 11.6813 | 11.675 | 11.6688 | 11.6627 | 11.6567 | 11.6449 | 11.6098 | 11.5728 | 11.537 | 11.172 | 11.1682 | 11.1645 | 11.1584 | 11.1522 | 11.143 | 11.1339 | 11.1237 | 11.1137 | 11.1039 | 11.0847 | 11.0334 | 10.9821 | 10.933 | 11.0022 | 10.9979 | 10.9936 | 10.9872 | 10.9809 | 10.9747 | 10.9685 | 10.9625 | 10.9565 | 10.9506 | 10.9391 | 10.9049 | 10.8689 | 10.834
KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 34.4884 | 34.4841 | 34.475 | 34.4644 | 34.4529 | 34.4411 | 34.429 | 34.4173 | 34.4043 | 34.3917 | 34.3708 | 33.5408 | 33.4758 | 33.4123 | 32.8914 | 32.8484 | 32.7799 | 32.7008 | 32.6153 | 32.5266 | 32.4363 | 32.3489 | 32.252 | 32.1673 | 32.1353 | 31.6966 | 31.6966 | 31.6966 | 33.425 | 33.4126 | 33.3857 | 33.3545 | 33.3209 | 33.286 | 33.2505 | 33.2161 | 33.1779 | 33.1407 | 33.0793 | 32.2865 | 32.2865 | 32.2865
| BUCKIE | CT |  |  |  | 34.4884 | 34.4841 | 34.475 | 34.4644 | 34.4529 | 34.4411 | 34.429 | 34.4173 | 34.4043 | 34.3917 | 34.3708 | 33.5408 | 33.4758 | 33.4123 | 32.8914 | 32.8484 | 32.7799 | 32.7008 | 32.6153 | 32.5266 | 32.4363 | 32.3489 | 32.252 | 32.1673 | 32.1353 | 31.6966 | 31.6966 | 31.6966 | 33.425 | 33.4126 | 33.3857 | 33.3545 | 33.3209 | 33.286 | 33.2505 | 33.2161 | 33.1779 | 33.1407 | 33.0793 | 32.2865 | 32.2865 | 32.2865
| BUCKIE | LW |  |  |  | 34.4893 | 34.4861 | 34.4797 | 34.4718 | 34.4629 | 34.4536 | 34.4438 | 34.4348 | 34.4249 | 34.4158 | 34.4027 | 33.5697 | 33.4989 | 33.4298 | 32.9021 | 32.8642 | 32.8152 | 32.7562 | 32.6897 | 32.62 | 32.5472 | 32.4794 | 32.4054 | 32.3379 | 32.2398 | 31.6966 | 31.6966 | 31.6966 | 33.4276 | 33.4184 | 33.3995 | 33.3763 | 33.3502 | 33.3227 | 33.2941 | 33.2674 | 33.2383 | 33.2117 | 33.1731 | 32.2865 | 32.2865 | 32.2865
| BUCKIE | ST |  |  |  | 34.4902 | 34.4888 | 34.4865 | 34.4834 | 34.4792 | 34.4715 | 34.4636 | 34.456 | 34.4475 | 34.4392 | 34.4258 | 34.0143 | 33.9863 | 33.9589 | 32.9136 | 32.8963 | 32.8692 | 32.8429 | 32.8118 | 32.7539 | 32.6951 | 32.6382 | 32.5746 | 32.5124 | 32.4122 | 31.916 | 31.916 | 31.916 | 33.4304 | 33.4262 | 33.4196 | 33.4104 | 33.3982 | 33.3754 | 33.3523 | 33.3299 | 33.3049 | 33.2804 | 33.241 | 32.7626 | 32.6803 | 32.6756
| BUCKIE | FS |  |  |  | 34.4908 | 34.4901 | 34.4894 | 34.4881 | 34.4865 | 34.4835 | 34.4805 | 34.4771 | 34.4736 | 34.4702 | 34.4646 | 34.4523 | 34.4421 | 34.432 | 32.921 | 32.9129 | 32.9042 | 32.8887 | 32.8689 | 32.844 | 32.8214 | 32.7958 | 32.7694 | 32.7442 | 32.7026 | 32.6108 | 32.5339 | 32.4584 | 33.4322 | 33.4303 | 33.4281 | 33.4244 | 33.4195 | 33.4109 | 33.402 | 33.3919 | 33.3815 | 33.3716 | 33.3552 | 33.3191 | 33.2888 | 33.2591
FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 2.1508 | 2.1501 | 2.148 | 2.1455 | 2.143 | 2.1424 | 2.1424 | 1.9914 | 1.9844 | 1.9772 | 1.9663 | 1.9227 | 1.8823 | 1.8426 | 2.1202 | 2.1189 | 2.1151 | 2.1106 | 2.1062 | 2.1025 | 2.0989 | 1.9562 | 1.9479 | 1.9395 | 1.9266 | 1.8753 | 1.8276 | 1.7808 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9498 | 1.9415 | 1.9331 | 1.9203 | 1.8691 | 1.8216 | 1.7749
| BUNOICH | CT |  |  |  | 2.1508 | 2.1502 | 2.1487 | 2.1469 | 2.1452 | 2.1435 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 1.9859 | 1.9421 | 1.9142 | 1.8867 | 2.1202 | 2.1191 | 2.1163 | 2.1131 | 2.1099 | 2.1068 | 2.1043 | 1.9852 | 1.9784 | 1.9715 | 1.9497 | 1.8981 | 1.8652 | 1.8328 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9787 | 1.9719 | 1.965 | 1.9433 | 1.8918 | 1.8591 | 1.8268
| BUNOICH | LW |  |  |  | 2.1508 | 2.1501 | 2.148 | 2.1455 | 2.143 | 2.1424 | 2.1424 | 1.9914 | 1.9844 | 1.9772 | 1.9663 | 1.9227 | 1.8823 | 1.8426 | 2.1202 | 2.1189 | 2.1151 | 2.1106 | 2.1062 | 2.1025 | 2.0989 | 1.9562 | 1.9479 | 1.9395 | 1.9266 | 1.8753 | 1.8276 | 1.7808 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9498 | 1.9415 | 1.9331 | 1.9203 | 1.8691 | 1.8216 | 1.7749
| BUNOICH | ST |  |  |  | 2.151 | 2.1508 | 2.1501 | 2.1492 | 2.148 | 2.1459 | 2.1438 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 1.9859 | 1.9682 | 1.9505 | 2.1206 | 2.1201 | 2.1189 | 2.1172 | 2.1151 | 2.1112 | 2.1074 | 2.0954 | 2.0954 | 2.0954 | 1.9848 | 1.9497 | 1.9288 | 1.908 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9976 | 1.9783 | 1.9433 | 1.9225 | 1.9017
| BUNOICH | FS |  |  |  | 2.1512 | 2.1511 | 2.1511 | 2.1508 | 2.1505 | 2.1498 | 2.1491 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1208 | 2.1207 | 2.1206 | 2.1201 | 2.1196 | 2.1183 | 2.117 | 2.0964 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101
THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9981 | 3.9841 | 3.9569 | 3.5692 | 2.9551 | 2.8021 | 4.0372 | 4.0362 | 4.0339 | 4.0336 | 4.0336 | 4.0336 | 3.9902 | 3.9749 | 3.9581 | 3.9418 | 3.9098 | 3.5629 | 3.0165 | 2.8377 | 4.0422 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9973 | 3.9823 | 3.9655 | 3.9491 | 3.9172 | 3.5081 | 2.8678 | 2.6833
| BURGARHILL | CT |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.6207 | 3.0417 | 2.923 | 4.0372 | 4.0364 | 4.0345 | 4.0336 | 4.0336 | 4.0336 | 4.0336 | 3.9996 | 3.9942 | 3.989 | 3.9787 | 3.6232 | 3.1176 | 2.9789 | 4.0422 | 4.0418 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9961 | 3.9861 | 3.5702 | 2.9721 | 2.829
| BURGARHILL | LW |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9982 | 3.5692 | 2.9551 | 2.8021 | 4.0372 | 4.0362 | 4.0339 | 4.0336 | 4.0336 | 4.0336 | 3.9942 | 3.9877 | 3.9801 | 3.9727 | 3.9582 | 3.5629 | 3.0165 | 2.8377 | 4.0422 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9948 | 3.9874 | 3.9801 | 3.9656 | 3.5081 | 2.8678 | 2.6833
| BURGARHILL | ST |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9981 | 3.9841 | 3.9569 | 3.7552 | 3.4628 | 3.3991 | 4.0375 | 4.0371 | 4.0362 | 4.0349 | 4.0339 | 4.0336 | 3.9902 | 3.9749 | 3.9581 | 3.9418 | 3.9098 | 3.7277 | 3.4729 | 3.3986 | 4.0424 | 4.0422 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9973 | 3.9823 | 3.9655 | 3.9491 | 3.9172 | 3.7032 | 3.3998 | 3.3232
| BURGARHILL | FS |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9957 | 3.9715 | 3.9486 | 4.0377 | 4.0376 | 4.0375 | 4.0371 | 4.0366 | 4.0343 | 4.0336 | 4.0336 | 4.0336 | 3.9983 | 3.9856 | 3.9553 | 3.927 | 3.9001 | 4.0424 | 4.0424 | 4.0424 | 4.0422 | 4.0419 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9928 | 3.9627 | 3.9343 | 3.9074
ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 19.138 | 19.0786 | 19.003 | 18.9338 | 18.867 | 18.8028 | 18.741 | 18.6817 | 18.649 | 18.6328 | 18.6009 | 18.5258 | 18.448 | 14.3863 | 16.8479 | 16.7653 | 16.6452 | 16.5292 | 16.4204 | 16.3816 | 16.3444 | 16.3086 | 16.2889 | 16.2791 | 16.2599 | 13.0216 | 12.1206 | 11.2305 | 18.3061 | 18.2297 | 18.1147 | 18.0017 | 17.8915 | 17.784 | 17.6825 | 17.5844 | 17.5121 | 17.4624 | 17.4283 | 17.3479 | 13.668 | 12.7381
| BURGHEAD | CT |  |  |  | 19.138 | 19.0786 | 19.003 | 18.9338 | 18.867 | 18.8028 | 18.741 | 18.6817 | 18.649 | 18.6328 | 18.6009 | 18.5258 | 18.448 | 18.3657 | 16.8479 | 16.7653 | 16.6452 | 16.5292 | 16.4204 | 16.3816 | 16.3444 | 16.3086 | 16.2889 | 16.2791 | 16.2599 | 13.3664 | 12.7306 | 12.1006 | 18.3061 | 18.2297 | 18.1147 | 18.0017 | 17.8915 | 17.784 | 17.6825 | 17.5844 | 17.5121 | 17.4624 | 17.4283 | 17.3479 | 17.2647 | 13.5394
| BURGHEAD | LW |  |  |  | 19.227 | 19.2167 | 19.2048 | 19.1914 | 19.1766 | 19.1606 | 19.1435 | 19.1255 | 19.1068 | 19.0875 | 19.0479 | 18.9423 | 18.8229 | 14.3863 | 16.9205 | 16.8749 | 16.7906 | 16.7003 | 16.6094 | 16.5964 | 16.5866 | 16.5763 | 16.565 | 16.5533 | 16.5294 | 13.0216 | 12.1206 | 11.2305 | 18.3978 | 18.3725 | 18.3184 | 18.2533 | 18.1871 | 18.1198 | 18.0555 | 17.9919 | 17.9694 | 17.9488 | 17.9064 | 17.7935 | 13.668 | 12.7381
| BURGHEAD | ST |  |  |  | 19.2407 | 19.2371 | 19.2324 | 19.2277 | 19.2232 | 19.2178 | 19.2125 | 19.2073 | 19.2025 | 19.1956 | 19.1822 | 19.1463 | 19.1146 | 19.0816 | 16.9426 | 16.9256 | 16.8881 | 16.8429 | 16.8024 | 16.7669 | 16.7348 | 16.7037 | 16.6704 | 16.6357 | 16.6088 | 16.5882 | 16.5697 | 16.5498 | 18.4162 | 18.4069 | 18.3888 | 18.3641 | 18.3357 | 18.31 | 18.2866 | 18.2639 | 18.24 | 18.214 | 18.1642 | 18.0426 | 17.9779 | 17.9425
| BURGHEAD | FS |  |  |  | 19.2371 | 19.2324 | 19.2276 | 19.2206 | 19.2137 | 19.2068 | 19.2001 | 19.1934 | 19.1869 | 19.1804 | 19.1678 | 19.1301 | 19.0928 | 19.0569 | 16.9463 | 16.9398 | 16.9314 | 16.9102 | 16.8864 | 16.8633 | 16.8423 | 16.8237 | 16.807 | 16.7906 | 16.7588 | 16.6787 | 16.602 | 16.5349 | 18.4151 | 18.4091 | 18.4025 | 18.3892 | 18.3749 | 18.361 | 18.3479 | 18.3336 | 18.3194 | 18.3054 | 18.2783 | 18.2069 | 18.137 | 18.0697
BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 11.9485 | 11.028 | 17.1556 | 17.0988 | 16.9576 | 16.7745 | 16.5745 | 16.4966 | 16.4783 | 16.4595 | 16.44 | 16.4207 | 16.3806 | 10.2399 | 8.9714 | 7.8582 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.2329 | 10.4986 | 8.9062 | 7.727 | 6.6985
| BURGHMUIR | CT |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1588 | 17.1157 | 17.0208 | 16.9031 | 16.7691 | 16.63 | 16.5059 | 16.4931 | 16.4795 | 16.4656 | 16.4359 | 16.3833 | 11.1813 | 10.4046 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 10.5494 | 9.7823 | 9.0595
| BURGHMUIR | LW |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 11.9485 | 11.028 | 17.1556 | 17.0988 | 16.9576 | 16.7745 | 16.5745 | 16.4966 | 16.4783 | 16.4595 | 16.44 | 16.4207 | 16.3806 | 10.2399 | 8.9714 | 7.8582 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.2329 | 10.4986 | 8.9062 | 7.727 | 6.6985
| BURGHMUIR | ST |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1743 | 17.1512 | 17.1077 | 17.0347 | 16.937 | 16.8528 | 16.7622 | 16.6686 | 16.5679 | 16.5045 | 16.4858 | 16.4507 | 16.4241 | 16.399 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.295 | 10.8362
| BURGHMUIR | FS |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1865 | 17.1806 | 17.1763 | 17.1537 | 17.1229 | 17.0932 | 17.0601 | 17.0202 | 16.9803 | 16.9406 | 16.8561 | 16.636 | 16.5051 | 16.4955 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365
CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0.0042829 | 0.0042829 | 0.0042829 | -0.0013455 | -0.0035029 | -0.0056141 | -0.007679 | -0.0097 | -0.011895 | -0.014074 | -0.018389 | -0.028843 | -0.039364 | -0.049779 | 0.0029645 | 0.0028709 | -0.00047622 | -0.0030752 | -0.0056205 | -0.0081111 | -0.010547 | -0.012929 | -0.015505 | -0.018064 | -0.02313 | -0.035443 | -0.047837 | -0.060107 | 0.0035415 | 0.0034916 | -0.00025282 | -0.0028527 | -0.0053987 | -0.0078902 | -0.010327 | -0.01271 | -0.015287 | -0.017847 | -0.022914 | -0.035192 | -0.047548 | -0.05978
| BUTTERBRIDGE | CT |  |  |  | 0.0042829 | 0.0042829 | 0.0042829 | -0.00012905 | -0.001638 | -0.0031146 | -0.0045589 | -0.0059711 | -0.007499 | -0.0090167 | -0.012035 | -0.019351 | -0.026714 | -0.034004 | 0.0029646 | 0.0028709 | 0.0028709 | -0.0016402 | -0.0034203 | -0.0051624 | -0.0068663 | -0.0085323 | -0.010335 | -0.012125 | -0.01567 | -0.024261 | -0.032936 | -0.041523 | 0.0035416 | 0.0034916 | 0.0034916 | -0.0014172 | -0.0031979 | -0.0049405 | -0.006645 | -0.0083115 | -0.010115 | -0.011906 | -0.015451 | -0.024044 | -0.032692 | -0.041253
| BUTTERBRIDGE | LW |  |  |  | 0.0042829 | 0.0042829 | 0.0042829 | -0.0013455 | -0.0035029 | -0.0056141 | -0.007679 | -0.0097 | -0.011895 | -0.014074 | -0.018389 | -0.028843 | -0.039364 | -0.049779 | 0.0029645 | 0.0028709 | -0.00047622 | -0.0030752 | -0.0056205 | -0.0081111 | -0.010547 | -0.012929 | -0.015505 | -0.018064 | -0.02313 | -0.035443 | -0.047837 | -0.060107 | 0.0035415 | 0.0034916 | -0.00025282 | -0.0028527 | -0.0053987 | -0.0078902 | -0.010327 | -0.01271 | -0.015287 | -0.017847 | -0.022914 | -0.035192 | -0.047548 | -0.05978
| BUTTERBRIDGE | ST |  |  |  | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | -0.0001408 | -0.0010978 | -0.0020307 | -0.0030377 | -0.0040281 | -0.0059591 | -0.010595 | -0.015139 | -0.01969 | 0.0030207 | 0.0029498 | 0.0028709 | 0.0028709 | -0.00049638 | -0.001654 | -0.0027831 | -0.0038837 | -0.0050716 | -0.00624 | -0.0085181 | -0.013979 | -0.019314 | -0.024661 | 0.0035609 | 0.0035364 | 0.0034916 | 0.0034916 | -0.00027299 | -0.001431 | -0.0025604 | -0.0036614 | -0.0048497 | -0.0060185 | -0.0082973 | -0.01376 | -0.019097 | -0.024442
| BUTTERBRIDGE | FS |  |  |  | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | 0.0042829 | -0.0015115 | -0.0032153 | -0.0047766 | 0.0030828 | 0.0030661 | 0.0030445 | 0.0029606 | 0.0028747 | 0.0028709 | 0.0028709 | 0.0028709 | 0.0028709 | -0.0001766 | -0.0010955 | -0.0032711 | -0.0052811 | -0.0071231 | 0.0035748 | 0.0035692 | 0.0035653 | 0.0035402 | 0.0035103 | 0.0034916 | 0.0034916 | 0.0034916 | 0.0034916 | 0.0034916 | -0.00087232 | -0.0030486 | -0.0050593 | -0.0069019
BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | NO | 9.4376 | 9.4376 | 7.7514 | 7.737 | 7.7221 | 7.7065 | 7.6905 | 7.6747 | 7.6576 | 7.6361 | 7.4193 | 6.8177 | 6.204 | 5.5911 | 9.3214 | 9.3038 | 9.253 | 9.1878 | 9.1204 | 9.0498 | 8.9882 | 8.9882 | 7.3196 | 7.1934 | 6.9377 | 6.228 | 5.5039 | 4.7809 | 9.2361 | 9.2299 | 9.2121 | 9.1894 | 9.1658 | 9.1411 | 7.3454 | 7.2362 | 7.118 | 6.9935 | 6.7411 | 6.0409 | 5.3265 | 4.6131
| CALLANDER | CT |  |  |  | 9.4376 | 9.4376 | 7.7542 | 7.7434 | 7.7322 | 7.7204 | 7.7082 | 7.6961 | 7.6831 | 7.6693 | 7.6412 | 7.1943 | 6.733 | 6.2712 | 9.3214 | 9.3059 | 9.2657 | 9.2171 | 9.1663 | 9.1128 | 9.0574 | 9.0029 | 8.9882 | 8.9882 | 7.2046 | 6.6723 | 6.128 | 5.5832 | 9.2361 | 9.2307 | 9.2166 | 9.1996 | 9.1819 | 9.1631 | 9.1438 | 9.1247 | 7.2944 | 7.1988 | 7.0045 | 6.4792 | 5.9422 | 5.4048
| CALLANDER | LW |  |  |  | 9.4376 | 9.4376 | 7.7514 | 7.737 | 7.7221 | 7.7065 | 7.6905 | 7.6747 | 7.6576 | 7.6361 | 7.4193 | 6.8177 | 6.204 | 5.5911 | 9.3215 | 9.3038 | 9.253 | 9.1878 | 9.1204 | 9.0498 | 8.9882 | 8.9882 | 7.3196 | 7.1934 | 6.9377 | 6.228 | 5.5039 | 4.7809 | 9.2361 | 9.2299 | 9.2121 | 9.1894 | 9.1658 | 9.1411 | 7.3454 | 7.2362 | 7.118 | 6.9935 | 6.7411 | 6.0409 | 5.3265 | 4.6131
| CALLANDER | ST |  |  |  | 9.4376 | 9.4376 | 9.4376 | 7.7562 | 7.7487 | 7.7409 | 7.7329 | 7.725 | 7.7164 | 7.7072 | 7.6885 | 7.6321 | 7.3432 | 7.0605 | 9.3265 | 9.3193 | 9.3022 | 9.2747 | 9.2407 | 9.2055 | 9.1692 | 9.1334 | 9.0944 | 9.0529 | 8.9882 | 7.1887 | 6.8479 | 6.5144 | 9.2379 | 9.2353 | 9.2293 | 9.2197 | 9.2079 | 9.1956 | 9.1828 | 9.1703 | 9.1567 | 9.1422 | 7.3318 | 6.9888 | 6.6525 | 6.3235
| CALLANDER | FS |  |  |  | 9.4376 | 9.4376 | 9.4376 | 9.4376 | 9.4376 | 9.4376 | 7.7589 | 7.7557 | 7.7524 | 7.749 | 7.742 | 7.7232 | 7.7037 | 7.6838 | 9.374 | 9.3287 | 9.3267 | 9.3197 | 9.311 | 9.2992 | 9.2869 | 9.2725 | 9.2578 | 9.2422 | 9.2106 | 9.1253 | 9.0373 | 8.9882 | 9.2596 | 9.2386 | 9.2379 | 9.2355 | 9.2324 | 9.2283 | 9.224 | 9.219 | 9.2138 | 9.2084 | 9.1973 | 9.1675 | 9.1367 | 7.2994
STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 5.7311 | 5.7305 | 5.7288 | 5.7266 | 5.7245 | 5.7224 | 5.7203 | 5.7183 | 5.7161 | 5.7139 | 5.7096 | 5.6948 | 3.6615 | 3.5089 | 5.1325 | 5.1294 | 5.1201 | 5.1087 | 5.0976 | 5.0866 | 5.0759 | 5.0653 | 5.0539 | 5.0425 | 5.0255 | 5.0255 | 3.5982 | 3.4198 | 5.1213 | 5.1141 | 5.0923 | 5.0655 | 5.0393 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.2876 | 3.1099
| CALLANISH | CT |  |  |  | 5.7311 | 5.7306 | 5.7291 | 5.7275 | 5.7259 | 5.7243 | 5.7227 | 5.7212 | 5.7195 | 5.7179 | 5.7146 | 5.7009 | 3.7367 | 3.5955 | 5.1325 | 5.1296 | 5.122 | 5.1134 | 5.1049 | 5.0966 | 5.0885 | 5.0805 | 5.0718 | 5.0632 | 5.0461 | 5.0255 | 3.6859 | 3.5212 | 5.1213 | 5.1145 | 5.0968 | 5.0765 | 5.0566 | 5.0371 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.3751 | 3.2107
| CALLANISH | LW |  |  |  | 5.7312 | 5.7305 | 5.7288 | 5.7266 | 5.7245 | 5.7224 | 5.7203 | 5.7183 | 5.7161 | 5.7139 | 5.7096 | 5.6948 | 3.6615 | 3.5089 | 5.1326 | 5.1294 | 5.1201 | 5.1087 | 5.0976 | 5.0866 | 5.0759 | 5.0653 | 5.0539 | 5.0425 | 5.0255 | 5.0255 | 3.5982 | 3.4198 | 5.1216 | 5.1141 | 5.0923 | 5.0655 | 5.0393 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.2876 | 3.1099
| CALLANISH | ST |  |  |  | 5.7314 | 5.7314 | 5.7313 | 5.7311 | 5.7309 | 5.7296 | 5.7284 | 5.7272 | 5.7259 | 5.7247 | 5.7222 | 5.7162 | 5.328 | 5.3222 | 5.1341 | 5.1338 | 5.1332 | 5.1323 | 5.1312 | 5.1247 | 5.1183 | 5.1121 | 5.1054 | 5.0987 | 5.0859 | 5.0546 | 4.8197 | 4.8137 | 5.1251 | 5.1245 | 5.1231 | 5.1209 | 5.1183 | 5.103 | 5.088 | 5.0734 | 5.0576 | 5.042 | 5.0182 | 5.0182 | 4.6406 | 3.983
| CALLANISH | FS |  |  |  | 5.7314 | 5.7314 | 5.7314 | 5.7311 | 5.7309 | 5.7304 | 5.73 | 5.7294 | 5.7289 | 5.7284 | 5.7273 | 5.7249 | 5.7226 | 5.7204 | 5.1341 | 5.134 | 5.1338 | 5.1326 | 5.1311 | 5.1288 | 5.1266 | 5.1237 | 5.1209 | 5.1181 | 5.1126 | 5.0998 | 5.0878 | 5.0766 | 5.1252 | 5.1248 | 5.1243 | 5.1215 | 5.1181 | 5.1128 | 5.1075 | 5.1007 | 5.094 | 5.0874 | 5.0746 | 5.0445 | 5.0182 | 5.0182
TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.84759 | 0.84731 | 0.8465 | 0.84551 | 0.84454 | 0.84359 | 0.84265 | 0.84174 | 0.84075 | 0.83977 | 0.83782 | 0.83091 | 0.82399 | 0.81718 | 0.72655 | 0.72514 | 0.7211 | 0.71614 | 0.71128 | 0.70649 | 0.70182 | 0.69724 | 0.69229 | 0.68738 | 0.6776 | 0.65059 | 0.62449 | 0.5988 | 0.66324 | 0.66156 | 0.65675 | 0.65086 | 0.64507 | 0.63938 | 0.63382 | 0.62838 | 0.62403 | 0.62026 | 0.61275 | 0.58748 | 0.57652 | 0.56573
| CALVINE | CT |  |  |  | 0.84759 | 0.84736 | 0.84675 | 0.84606 | 0.84538 | 0.8447 | 0.84405 | 0.84341 | 0.84271 | 0.84202 | 0.84065 | 0.83582 | 0.831 | 0.82625 | 0.72655 | 0.72538 | 0.72234 | 0.71886 | 0.71545 | 0.71208 | 0.7088 | 0.70558 | 0.7021 | 0.69865 | 0.69176 | 0.66911 | 0.65092 | 0.63303 | 0.66324 | 0.66184 | 0.65823 | 0.6541 | 0.65003 | 0.64603 | 0.64212 | 0.6383 | 0.63415 | 0.63005 | 0.62362 | 0.60508 | 0.58762 | 0.58011
| CALVINE | LW |  |  |  | 0.84759 | 0.84731 | 0.8465 | 0.84551 | 0.84454 | 0.84359 | 0.84265 | 0.84174 | 0.84075 | 0.83977 | 0.83782 | 0.83091 | 0.82399 | 0.81718 | 0.72655 | 0.72514 | 0.7211 | 0.71614 | 0.71128 | 0.70649 | 0.70182 | 0.69724 | 0.69229 | 0.68738 | 0.6776 | 0.65059 | 0.62449 | 0.5988 | 0.66324 | 0.66156 | 0.65675 | 0.65086 | 0.64507 | 0.63938 | 0.63382 | 0.62838 | 0.62403 | 0.62026 | 0.61275 | 0.58748 | 0.57652 | 0.56573
| CALVINE | ST |  |  |  | 0.84767 | 0.84757 | 0.84732 | 0.84694 | 0.84649 | 0.84584 | 0.8452 | 0.84458 | 0.84391 | 0.84325 | 0.84196 | 0.83883 | 0.83578 | 0.83276 | 0.72696 | 0.72644 | 0.72521 | 0.7233 | 0.72102 | 0.71775 | 0.71456 | 0.71146 | 0.7081 | 0.7048 | 0.69833 | 0.68266 | 0.66897 | 0.65758 | 0.66373 | 0.6631 | 0.66164 | 0.65937 | 0.65666 | 0.65277 | 0.64898 | 0.64529 | 0.64129 | 0.63737 | 0.62967 | 0.61663 | 0.60493 | 0.59332
| CALVINE | FS |  |  |  | 0.84772 | 0.84771 | 0.84769 | 0.84758 | 0.84745 | 0.84724 | 0.84703 | 0.84675 | 0.84649 | 0.84623 | 0.84571 | 0.84449 | 0.84336 | 0.84232 | 0.72721 | 0.72713 | 0.72704 | 0.7265 | 0.72585 | 0.72477 | 0.72371 | 0.72235 | 0.72102 | 0.71971 | 0.71714 | 0.71102 | 0.70537 | 0.70016 | 0.66402 | 0.66393 | 0.66382 | 0.66318 | 0.66241 | 0.66113 | 0.65986 | 0.65825 | 0.65666 | 0.6551 | 0.65204 | 0.64477 | 0.63804 | 0.63185
CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 19.2521 | 19.1156 | 18.9405 | 18.7644 | 18.5946 | 14.5392 | 14.3927 | 14.252 | 14.165 | 14.1217 | 14.0368 | 13.7425 | 13.267 | 12.6181 | 16.8469 | 16.7422 | 16.601 | 16.4566 | 16.3185 | 16.1861 | 16.058 | 15.948 | 15.9061 | 15.8853 | 15.8444 | 13.3063 | 12.6438 | 12.0053 | 16.3254 | 16.178 | 15.9825 | 15.7837 | 15.593 | 13.6902 | 13.5562 | 13.4274 | 13.3459 | 13.3035 | 13.086 | 12.3339 | 11.5915 | 10.8794
| CAMPBELTOWN | CT |  |  |  | 19.2521 | 19.1156 | 18.9405 | 18.7644 | 18.5946 | 14.5392 | 14.3927 | 14.252 | 14.165 | 14.1217 | 14.0368 | 13.7425 | 13.267 | 12.6181 | 16.8469 | 16.7422 | 16.601 | 16.4566 | 16.3185 | 16.1861 | 16.058 | 15.948 | 15.9061 | 15.8853 | 15.8444 | 13.3063 | 12.6438 | 12.0053 | 16.3254 | 16.178 | 15.9825 | 15.7837 | 15.593 | 13.6902 | 13.5562 | 13.4274 | 13.3459 | 13.3035 | 13.086 | 12.3339 | 11.5915 | 10.8794
| CAMPBELTOWN | LW |  |  |  | 19.4483 | 19.4256 | 19.3993 | 19.3698 | 19.3372 | 19.3019 | 19.2642 | 19.2244 | 19.1752 | 19.1247 | 19.0207 | 18.6578 | 14.0908 | 13.1996 | 16.9847 | 16.9596 | 16.9224 | 16.8787 | 16.8354 | 16.7922 | 16.7477 | 16.7021 | 16.6486 | 16.5941 | 16.4839 | 16.188 | 13.1641 | 12.2976 | 16.5257 | 16.4941 | 16.45 | 16.3987 | 16.3466 | 16.3014 | 16.2631 | 16.2227 | 16.1728 | 16.1214 | 16.0159 | 13.337 | 12.3807 | 11.4067
| CAMPBELTOWN | ST |  |  |  | 19.4784 | 19.4706 | 19.4601 | 19.4499 | 19.44 | 19.4279 | 19.4162 | 19.4048 | 19.3933 | 19.3765 | 19.3441 | 19.2121 | 19.1044 | 19.0024 | 17.0092 | 16.9994 | 16.9856 | 16.969 | 16.9523 | 16.9306 | 16.9092 | 16.8882 | 16.8661 | 16.8409 | 16.7928 | 16.6395 | 16.5042 | 16.3729 | 16.5595 | 16.5476 | 16.5309 | 16.5118 | 16.4927 | 16.4682 | 16.4441 | 16.4205 | 16.3958 | 16.377 | 16.3442 | 16.2102 | 16.1009 | 15.9973
| CAMPBELTOWN | FS |  |  |  | 19.4706 | 19.4601 | 19.4496 | 19.4342 | 19.4189 | 19.4038 | 19.3889 | 19.3743 | 19.3598 | 19.3456 | 19.3177 | 19.2347 | 19.1457 | 19.059 | 17.0063 | 16.9972 | 16.9884 | 16.9743 | 16.9606 | 16.9455 | 16.9307 | 16.9148 | 16.8992 | 16.8838 | 16.8539 | 16.7719 | 16.6875 | 16.6063 | 16.5539 | 16.5416 | 16.5296 | 16.5108 | 16.4925 | 16.473 | 16.4537 | 16.4336 | 16.4138 | 16.3943 | 16.3563 | 16.2498 | 16.1428 | 16.0548
COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 11.9225 | 14.369 | 14.3484 | 14.2895 | 14.217 | 14.1453 | 14.074 | 14.0044 | 13.9358 | 13.8616 | 13.7948 | 13.7226 | 13.4216 | 11.6174 | 11.0314 | 14.5283 | 14.523 | 14.5077 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 11.6567 | 11.0718
| CAPUTH | CT |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 15.1495 | 14.3712 | 14.3574 | 14.3219 | 14.281 | 14.2405 | 14.1998 | 14.1602 | 14.1212 | 14.0789 | 14.0371 | 13.9523 | 13.6485 | 13.4684 | 11.9152 | 14.5288 | 14.5253 | 14.5161 | 14.5055 | 14.495 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 14.4062 | 11.954
| CAPUTH | LW |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 11.9225 | 14.369 | 14.3484 | 14.2895 | 14.217 | 14.1453 | 14.074 | 14.0044 | 13.9358 | 13.8616 | 13.7948 | 13.7226 | 13.4216 | 11.6174 | 11.0314 | 14.5283 | 14.523 | 14.5077 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 11.6567 | 11.0718
| CAPUTH | ST |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1916 | 15.1916 | 15.1916 | 14.4545 | 14.3673 | 14.3493 | 14.3213 | 14.2876 | 14.2397 | 14.1931 | 14.1474 | 14.0979 | 14.0494 | 13.953 | 13.7379 | 13.6268 | 13.5179 | 14.5504 | 14.5279 | 14.5232 | 14.5159 | 14.5072 | 14.4948 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4494 | 14.4494 | 14.4494
| CAPUTH | FS |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 14.4581 | 14.4569 | 14.3759 | 14.3679 | 14.3583 | 14.3424 | 14.3269 | 14.307 | 14.2874 | 14.2682 | 14.2303 | 14.1393 | 14.0552 | 13.9774 | 14.5514 | 14.5511 | 14.5301 | 14.528 | 14.5255 | 14.5214 | 14.5174 | 14.5122 | 14.5072 | 14.5022 | 14.4926 | 14.4926 | 14.4926 | 14.4926
ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 13.8338 | 12.9303 | 18.6479 | 18.5904 | 18.441 | 18.284 | 18.2305 | 18.218 | 18.2058 | 18.1939 | 18.181 | 18.1681 | 18.1428 | 13.266 | 12.1654 | 11.0729 | 17.7946 | 17.7612 | 17.6742 | 17.595 | 17.5318 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.5258 | 12.5073 | 11.4904 | 10.481
| CARNOUSTIE | CT |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 14.1757 | 18.6479 | 18.5971 | 18.4761 | 18.3382 | 18.2628 | 18.2311 | 18.2217 | 18.2122 | 18.2019 | 18.1919 | 18.1728 | 18.1326 | 13.3715 | 12.5789 | 17.7946 | 17.7651 | 17.6947 | 17.6241 | 17.5764 | 17.5349 | 17.4928 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.341 | 12.6048 | 11.8725
| CARNOUSTIE | LW |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 13.8338 | 12.9303 | 18.6485 | 18.5904 | 18.441 | 18.284 | 18.2305 | 18.218 | 18.2058 | 18.1939 | 18.181 | 18.1681 | 18.1428 | 13.266 | 12.1654 | 11.0729 | 17.7949 | 17.7612 | 17.6742 | 17.595 | 17.5318 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.5258 | 12.5073 | 11.4904 | 10.481
| CARNOUSTIE | ST |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 18.6647 | 18.639 | 18.5848 | 18.5069 | 18.4219 | 18.3603 | 18.3003 | 18.2733 | 18.2441 | 18.2314 | 18.2213 | 18.1966 | 18.1724 | 18.148 | 17.8044 | 17.7894 | 17.7579 | 17.7126 | 17.6632 | 17.6324 | 17.6091 | 17.5856 | 17.5602 | 17.5359 | 17.4909 | 17.4874 | 17.4874 | 13.6226
| CARNOUSTIE | FS |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 18.6761 | 18.6685 | 18.6574 | 18.6326 | 18.6078 | 18.5865 | 18.5653 | 18.5387 | 18.5128 | 18.4875 | 18.4384 | 18.3257 | 18.2676 | 18.233 | 17.811 | 17.8066 | 17.8001 | 17.7857 | 17.7713 | 17.7589 | 17.7466 | 17.7311 | 17.716 | 17.7013 | 17.6728 | 17.6195 | 17.5806 | 17.5432
KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.054454 | 0.053729 | 0.051759 | 0.05129 | 0.050921 | 0.050561 | 0.050255 | 0.050255 | 0.050255 | 0.050255 | 0.050255 | -0.01597 | -0.035894 | -0.055592 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | -0.0088181 | -0.028748 | -0.048453
| CASHLIE | CT |  |  |  | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.054455 | 0.053851 | 0.052284 | 0.051497 | 0.051239 | 0.050987 | 0.05074 | 0.050498 | 0.050255 | 0.050255 | 0.050255 | 0.050255 | -0.011998 | -0.025798 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | -0.0048453 | -0.01865
| CASHLIE | LW |  |  |  | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.054454 | 0.053729 | 0.051759 | 0.05129 | 0.050921 | 0.050561 | 0.050255 | 0.050255 | 0.050255 | 0.050255 | 0.050255 | -0.01597 | -0.035894 | -0.055592 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | -0.0088181 | -0.028748 | -0.048453
| CASHLIE | ST |  |  |  | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.054667 | 0.054397 | 0.053767 | 0.052786 | 0.051753 | 0.051494 | 0.05133 | 0.05117 | 0.050998 | 0.050829 | 0.050498 | 0.050255 | 0.050255 | 0.050255 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292
| CASHLIE | FS |  |  |  | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.10678 | 0.054792 | 0.054757 | 0.054712 | 0.054436 | 0.054108 | 0.053728 | 0.053351 | 0.052867 | 0.052392 | 0.051979 | 0.051595 | 0.051257 | 0.050965 | 0.050698 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292 | 0.061292
KILLIN | CHAORACH | MINIMUM HEADROOM | NN 4540027553 | YES | YES | 0.94986 | 0.94985 | 0.94981 | 0.94977 | 0.94972 | 0.94968 | 0.94964 | 0.9496 | 0.94955 | 0.94951 | 0.94942 | 0.94921 | 0.949 | 0.94879 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.0429 | 1.0428 | 1.0423 | 1.0417 | 1.0412 | 1.0406 | 1.0401 | 1.0396 | 1.039 | 1.0384 | 1.0373 | 1.0346 | 1.0319 | 1.0292
| CHAORACH | CT |  |  |  | 0.94986 | 0.94985 | 0.94982 | 0.94979 | 0.94976 | 0.94973 | 0.9497 | 0.94967 | 0.94964 | 0.94961 | 0.94955 | 0.9494 | 0.94925 | 0.94911 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.0429 | 1.0428 | 1.0425 | 1.0421 | 1.0417 | 1.0413 | 1.0409 | 1.0405 | 1.0401 | 1.0397 | 1.039 | 1.0371 | 1.0352 | 1.0333
| CHAORACH | LW |  |  |  | 0.94986 | 0.94985 | 0.94981 | 0.94977 | 0.94972 | 0.94968 | 0.94964 | 0.9496 | 0.94955 | 0.94951 | 0.94942 | 0.94921 | 0.949 | 0.94879 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.0429 | 1.0428 | 1.0423 | 1.0417 | 1.0412 | 1.0406 | 1.0401 | 1.0396 | 1.039 | 1.0384 | 1.0373 | 1.0346 | 1.0319 | 1.0292
| CHAORACH | ST |  |  |  | 0.94987 | 0.94986 | 0.94985 | 0.94983 | 0.94981 | 0.94979 | 0.94977 | 0.94975 | 0.94973 | 0.94971 | 0.94967 | 0.94958 | 0.94949 | 0.9494 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.043 | 1.0429 | 1.0428 | 1.0426 | 1.0423 | 1.0421 | 1.0418 | 1.0416 | 1.0413 | 1.041 | 1.0405 | 1.0393 | 1.0382 | 1.037
| CHAORACH | FS |  |  |  | 0.94987 | 0.94987 | 0.94987 | 0.94986 | 0.94986 | 0.94985 | 0.94984 | 0.94984 | 0.94983 | 0.94982 | 0.9498 | 0.94977 | 0.94973 | 0.9497 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.043 | 1.043 | 1.043 | 1.0429 | 1.0429 | 1.0428 | 1.0427 | 1.0426 | 1.0425 | 1.0424 | 1.0422 | 1.0417 | 1.0413 | 1.0408
ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.457 | 15.4539 | 15.4448 | 15.4336 | 15.4227 | 15.4119 | 15.4014 | 15.3911 | 15.38 | 15.3689 | 15.347 | 15.2751 | 15.2035 | 15.1827 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
| CHARLES AVENUE | CT |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.457 | 15.4539 | 15.4461 | 15.4371 | 15.4284 | 15.4198 | 15.4114 | 15.4031 | 15.3941 | 15.3852 | 15.3677 | 15.3139 | 15.2601 | 15.2064 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
| CHARLES AVENUE | LW |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4572 | 15.454 | 15.4448 | 15.4336 | 15.4227 | 15.4119 | 15.4014 | 15.3911 | 15.38 | 15.3689 | 15.347 | 15.2751 | 15.2035 | 15.1827 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
| CHARLES AVENUE | ST |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4582 | 15.4571 | 15.4544 | 15.4504 | 15.4456 | 15.4394 | 15.4333 | 15.4274 | 15.421 | 15.4147 | 15.4025 | 15.3719 | 15.3421 | 15.312 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
| CHARLES AVENUE | FS |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4587 | 15.4585 | 15.4583 | 15.4571 | 15.4558 | 15.4538 | 15.4518 | 15.4492 | 15.4467 | 15.4443 | 15.4395 | 15.428 | 15.4172 | 15.4068 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | NO | 17.5071 | 17.5045 | 17.4973 | 17.4885 | 17.48 | 17.4712 | 17.4619 | 17.4528 | 17.4425 | 17.4313 | 17.4121 | 17.3512 | 17.3512 | 17.3512 | 16.8106 | 16.8066 | 16.7954 | 16.7818 | 16.7688 | 16.755 | 16.7407 | 16.7267 | 16.7107 | 16.6934 | 16.6584 | 16.5112 | 16.505 | 16.505 | 16.783 | 16.7795 | 16.7695 | 16.7573 | 16.7457 | 16.7334 | 16.7206 | 16.7081 | 16.6938 | 16.6784 | 16.6471 | 16.6264 | 16.6104 | 16.5951
| CHARLESTON | CT |  |  |  | 17.5071 | 17.505 | 17.4995 | 17.4933 | 17.4872 | 17.4811 | 17.4754 | 17.4699 | 17.4635 | 17.4556 | 17.4389 | 17.3761 | 17.3512 | 17.3512 | 16.8106 | 16.8073 | 16.7989 | 16.7893 | 16.7799 | 16.7704 | 16.7616 | 16.753 | 16.7432 | 16.7309 | 16.7052 | 16.5664 | 16.5071 | 16.505 | 16.783 | 16.7801 | 16.7725 | 16.764 | 16.7556 | 16.7472 | 16.7393 | 16.7316 | 16.7229 | 16.7119 | 16.689 | 16.6347 | 16.6223 | 16.6106
| CHARLESTON | LW |  |  |  | 17.5071 | 17.5045 | 17.4973 | 17.4885 | 17.48 | 17.4712 | 17.4619 | 17.4528 | 17.4425 | 17.4313 | 17.4121 | 17.3512 | 17.3512 | 17.3512 | 16.8106 | 16.8066 | 16.7954 | 16.7818 | 16.7688 | 16.755 | 16.7407 | 16.7267 | 16.7107 | 16.6934 | 16.6584 | 16.5112 | 16.505 | 16.505 | 16.783 | 16.7795 | 16.7695 | 16.7573 | 16.7457 | 16.7334 | 16.7206 | 16.7081 | 16.6938 | 16.6784 | 16.6471 | 16.6264 | 16.6104 | 16.5951
| CHARLESTON | ST |  |  |  | 17.5089 | 17.5079 | 17.5057 | 17.5023 | 17.4982 | 17.4883 | 17.4787 | 17.4694 | 17.4591 | 17.4479 | 17.4251 | 17.3887 | 17.3587 | 17.3512 | 16.8134 | 16.8119 | 16.8084 | 16.8031 | 16.7969 | 16.7815 | 16.7667 | 16.7523 | 16.7364 | 16.719 | 16.6838 | 16.5986 | 16.522 | 16.5083 | 16.7855 | 16.7842 | 16.7811 | 16.7763 | 16.7707 | 16.757 | 16.7439 | 16.731 | 16.7168 | 16.7013 | 16.6698 | 16.6377 | 16.6305 | 16.6235
| CHARLESTON | FS |  |  |  | 17.5103 | 17.51 | 17.5098 | 17.5088 | 17.5077 | 17.5046 | 17.5015 | 17.4975 | 17.4934 | 17.4892 | 17.4808 | 17.46 | 17.4419 | 17.4258 | 16.8156 | 16.8152 | 16.8148 | 16.8133 | 16.8116 | 16.8067 | 16.8019 | 16.7958 | 16.7894 | 16.7828 | 16.7699 | 16.7377 | 16.7098 | 16.6848 | 16.7875 | 16.7871 | 16.7868 | 16.7854 | 16.7839 | 16.7796 | 16.7753 | 16.7698 | 16.7641 | 16.7582 | 16.7467 | 16.718 | 16.693 | 16.6707
ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 4.6625 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1357 | 3.1061 | 3.0473 | 2.9065 | 2.7641 | 2.6246 | 4.5327 | 4.1933 | 4.1698 | 3.2793 | 3.2455 | 3.2124 | 3.1798 | 3.1478 | 3.1132 | 3.0788 | 3.0106 | 2.8472 | 2.6819 | 2.5199 | 4.8273 | 3.2335 | 3.2128 | 3.1785 | 3.1448 | 3.1117 | 3.0792 | 3.0473 | 3.0128 | 2.9784 | 2.9104 | 2.7473 | 2.5823 | 2.4207
| CLACHAN | CT |  |  |  | 4.6625 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.139 | 3.0177 | 2.8951 | 2.7745 | 4.5328 | 4.1949 | 4.1778 | 3.2998 | 3.2768 | 3.2543 | 3.2321 | 3.2104 | 3.1868 | 3.1634 | 3.117 | 2.9761 | 2.8339 | 2.6939 | 4.8273 | 3.2336 | 3.2223 | 3.199 | 3.1761 | 3.1536 | 3.1314 | 3.1097 | 3.0862 | 3.0629 | 3.0166 | 2.876 | 2.734 | 2.5943
| CLACHAN | LW |  |  |  | 4.6625 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1357 | 3.1061 | 3.0473 | 2.9065 | 2.7641 | 2.6246 | 4.5327 | 4.1933 | 4.1698 | 3.2793 | 3.2455 | 3.2124 | 3.1798 | 3.1478 | 3.1132 | 3.0788 | 3.0106 | 2.8472 | 2.6819 | 2.5199 | 4.8273 | 3.2335 | 3.2128 | 3.1785 | 3.1448 | 3.1117 | 3.0792 | 3.0473 | 3.0128 | 2.9784 | 2.9104 | 2.7473 | 2.5823 | 2.4207
| CLACHAN | ST |  |  |  | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.5354 | 4.535 | 4.5339 | 4.5323 | 4.5304 | 4.5213 | 4.5125 | 4.5038 | 4.4945 | 4.4852 | 4.4673 | 4.4238 | 4.4007 | 4.3894 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273
| CLACHAN | FS |  |  |  | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.5356 | 4.5355 | 4.5355 | 4.535 | 4.5345 | 4.5315 | 4.5286 | 4.5248 | 4.5211 | 4.5174 | 4.5103 | 4.4935 | 4.4778 | 4.463 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273
CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.069894 | 0.069586 | 0.0687 | 0.067972 | 0.067414 | 0.066868 | 0.066334 | 0.065812 | 0.065248 | 0.064999 | 0.064999 | 0.064999 | 0.064999 | 0.064999 | 0.080983 | 0.080841 | 0.080679 | 0.08048 | 0.080286 | 0.080096 | 0.07991 | 0.079729 | 0.079533 | 0.079338 | 0.079052 | 0.079052 | 0.079052 | 0.079052
| CLAONAIG | CT |  |  |  | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.069894 | 0.069638 | 0.068973 | 0.068287 | 0.067896 | 0.067514 | 0.06714 | 0.066775 | 0.06638 | 0.065988 | 0.065212 | 0.064999 | 0.064999 | 0.064999 | 0.080983 | 0.080859 | 0.080729 | 0.08059 | 0.080454 | 0.080321 | 0.080191 | 0.080064 | 0.079927 | 0.07979 | 0.07952 | 0.079052 | 0.079052 | 0.079052
| CLAONAIG | LW |  |  |  | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.069894 | 0.069586 | 0.0687 | 0.067972 | 0.067414 | 0.066868 | 0.066334 | 0.065812 | 0.065248 | 0.064999 | 0.064999 | 0.064999 | 0.064999 | 0.064999 | 0.080983 | 0.080841 | 0.080679 | 0.08048 | 0.080286 | 0.080096 | 0.07991 | 0.079729 | 0.079533 | 0.079338 | 0.079052 | 0.079052 | 0.079052 | 0.079052
| CLAONAIG | ST |  |  |  | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.069984 | 0.06987 | 0.069603 | 0.069187 | 0.068692 | 0.068235 | 0.06794 | 0.067652 | 0.067341 | 0.067035 | 0.066439 | 0.06501 | 0.064999 | 0.064999 | 0.081027 | 0.080972 | 0.080844 | 0.080768 | 0.080677 | 0.080572 | 0.080469 | 0.080369 | 0.080261 | 0.080154 | 0.079947 | 0.07945 | 0.079052 | 0.079052
| CLAONAIG | FS |  |  |  | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.12483 | 0.070037 | 0.070022 | 0.070003 | 0.069887 | 0.069748 | 0.069558 | 0.06937 | 0.069129 | 0.068891 | 0.068658 | 0.068282 | 0.067717 | 0.067196 | 0.066715 | 0.081053 | 0.081046 | 0.081037 | 0.08098 | 0.080913 | 0.080836 | 0.080801 | 0.080757 | 0.080714 | 0.080671 | 0.080588 | 0.080392 | 0.08021 | 0.080043
CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 31.3312 | 31.2584 | 31.0888 | 30.9166 | 30.7477 | 30.5819 | 30.4189 | 30.2588 | 30.1759 | 30.1446 | 30.0819 | 30.0162 | 23.4999 | 21.6873 | 31.5658 | 31.4722 | 31.2101 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 22.2249
| CLAYHILLS | CT |  |  |  | 33.5298 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 31.3488 | 31.3174 | 31.2405 | 31.1565 | 31.097 | 31.0384 | 30.9808 | 30.9244 | 30.8634 | 30.8029 | 30.683 | 30.3081 | 30.1472 | 30.0799 | 31.5886 | 31.5481 | 31.4491 | 31.3362 | 31.2253 | 31.1162 | 31.0139 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857
| CLAYHILLS | LW |  |  |  | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 31.3312 | 31.2584 | 31.0888 | 30.9166 | 30.7477 | 30.5819 | 30.4189 | 30.2588 | 30.1759 | 30.1446 | 30.0819 | 30.0162 | 23.4999 | 21.6873 | 31.5658 | 31.4722 | 31.2101 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 22.2249
| CLAYHILLS | ST |  |  |  | 33.527 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 31.3465 | 31.3066 | 31.2159 | 31.1027 | 30.9862 | 30.8872 | 30.7903 | 30.6955 | 30.5932 | 30.4927 | 30.2965 | 30.1244 | 30.0354 | 30.0162 | 31.5856 | 31.5343 | 31.4175 | 31.236 | 31.0231 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857 | 30.9857
| CLAYHILLS | FS |  |  |  | 33.5508 | 33.5448 | 33.5382 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 33.5121 | 31.3665 | 31.3615 | 31.3559 | 31.3242 | 31.2867 | 31.244 | 31.2017 | 31.1528 | 31.116 | 31.0799 | 31.0099 | 30.8437 | 30.6844 | 30.5318 | 31.6112 | 31.6048 | 31.5977 | 31.5569 | 31.5086 | 31.4536 | 31.3992 | 31.3294 | 31.2608 | 31.1936 | 31.064 | 30.9857 | 30.9857 | 30.9857
DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | NO | 0.45981 | 0.45971 | 0.45943 | 0.45908 | 0.45874 | 0.45841 | 0.45808 | 0.45777 | 0.45731 | 0.45677 | 0.45571 | 0.45546 | 0.45546 | 0.45546 | 0.43521 | 0.4344 | 0.4321 | 0.42953 | 0.42785 | 0.4262 | 0.42458 | 0.423 | 0.42072 | 0.41803 | 0.4128 | 0.37927 | 0.37098 | -0.054741 | 0.56461 | 0.56403 | 0.56236 | 0.56032 | 0.55832 | 0.55637 | 0.55446 | 0.55259 | 0.5499 | 0.54672 | 0.54053 | 0.51178 | 0.49719 | 0.49439
| COLDBACKIE | CT |  |  |  | 0.45981 | 0.45973 | 0.45952 | 0.45927 | 0.45903 | 0.4588 | 0.45857 | 0.45835 | 0.45811 | 0.45787 | 0.4574 | 0.45546 | 0.45546 | 0.45546 | 0.43521 | 0.43453 | 0.4328 | 0.43083 | 0.4293 | 0.42814 | 0.42701 | 0.4259 | 0.4247 | 0.42351 | 0.42116 | 0.39402 | 0.37098 | 0.37098 | 0.56461 | 0.56412 | 0.56287 | 0.56144 | 0.56004 | 0.55868 | 0.55733 | 0.55602 | 0.5546 | 0.55319 | 0.55041 | 0.52125 | 0.50358 | 0.4966
| COLDBACKIE | LW |  |  |  | 0.45981 | 0.45971 | 0.45943 | 0.45908 | 0.45874 | 0.45841 | 0.45808 | 0.45777 | 0.45742 | 0.45708 | 0.45641 | 0.45546 | 0.45546 | 0.45546 | 0.43521 | 0.4344 | 0.4321 | 0.42953 | 0.42785 | 0.4262 | 0.42458 | 0.423 | 0.42129 | 0.41959 | 0.41625 | 0.37927 | 0.37098 | -0.054741 | 0.56461 | 0.56403 | 0.56236 | 0.56032 | 0.55832 | 0.55637 | 0.55446 | 0.55259 | 0.55057 | 0.54856 | 0.5446 | 0.51178 | 0.49719 | 0.49439
| COLDBACKIE | ST |  |  |  | 0.45984 | 0.4598 | 0.45972 | 0.45958 | 0.45943 | 0.45889 | 0.45837 | 0.45786 | 0.45731 | 0.45677 | 0.45571 | 0.45546 | 0.45546 | 0.45546 | 0.43544 | 0.43514 | 0.43444 | 0.43336 | 0.43207 | 0.42859 | 0.426 | 0.42346 | 0.42072 | 0.41803 | 0.4128 | 0.4001 | 0.38747 | 0.3749 | 0.56478 | 0.56456 | 0.56406 | 0.56327 | 0.56234 | 0.55921 | 0.55614 | 0.55314 | 0.5499 | 0.54672 | 0.54053 | 0.52551 | 0.51704 | 0.50897
| COLDBACKIE | FS |  |  |  | 0.45986 | 0.45985 | 0.45985 | 0.45981 | 0.45976 | 0.45954 | 0.45933 | 0.45905 | 0.45878 | 0.45851 | 0.45799 | 0.45676 | 0.4556 | 0.45546 | 0.43558 | 0.43554 | 0.43549 | 0.43518 | 0.43482 | 0.43304 | 0.43129 | 0.42938 | 0.42802 | 0.42669 | 0.4241 | 0.41799 | 0.41225 | 0.40687 | 0.56488 | 0.56485 | 0.56482 | 0.56459 | 0.56433 | 0.56304 | 0.56177 | 0.56014 | 0.55853 | 0.55696 | 0.55389 | 0.54666 | 0.53988 | 0.53352
DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.053355 | 0.053154 | 0.052572 | 0.052009 | 0.051643 | 0.051285 | 0.050934 | 0.050592 | 0.050222 | 0.049854 | 0.049604 | 0.049604 | 0.049604 | 0.049604 | 0.06181 | 0.061712 | 0.061596 | 0.061466 | 0.061338 | 0.061214 | 0.061092 | 0.060973 | 0.060844 | 0.060716 | 0.060463 | 0.060328 | 0.060328 | 0.060328
| COLINTRAIVE | CT |  |  |  | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.053356 | 0.053187 | 0.052751 | 0.052254 | 0.051959 | 0.051709 | 0.051464 | 0.051224 | 0.050965 | 0.050707 | 0.050198 | 0.049604 | 0.049604 | 0.049604 | 0.06181 | 0.061728 | 0.061629 | 0.061538 | 0.061448 | 0.061361 | 0.061276 | 0.061193 | 0.061102 | 0.061013 | 0.060836 | 0.060407 | 0.060328 | 0.060328
| COLINTRAIVE | LW |  |  |  | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.053355 | 0.053154 | 0.052572 | 0.052009 | 0.051643 | 0.051285 | 0.050934 | 0.050592 | 0.050222 | 0.049854 | 0.049604 | 0.049604 | 0.049604 | 0.049604 | 0.06181 | 0.061712 | 0.061596 | 0.061466 | 0.061338 | 0.061214 | 0.061092 | 0.060973 | 0.060844 | 0.060716 | 0.060463 | 0.060328 | 0.060328 | 0.060328
| COLINTRAIVE | ST |  |  |  | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.053415 | 0.05334 | 0.053164 | 0.052892 | 0.052567 | 0.05225 | 0.052051 | 0.051893 | 0.051722 | 0.051553 | 0.051226 | 0.050441 | 0.049675 | 0.049604 | 0.061839 | 0.061802 | 0.061717 | 0.061654 | 0.061595 | 0.061537 | 0.06148 | 0.061425 | 0.061366 | 0.061307 | 0.061193 | 0.06092 | 0.060654 | 0.060387
| COLINTRAIVE | FS |  |  |  | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.095261 | 0.053449 | 0.05344 | 0.053427 | 0.053351 | 0.05326 | 0.053154 | 0.05305 | 0.052916 | 0.052784 | 0.052654 | 0.052402 | 0.051981 | 0.051691 | 0.051427 | 0.061856 | 0.061851 | 0.061845 | 0.061808 | 0.061764 | 0.061712 | 0.061683 | 0.061659 | 0.061635 | 0.061611 | 0.061565 | 0.061456 | 0.061355 | 0.061263
STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 4.6881 | 4.684 | 4.6725 | 4.6582 | 4.6443 | 4.6306 | 4.6225 | 3.2003 | 3.0511 | 2.9027 | 2.6087 | 1.4659 | 1.1158 | 0.77161 | 4.7248 | 4.7119 | 4.675 | 3.2733 | 3.1024 | 2.9347 | 2.7698 | 2.6077 | 2.4324 | 2.258 | 1.9125 | 0.91859 | 0.5072 | 0.10279 | 4.348 | 4.3369 | 4.3048 | 4.2653 | 3.2818 | 3.1256 | 2.9721 | 2.8214 | 2.6581 | 2.4958 | 2.1593 | 0.93787 | 0.53557 | 0.14009
| COLL | CT |  |  |  | 4.6882 | 4.685 | 4.6767 | 4.6672 | 4.6579 | 4.6487 | 4.6397 | 4.6309 | 4.6225 | 3.2834 | 3.0873 | 2.04 | 1.7865 | 1.5373 | 4.7251 | 4.7149 | 4.6885 | 4.6582 | 3.2688 | 3.1569 | 3.0468 | 2.9387 | 2.8217 | 2.7054 | 2.4749 | 1.5933 | 1.2954 | 1.0026 | 4.3483 | 4.3395 | 4.3165 | 4.2902 | 4.2643 | 4.24 | 3.23 | 3.1294 | 3.0205 | 2.9122 | 2.6977 | 1.596 | 1.3063 | 1.02
| COLL | LW |  |  |  | 4.6881 | 4.684 | 4.6725 | 4.6582 | 4.6443 | 4.6306 | 4.6225 | 3.2003 | 3.0511 | 2.9027 | 2.6087 | 1.4659 | 1.1158 | 0.77161 | 4.7248 | 4.7119 | 4.675 | 3.2733 | 3.1024 | 2.9347 | 2.7698 | 2.6077 | 2.4324 | 2.258 | 1.9125 | 0.91859 | 0.5072 | 0.10279 | 4.348 | 4.3369 | 4.3048 | 4.2653 | 3.2818 | 3.1256 | 2.9721 | 2.8214 | 2.6581 | 2.4958 | 2.1593 | 0.93787 | 0.53557 | 0.14009
| COLL | ST |  |  |  | 4.6893 | 4.6878 | 4.6845 | 4.6792 | 4.673 | 4.6702 | 4.6675 | 4.6649 | 4.662 | 4.6592 | 4.6538 | 3.1836 | 3.0465 | 2.9101 | 4.7286 | 4.7241 | 4.7134 | 4.6966 | 4.6766 | 4.6679 | 4.6593 | 4.6508 | 4.6418 | 3.2853 | 3.2185 | 2.7626 | 2.6015 | 2.4412 | 4.3514 | 4.3474 | 4.3381 | 4.3236 | 4.3062 | 4.2985 | 4.2911 | 4.2837 | 4.2758 | 4.2681 | 4.2529 | 2.8249 | 2.675 | 2.5258
| COLL | FS |  |  |  | 4.6899 | 4.6897 | 4.6895 | 4.688 | 4.6862 | 4.6852 | 4.6843 | 4.683 | 4.6818 | 4.6806 | 4.6783 | 4.6728 | 4.6677 | 4.6629 | 4.7307 | 4.7301 | 4.7293 | 4.7245 | 4.7188 | 4.7157 | 4.7126 | 4.7087 | 4.7048 | 4.701 | 4.6936 | 4.6761 | 4.6598 | 4.6444 | 4.3532 | 4.3527 | 4.352 | 4.3478 | 4.3428 | 4.3401 | 4.3375 | 4.334 | 4.3307 | 4.3274 | 4.3209 | 4.3058 | 4.2915 | 4.2782
CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 32.9044 | 32.8908 | 32.852 | 32.8045 | 32.758 | 32.7176 | 32.7052 | 32.6931 | 32.68 | 32.667 | 32.6408 | 32.5675 | 32.4933 | 32.4199 | 31.8358 | 31.8196 | 31.7734 | 31.7168 | 31.6614 | 31.6072 | 31.5541 | 31.5022 | 31.4461 | 31.3904 | 31.2785 | 30.9645 | 30.6509 | 30.3425 | 29.0568 | 29.0495 | 29.0289 | 29.0037 | 28.9789 | 28.9547 | 28.9311 | 28.9079 | 28.8829 | 28.858 | 28.8081 | 28.668 | 28.526 | 28.4216
| COMMERCE STREET | CT |  |  |  | 32.9044 | 32.8932 | 32.8642 | 32.8311 | 32.7987 | 32.7669 | 32.7358 | 32.7156 | 32.7064 | 32.6973 | 32.6793 | 32.63 | 32.5802 | 32.5313 | 31.8358 | 31.8224 | 31.7879 | 31.7484 | 31.7098 | 31.672 | 31.635 | 31.5987 | 31.5595 | 31.5206 | 31.4435 | 31.2322 | 31.0187 | 30.8106 | 29.0568 | 29.0508 | 29.0354 | 29.0178 | 29.0006 | 28.9837 | 28.9671 | 28.951 | 28.9335 | 28.9161 | 28.8817 | 28.7874 | 28.6922 | 28.5986
| COMMERCE STREET | LW |  |  |  | 32.9044 | 32.8908 | 32.852 | 32.8045 | 32.758 | 32.7176 | 32.7052 | 32.6931 | 32.68 | 32.667 | 32.6408 | 32.5675 | 32.4933 | 32.4199 | 31.8358 | 31.8196 | 31.7734 | 31.7168 | 31.6614 | 31.6072 | 31.5541 | 31.5022 | 31.4461 | 31.3904 | 31.2785 | 30.9645 | 30.6509 | 30.3425 | 29.0568 | 29.0495 | 29.0289 | 29.0037 | 28.9789 | 28.9547 | 28.9311 | 28.9079 | 28.8829 | 28.858 | 28.8081 | 28.668 | 28.526 | 28.4216
| COMMERCE STREET | ST |  |  |  | 33.0406 | 32.9033 | 32.8916 | 32.8733 | 32.8516 | 32.825 | 32.7991 | 32.7737 | 32.7463 | 32.7195 | 32.7049 | 32.6682 | 32.6322 | 32.5966 | 31.998 | 31.8344 | 31.8205 | 31.7988 | 31.7729 | 31.7412 | 31.7103 | 31.68 | 31.6474 | 31.6153 | 31.5527 | 31.3956 | 31.2414 | 31.0889 | 29.1292 | 29.0562 | 29.0499 | 29.0402 | 29.0287 | 29.0146 | 29.0007 | 28.9873 | 28.9727 | 28.9584 | 28.9305 | 28.8603 | 28.7915 | 28.7235
| COMMERCE STREET | FS |  |  |  | 33.043 | 33.0422 | 32.9091 | 32.904 | 32.8979 | 32.8898 | 32.8818 | 32.8715 | 32.8614 | 32.8514 | 32.8321 | 32.7862 | 32.7425 | 32.7144 | 32.0008 | 32 | 31.8414 | 31.8353 | 31.828 | 31.8184 | 31.8088 | 31.7966 | 31.7845 | 31.7726 | 31.7497 | 31.695 | 31.6429 | 31.5937 | 29.1304 | 29.13 | 29.0593 | 29.0565 | 29.0533 | 29.049 | 29.0447 | 29.0393 | 29.0339 | 29.0286 | 29.0183 | 28.9939 | 28.9707 | 28.9488
ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | -0.00094984 | -0.0048268 | -0.0086646 | 0.006843 | 0.0067085 | 0.0063553 | 0.0061721 | 0.0061497 | 0.0061497 | 0.0061497 | -9.0569e-05 | -0.0010408 | -0.0019844 | -0.0038518 | -0.0083754 | -0.012927 | -0.017433 | 0.0077517 | 0.0076864 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | -0.00067682 | -0.0024962 | -0.0070212 | -0.011574 | -0.016082
| COMRIE | CT |  |  |  | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | -0.00016545 | -0.0028519 | 0.0068431 | 0.006731 | 0.0064457 | 0.0062197 | 0.0061607 | 0.0061497 | 0.0061497 | 0.0061497 | 0.0061497 | 0.0061497 | -0.0011018 | -0.0042682 | -0.0074545 | -0.010608 | 0.0077517 | 0.0076973 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | -0.0029127 | -0.0061 | -0.009255
| COMRIE | LW |  |  |  | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | -0.00094984 | -0.0048268 | -0.0086646 | 0.006843 | 0.0067085 | 0.0063553 | 0.0061721 | 0.0061497 | 0.0061497 | 0.0061497 | -9.0569e-05 | -0.0010408 | -0.0019844 | -0.0038518 | -0.0083754 | -0.012927 | -0.017433 | 0.0077517 | 0.0076864 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | -0.00067682 | -0.0024962 | -0.0070212 | -0.011574 | -0.016082
| COMRIE | ST |  |  |  | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.0068825 | 0.0068325 | 0.0067156 | 0.0065339 | 0.0063525 | 0.0062192 | 0.0061818 | 0.0061497 | 0.0061497 | 0.0061497 | 0.0061497 | -0.00047834 | -0.0024452 | -0.004415 | 0.0077708 | 0.0077466 | 0.0076898 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | -0.0011257 | -0.0030596
| COMRIE | FS |  |  |  | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.012593 | 0.0069057 | 0.0068993 | 0.0068911 | 0.00684 | 0.0067794 | 0.006709 | 0.0066394 | 0.0065497 | 0.0064618 | 0.0063965 | 0.0062696 | 0.0061656 | 0.0061497 | 0.0061497 | 0.0077821 | 0.007779 | 0.007775 | 0.0077502 | 0.0077208 | 0.0076866 | 0.0076528 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474 | 0.0076474
TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 3.8105 | 3.6373 | 3.4669 | 4.8474 | 4.8444 | 4.8372 | 4.8282 | 4.819 | 4.8096 | 4.7999 | 4.7912 | 4.7834 | 4.7757 | 4.7531 | 3.6404 | 3.45 | 3.2605 | 4.7479 | 4.7475 | 4.7464 | 4.7451 | 4.7437 | 4.7423 | 4.7409 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 3.6552 | 3.4582 | 3.2644
| CONNEL | CT |  |  |  | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 3.8622 | 3.7283 | 3.5965 | 4.8474 | 4.8444 | 4.8379 | 4.8303 | 4.8224 | 4.8143 | 4.8061 | 4.7984 | 4.7913 | 4.7841 | 4.7703 | 3.6972 | 3.55 | 3.4052 | 4.7479 | 4.7475 | 4.7465 | 4.7454 | 4.7442 | 4.743 | 4.7418 | 4.7406 | 4.7405 | 4.7405 | 4.7405 | 3.7139 | 3.5616 | 3.4118
| CONNEL | LW |  |  |  | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 3.8105 | 3.6373 | 3.4669 | 4.8476 | 4.8445 | 4.8372 | 4.8282 | 4.819 | 4.8096 | 4.7999 | 4.7912 | 4.7834 | 4.7757 | 4.7606 | 3.6404 | 3.45 | 3.2605 | 4.7479 | 4.7475 | 4.7464 | 4.7451 | 4.7437 | 4.7423 | 4.7409 | 4.7405 | 4.7405 | 4.7405 | 4.7405 | 3.6552 | 3.4582 | 3.2644
| CONNEL | ST |  |  |  | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.0234 | 5.0234 | 3.9483 | 4.8486 | 4.8472 | 4.8447 | 4.841 | 4.8366 | 4.8241 | 4.8118 | 4.7999 | 4.7879 | 4.776 | 4.7531 | 3.9007 | 3.8194 | 3.7386 | 4.7481 | 4.7479 | 4.7475 | 4.747 | 4.7463 | 4.7445 | 4.7426 | 4.7409 | 4.7405 | 4.7405 | 4.7405 | 3.9468 | 3.8628 | 3.7792
| CONNEL | FS |  |  |  | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 5.2145 | 4.8492 | 4.8487 | 4.8481 | 4.8469 | 4.8454 | 4.8412 | 4.837 | 4.8319 | 4.8272 | 4.8225 | 4.8135 | 4.7926 | 4.7733 | 4.7552 | 4.7482 | 4.7481 | 4.748 | 4.7478 | 4.7476 | 4.747 | 4.7464 | 4.7456 | 4.7449 | 4.7442 | 4.7429 | 4.7405 | 4.7405 | 4.7405
BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 5.953 | 5.2292 | 4.7389 | 4.2591 | 7.4422 | 7.4261 | 7.3817 | 7.3707 | 7.3634 | 5.7304 | 5.6046 | 5.4412 | 5.3103 | 5.1795 | 4.9351 | 4.2159 | 3.625 | 3.0467 | 7.6176 | 7.6079 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 5.6265 | 5.499 | 5.3716 | 5.1335 | 4.3372 | 3.7616 | 3.1984
| CONON BRIDGE | CT |  |  |  | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 5.953 | 5.2425 | 4.8825 | 4.5284 | 7.4422 | 7.4261 | 7.3817 | 7.3707 | 7.3634 | 5.7304 | 5.6046 | 5.4412 | 5.3103 | 5.1795 | 4.9351 | 4.2319 | 3.798 | 3.3713 | 7.6176 | 7.6079 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 5.6265 | 5.499 | 5.3716 | 5.1335 | 4.3528 | 3.9302 | 3.5146
| CONON BRIDGE | LW |  |  |  | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 6.0576 | 5.2292 | 4.7389 | 4.2591 | 7.4441 | 7.4293 | 7.3862 | 7.3718 | 7.3647 | 7.3593 | 5.6613 | 5.5155 | 5.4016 | 5.2883 | 5.0693 | 4.2159 | 3.625 | 3.0467 | 7.6187 | 7.6098 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 5.6989 | 5.5879 | 5.4775 | 5.2642 | 4.3372 | 3.7616 | 3.1984
| CONON BRIDGE | ST |  |  |  | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.2557 | 6.0037 | 5.8076 | 7.4491 | 7.4422 | 7.4238 | 7.4125 | 7.3953 | 7.3814 | 7.3739 | 7.3696 | 7.3665 | 7.3634 | 5.7417 | 5.349 | 5.0951 | 4.8435 | 7.6217 | 7.6176 | 7.6065 | 7.5998 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 5.4888 | 5.2415 | 4.9964
| CONON BRIDGE | FS |  |  |  | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 8.4204 | 7.4527 | 7.4496 | 7.4424 | 7.4384 | 7.4323 | 7.4271 | 7.4219 | 7.4134 | 7.4071 | 7.401 | 7.3891 | 7.3734 | 7.3688 | 7.3643 | 7.6238 | 7.622 | 7.6177 | 7.6153 | 7.6116 | 7.6085 | 7.6054 | 7.6003 | 7.5966 | 7.5942 | 7.5942 | 7.5942 | 7.5942 | 7.5942
GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.23531 | 0.23504 | 0.23425 | 0.23328 | 0.23234 | 0.23142 | 0.23051 | 0.22963 | 0.22868 | 0.22773 | 0.22586 | 0.21752 | 0.21234 | 0.21129 | 0.21018 | 0.21007 | 0.20976 | 0.20938 | 0.20901 | 0.20865 | 0.20829 | 0.20795 | 0.20757 | 0.2072 | 0.20646 | 0.20317 | 0.20064 | 0.20038
| CONON FALLS | CT |  |  |  | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.23531 | 0.23508 | 0.23449 | 0.23381 | 0.23315 | 0.23251 | 0.23187 | 0.23125 | 0.23058 | 0.22992 | 0.22861 | 0.22201 | 0.21624 | 0.2129 | 0.21018 | 0.21009 | 0.20986 | 0.20959 | 0.20933 | 0.20908 | 0.20883 | 0.20858 | 0.20832 | 0.20806 | 0.20754 | 0.20478 | 0.20277 | 0.20097
| CONON FALLS | LW |  |  |  | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.23531 | 0.23504 | 0.23425 | 0.23328 | 0.23234 | 0.23142 | 0.23051 | 0.22963 | 0.22868 | 0.22773 | 0.22586 | 0.21752 | 0.21234 | 0.21129 | 0.21018 | 0.21007 | 0.20976 | 0.20938 | 0.20901 | 0.20865 | 0.20829 | 0.20795 | 0.20757 | 0.2072 | 0.20646 | 0.20317 | 0.20064 | 0.20038
| CONON FALLS | ST |  |  |  | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.23539 | 0.23529 | 0.23505 | 0.23468 | 0.23424 | 0.23333 | 0.23245 | 0.23158 | 0.23065 | 0.22973 | 0.22795 | 0.22366 | 0.22019 | 0.21674 | 0.21021 | 0.21017 | 0.21008 | 0.20993 | 0.20976 | 0.2094 | 0.20905 | 0.20871 | 0.20835 | 0.20799 | 0.20728 | 0.20558 | 0.20401 | 0.20293
| CONON FALLS | FS |  |  |  | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.30698 | 0.23544 | 0.23543 | 0.23541 | 0.2353 | 0.23518 | 0.23488 | 0.23459 | 0.2342 | 0.23383 | 0.23347 | 0.23276 | 0.23108 | 0.22951 | 0.22803 | 0.21023 | 0.21023 | 0.21022 | 0.21018 | 0.21013 | 0.21001 | 0.2099 | 0.20975 | 0.2096 | 0.20946 | 0.20918 | 0.20852 | 0.2079 | 0.20732
DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 22.8003 | 22.7551 | 22.6816 | 22.6195 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 21.9819 | 21.9084 | 21.7887 | 21.6877 | 21.6159 | 21.5437 | 21.4702 | 21.3982 | 21.3174 | 21.2327 | 21.0656 | 20.9313 | 20.9313 | 20.9313 | 23.5627 | 23.5376 | 23.4968 | 23.4623 | 23.4379 | 23.4132 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023
| CONSTABLE STREET | CT |  |  |  | 22.8004 | 22.7609 | 22.6976 | 22.6484 | 22.6133 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 21.9821 | 21.9178 | 21.8147 | 21.7347 | 21.6776 | 21.6153 | 21.5448 | 21.4745 | 21.405 | 21.3346 | 21.199 | 21.0056 | 20.9525 | 20.9313 | 23.5628 | 23.5408 | 23.5057 | 23.4784 | 23.4589 | 23.4377 | 23.4136 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023
| CONSTABLE STREET | LW |  |  |  | 22.8003 | 22.7551 | 22.6816 | 22.6195 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 21.9819 | 21.9084 | 21.7887 | 21.6877 | 21.6159 | 21.5437 | 21.4702 | 21.3982 | 21.3174 | 21.2327 | 21.0656 | 20.9313 | 20.9313 | 20.9313 | 23.5627 | 23.5376 | 23.4968 | 23.4623 | 23.4379 | 23.4132 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023
| CONSTABLE STREET | ST |  |  |  | 22.8077 | 22.7797 | 22.7376 | 22.6968 | 22.6588 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 22.6025 | 21.994 | 21.9484 | 21.8799 | 21.8135 | 21.7517 | 21.6586 | 21.5612 | 21.4651 | 21.3655 | 21.2662 | 21.0745 | 20.9696 | 20.9313 | 20.9313 | 23.5668 | 23.5513 | 23.5279 | 23.5053 | 23.4842 | 23.4524 | 23.4192 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023 | 23.4023
| CONSTABLE STREET | FS |  |  |  | 22.8171 | 22.8043 | 22.7905 | 22.7788 | 22.7707 | 22.7529 | 22.7355 | 22.7141 | 22.6925 | 22.6707 | 22.6283 | 22.6025 | 22.6025 | 22.6025 | 22.0093 | 21.9885 | 21.9661 | 21.947 | 21.9337 | 21.9048 | 21.8765 | 21.8416 | 21.8064 | 21.7709 | 21.702 | 21.5432 | 21.4021 | 21.274 | 23.5721 | 23.565 | 23.5573 | 23.5508 | 23.5463 | 23.5364 | 23.5267 | 23.5149 | 23.5029 | 23.4907 | 23.4672 | 23.4131 | 23.4023 | 23.4023
ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.012831 | 0.012793 | 0.012682 | 0.012547 | 0.012414 | 0.012285 | 0.012158 | 0.012034 | 0.011929 | 0.011828 | 0.011629 | 0.011477 | 0.011437 | 0.011437 | 0.014467 | 0.014448 | 0.014394 | 0.014329 | 0.014264 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222
| CONTULLICH | CT |  |  |  | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.012831 | 0.012799 | 0.012716 | 0.012622 | 0.012529 | 0.012438 | 0.012349 | 0.012263 | 0.012169 | 0.012076 | 0.011923 | 0.011585 | 0.011501 | 0.011437 | 0.014467 | 0.014451 | 0.014411 | 0.014365 | 0.01432 | 0.014276 | 0.014233 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222
| CONTULLICH | LW |  |  |  | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.012831 | 0.012793 | 0.012682 | 0.012547 | 0.012414 | 0.012285 | 0.012158 | 0.012034 | 0.011929 | 0.011828 | 0.011629 | 0.011477 | 0.011437 | 0.011437 | 0.014467 | 0.014448 | 0.014394 | 0.014329 | 0.014264 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222 | 0.014222
| CONTULLICH | ST |  |  |  | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.012843 | 0.012828 | 0.012795 | 0.012743 | 0.012681 | 0.012621 | 0.012562 | 0.012505 | 0.012443 | 0.012382 | 0.012264 | 0.011989 | 0.011779 | 0.011578 | 0.014472 | 0.014465 | 0.014449 | 0.014424 | 0.014394 | 0.014365 | 0.014336 | 0.014308 | 0.014278 | 0.014249 | 0.014222 | 0.014222 | 0.014222 | 0.014222
| CONTULLICH | FS |  |  |  | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.02342 | 0.012849 | 0.012847 | 0.012845 | 0.012831 | 0.012813 | 0.012793 | 0.012773 | 0.012748 | 0.012722 | 0.012698 | 0.01265 | 0.012537 | 0.012432 | 0.012336 | 0.014476 | 0.014475 | 0.014474 | 0.014467 | 0.014458 | 0.014448 | 0.014439 | 0.014426 | 0.014414 | 0.014402 | 0.014379 | 0.014324 | 0.014273 | 0.014226
FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | 3.1001 | 2.9996 | 2.4139 | 2.2964 | 2.1831 | 2.074 | 1.9326 | 1.79 | 1.7036 | 1.6444 | 1.5276 | 1.3184 | 1.1175 | 0.91484 | 3.0944 | 3.0258 | 2.9352 | 2.3625 | 2.2217 | 2.0855 | 1.9538 | 1.8266 | 1.745 | 1.6858 | 1.5689 | 1.3705 | 1.1785 | 0.98551 | 3.1387 | 3.0519 | 2.4205 | 2.248 | 2.0809 | 1.9193 | 1.7632 | 1.6125 | 1.519 | 1.4533 | 1.3237 | 1.0968 | 0.87826 | 0.65809
| CORRAN | CT |  |  |  | 3.1001 | 2.9996 | 2.4139 | 2.2964 | 2.1831 | 2.074 | 1.9326 | 1.79 | 1.7036 | 1.6444 | 1.5276 | 1.3184 | 1.1175 | 0.91484 | 3.0944 | 3.0258 | 2.9352 | 2.3625 | 2.2217 | 2.0855 | 1.9538 | 1.8266 | 1.745 | 1.6858 | 1.5689 | 1.3705 | 1.1785 | 0.98551 | 3.1387 | 3.0519 | 2.4205 | 2.248 | 2.0809 | 1.9193 | 1.7632 | 1.6125 | 1.519 | 1.4533 | 1.3237 | 1.0968 | 0.87826 | 0.65809
| CORRAN | LW |  |  |  | 3.2445 | 3.2278 | 3.2085 | 3.1867 | 3.1627 | 3.1367 | 3.1089 | 3.0796 | 2.4333 | 2.3521 | 2.189 | 1.9236 | 1.656 | 1.3772 | 3.1898 | 3.176 | 3.1553 | 3.1313 | 3.106 | 3.0795 | 2.4694 | 2.3897 | 2.3068 | 2.2236 | 2.0568 | 1.8063 | 1.5533 | 1.2917 | 3.2635 | 3.249 | 3.2323 | 3.2135 | 3.1928 | 3.1703 | 2.4247 | 2.3371 | 2.2465 | 2.1554 | 1.9726 | 1.6854 | 1.3956 | 1.0947
| CORRAN | ST |  |  |  | 3.2667 | 3.2609 | 3.2532 | 3.2457 | 3.2384 | 3.2295 | 3.2209 | 3.2125 | 3.2044 | 3.1925 | 3.1698 | 3.1173 | 3.0701 | 3.0248 | 3.2052 | 3.2004 | 3.1929 | 3.1843 | 3.1751 | 3.1674 | 3.16 | 3.1528 | 3.1456 | 3.1359 | 3.1174 | 3.0741 | 2.4844 | 2.3938 | 3.2826 | 3.2776 | 3.271 | 3.2645 | 3.2582 | 3.2505 | 3.2431 | 3.2358 | 3.2288 | 3.2186 | 3.1989 | 3.1535 | 2.433 | 2.3312
| CORRAN | FS |  |  |  | 3.2609 | 3.2532 | 3.2455 | 3.2341 | 3.2228 | 3.2117 | 3.2008 | 3.19 | 3.1794 | 3.1689 | 3.1483 | 3.0872 | 3.0324 | 2.9813 | 3.2018 | 3.1966 | 3.1914 | 3.1828 | 3.1741 | 3.1662 | 3.1584 | 3.1505 | 3.1428 | 3.1352 | 3.1202 | 3.0766 | 3.0374 | 3.0008 | 3.2776 | 3.271 | 3.2643 | 3.2545 | 3.2448 | 3.2352 | 3.2257 | 3.2164 | 3.2072 | 3.1981 | 3.1804 | 3.1276 | 3.0802 | 2.4931
KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 3.2386 | 2.586 | 2.3873 | 4.101 | 4.1001 | 4.0977 | 4.0947 | 4.0914 | 4.0882 | 4.085 | 4.0819 | 4.0784 | 4.075 | 3.2912 | 3.0536 | 2.4714 | 2.2407 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 3.1348 | 2.4525 | 2.2191
| COSHIEVILLE | CT |  |  |  | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 2.783 | 2.6418 | 4.101 | 4.1003 | 4.0984 | 4.0963 | 4.094 | 4.0917 | 4.0894 | 4.0872 | 4.0847 | 4.0821 | 4.0775 | 3.2174 | 2.7 | 2.5361 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 3.273 | 2.6698 | 2.5162
| COSHIEVILLE | LW |  |  |  | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 3.2386 | 2.586 | 2.3873 | 4.101 | 4.1001 | 4.0977 | 4.0947 | 4.0914 | 4.0882 | 4.085 | 4.0819 | 4.0784 | 4.075 | 3.2912 | 3.0536 | 2.4714 | 2.2407 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 3.1348 | 2.4525 | 2.2191
| COSHIEVILLE | ST |  |  |  | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 3.1841 | 3.1029 | 4.1012 | 4.1009 | 4.1002 | 4.099 | 4.0975 | 4.0954 | 4.0935 | 4.0915 | 4.0893 | 4.0871 | 4.0831 | 4.0741 | 3.0805 | 2.9862 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 3.0699 | 2.9971
| COSHIEVILLE | FS |  |  |  | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1971 | 4.1014 | 4.1013 | 4.1013 | 4.101 | 4.1005 | 4.0998 | 4.099 | 4.0981 | 4.0972 | 4.0963 | 4.0946 | 4.0908 | 4.0873 | 4.0842 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266 | 4.2266
COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 11.1952 | 11.1506 | 11.0933 | 11.0346 | 10.9779 | 10.9234 | 10.8709 | 10.8206 | 10.7888 | 10.773 | 10.7419 | 10.2627 | 10.173 | 7.4596 | 11.2605 | 11.2312 | 11.1923 | 11.1522 | 11.1134 | 11.0759 | 11.0393 | 11.004 | 10.9804 | 10.9668 | 10.9405 | 10.6201 | 7.3144 | 6.9045 | 10.1708 | 10.1284 | 10.0741 | 10.0184 | 9.9647 | 9.9129 | 9.8632 | 9.8154 | 9.7853 | 9.7703 | 9.7408 | 9.2864 | 7.3536 | 6.9636
| COUPAR ANGUS | CT |  |  |  | 11.1952 | 11.1506 | 11.0933 | 11.0346 | 10.9779 | 10.9234 | 10.8709 | 10.8206 | 10.7888 | 10.773 | 10.7419 | 10.2627 | 10.173 | 7.4596 | 11.2605 | 11.2312 | 11.1923 | 11.1522 | 11.1134 | 11.0759 | 11.0393 | 11.004 | 10.9804 | 10.9668 | 10.9405 | 10.6201 | 7.3507 | 7.0244 | 10.1708 | 10.1284 | 10.0741 | 10.0184 | 9.9647 | 9.9129 | 9.8632 | 9.8154 | 9.7853 | 9.7703 | 9.7408 | 9.2864 | 7.3536 | 6.9863
| COUPAR ANGUS | LW |  |  |  | 11.2594 | 11.252 | 11.2434 | 11.2337 | 11.2231 | 11.2115 | 11.1992 | 11.1862 | 11.1697 | 11.1527 | 11.1178 | 10.6249 | 10.5087 | 7.5066 | 11.3014 | 11.2956 | 11.2869 | 11.2769 | 11.2662 | 11.2549 | 11.2426 | 11.2301 | 11.2149 | 11.1994 | 11.1687 | 10.8376 | 7.3144 | 6.9045 | 10.2316 | 10.2246 | 10.2164 | 10.2073 | 10.1972 | 10.1862 | 10.1745 | 10.1622 | 10.1465 | 10.1304 | 10.0973 | 9.6298 | 9.5197 | 6.9636
| COUPAR ANGUS | ST |  |  |  | 11.2692 | 11.2667 | 11.2633 | 11.2599 | 11.2567 | 11.2527 | 11.2489 | 11.2452 | 11.2413 | 11.2357 | 11.2249 | 10.9951 | 10.9658 | 10.9305 | 11.308 | 11.3061 | 11.3032 | 11.3 | 11.2967 | 11.2925 | 11.2881 | 11.2837 | 11.2791 | 11.2733 | 11.2624 | 11.108 | 11.0824 | 11.0533 | 10.241 | 10.2385 | 10.2353 | 10.2321 | 10.229 | 10.2253 | 10.2217 | 10.2181 | 10.2145 | 10.2092 | 10.1989 | 9.981 | 9.9532 | 9.9197
| COUPAR ANGUS | FS |  |  |  | 11.2667 | 11.2633 | 11.2598 | 11.2548 | 11.2498 | 11.2448 | 11.24 | 11.2352 | 11.2305 | 11.2258 | 11.2167 | 11.1895 | 11.1602 | 11.1316 | 11.3065 | 11.3042 | 11.3019 | 11.2983 | 11.2947 | 11.2909 | 11.2871 | 11.2832 | 11.2793 | 11.2755 | 11.2681 | 11.2476 | 11.2263 | 11.2057 | 10.2385 | 10.2353 | 10.232 | 10.2272 | 10.2225 | 10.2178 | 10.2132 | 10.2087 | 10.2042 | 10.1998 | 10.1911 | 10.1654 | 10.1376 | 10.1104
CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | NO | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.8815 | 22.0049 | 21.1062 | 20.2237 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 22.5973 | 22.2563 | 21.9209 | 21.592 | 21.2361 | 20.8828 | 20.171 | 19.1419 | 18.0867 | 17.0507 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 22.8369 | 22.4958 | 22.1604 | 21.8314 | 21.4753 | 21.1219 | 20.4098 | 19.3804 | 18.3249 | 17.2885
| CRAIGIEBUCKLER | CT |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.7324 | 22.1337 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 22.7729 | 22.5583 | 22.3459 | 22.1135 | 21.882 | 21.4352 | 20.7221 | 19.9959 | 19.293 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 22.7979 | 22.5855 | 22.3531 | 22.1215 | 21.6745 | 20.9612 | 20.2347 | 19.5316
| CRAIGIEBUCKLER | LW |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.8815 | 22.0049 | 21.1062 | 20.2237 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 22.5973 | 22.2563 | 21.9209 | 21.592 | 21.2361 | 20.8828 | 20.171 | 19.1419 | 18.0867 | 17.0507 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 22.8369 | 22.4958 | 22.1604 | 21.8314 | 21.4753 | 21.1219 | 20.4098 | 19.3804 | 18.3249 | 17.2885
| CRAIGIEBUCKLER | ST |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 24.9599 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 22.8974 | 22.7996 | 22.6168 | 22.1344 | 21.655 | 21.1898 | 25.135 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 22.8564 | 22.374 | 21.8944 | 21.429
| CRAIGIEBUCKLER | FS |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 24.9741 | 24.9679 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 24.7352 | 25.1386 | 25.137 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862 | 25.0862
CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 35.0496 | 35.0487 | 35.0463 | 35.0433 | 35.0403 | 35.0374 | 35.0346 | 35.0318 | 35.0288 | 35.0258 | 35.0194 | 34.9924 | 34.9645 | 34.9371 | 31.8051 | 31.7954 | 31.7685 | 31.7354 | 31.7027 | 31.6706 | 31.639 | 31.608 | 31.5745 | 31.5414 | 31.4705 | 31.4167 | 31.3619 | 31.3263 | 32.0543 | 32.0507 | 32.0405 | 32.028 | 32.0156 | 32.0035 | 31.9915 | 31.9798 | 31.9671 | 31.9545 | 31.9277 | 31.8568 | 31.8568 | 31.8568
| CRAIGINCHES | CT |  |  |  | 35.0496 | 35.0488 | 35.047 | 35.0449 | 35.0429 | 35.0408 | 35.0388 | 35.0368 | 35.0347 | 35.0326 | 35.0283 | 35.0079 | 34.9871 | 34.9671 | 31.8051 | 31.797 | 31.7769 | 31.7537 | 31.7308 | 31.7082 | 31.6858 | 31.6638 | 31.64 | 31.6165 | 31.5696 | 31.4473 | 31.4064 | 31.3668 | 32.0544 | 32.0513 | 32.0437 | 32.0349 | 32.0262 | 32.0177 | 32.0092 | 32.0009 | 31.9919 | 31.983 | 31.9652 | 31.8796 | 31.8568 | 31.8568
| CRAIGINCHES | LW |  |  |  | 35.0496 | 35.0487 | 35.0463 | 35.0433 | 35.0403 | 35.0374 | 35.0346 | 35.0318 | 35.0288 | 35.0258 | 35.0194 | 34.9924 | 34.9645 | 34.9371 | 31.8051 | 31.7954 | 31.7685 | 31.7354 | 31.7027 | 31.6706 | 31.639 | 31.608 | 31.5745 | 31.5414 | 31.4705 | 31.4167 | 31.3619 | 31.3263 | 32.0543 | 32.0507 | 32.0405 | 32.028 | 32.0156 | 32.0035 | 31.9915 | 31.9798 | 31.9671 | 31.9545 | 31.9277 | 31.8568 | 31.8568 | 31.8568
| CRAIGINCHES | ST |  |  |  | 35.0572 | 35.0495 | 35.0487 | 35.0476 | 35.0462 | 35.0438 | 35.0415 | 35.0391 | 35.0366 | 35.0341 | 35.0293 | 35.0157 | 35.0023 | 34.9894 | 31.8901 | 31.8042 | 31.796 | 31.7834 | 31.7683 | 31.7415 | 31.7152 | 31.6894 | 31.6614 | 31.6341 | 31.5803 | 31.4627 | 31.4363 | 31.4108 | 32.0865 | 32.054 | 32.0509 | 32.0461 | 32.0404 | 32.0303 | 32.0203 | 32.0106 | 32 | 31.9896 | 31.9693 | 31.9123 | 31.8568 | 31.8568
| CRAIGINCHES | FS |  |  |  | 35.0747 | 35.0573 | 35.0498 | 35.0495 | 35.0491 | 35.0484 | 35.0476 | 35.0466 | 35.0456 | 35.0447 | 35.0428 | 35.0383 | 35.0337 | 35.0291 | 32.0835 | 31.8911 | 31.8081 | 31.8045 | 31.8003 | 31.7917 | 31.7831 | 31.7721 | 31.7613 | 31.7507 | 31.7301 | 31.6803 | 31.6294 | 31.5783 | 32.2476 | 32.0869 | 32.0555 | 32.0541 | 32.0525 | 32.0493 | 32.046 | 32.0419 | 32.0378 | 32.0338 | 32.026 | 32.0071 | 31.9879 | 31.9685
CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | NO | 12.4582 | 12.3725 | 12.2625 | 12.1556 | 12.0524 | 11.9531 | 11.8576 | 11.766 | 9.7604 | 9.479 | 9.0332 | 7.5758 | 6.768 | 5.9398 | 10.6098 | 9.9884 | 9.9019 | 9.6422 | 9.3678 | 9.0736 | 8.7656 | 8.4368 | 8.0702 | 7.6732 | 7.0473 | 5.6288 | 4.7668 | 3.8934 | 10.7743 | 10.6712 | 9.9754 | 9.6996 | 9.4107 | 9.0958 | 8.7664 | 8.4145 | 8.0742 | 7.7415 | 7.1636 | 5.533 | 4.6205 | 3.6894
| CRAIGTON | CT |  |  |  | 12.4582 | 12.3725 | 12.2625 | 12.1556 | 12.0524 | 11.9531 | 11.8576 | 11.766 | 9.7604 | 9.479 | 9.0332 | 7.6146 | 7.0311 | 6.4685 | 10.6098 | 9.9884 | 9.9019 | 9.6422 | 9.3678 | 9.0736 | 8.7656 | 8.4368 | 8.1104 | 7.7846 | 7.2736 | 5.9576 | 5.3348 | 4.7417 | 10.7743 | 10.6712 | 9.9754 | 9.6996 | 9.4107 | 9.0958 | 8.7664 | 8.4145 | 8.0742 | 7.7415 | 7.2168 | 5.6977 | 5.0381 | 4.4056
| CRAIGTON | LW |  |  |  | 12.5814 | 12.5671 | 12.5506 | 12.5321 | 12.5116 | 12.4894 | 12.4658 | 12.4408 | 9.9996 | 9.6503 | 9.0941 | 7.5758 | 6.768 | 5.9398 | 10.7042 | 10.6162 | 10.5873 | 9.7504 | 9.4541 | 9.1394 | 8.8057 | 8.453 | 8.0702 | 7.6732 | 7.0473 | 5.6288 | 4.7668 | 3.8934 | 10.8986 | 10.8637 | 10.8464 | 9.9196 | 9.6199 | 9.2994 | 8.9597 | 8.6005 | 8.2102 | 7.8055 | 7.1636 | 5.533 | 4.6205 | 3.6894
| CRAIGTON | ST |  |  |  | 12.6003 | 12.5953 | 12.5888 | 12.5824 | 12.5762 | 12.5686 | 12.5612 | 12.5541 | 12.5471 | 12.5368 | 12.5172 | 9.729 | 9.3791 | 9.0424 | 10.7447 | 10.6976 | 10.6344 | 10.6084 | 9.9839 | 9.8243 | 9.654 | 9.4683 | 9.2591 | 9.0286 | 8.6633 | 7.8758 | 7.4869 | 7.1169 | 10.9243 | 10.9083 | 10.8863 | 10.8789 | 10.8726 | 10.8648 | 9.8323 | 9.6448 | 9.4337 | 9.2005 | 8.8301 | 7.9441 | 7.5423 | 7.1575
| CRAIGTON | FS |  |  |  | 12.5953 | 12.5888 | 12.5822 | 12.5725 | 12.5629 | 12.5534 | 12.5441 | 12.5349 | 12.5258 | 12.5169 | 12.4994 | 12.4472 | 12.3921 | 12.3384 | 10.762 | 10.7349 | 10.7084 | 10.6686 | 10.6254 | 10.5986 | 10.5869 | 10.5782 | 9.974 | 9.8816 | 9.7348 | 9.5092 | 9.3382 | 9.1828 | 10.9247 | 10.9125 | 10.9004 | 10.8823 | 10.8635 | 10.8492 | 10.8397 | 10.8302 | 10.8209 | 10.8117 | 9.8951 | 9.6587 | 9.4738 | 9.3048
BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | NO | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 17.5824 | 17.5411 | 17.4507 | 17.3447 | 17.2361 | 17.1297 | 17.0307 | 17.0044 | 16.9867 | 16.9708 | 16.938 | 13.4935 | 12.5609 | 11.6958 | 17.6286 | 17.5867 | 17.495 | 17.3876 | 17.3328 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 13.6502 | 12.7065 | 11.8312
| CRIEFF | CT |  |  |  | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 17.583 | 17.5483 | 17.4777 | 17.4003 | 17.3199 | 17.2399 | 17.1638 | 17.0855 | 17.0228 | 17.0003 | 16.9746 | 16.9078 | 13.5684 | 12.9282 | 17.6292 | 17.594 | 17.5224 | 17.444 | 17.3625 | 17.3338 | 17.3143 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 13.7259 | 13.0781
| CRIEFF | LW |  |  |  | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 17.5824 | 17.5411 | 17.4507 | 17.3447 | 17.2361 | 17.1297 | 17.0307 | 17.0044 | 16.9867 | 16.9708 | 16.938 | 13.4935 | 12.5609 | 11.6958 | 17.6286 | 17.5867 | 17.495 | 17.3876 | 17.3328 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 13.6502 | 12.7065 | 11.8312
| CRIEFF | ST |  |  |  | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 17.5933 | 17.5743 | 17.5416 | 17.4983 | 17.4461 | 17.3829 | 17.3226 | 17.2612 | 17.194 | 17.1267 | 17.02 | 16.9687 | 16.9317 | 16.8962 | 17.6396 | 17.6204 | 17.5872 | 17.5433 | 17.4904 | 17.4264 | 17.3652 | 17.3392 | 17.322 | 17.3105 | 17.3105 | 17.3105 | 17.3105 | 17.3105
| CRIEFF | FS |  |  |  | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 21.6078 | 17.6004 | 17.5928 | 17.584 | 17.5684 | 17.5504 | 17.5279 | 17.5071 | 17.4817 | 17.4559 | 17.4302 | 17.3775 | 17.2485 | 17.1417 | 17.055 | 17.6468 | 17.639 | 17.6301 | 17.6143 | 17.5961 | 17.5733 | 17.5523 | 17.5265 | 17.5003 | 17.4743 | 17.4209 | 17.3359 | 17.3105 | 17.3105
PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | -0.11042 | -0.22969 | 0.47307 | 0.47106 | 0.46529 | 0.45822 | 0.45131 | 0.44456 | 0.44015 | 0.43934 | 0.43847 | 0.43782 | 0.43782 | -0.13813 | -0.29161 | -0.44288 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | -0.083389 | -0.23301 | -0.38089
| CRINAN | CT |  |  |  | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | -0.018694 | -0.10338 | 0.47307 | 0.4714 | 0.46707 | 0.46212 | 0.45728 | 0.45256 | 0.44793 | 0.44341 | 0.44022 | 0.43961 | 0.43841 | -0.066146 | -0.17528 | -0.28268 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | -0.013209 | -0.1196 | -0.22431
| CRINAN | LW |  |  |  | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | -0.11042 | -0.22969 | 0.47307 | 0.47106 | 0.46529 | 0.45822 | 0.45131 | 0.44456 | 0.44015 | 0.43934 | 0.43847 | 0.43782 | 0.43782 | -0.13813 | -0.29161 | -0.44288 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | -0.083389 | -0.23301 | -0.38089
| CRINAN | ST |  |  |  | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | -0.03771 | 0.47364 | 0.47288 | 0.47109 | 0.4683 | 0.46499 | 0.45481 | 0.44486 | 0.4398 | 0.43848 | 0.43782 | 0.43782 | -0.066633 | -0.13313 | -0.1994 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | -0.013684 | -0.078514 | -0.14311
| CRINAN | FS |  |  |  | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.4055 | 0.474 | 0.4739 | 0.47377 | 0.47299 | 0.47206 | 0.46875 | 0.46546 | 0.46123 | 0.45709 | 0.45303 | 0.44513 | 0.4387 | 0.43782 | -0.0014913 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546 | 0.45546
PORT ANN | CROMALT | MINIMUM HEADROOM | NN 0839507755 | YES | YES | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 2.9346 | 2.9252 | 2.9122 | 2.9062 | 2.9005 | 2.8961 | 2.8944 | 2.8927 | 2.8908 | 2.889 | 2.8855 | 2.8764 | 2.8671 | 2.8621 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295
| CROMALT | CT |  |  |  | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 2.9349 | 2.927 | 2.9163 | 2.9124 | 2.9084 | 2.9035 | 2.8974 | 2.8949 | 2.8934 | 2.892 | 2.8896 | 2.8837 | 2.8777 | 2.8718 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295
| CROMALT | LW |  |  |  | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 2.9346 | 2.9252 | 2.9122 | 2.9062 | 2.9005 | 2.8961 | 2.8944 | 2.8927 | 2.8908 | 2.889 | 2.8855 | 2.8764 | 2.8671 | 2.8621 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295
| CROMALT | ST |  |  |  | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 2.9376 | 2.9324 | 2.9261 | 2.9241 | 2.9213 | 2.9179 | 2.9136 | 2.9096 | 2.9062 | 2.9031 | 2.8979 | 2.8929 | 2.8889 | 2.8849 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295
| CROMALT | FS |  |  |  | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 3.1063 | 2.9401 | 2.937 | 2.9341 | 2.9331 | 2.932 | 2.9307 | 2.9294 | 2.928 | 2.9266 | 2.9252 | 2.9227 | 2.9177 | 2.9131 | 2.9089 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295 | 2.9295
ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 19.5785 | 19.5688 | 19.5494 | 19.5231 | 19.4964 | 19.4777 | 19.4596 | 19.4436 | 19.4275 | 19.4134 | 19.3874 | 19.3427 | 19.2929 | 19.2374 | 17.3917 | 17.3607 | 17.2987 | 17.2148 | 17.1293 | 17.0449 | 16.9578 | 16.8811 | 16.8325 | 16.8036 | 16.7507 | 16.7112 | 16.7112 | 16.7112 | 17.4474 | 17.4342 | 17.4078 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
| CROSSHILLS | CT |  |  |  | 19.5785 | 19.5688 | 19.5494 | 19.5231 | 19.4964 | 19.4777 | 19.4596 | 19.4436 | 19.4275 | 19.4134 | 19.3874 | 19.3427 | 19.301 | 19.2605 | 17.3917 | 17.3607 | 17.2987 | 17.2148 | 17.1293 | 17.0449 | 16.9578 | 16.8811 | 16.8325 | 16.8036 | 16.7507 | 16.7112 | 16.7112 | 16.7112 | 17.4474 | 17.4342 | 17.4078 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
| CROSSHILLS | LW |  |  |  | 19.5803 | 19.5727 | 19.5582 | 19.5359 | 19.513 | 19.4894 | 19.4676 | 19.4519 | 19.4369 | 19.4253 | 19.4055 | 19.3499 | 19.2929 | 19.2374 | 17.3975 | 17.3731 | 17.3267 | 17.2555 | 17.1824 | 17.1071 | 16.9963 | 16.9208 | 16.8517 | 16.8279 | 16.7875 | 16.7112 | 16.7112 | 16.7112 | 17.4498 | 17.4394 | 17.4197 | 17.3894 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
| CROSSHILLS | ST |  |  |  | 19.5831 | 19.5799 | 19.5761 | 19.5676 | 19.5573 | 19.5417 | 19.5146 | 19.491 | 19.477 | 19.4685 | 19.4533 | 19.4252 | 19.4 | 19.3756 | 17.4064 | 17.3963 | 17.384 | 17.3568 | 17.3241 | 17.274 | 17.1875 | 17.1122 | 17.0414 | 17.0009 | 16.9275 | 16.8277 | 16.7763 | 16.7264 | 17.4536 | 17.4493 | 17.4441 | 17.4325 | 17.4186 | 17.3973 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
| CROSSHILLS | FS |  |  |  | 19.5849 | 19.5837 | 19.5833 | 19.5805 | 19.5775 | 19.5719 | 19.5613 | 19.5512 | 19.5418 | 19.5337 | 19.5192 | 19.4918 | 19.4779 | 19.469 | 17.4123 | 17.4083 | 17.4069 | 17.3982 | 17.3884 | 17.3705 | 17.3367 | 17.3046 | 17.2744 | 17.2486 | 17.2023 | 17.1149 | 17.0455 | 17.0031 | 17.4561 | 17.4544 | 17.4538 | 17.4501 | 17.4459 | 17.4383 | 17.424 | 17.4103 | 17.3975 | 17.3865 | 17.3839 | 17.3839 | 17.3839 | 17.3839
KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.1307 | 8.5508 | 8.5473 | 8.54 | 8.5292 | 8.5187 | 8.5092 | 8.4995 | 8.4923 | 8.4851 | 8.4743 | 8.4506 | 7.2219 | 6.4238 | 5.988 | 8.9752 | 8.9727 | 8.9674 | 8.9596 | 8.9521 | 8.9453 | 8.9383 | 8.9331 | 8.9278 | 8.92 | 8.903 | 8.8135 | 6.7104 | 6.3017
| CULLEN | CT |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.3748 | 8.5509 | 8.5479 | 8.5422 | 8.5339 | 8.5259 | 8.5187 | 8.5112 | 8.5054 | 8.499 | 8.4926 | 8.4812 | 7.3572 | 6.6449 | 6.2926 | 8.9753 | 8.9731 | 8.969 | 8.9631 | 8.9573 | 8.9521 | 8.9467 | 8.9425 | 8.9379 | 8.9333 | 8.925 | 8.8444 | 6.9178 | 6.5873
| CULLEN | LW |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.1307 | 8.5508 | 8.5473 | 8.54 | 8.5292 | 8.5187 | 8.5092 | 8.4995 | 8.4923 | 8.4851 | 8.4779 | 8.4637 | 7.2219 | 6.4238 | 5.988 | 8.9752 | 8.9727 | 8.9674 | 8.9596 | 8.9521 | 8.9453 | 8.9383 | 8.9331 | 8.9278 | 8.9226 | 8.9124 | 8.8135 | 6.7104 | 6.3017
| CULLEN | ST |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.2543 | 9.2543 | 8.5517 | 8.55 | 8.5473 | 8.5423 | 8.537 | 8.524 | 8.5111 | 8.4994 | 8.4868 | 8.4743 | 8.4506 | 7.4396 | 7.0896 | 6.9181 | 8.9759 | 8.9747 | 8.9727 | 8.9691 | 8.9652 | 8.9559 | 8.9466 | 8.9382 | 8.9291 | 8.92 | 8.903 | 8.8633 | 7.3878 | 7.2383
| CULLEN | FS |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 8.5524 | 8.5517 | 8.5509 | 8.5489 | 8.5469 | 8.5422 | 8.5375 | 8.5322 | 8.5271 | 8.5221 | 8.5124 | 8.4901 | 8.47 | 8.4506 | 8.9763 | 8.9758 | 8.9753 | 8.9738 | 8.9724 | 8.969 | 8.9656 | 8.9618 | 8.9582 | 8.9545 | 8.9475 | 8.9315 | 8.917 | 8.9029
INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | NO | 23.5162 | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 23.1272 | 22.0118 | 21.3966 | 21.3155 | 28.2272 | 28.0094 | 27.7852 | 27.5625 | 27.4066 | 27.3658 | 27.3218 | 27.277 | 27.2021 | 20.8558 | 19.4932 | 18.1643 | 21.2924 | 21.2669 | 28.2938 | 28.2252 | 28.1545 | 28.0843 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.0637 | 19.7212 | 18.4118
| CULLODEN | CT |  |  |  | 23.5162 | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.3983 | 21.3308 | 28.282 | 28.123 | 27.9569 | 27.7893 | 27.6235 | 27.4488 | 27.3906 | 27.354 | 27.2932 | 27.2029 | 21.2625 | 20.3569 | 21.293 | 21.2717 | 28.3111 | 28.261 | 28.2086 | 28.1558 | 28.1035 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.4644 | 20.5721
| CULLODEN | LW |  |  |  | 23.5162 | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 23.1272 | 22.0118 | 21.3966 | 21.3155 | 28.2272 | 28.0094 | 27.7852 | 27.5625 | 27.4066 | 27.3658 | 27.3218 | 27.277 | 27.2021 | 20.8558 | 19.4932 | 18.1643 | 21.2924 | 21.2669 | 28.2938 | 28.2252 | 28.1545 | 28.0843 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.0637 | 19.7212 | 18.4118
| CULLODEN | ST |  |  |  | 23.5162 | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.4952 | 21.385 | 28.4084 | 28.3211 | 28.2168 | 28.1174 | 28.0193 | 27.9152 | 27.7979 | 27.6742 | 27.475 | 27.368 | 27.3108 | 27.2552 | 21.3235 | 21.2888 | 28.351 | 28.3234 | 28.2905 | 28.2592 | 28.2283 | 28.1955 | 28.1585 | 28.1195 | 28.0727 | 28.0727 | 28.0727 | 28.0727
| CULLODEN | FS |  |  |  | 23.5162 | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.5109 | 21.4215 | 28.4867 | 28.4535 | 28.4158 | 28.3784 | 28.3416 | 28.2978 | 28.2523 | 28.2051 | 28.1285 | 27.9925 | 27.8794 | 27.7727 | 21.3285 | 21.3003 | 28.3756 | 28.3652 | 28.3533 | 28.3415 | 28.3299 | 28.3161 | 28.3017 | 28.2869 | 28.2627 | 28.2199 | 28.1842 | 28.1506
CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | NO | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 22.2283 | 21.4977 | 25.4779 | 25.4303 | 25.3126 | 25.1776 | 25.0584 | 25.034 | 25.0096 | 24.9852 | 24.9588 | 24.9345 | 21.7244 | 20.8874 | 19.6731 | 18.8387 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.8277 | 21.5603 | 21.0533 | 20.2016 | 18.8947 | 18.0458
| CULTER | CT |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 27.8172 | 23.1527 | 25.4819 | 25.4481 | 25.3734 | 25.2957 | 25.2172 | 25.137 | 25.0605 | 25.0452 | 25.0288 | 25.014 | 24.987 | 24.9335 | 21.2793 | 20.7305 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.5489 | 20.529 | 19.9706
| CULTER | LW |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 22.2283 | 21.4977 | 25.4779 | 25.4303 | 25.3126 | 25.1776 | 25.0584 | 25.034 | 25.0096 | 24.9852 | 24.9588 | 24.9345 | 21.7244 | 20.8874 | 19.6731 | 18.8387 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.8277 | 21.5603 | 21.0533 | 20.2016 | 18.8947 | 18.0458
| CULTER | ST |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.0277 | 28.0277 | 25.4899 | 25.4682 | 25.425 | 25.367 | 25.2975 | 25.2499 | 25.2009 | 25.1508 | 25.0966 | 25.0593 | 25.0439 | 25.0057 | 24.8372 | 22.0295 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.7195 | 21.3281
| CULTER | FS |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 25.4987 | 25.4922 | 25.4841 | 25.4668 | 25.4467 | 25.4299 | 25.4129 | 25.3922 | 25.3711 | 25.3526 | 25.3195 | 25.2447 | 25.1752 | 25.1075 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887
ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 31.4336 | 31.4248 | 31.3982 | 31.3625 | 31.3233 | 31.2832 | 31.2423 | 31.2073 | 31.1737 | 31.1403 | 31.0742 | 30.8262 | 30.569 | 30.3167 | 29.504 | 29.4914 | 29.4533 | 29.4021 | 29.3458 | 29.2883 | 29.2297 | 29.1795 | 29.1313 | 29.0834 | 28.9886 | 28.6771 | 28.6104 | 28.6104 | 29.7599 | 29.7449 | 29.6996 | 29.6386 | 29.5718 | 29.5033 | 29.4336 | 29.3992 | 29.383 | 29.367 | 29.3352 | 29.2159 | 29.0922 | 28.996
| CUMMING STREET | CT |  |  |  | 31.4336 | 31.4263 | 31.4063 | 31.3807 | 31.3521 | 31.3228 | 31.2934 | 31.268 | 31.243 | 31.2168 | 31.1664 | 30.9843 | 30.7984 | 30.6156 | 29.5041 | 29.4936 | 29.4649 | 29.4282 | 29.3872 | 29.3451 | 29.303 | 29.2666 | 29.2308 | 29.1932 | 29.1209 | 28.8597 | 28.6626 | 28.6104 | 29.7599 | 29.7475 | 29.7134 | 29.6698 | 29.621 | 29.5709 | 29.5208 | 29.4775 | 29.4349 | 29.4038 | 29.3795 | 29.292 | 29.2026 | 29.1147
| CUMMING STREET | LW |  |  |  | 31.4336 | 31.4248 | 31.3982 | 31.3625 | 31.3233 | 31.2832 | 31.2423 | 31.2073 | 31.1737 | 31.1403 | 31.0742 | 30.8262 | 30.569 | 30.3167 | 29.504 | 29.4914 | 29.4533 | 29.4021 | 29.3458 | 29.2883 | 29.2297 | 29.1795 | 29.1313 | 29.0834 | 28.9886 | 28.6771 | 28.6104 | 28.6104 | 29.7599 | 29.7449 | 29.6996 | 29.6386 | 29.5718 | 29.5033 | 29.4336 | 29.3992 | 29.383 | 29.367 | 29.3352 | 29.2159 | 29.0922 | 28.996
| CUMMING STREET | ST |  |  |  | 31.4358 | 31.4322 | 31.4231 | 31.4075 | 31.3871 | 31.3592 | 31.3314 | 31.3065 | 31.2812 | 31.2553 | 31.2054 | 31.0911 | 30.9772 | 30.8643 | 29.5073 | 29.5021 | 29.489 | 29.4667 | 29.4374 | 29.3973 | 29.3576 | 29.3219 | 29.2856 | 29.2483 | 29.1768 | 29.0128 | 28.8495 | 28.697 | 29.7638 | 29.7576 | 29.7421 | 29.7155 | 29.6806 | 29.633 | 29.5857 | 29.5432 | 29.5 | 29.4557 | 29.3983 | 29.3433 | 29.2886 | 29.2343
| CUMMING STREET | FS |  |  |  | 31.4375 | 31.437 | 31.436 | 31.4313 | 31.4251 | 31.4155 | 31.4058 | 31.395 | 31.3852 | 31.3754 | 31.3563 | 31.3121 | 31.2729 | 31.2345 | 29.5096 | 29.5089 | 29.5075 | 29.5008 | 29.4919 | 29.4781 | 29.4642 | 29.4488 | 29.4347 | 29.4206 | 29.3932 | 29.3298 | 29.2735 | 29.2186 | 29.7666 | 29.7657 | 29.7641 | 29.7561 | 29.7454 | 29.7291 | 29.7125 | 29.6942 | 29.6774 | 29.6607 | 29.6281 | 29.5526 | 29.4857 | 29.4203
ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 7.5498 | 7.2764 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 7.7228 | 7.3878 | 7.0559 | 6.7338 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 7.6945 | 7.3636 | 7.0425
| DALCHONZIE | CT |  |  |  | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 7.7806 | 7.5755 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 7.5773 | 7.3278 | 7.0862 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 7.6346 | 7.3938
| DALCHONZIE | LW |  |  |  | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 7.5498 | 7.2764 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 7.7228 | 7.3878 | 7.0559 | 6.7338 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 7.6945 | 7.3636 | 7.0425
| DALCHONZIE | ST |  |  |  | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 7.7921 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442
| DALCHONZIE | FS |  |  |  | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 9.1137 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.5411 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442 | 8.8442
NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.4466 | 14.2204 | 14.052 | 13.905 | 13.7604 | 15.1503 | 15.143 | 15.1312 | 15.1171 | 15.1017 | 15.0852 | 15.0655 | 13.7123 | 13.5344 | 13.3476 | 13.0807 | 12.8821 | 12.7087 | 12.5381 | 15.2217 | 15.213 | 15.1988 | 15.1817 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7402 | 13.5582 | 13.2983 | 13.1048 | 12.9359 | 12.7697
| DALCROSS | CT |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.5006 | 14.2536 | 14.0578 | 13.9438 | 13.8439 | 15.1503 | 15.1435 | 15.1323 | 15.1195 | 15.1055 | 15.0899 | 15.0718 | 13.7704 | 13.5979 | 13.4113 | 13.1199 | 12.8889 | 12.7544 | 12.6366 | 15.2217 | 15.2135 | 15.2001 | 15.1847 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.6203 | 13.3365 | 13.1115 | 12.9805 | 12.8657
| DALCROSS | LW |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.4466 | 14.2204 | 14.052 | 13.905 | 13.7604 | 15.1503 | 15.143 | 15.1312 | 15.1171 | 15.1017 | 15.0852 | 15.0655 | 13.7123 | 13.5344 | 13.3476 | 13.0807 | 12.8821 | 12.7087 | 12.5381 | 15.2218 | 15.213 | 15.1988 | 15.1817 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7402 | 13.5582 | 13.2983 | 13.1048 | 12.9359 | 12.7697
| DALCROSS | ST |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.5205 | 15.153 | 15.1491 | 15.1437 | 15.1369 | 15.1287 | 15.1204 | 15.1104 | 15.099 | 15.0861 | 15.0715 | 13.7526 | 13.5945 | 13.5094 | 13.4348 | 15.2251 | 15.2203 | 15.2139 | 15.2056 | 15.1958 | 15.1858 | 15.1737 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7987 | 13.7158 | 13.6432
| DALCROSS | FS |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 15.1552 | 15.153 | 15.1507 | 15.1476 | 15.1442 | 15.1406 | 15.1364 | 15.1318 | 15.1266 | 15.121 | 15.1126 | 15.1034 | 15.0989 | 15.0956 | 15.2277 | 15.225 | 15.2222 | 15.2185 | 15.2144 | 15.2101 | 15.2051 | 15.1995 | 15.1933 | 15.1865 | 15.1764 | 15.1727 | 15.1727 | 15.1727
TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.096899 | 0.095627 | 0.0938 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | -5.099e-05 | -0.037117 | -0.073672 | 0.11418 | 0.11375 | 0.11312 | 0.11234 | 0.11199 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | -0.029962 | -0.066528
| DALMALLY | CT |  |  |  | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.096978 | 0.095861 | 0.094352 | 0.092601 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | -0.0080774 | -0.033488 | 0.1142 | 0.11383 | 0.11331 | 0.1127 | 0.11245 | 0.11221 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | -0.00091231 | -0.026331
| DALMALLY | LW |  |  |  | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.096899 | 0.095627 | 0.0938 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | -5.099e-05 | -0.037117 | -0.073672 | 0.11418 | 0.11375 | 0.11312 | 0.11234 | 0.11199 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | -0.029962 | -0.066528
| DALMALLY | ST |  |  |  | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.097553 | 0.096523 | 0.095646 | 0.094548 | 0.094068 | 0.093091 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | 0.092047 | -0.0038353 | 0.1143 | 0.11406 | 0.11376 | 0.11338 | 0.11321 | 0.11287 | 0.11249 | 0.1121 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195 | 0.11195
| DALMALLY | FS |  |  |  | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.17677 | 0.098084 | 0.097345 | 0.09668 | 0.096156 | 0.095954 | 0.095588 | 0.095222 | 0.094783 | 0.09436 | 0.093948 | 0.093157 | 0.092047 | 0.092047 | 0.092047 | 0.1144 | 0.11426 | 0.11412 | 0.11394 | 0.11387 | 0.11374 | 0.11361 | 0.11346 | 0.11331 | 0.11317 | 0.11289 | 0.11232 | 0.11195 | 0.11195
INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | NO | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1724 | 17.1175 | 16.9711 | 16.7931 | 16.6355 | 16.6052 | 16.5812 | 16.5575 | 16.532 | 16.5066 | 16.4566 | 16.3657 | 11.046 | 10.0182 | 17.4302 | 17.4086 | 17.351 | 17.2886 | 17.2455 | 17.2032 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.167 | 10.1271
| DALNEIGH | CT |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1732 | 17.1282 | 17.0197 | 16.8964 | 16.7805 | 16.6693 | 16.6189 | 16.6023 | 16.5844 | 16.5668 | 16.5323 | 16.4676 | 16.3985 | 11.7118 | 17.4305 | 17.4129 | 17.3702 | 17.3216 | 17.2853 | 17.2561 | 17.227 | 17.198 | 17.167 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.8408
| DALNEIGH | LW |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1724 | 17.1175 | 16.9711 | 16.7931 | 16.6355 | 16.6052 | 16.5812 | 16.5575 | 16.532 | 16.5066 | 16.4566 | 16.3657 | 11.046 | 10.0182 | 17.4302 | 17.4086 | 17.351 | 17.2886 | 17.2455 | 17.2032 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.167 | 10.1271
| DALNEIGH | ST |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1902 | 17.1699 | 17.1272 | 17.0633 | 16.9912 | 16.936 | 16.8809 | 16.8262 | 16.7677 | 16.7111 | 16.6263 | 16.5871 | 16.5457 | 16.5049 | 17.4372 | 17.4293 | 17.4125 | 17.3873 | 17.3589 | 17.3372 | 17.3155 | 17.297 | 17.2821 | 17.2676 | 17.2398 | 17.1717 | 17.1656 | 17.1656
| DALNEIGH | FS |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.2002 | 17.1953 | 17.1897 | 17.1696 | 17.148 | 17.1294 | 17.1108 | 17.0872 | 17.0641 | 17.0414 | 16.9977 | 16.8959 | 16.7945 | 16.6944 | 17.4412 | 17.4392 | 17.437 | 17.4291 | 17.4206 | 17.4133 | 17.406 | 17.3967 | 17.3876 | 17.3787 | 17.3615 | 17.3214 | 17.2889 | 17.2634
COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | YES | 3.5129 | 3.5123 | 3.5106 | 3.5085 | 3.5064 | 3.5044 | 3.5024 | 3.5004 | 3.4983 | 3.4963 | 3.4921 | 3.403 | 3.3928 | 2.4424 | 3.3631 | 3.3611 | 3.3551 | 3.3478 | 3.3406 | 3.3336 | 3.3267 | 3.32 | 3.3127 | 3.3074 | 3.3046 | 2.492 | 2.3582 | 2.2261 | 3.3305 | 3.3297 | 3.3277 | 3.3251 | 3.3226 | 3.3202 | 3.3178 | 3.3155 | 3.3129 | 3.3104 | 3.3054 | 3.2075 | 2.4148 | 2.291
| DALRULZION | CT |  |  |  | 3.5129 | 3.5124 | 3.5111 | 3.5096 | 3.5082 | 3.5068 | 3.5054 | 3.504 | 3.5025 | 3.5011 | 3.4982 | 3.412 | 3.4049 | 3.3979 | 3.3631 | 3.3614 | 3.3569 | 3.3518 | 3.3468 | 3.3418 | 3.337 | 3.3323 | 3.3272 | 3.3221 | 3.3121 | 3.253 | 3.2482 | 2.4258 | 3.3305 | 3.3299 | 3.3283 | 3.3265 | 3.3248 | 3.3231 | 3.3214 | 3.3197 | 3.318 | 3.3162 | 3.3127 | 3.2184 | 3.2099 | 2.4783
| DALRULZION | LW |  |  |  | 3.5129 | 3.5123 | 3.5106 | 3.5085 | 3.5064 | 3.5044 | 3.5024 | 3.5004 | 3.4983 | 3.4963 | 3.4921 | 3.403 | 3.3928 | 2.4424 | 3.3631 | 3.3611 | 3.3551 | 3.3478 | 3.3406 | 3.3336 | 3.3267 | 3.32 | 3.3127 | 3.3074 | 3.3046 | 2.492 | 2.3582 | 2.2261 | 3.3305 | 3.3297 | 3.3277 | 3.3251 | 3.3226 | 3.3202 | 3.3178 | 3.3155 | 3.3129 | 3.3104 | 3.3054 | 3.2075 | 2.4148 | 2.291
| DALRULZION | ST |  |  |  | 3.5131 | 3.5129 | 3.5123 | 3.5115 | 3.5106 | 3.5094 | 3.5083 | 3.5072 | 3.5061 | 3.5049 | 3.5027 | 3.4577 | 3.4525 | 3.4472 | 3.3638 | 3.363 | 3.3612 | 3.3584 | 3.355 | 3.3511 | 3.3472 | 3.3435 | 3.3394 | 3.3355 | 3.3277 | 3.2826 | 3.279 | 3.2755 | 3.3307 | 3.3304 | 3.3298 | 3.3288 | 3.3276 | 3.3263 | 3.3249 | 3.3236 | 3.3222 | 3.3208 | 3.3181 | 3.2687 | 3.2624 | 3.2561
| DALRULZION | FS |  |  |  | 3.5132 | 3.5132 | 3.5131 | 3.5129 | 3.5126 | 3.5123 | 3.512 | 3.5116 | 3.5112 | 3.5108 | 3.51 | 3.5082 | 3.5065 | 3.505 | 3.3641 | 3.364 | 3.3639 | 3.3631 | 3.3621 | 3.361 | 3.3599 | 3.3585 | 3.3571 | 3.3558 | 3.3531 | 3.3469 | 3.3411 | 3.3358 | 3.3308 | 3.3308 | 3.3307 | 3.3304 | 3.3301 | 3.3297 | 3.3294 | 3.3289 | 3.3284 | 3.3279 | 3.327 | 3.3248 | 3.3228 | 3.3209
BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.40096 | 0.39964 | 0.39571 | 0.3908 | 0.38593 | 0.38115 | 0.37644 | 0.37182 | 0.36808 | 0.36665 | 0.36382 | 0.35706 | 0.35463 | 0.35223 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313
| DALWHINNIE | CT |  |  |  | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.40096 | 0.39987 | 0.39693 | 0.39352 | 0.39014 | 0.38681 | 0.38354 | 0.38032 | 0.37683 | 0.37336 | 0.36798 | 0.36316 | 0.35824 | 0.35584 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313
| DALWHINNIE | LW |  |  |  | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.40096 | 0.39964 | 0.39571 | 0.3908 | 0.38593 | 0.38115 | 0.37644 | 0.37182 | 0.36808 | 0.36665 | 0.36382 | 0.35706 | 0.35463 | 0.35223 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313
| DALWHINNIE | ST |  |  |  | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.40135 | 0.40087 | 0.39972 | 0.39789 | 0.39568 | 0.3935 | 0.39136 | 0.38926 | 0.38698 | 0.38474 | 0.38035 | 0.36973 | 0.36588 | 0.36284 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313
| DALWHINNIE | FS |  |  |  | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.45741 | 0.40157 | 0.40152 | 0.40145 | 0.40096 | 0.40036 | 0.39966 | 0.39896 | 0.39806 | 0.39716 | 0.39628 | 0.39455 | 0.39043 | 0.38652 | 0.38289 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313 | 0.42313
WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 30.1974 | 30.1068 | 29.9678 | 29.8279 | 29.6922 | 29.5606 | 29.433 | 29.3096 | 29.2145 | 29.1578 | 29.1062 | 28.9728 | 28.8325 | 28.6862 | 27.4003 | 27.317 | 27.1822 | 27.0443 | 26.9219 | 26.8109 | 26.7032 | 26.599 | 26.5173 | 26.4533 | 26.3267 | 25.6242 | 25.1964 | 25.0014 | 26.263 | 26.1707 | 26.0258 | 25.8789 | 25.7363 | 25.5979 | 25.4637 | 25.3337 | 25.2309 | 25.1498 | 24.9893 | 24.7551 | 24.6514 | 24.5409
| DENBURN | CT |  |  |  | 30.1974 | 30.1068 | 29.9678 | 29.8279 | 29.6922 | 29.5606 | 29.433 | 29.3096 | 29.2145 | 29.1578 | 29.1062 | 28.9728 | 28.8325 | 28.6862 | 27.4003 | 27.317 | 27.1822 | 27.0443 | 26.9219 | 26.8109 | 26.7032 | 26.599 | 26.5173 | 26.4533 | 26.3267 | 25.9403 | 25.5445 | 25.1504 | 26.263 | 26.1707 | 26.0258 | 25.8789 | 25.7363 | 25.5979 | 25.4637 | 25.3337 | 25.2309 | 25.1498 | 24.9893 | 24.7551 | 24.6514 | 24.5409
| DENBURN | LW |  |  |  | 30.2989 | 30.2595 | 30.1679 | 30.057 | 29.9464 | 29.8363 | 29.7831 | 29.7533 | 29.7201 | 29.6862 | 29.617 | 29.4084 | 29.1775 | 28.9352 | 27.4849 | 27.4412 | 27.3344 | 27.2134 | 27.1154 | 27.0178 | 26.9208 | 26.8245 | 26.7196 | 26.6148 | 26.402 | 25.6242 | 25.1964 | 25.0014 | 26.3624 | 26.3188 | 26.215 | 26.0892 | 25.9639 | 25.8395 | 25.7157 | 25.593 | 25.4726 | 25.4488 | 25.3997 | 25.269 | 25.1176 | 24.9536
| DENBURN | ST |  |  |  | 30.3196 | 30.2991 | 30.2557 | 30.1914 | 30.1159 | 30.03 | 29.9459 | 29.8637 | 29.849 | 29.8325 | 29.8005 | 29.7169 | 29.6373 | 29.554 | 27.5041 | 27.4806 | 27.4296 | 27.353 | 27.263 | 27.1862 | 27.111 | 27.0375 | 26.9588 | 26.8793 | 26.7242 | 26.3307 | 25.9443 | 25.5593 | 26.3836 | 26.3605 | 26.3111 | 26.2376 | 26.1509 | 26.0524 | 25.956 | 25.8617 | 25.7608 | 25.6589 | 25.5597 | 25.5175 | 25.4787 | 25.4358
| DENBURN | FS |  |  |  | 30.3234 | 30.3162 | 30.3085 | 30.2886 | 30.2666 | 30.2346 | 30.2029 | 30.1646 | 30.1269 | 30.0899 | 30.018 | 29.8381 | 29.722 | 29.6653 | 27.5104 | 27.5036 | 27.4964 | 27.4751 | 27.4513 | 27.4152 | 27.3794 | 27.3355 | 27.2923 | 27.2499 | 27.1808 | 27.0228 | 26.8682 | 26.7201 | 26.3888 | 26.3813 | 26.3734 | 26.3518 | 26.3277 | 26.292 | 26.2566 | 26.2135 | 26.1712 | 26.1296 | 26.0488 | 25.8479 | 25.6515 | 25.4634
TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42445123 | YES | YES | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.5483 | 5.5406 | 5.5284 | 5.5136 | 5.5002 | 5.4875 | 5.475 | 5.4629 | 5.4497 | 5.4366 | 5.4201 | 3.7031 | 2.8797 | 2.7079 | 3.6959 | 3.6902 | 3.6813 | 3.6704 | 3.6605 | 3.6508 | 3.6398 | 3.6291 | 3.6175 | 3.6059 | 3.5831 | 2.5424 | 1.5472 | 1.37
| DERVAIG | CT |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.5485 | 5.542 | 5.5328 | 5.5223 | 5.5127 | 5.5033 | 5.4936 | 5.4845 | 5.4747 | 5.4653 | 5.4472 | 3.7782 | 2.9995 | 2.8637 | 3.696 | 3.6912 | 3.6844 | 3.6767 | 3.6697 | 3.6628 | 3.6557 | 3.6482 | 3.6395 | 3.6313 | 3.6153 | 2.6284 | 1.6708 | 1.5307
| DERVAIG | LW |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.5483 | 5.5406 | 5.5284 | 5.5136 | 5.5002 | 5.4875 | 5.475 | 5.4629 | 5.4497 | 5.4366 | 5.4201 | 3.7031 | 2.8797 | 2.7079 | 3.6959 | 3.6902 | 3.6813 | 3.6704 | 3.6605 | 3.6508 | 3.6398 | 3.6291 | 3.6175 | 3.6059 | 3.5831 | 2.5424 | 1.5472 | 1.37
| DERVAIG | ST |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.5802 | 3.7736 | 3.7736 | 5.5508 | 5.547 | 5.543 | 5.5371 | 5.5307 | 5.5174 | 5.5041 | 5.4913 | 5.4775 | 5.4642 | 5.4385 | 5.2017 | 3.771 | 3.7 | 3.6976 | 3.6949 | 3.6919 | 3.6876 | 3.6829 | 3.6732 | 3.6634 | 3.654 | 3.642 | 3.6303 | 3.6076 | 3.112 | 2.6226 | 2.5412
| DERVAIG | FS |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.5525 | 5.5508 | 5.5501 | 5.5481 | 5.5461 | 5.5417 | 5.5373 | 5.5318 | 5.5264 | 5.5211 | 5.5108 | 5.4868 | 5.4645 | 5.4437 | 3.6989 | 3.6977 | 3.6971 | 3.6956 | 3.6942 | 3.691 | 3.6878 | 3.6837 | 3.6797 | 3.6758 | 3.6683 | 3.6503 | 3.6305 | 3.6122
BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4188 | 12.6225 | 11.8438 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.8298 | 11.8864 | 10.9639 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7139 | 12.2267 | 11.337 | 10.4383
| DINGWALL | CT |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4941 | 12.9186 | 12.353 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.919 | 12.2372 | 11.5671 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7139 | 12.3108 | 11.6678 | 11.0359
| DINGWALL | LW |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4188 | 12.6225 | 11.8438 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.8298 | 11.8864 | 10.9639 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 12.2267 | 11.337 | 10.4383
| DINGWALL | ST |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.1797 | 14.1797 | 14.1797 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.5124 | 13.5124 | 13.5124 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.4088 | 13.4088 | 13.0919
| DINGWALL | FS |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262
CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.32367 | 0.32218 | 0.31953 | 0.31728 | 0.31629 | 0.31533 | 0.3144 | 0.31349 | 0.3125 | 0.31152 | 0.30961 | 0.30184 | 0.30184 | 0.30184 | 0.37564 | 0.37524 | 0.37475 | 0.3743 | 0.37396 | 0.37363 | 0.3733 | 0.37299 | 0.37264 | 0.3723 | 0.37164 | 0.36754 | 0.3671 | 0.3671
| DIPPEN | CT |  |  |  | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.32371 | 0.32246 | 0.32034 | 0.31858 | 0.31737 | 0.31664 | 0.31583 | 0.31502 | 0.31423 | 0.3135 | 0.31216 | 0.30184 | 0.30184 | 0.30184 | 0.37566 | 0.37529 | 0.3749 | 0.37458 | 0.37434 | 0.37408 | 0.3738 | 0.37352 | 0.37324 | 0.37299 | 0.37252 | 0.36754 | 0.3671 | 0.3671
| DIPPEN | LW |  |  |  | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.32367 | 0.32218 | 0.31953 | 0.31728 | 0.31629 | 0.31533 | 0.3144 | 0.31349 | 0.3125 | 0.31152 | 0.30961 | 0.30184 | 0.30184 | 0.30184 | 0.37564 | 0.37524 | 0.37475 | 0.3743 | 0.37396 | 0.37363 | 0.3733 | 0.37299 | 0.37264 | 0.3723 | 0.37164 | 0.36836 | 0.3671 | 0.3671
| DIPPEN | ST |  |  |  | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.32415 | 0.32338 | 0.32227 | 0.32125 | 0.32037 | 0.31869 | 0.31719 | 0.31627 | 0.31533 | 0.31445 | 0.3128 | 0.30882 | 0.3049 | 0.30184 | 0.37587 | 0.37549 | 0.37525 | 0.37507 | 0.3749 | 0.3746 | 0.37427 | 0.37395 | 0.37363 | 0.37332 | 0.37274 | 0.37136 | 0.37 | 0.36864
| DIPPEN | FS |  |  |  | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.57967 | 0.32451 | 0.32412 | 0.32371 | 0.32331 | 0.32302 | 0.32242 | 0.32183 | 0.3211 | 0.32039 | 0.31969 | 0.31835 | 0.31636 | 0.3149 | 0.31353 | 0.37604 | 0.37585 | 0.37565 | 0.37546 | 0.37539 | 0.37528 | 0.37517 | 0.37504 | 0.37491 | 0.37478 | 0.37453 | 0.37399 | 0.37348 | 0.373
BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 8.5193 | 8.5177 | 8.515 | 8.5117 | 8.5086 | 8.5054 | 8.5001 | 8.497 | 8.4936 | 8.4903 | 8.4838 | 8.4609 | 8.4375 | 8.4171 | 7.7368 | 7.7286 | 7.715 | 7.6983 | 7.6819 | 7.6659 | 7.6384 | 7.6225 | 7.6117 | 7.6077 | 7.6039 | 7.6039 | 7.6039 | 5.8841 | 8.2083 | 8.2066 | 8.2037 | 8.2001 | 8.1966 | 8.1932 | 8.1873 | 8.1839 | 8.1802 | 8.1766 | 8.1695 | 8.1444 | 8.1187 | 8.0936
| DORNOCH | CT |  |  |  | 8.5193 | 8.5179 | 8.516 | 8.5138 | 8.5116 | 8.5094 | 8.5053 | 8.5031 | 8.5007 | 8.4983 | 8.4936 | 8.4761 | 8.4585 | 8.4411 | 7.7368 | 7.7301 | 7.7202 | 7.7088 | 7.6975 | 7.6862 | 7.6651 | 7.6538 | 7.6415 | 7.6292 | 7.6117 | 7.6039 | 7.6039 | 7.6039 | 8.2084 | 8.2069 | 8.2048 | 8.2024 | 8.2 | 8.1975 | 8.193 | 8.1906 | 8.188 | 8.1853 | 8.1802 | 8.1611 | 8.1417 | 8.1227
| DORNOCH | LW |  |  |  | 8.5193 | 8.5177 | 8.515 | 8.5117 | 8.5086 | 8.5054 | 8.5001 | 8.497 | 8.4936 | 8.4903 | 8.4838 | 8.4609 | 8.4375 | 8.4171 | 7.7368 | 7.7286 | 7.715 | 7.6983 | 7.6819 | 7.6659 | 7.6384 | 7.6225 | 7.6117 | 7.6077 | 7.6039 | 7.6039 | 7.6039 | 5.8841 | 8.2083 | 8.2066 | 8.2037 | 8.2001 | 8.1966 | 8.1932 | 8.1873 | 8.1839 | 8.1802 | 8.1766 | 8.1695 | 8.1444 | 8.1187 | 8.0936
| DORNOCH | ST |  |  |  | 8.5195 | 8.5188 | 8.5181 | 8.5169 | 8.5156 | 8.5137 | 8.5105 | 8.5087 | 8.5067 | 8.5047 | 8.5008 | 8.4916 | 8.4825 | 8.4734 | 7.7382 | 7.7346 | 7.7308 | 7.7249 | 7.7179 | 7.7082 | 7.6921 | 7.6826 | 7.6723 | 7.6621 | 7.6423 | 7.6093 | 7.6039 | 7.6039 | 8.2087 | 8.2079 | 8.2071 | 8.2058 | 8.2043 | 8.2022 | 8.1988 | 8.1968 | 8.1946 | 8.1924 | 8.1881 | 8.178 | 8.168 | 8.1581
| DORNOCH | FS |  |  |  | 8.5197 | 8.5194 | 8.5193 | 8.519 | 8.5185 | 8.5179 | 8.5168 | 8.516 | 8.5152 | 8.5144 | 8.5128 | 8.5092 | 8.5059 | 8.5027 | 7.739 | 7.7375 | 7.7371 | 7.7353 | 7.7331 | 7.7299 | 7.7241 | 7.7199 | 7.7158 | 7.7117 | 7.7038 | 7.6855 | 7.6684 | 7.6521 | 8.2088 | 8.2085 | 8.2084 | 8.208 | 8.2076 | 8.2069 | 8.2056 | 8.2048 | 8.2039 | 8.203 | 8.2013 | 8.1974 | 8.1937 | 8.1902
CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 2.9796 | 2.9787 | 2.9761 | 2.9729 | 2.9697 | 2.9666 | 2.9636 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.4373 | 2.3602 | 2.2841 | 2.9741 | 2.9696 | 2.9566 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4206 | 2.3296 | 2.2399 | 2.9986 | 2.9975 | 2.9943 | 2.9905 | 2.9867 | 2.983 | 2.9793 | 2.9757 | 2.9719 | 2.968 | 2.9604 | 2.4256 | 2.3346 | 2.2448
| DOUGLAS PIER | CT |  |  |  | 2.9796 | 2.9788 | 2.9769 | 2.9746 | 2.9724 | 2.9702 | 2.968 | 2.9659 | 2.9637 | 2.9624 | 2.9624 | 2.9624 | 2.4641 | 2.3888 | 2.9741 | 2.9703 | 2.9605 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4522 | 2.3634 | 2.9986 | 2.9977 | 2.9953 | 2.9926 | 2.9899 | 2.9873 | 2.9847 | 2.9822 | 2.9794 | 2.9767 | 2.9713 | 2.9632 | 2.4572 | 2.3683
| DOUGLAS PIER | LW |  |  |  | 2.9796 | 2.9787 | 2.9761 | 2.9729 | 2.9697 | 2.9666 | 2.9636 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.4373 | 2.3602 | 2.2841 | 2.9741 | 2.9696 | 2.9566 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4206 | 2.3296 | 2.2399 | 2.9986 | 2.9975 | 2.9943 | 2.9905 | 2.9867 | 2.983 | 2.9793 | 2.9757 | 2.9719 | 2.968 | 2.9604 | 2.4256 | 2.3346 | 2.2448
| DOUGLAS PIER | ST |  |  |  | 2.98 | 2.9799 | 2.9798 | 2.9796 | 2.9793 | 2.9787 | 2.9781 | 2.9775 | 2.9768 | 2.9762 | 2.975 | 2.972 | 2.9691 | 2.9662 | 2.9762 | 2.9759 | 2.9751 | 2.974 | 2.9726 | 2.9696 | 2.9666 | 2.9636 | 2.9605 | 2.9573 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9991 | 2.999 | 2.9988 | 2.9985 | 2.9982 | 2.9975 | 2.9967 | 2.996 | 2.9953 | 2.9945 | 2.993 | 2.9895 | 2.986 | 2.9825
| DOUGLAS PIER | FS |  |  |  | 2.98 | 2.98 | 2.98 | 2.98 | 2.9799 | 2.9797 | 2.9795 | 2.9792 | 2.979 | 2.9787 | 2.9782 | 2.9771 | 2.976 | 2.975 | 2.9763 | 2.9763 | 2.9763 | 2.9759 | 2.9756 | 2.9745 | 2.9735 | 2.9722 | 2.971 | 2.9697 | 2.9673 | 2.9616 | 2.9563 | 2.9536 | 2.9991 | 2.9991 | 2.9991 | 2.999 | 2.9989 | 2.9987 | 2.9984 | 2.9981 | 2.9978 | 2.9975 | 2.9969 | 2.9955 | 2.9943 | 2.9931
DOUNREAY | DOUNREAY | MINIMUM HEADROOM | NC 98156665 | NO | NO | 19.8405 | 19.7483 | 19.6286 | 19.5143 | 19.4088 | 19.3072 | 19.2095 | 19.1156 | 19.0711 | 19.0478 | 19.0021 | 18.899 | 18.8067 | 18.7131 | 18.5071 | 18.452 | 18.3792 | 18.3091 | 18.2413 | 18.176 | 18.1131 | 18.0527 | 18.0221 | 18.0045 | 17.97 | 17.9026 | 17.8417 | 17.7878 | 18.6926 | 18.6095 | 18.5028 | 18.4011 | 18.3031 | 18.2087 | 18.1179 | 18.0308 | 17.9906 | 17.9707 | 17.9315 | 17.8365 | 17.7552 | 17.6726
| DOUNREAY | CT |  |  |  | 19.8405 | 19.7483 | 19.6286 | 19.5143 | 19.4088 | 19.3072 | 19.2095 | 19.1156 | 19.0711 | 19.0478 | 19.0021 | 18.899 | 18.8067 | 18.7131 | 18.5071 | 18.452 | 18.3792 | 18.3091 | 18.2413 | 18.176 | 18.1131 | 18.0527 | 18.0221 | 18.0045 | 17.97 | 17.9026 | 17.8417 | 17.7878 | 18.6926 | 18.6095 | 18.5028 | 18.4011 | 18.3031 | 18.2087 | 18.1179 | 18.0308 | 17.9906 | 17.9707 | 17.9315 | 17.8365 | 17.7552 | 17.6726
| DOUNREAY | LW |  |  |  | 19.9713 | 19.9547 | 19.933 | 19.9082 | 19.8814 | 19.8529 | 19.8229 | 19.7916 | 19.7621 | 19.7336 | 19.6772 | 19.5412 | 19.4088 | 19.2704 | 18.584 | 18.573 | 18.5567 | 18.5377 | 18.5177 | 18.4967 | 18.4749 | 18.4524 | 18.4307 | 18.4086 | 18.3636 | 18.2744 | 18.1873 | 18.0967 | 18.8122 | 18.7984 | 18.7824 | 18.7643 | 18.7445 | 18.723 | 18.7 | 18.6757 | 18.6535 | 18.6307 | 18.5836 | 18.4583 | 18.3365 | 18.209
| DOUNREAY | ST |  |  |  | 19.9918 | 19.9861 | 19.9778 | 19.9691 | 19.9602 | 19.9516 | 19.9432 | 19.9351 | 19.9273 | 19.9161 | 19.8946 | 19.8457 | 19.802 | 19.7615 | 18.5964 | 18.5926 | 18.5867 | 18.5799 | 18.5726 | 18.5671 | 18.5618 | 18.5566 | 18.5515 | 18.5444 | 18.5309 | 18.4999 | 18.472 | 18.446 | 18.8305 | 18.8257 | 18.8194 | 18.8132 | 18.8071 | 18.7998 | 18.7926 | 18.7857 | 18.779 | 18.7693 | 18.7507 | 18.7084 | 18.6709 | 18.6363
| DOUNREAY | FS |  |  |  | 19.9868 | 19.9798 | 19.9727 | 19.9618 | 19.951 | 19.9407 | 19.9307 | 19.9206 | 19.9108 | 19.9011 | 19.882 | 19.8256 | 19.776 | 19.7299 | 18.5937 | 18.5895 | 18.5852 | 18.5784 | 18.5714 | 18.5653 | 18.5592 | 18.5531 | 18.5471 | 18.5412 | 18.5297 | 18.4957 | 18.4657 | 18.4379 | 18.8257 | 18.8194 | 18.813 | 18.8036 | 18.7943 | 18.7851 | 18.776 | 18.7671 | 18.7583 | 18.7496 | 18.7326 | 18.682 | 18.6375 | 18.5963
ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 3.1248 | 3.074 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.0901 | 3.0304 | 3.9314 | 3.9312 | 3.9305 | 3.9297 | 3.929 | 3.9282 | 3.9275 | 3.9267 | 3.9254 | 3.9241 | 3.9215 | 3.9148 | 3.6265 | 3.2846
| DRIMORE | CT |  |  |  | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 3.1609 | 3.124 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.1325 | 3.0892 | 3.9314 | 3.9312 | 3.9307 | 3.9302 | 3.9296 | 3.9291 | 3.9286 | 3.9281 | 3.9275 | 3.927 | 3.9259 | 3.9171 | 3.6303 | 3.6264
| DRIMORE | LW |  |  |  | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 3.1248 | 3.074 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.0901 | 3.0304 | 3.9314 | 3.9312 | 3.9305 | 3.9297 | 3.929 | 3.9282 | 3.9275 | 3.9267 | 3.926 | 3.9252 | 3.9237 | 3.9148 | 3.6265 | 3.2846
| DRIMORE | ST |  |  |  | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 3.9765 | 3.9765 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.2648 | 3.2393 | 3.9315 | 3.9314 | 3.9312 | 3.9309 | 3.9305 | 3.9292 | 3.928 | 3.9267 | 3.9254 | 3.9241 | 3.9215 | 3.9171 | 3.7733 | 3.771
| DRIMORE | FS |  |  |  | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 4.1124 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.852 | 3.9315 | 3.9315 | 3.9315 | 3.9314 | 3.9313 | 3.9309 | 3.9304 | 3.9299 | 3.9293 | 3.9288 | 3.9278 | 3.9254 | 3.9231 | 3.921
CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | YES | 7.385 | 7.3836 | 7.3805 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6978 | 6.6968 | 6.6947 | 6.6922 | 6.6896 | 6.6872 | 6.6847 | 6.6823 | 6.6797 | 6.6772 | 6.6721 | 5.663 | 5.4282 | 5.1821 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 5.658 | 5.4141
| DRUMNADROCHIT | CT |  |  |  | 7.3851 | 7.384 | 7.3819 | 7.3795 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6979 | 6.6971 | 6.6957 | 6.694 | 6.6924 | 6.6908 | 6.6892 | 6.6877 | 6.686 | 6.6844 | 6.6811 | 6.6719 | 6.6625 | 5.5448 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
| DRUMNADROCHIT | LW |  |  |  | 7.385 | 7.3836 | 7.3805 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6978 | 6.6968 | 6.6947 | 6.6922 | 6.6896 | 6.6872 | 6.6847 | 6.6823 | 6.6797 | 6.6772 | 6.6721 | 5.663 | 5.4282 | 5.1821 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 5.658 | 5.4141
| DRUMNADROCHIT | ST |  |  |  | 7.3856 | 7.385 | 7.3841 | 7.3827 | 7.381 | 7.3793 | 7.3777 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6982 | 6.6978 | 6.6972 | 6.6962 | 6.6951 | 6.694 | 6.6928 | 6.6918 | 6.6906 | 6.6895 | 6.6873 | 6.6819 | 6.6764 | 6.671 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
| DRUMNADROCHIT | FS |  |  |  | 7.386 | 7.3858 | 7.3857 | 7.3853 | 7.3848 | 7.3842 | 7.3837 | 7.383 | 7.3823 | 7.3817 | 7.3804 | 7.3775 | 7.3775 | 7.3775 | 6.6985 | 6.6983 | 6.6983 | 6.698 | 6.6976 | 6.6973 | 6.6969 | 6.6964 | 6.696 | 6.6955 | 6.6947 | 6.6926 | 6.6907 | 6.6888 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | YES | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.080727 | 0.080503 | 0.079864 | 0.079083 | 0.078319 | 0.077571 | 0.07684 | 0.076124 | 0.075411 | 0.074831 | 0.073683 | 0.071945 | -0.0028968 | -0.029514 | 0.091011 | 0.090903 | 0.090592 | 0.090213 | 0.089842 | 0.089479 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | -0.014054
| DRUMRUNIE | CT |  |  |  | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.080727 | 0.080541 | 0.080061 | 0.079514 | 0.078978 | 0.078455 | 0.077942 | 0.077439 | 0.076897 | 0.076358 | 0.075368 | 0.071945 | 0.071945 | -0.0077928 | 0.091012 | 0.090921 | 0.090688 | 0.090422 | 0.090162 | 0.089908 | 0.089659 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465
| DRUMRUNIE | LW |  |  |  | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.080727 | 0.080503 | 0.079864 | 0.079083 | 0.078319 | 0.077571 | 0.07684 | 0.076124 | 0.075411 | 0.074831 | 0.073683 | 0.071945 | -0.0028968 | -0.029514 | 0.091011 | 0.090903 | 0.090592 | 0.090213 | 0.089842 | 0.089479 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | 0.089465 | -0.014054
| DRUMRUNIE | ST |  |  |  | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.080792 | 0.080709 | 0.080515 | 0.080215 | 0.079858 | 0.079439 | 0.07903 | 0.07863 | 0.0782 | 0.077776 | 0.076952 | 0.075122 | 0.073635 | 0.072685 | 0.091043 | 0.091003 | 0.090909 | 0.090763 | 0.090589 | 0.090386 | 0.090187 | 0.089993 | 0.089784 | 0.089578 | 0.089465 | 0.089465 | 0.089465 | 0.089465
| DRUMRUNIE | FS |  |  |  | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.14733 | 0.080831 | 0.08082 | 0.080805 | 0.080721 | 0.08062 | 0.080234 | 0.079849 | 0.079351 | 0.07886 | 0.078377 | 0.077457 | 0.075346 | 0.073804 | 0.072738 | 0.091062 | 0.091057 | 0.09105 | 0.091009 | 0.09096 | 0.090772 | 0.090585 | 0.090343 | 0.090105 | 0.08987 | 0.089465 | 0.089465 | 0.089465 | 0.089465
STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 5.8269 | 5.7909 | 5.7446 | 5.6961 | 5.6494 | 5.6045 | 5.5613 | 5.5198 | 5.493 | 5.4797 | 5.4535 | 5.3861 | 5.2802 | 4.9031 | 7.5733 | 7.5511 | 7.5212 | 7.489 | 7.4571 | 7.4255 | 7.3943 | 7.3642 | 7.3423 | 7.3276 | 7.2978 | 7.1724 | 5.7511 | 5.3678 | 5.8743 | 5.8293 | 5.7683 | 5.7023 | 5.6367 | 5.5715 | 5.5071 | 5.4448 | 5.399 | 5.3674 | 5.3034 | 5.0272 | 4.648 | 4.2352
| DRYMEN | CT |  |  |  | 5.8269 | 5.7909 | 5.7446 | 5.6961 | 5.6494 | 5.6045 | 5.5613 | 5.5198 | 5.493 | 5.4797 | 5.4535 | 5.3861 | 5.3077 | 5.044 | 7.5733 | 7.5511 | 7.5212 | 7.489 | 7.4571 | 7.4255 | 7.3943 | 7.3642 | 7.3423 | 7.3276 | 7.2978 | 7.1724 | 5.9197 | 5.6391 | 5.8743 | 5.8293 | 5.7683 | 5.7023 | 5.6367 | 5.5715 | 5.5071 | 5.4448 | 5.399 | 5.3674 | 5.3034 | 5.0272 | 4.7339 | 4.4331
| DRYMEN | LW |  |  |  | 5.8788 | 5.8728 | 5.8658 | 5.858 | 5.8494 | 5.8401 | 5.8301 | 5.8196 | 5.8059 | 5.7918 | 5.7629 | 5.6291 | 5.2802 | 4.9031 | 7.6024 | 7.5948 | 7.5786 | 7.5582 | 7.5368 | 7.5142 | 7.4908 | 7.4673 | 7.4405 | 7.4125 | 7.3557 | 7.1954 | 5.7511 | 5.3678 | 5.9326 | 5.9162 | 5.8802 | 5.8349 | 5.7872 | 5.737 | 5.6851 | 5.633 | 5.5738 | 5.5121 | 5.3867 | 5.0322 | 4.648 | 4.2352
| DRYMEN | ST |  |  |  | 5.8867 | 5.8846 | 5.8819 | 5.8792 | 5.8766 | 5.8734 | 5.8703 | 5.8673 | 5.8641 | 5.8595 | 5.8506 | 5.8258 | 5.8012 | 5.7711 | 7.6081 | 7.6051 | 7.5991 | 7.5904 | 7.58 | 7.5689 | 7.5576 | 7.5465 | 7.5345 | 7.521 | 7.494 | 7.4224 | 7.3519 | 7.279 | 5.9444 | 5.9379 | 5.9246 | 5.9052 | 5.8818 | 5.8569 | 5.8316 | 5.8067 | 5.7796 | 5.7495 | 5.6892 | 5.5293 | 5.3717 | 5.2097
| DRYMEN | FS |  |  |  | 5.8846 | 5.8819 | 5.8791 | 5.875 | 5.871 | 5.867 | 5.8631 | 5.8592 | 5.8554 | 5.8516 | 5.8442 | 5.8223 | 5.7984 | 5.7751 | 7.6077 | 7.6058 | 7.6038 | 7.5996 | 7.5949 | 7.5896 | 7.5841 | 7.5781 | 7.5721 | 7.5659 | 7.5535 | 7.5191 | 7.4831 | 7.4472 | 5.9439 | 5.94 | 5.9358 | 5.9268 | 5.9168 | 5.9052 | 5.8934 | 5.8802 | 5.867 | 5.8534 | 5.8262 | 5.7511 | 5.6726 | 5.5941
DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.2985 | 3.2345 | 3.1639 | 3.0932 | 2.9532 | 2.1784 | 1.9962 | 1.817 | 4.1087 | 4.1075 | 4.1041 | 4.0999 | 4.0958 | 4.0917 | 3.2333 | 3.1599 | 3.0803 | 3.0013 | 2.8448 | 2.2198 | 2.0051 | 1.794 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 3.2451 | 3.1686 | 3.0934 | 3.0121 | 2.9312 | 2.7711 | 1.9617 | 1.7533 | 1.5483
| DRYNOCH | CT |  |  |  | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.2698 | 3.1771 | 2.429 | 2.2833 | 2.138 | 4.1087 | 4.1078 | 4.1053 | 4.1025 | 4.0997 | 4.097 | 4.0943 | 4.0916 | 3.2536 | 3.2004 | 3.095 | 2.5161 | 2.3455 | 2.1722 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 3.2947 | 3.2441 | 3.1893 | 3.1349 | 3.0271 | 2.2547 | 2.0837 | 1.9154
| DRYNOCH | LW |  |  |  | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.2985 | 3.2345 | 3.1639 | 3.0932 | 2.9532 | 2.1784 | 1.9962 | 1.817 | 4.1087 | 4.1075 | 4.1041 | 4.0999 | 4.0958 | 4.0917 | 3.2333 | 3.1599 | 3.0803 | 3.0013 | 2.8448 | 2.2198 | 2.0051 | 1.794 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 3.2451 | 3.1686 | 3.0934 | 3.0121 | 2.9312 | 2.7711 | 1.9617 | 1.7533 | 1.5483
| DRYNOCH | ST |  |  |  | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.1173 | 3.042 | 2.9672 | 4.1092 | 4.1089 | 4.1084 | 4.1075 | 4.1065 | 4.1055 | 4.1046 | 4.1036 | 4.1027 | 4.1017 | 4.0998 | 3.1657 | 3.0793 | 2.9935 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 3.0093 | 2.9209 | 2.8331
| DRYNOCH | FS |  |  |  | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 3.7477 | 4.1093 | 4.1092 | 4.1092 | 4.1089 | 4.1086 | 4.1082 | 4.1079 | 4.1075 | 4.1071 | 4.1067 | 4.106 | 4.1042 | 4.1025 | 4.1009 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218 | 4.0218
KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 7.924 | 7.8307 | 7.7096 | 7.5916 | 7.4769 | 7.3663 | 7.2598 | 7.1572 | 7.0957 | 7.0641 | 7.0022 | 6.8392 | 6.6606 | 6.4708 | 8.9459 | 8.8601 | 8.736 | 8.6193 | 8.4964 | 8.3758 | 8.258 | 8.1413 | 8.0709 | 8.0238 | 7.9333 | 7.7275 | 7.6042 | 7.4763 | 8.2102 | 8.1046 | 7.9545 | 7.8144 | 7.7011 | 7.6026 | 7.5077 | 7.4164 | 7.3616 | 7.3333 | 7.278 | 7.1315 | 6.9712 | 6.8009
| DUFFTOWN | CT |  |  |  | 7.924 | 7.8307 | 7.7096 | 7.5916 | 7.4769 | 7.3663 | 7.2598 | 7.1572 | 7.0957 | 7.0641 | 7.0022 | 6.8392 | 6.6606 | 6.4708 | 8.9459 | 8.8601 | 8.736 | 8.6193 | 8.4964 | 8.3758 | 8.258 | 8.1413 | 8.0709 | 8.0238 | 7.9333 | 7.7275 | 7.6042 | 7.4763 | 8.2102 | 8.1046 | 7.9545 | 7.8144 | 7.7011 | 7.6026 | 7.5077 | 7.4164 | 7.3616 | 7.3333 | 7.278 | 7.1315 | 6.9712 | 6.8009
| DUFFTOWN | LW |  |  |  | 8.0577 | 8.0419 | 8.0221 | 8.0006 | 7.976 | 7.9494 | 7.9211 | 7.8911 | 7.8573 | 7.8225 | 7.7512 | 7.5493 | 7.3101 | 7.0378 | 9.0626 | 9.0446 | 9.0082 | 8.9745 | 8.9278 | 8.878 | 8.8249 | 8.7691 | 8.7231 | 8.6765 | 8.5827 | 8.1967 | 7.9055 | 7.7332 | 8.355 | 8.3336 | 8.2924 | 8.2537 | 8.2012 | 8.145 | 8.0953 | 8.0684 | 8.0382 | 8.0072 | 7.9435 | 7.7623 | 7.5479 | 7.3041
| DUFFTOWN | ST |  |  |  | 8.0783 | 8.0728 | 8.0649 | 8.0575 | 8.0495 | 8.0389 | 8.0285 | 8.0181 | 8.0085 | 7.9952 | 7.9698 | 7.9022 | 7.838 | 7.7653 | 9.0816 | 9.0753 | 9.0604 | 9.0484 | 9.0286 | 8.9938 | 8.9589 | 8.9227 | 8.8935 | 8.8596 | 8.7949 | 8.6419 | 8.4947 | 8.3411 | 8.3784 | 8.3708 | 8.3541 | 8.3403 | 8.3185 | 8.2807 | 8.2428 | 8.2037 | 8.1729 | 8.1609 | 8.138 | 8.0771 | 8.0192 | 7.9538
| DUFFTOWN | FS |  |  |  | 8.073 | 8.0659 | 8.0585 | 8.0478 | 8.037 | 8.0258 | 8.0148 | 8.0037 | 7.993 | 7.9825 | 7.9619 | 7.9017 | 7.8387 | 7.7773 | 9.0777 | 9.0713 | 9.0621 | 9.0512 | 9.0371 | 9.018 | 8.9987 | 8.9774 | 8.9594 | 8.9416 | 8.9067 | 8.8163 | 8.7287 | 8.6435 | 8.3734 | 8.3655 | 8.3547 | 8.3414 | 8.3249 | 8.3032 | 8.2813 | 8.2573 | 8.2368 | 8.2166 | 8.1768 | 8.0782 | 8.0218 | 7.9671
BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | NO | 19.7252 | 19.6535 | 19.5615 | 19.4775 | 19.3965 | 19.3185 | 19.2435 | 19.1715 | 19.132 | 19.1123 | 19.0737 | 11.5859 | 9.6145 | 7.6397 | 16.9594 | 16.8521 | 16.6504 | 16.4347 | 16.2534 | 16.0695 | 15.9192 | 15.8587 | 15.8165 | 11.0529 | 9.8225 | 7.6605 | 5.4411 | 3.1871 | 17.0346 | 16.946 | 16.8121 | 16.6785 | 16.5466 | 16.4156 | 16.2865 | 16.1612 | 11.3212 | 10.7361 | 9.486 | 7.2466 | 4.9439 | 2.6379
| DUNBLANE | CT |  |  |  | 19.7252 | 19.6535 | 19.5615 | 19.4775 | 19.3965 | 19.3185 | 19.2435 | 19.1715 | 19.132 | 19.1123 | 19.0737 | 18.9831 | 11.8759 | 10.4042 | 16.9594 | 16.8521 | 16.6504 | 16.4347 | 16.2534 | 16.0695 | 15.9192 | 15.8587 | 15.8165 | 15.7855 | 15.7365 | 9.9285 | 8.2748 | 6.6138 | 17.0346 | 16.946 | 16.8121 | 16.6785 | 16.5466 | 16.4156 | 16.2865 | 16.1612 | 16.0649 | 16.0378 | 10.974 | 9.3989 | 7.6874 | 5.9668
| DUNBLANE | LW |  |  |  | 19.8282 | 19.8162 | 19.8025 | 19.7869 | 19.7698 | 19.7513 | 19.7315 | 19.7106 | 19.6879 | 19.6645 | 19.6164 | 11.5859 | 9.6145 | 7.6397 | 17.0366 | 16.9558 | 16.7408 | 16.5166 | 16.3061 | 16.2005 | 16.1607 | 16.1207 | 16.0919 | 11.0529 | 9.8225 | 7.6605 | 5.4411 | 3.1871 | 17.1377 | 17.1031 | 17.0248 | 16.928 | 16.8284 | 16.7253 | 16.6555 | 16.6346 | 11.3212 | 10.7361 | 9.486 | 7.2466 | 4.9439 | 2.6379
| DUNBLANE | ST |  |  |  | 19.844 | 19.8398 | 19.8344 | 19.829 | 19.8238 | 19.8175 | 19.8113 | 19.8053 | 19.7998 | 19.7918 | 19.7764 | 19.7349 | 19.6978 | 19.658 | 17.0688 | 17.0357 | 16.9612 | 16.8458 | 16.7059 | 16.6329 | 16.5636 | 16.4956 | 16.4222 | 16.342 | 16.2251 | 16.1453 | 11.3951 | 10.3476 | 17.1599 | 17.1463 | 17.1186 | 17.0781 | 17.0301 | 16.9977 | 16.9646 | 16.9321 | 16.8976 | 16.8586 | 16.7799 | 16.6589 | 11.0714 | 10.033
| DUNBLANE | FS |  |  |  | 19.8398 | 19.8344 | 19.8289 | 19.8207 | 19.8127 | 19.8048 | 19.797 | 19.7893 | 19.7817 | 19.7742 | 19.7596 | 19.716 | 19.6709 | 19.6272 | 17.1315 | 17.0698 | 17.058 | 17.0194 | 16.9742 | 16.9397 | 16.9045 | 16.8643 | 16.8236 | 16.7808 | 16.6942 | 16.4934 | 16.2993 | 16.1402 | 17.1765 | 17.1528 | 17.145 | 17.1266 | 17.1062 | 17.0893 | 17.0722 | 17.0536 | 17.035 | 17.0158 | 16.9773 | 16.8689 | 16.7567 | 16.644
DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 28.2095 | 28.1196 | 28.0043 | 27.8949 | 27.7893 | 27.6877 | 27.59 | 27.4961 | 27.4536 | 27.4324 | 27.3908 | 27.2902 | 27.2022 | 27.1132 | 26.4974 | 26.4027 | 26.2533 | 26.1008 | 25.9521 | 25.8076 | 25.668 | 25.5326 | 25.4341 | 25.3534 | 25.1937 | 25.0743 | 22.5671 | 21.6915 | 26.5853 | 26.4839 | 26.3426 | 26.2044 | 26.0703 | 25.947 | 25.846 | 25.7491 | 25.7051 | 25.6832 | 25.6402 | 25.5363 | 25.4453 | 22.0987
| DUNOON | CT |  |  |  | 28.2095 | 28.1196 | 28.0043 | 27.8949 | 27.7893 | 27.6877 | 27.59 | 27.4961 | 27.4536 | 27.4324 | 27.3908 | 27.2902 | 27.2022 | 27.1132 | 26.4974 | 26.4027 | 26.2533 | 26.1008 | 25.9521 | 25.8076 | 25.668 | 25.5326 | 25.4341 | 25.3534 | 25.1937 | 25.0743 | 22.6155 | 21.9567 | 26.5853 | 26.4839 | 26.3426 | 26.2044 | 26.0703 | 25.947 | 25.846 | 25.7491 | 25.7051 | 25.6832 | 25.6402 | 25.5363 | 25.4453 | 22.269
| DUNOON | LW |  |  |  | 28.3386 | 28.3237 | 28.3064 | 28.2869 | 28.2655 | 28.2422 | 28.2174 | 28.1912 | 28.1675 | 28.1432 | 28.0931 | 27.9597 | 27.8319 | 27.6999 | 26.6035 | 26.5689 | 26.4902 | 26.3954 | 26.3004 | 26.2053 | 26.1102 | 26.0154 | 25.9166 | 25.8177 | 25.6203 | 25.4483 | 22.5671 | 21.6915 | 26.7195 | 26.6951 | 26.6518 | 26.6006 | 26.5479 | 26.52 | 26.4943 | 26.4672 | 26.4428 | 26.4176 | 26.3659 | 26.228 | 26.096 | 22.0987
| DUNOON | ST |  |  |  | 28.3584 | 28.3532 | 28.3464 | 28.3397 | 28.3331 | 28.3252 | 28.3175 | 28.31 | 28.3028 | 28.2923 | 28.2723 | 28.2271 | 28.1874 | 28.1512 | 26.631 | 26.6197 | 26.5977 | 26.567 | 26.5311 | 26.4824 | 26.4351 | 26.3889 | 26.3398 | 26.2887 | 26.1894 | 25.9513 | 25.7198 | 25.575 | 26.7444 | 26.7363 | 26.7227 | 26.7059 | 26.6871 | 26.6622 | 26.6381 | 26.6146 | 26.5901 | 26.5717 | 26.551 | 26.5044 | 26.4633 | 26.4259
| DUNOON | FS |  |  |  | 28.3532 | 28.3464 | 28.3395 | 28.3293 | 28.3192 | 28.3093 | 28.2995 | 28.2899 | 28.2804 | 28.271 | 28.2526 | 28.198 | 28.1503 | 28.1062 | 26.6335 | 26.6266 | 26.6196 | 26.6039 | 26.5871 | 26.565 | 26.5432 | 26.5175 | 26.4922 | 26.4674 | 26.4191 | 26.2958 | 26.1832 | 26.0784 | 26.7417 | 26.7341 | 26.7264 | 26.7129 | 26.6992 | 26.6834 | 26.6678 | 26.6508 | 26.634 | 26.6175 | 26.5854 | 26.4978 | 26.425 | 26.3794
DUNVEGAN | DUNVEGAN GRID | MINIMUM HEADROOM | NG 27604720 | YES | YES | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
| DUNVEGAN GRID | CT |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
| DUNVEGAN GRID | LW |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
| DUNVEGAN GRID | ST |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2585 | 3.2585 | 3.2585 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2669 | 3.2669 | 3.2669 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2583 | 3.2583 | 3.2583
| DUNVEGAN GRID | FS |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 30.5898 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 27.7861 | 27.7532 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 22.8018 | 21.9715 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 27.9869 | 22.4425
| DYCE NORTH | CT |  |  |  | 30.5898 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 27.7861 | 27.7562 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6306 | 27.6306 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 27.9869 | 27.9869
| DYCE NORTH | LW |  |  |  | 30.59 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 27.787 | 27.7532 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 22.8018 | 21.9715 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 27.9869 | 22.4425
| DYCE NORTH | ST |  |  |  | 30.6416 | 30.5897 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5273 | 30.5273 | 27.9885 | 27.7859 | 27.7571 | 27.7124 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6621 | 27.6621 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.0424 | 28.0424
| DYCE NORTH | FS |  |  |  | 30.6434 | 30.643 | 30.5937 | 30.5905 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 27.9956 | 27.9937 | 27.8013 | 27.789 | 27.7743 | 27.7598 | 27.7454 | 27.727 | 27.7089 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 27.6936 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098 | 28.098
THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.18585 | 0.18587 | 0.18589 | 0.18573 | 0.18549 | 0.18521 | 0.18491 | 0.18461 | 0.18425 | 0.1839 | 0.18316 | 0.18129 | 0.17938 | -0.0060906 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | -0.0036173
| EDAY | CT |  |  |  | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.18589 | 0.18593 | 0.18593 | 0.18584 | 0.1857 | 0.18553 | 0.18536 | 0.18517 | 0.18494 | 0.1847 | 0.18421 | 0.18293 | 0.1816 | 0.18025 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807
| EDAY | LW |  |  |  | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.18589 | 0.18594 | 0.1859 | 0.18573 | 0.18549 | 0.18521 | 0.18491 | 0.18461 | 0.18425 | 0.1839 | 0.18316 | 0.18129 | 0.17938 | -0.0060906 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | -0.0036173
| EDAY | ST |  |  |  | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.18587 | 0.18591 | 0.18594 | 0.18594 | 0.1859 | 0.18584 | 0.18576 | 0.18567 | 0.18555 | 0.18543 | 0.18516 | 0.1844 | 0.18362 | 0.18281 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807
| EDAY | FS |  |  |  | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.15202 | 0.18585 | 0.18587 | 0.18589 | 0.18592 | 0.18594 | 0.18595 | 0.18596 | 0.18596 | 0.18595 | 0.18593 | 0.18588 | 0.1857 | 0.18549 | 0.18525 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807 | 0.13807
FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | NO | YES | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.2814 | 7.0953 | 6.8614 | 7.9961 | 7.9957 | 7.9946 | 7.9933 | 7.9925 | 7.9918 | 7.991 | 7.9903 | 7.9892 | 7.9879 | 7.9853 | 7.4435 | 7.1654 | 6.8917 | 7.9254 | 7.919 | 7.9036 | 7.8838 | 7.8727 | 7.8617 | 7.8509 | 7.8398 | 7.8244 | 7.8051 | 7.768 | 7.1386 | 6.8819 | 6.6294
| EDZELL | CT |  |  |  | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.2814 | 7.2525 | 7.0972 | 7.9961 | 7.9957 | 7.9946 | 7.9934 | 7.9927 | 7.9919 | 7.9911 | 7.9903 | 7.9894 | 7.9886 | 7.9871 | 7.5335 | 7.3491 | 7.1675 | 7.9254 | 7.919 | 7.9036 | 7.8854 | 7.875 | 7.8643 | 7.8525 | 7.8398 | 7.8265 | 7.815 | 7.7931 | 7.2216 | 7.0515 | 6.8839
| EDZELL | LW |  |  |  | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.2814 | 7.0953 | 6.8614 | 7.9962 | 7.9957 | 7.9946 | 7.9933 | 7.9925 | 7.9918 | 7.991 | 7.9903 | 7.9895 | 7.9887 | 7.9872 | 7.4435 | 7.1654 | 6.8917 | 7.9259 | 7.9195 | 7.9037 | 7.8838 | 7.8727 | 7.8617 | 7.8509 | 7.8403 | 7.8289 | 7.8177 | 7.7957 | 7.1386 | 6.8819 | 6.6294
| EDZELL | ST |  |  |  | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.4792 | 7.4792 | 7.4599 | 7.9962 | 7.996 | 7.9955 | 7.9949 | 7.9945 | 7.9933 | 7.992 | 7.9906 | 7.9892 | 7.9879 | 7.9853 | 7.7262 | 7.6082 | 7.4911 | 7.9268 | 7.9236 | 7.9167 | 7.9073 | 7.9022 | 7.8837 | 7.8646 | 7.8451 | 7.8244 | 7.8051 | 7.768 | 7.4618 | 7.3529 | 7.2448
| EDZELL | FS |  |  |  | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.6731 | 7.9963 | 7.9962 | 7.996 | 7.9957 | 7.9956 | 7.9951 | 7.9947 | 7.9941 | 7.9936 | 7.993 | 7.992 | 7.9896 | 7.9873 | 7.9852 | 7.9274 | 7.9259 | 7.9233 | 7.9194 | 7.9176 | 7.911 | 7.9044 | 7.8962 | 7.8883 | 7.8804 | 7.8651 | 7.8299 | 7.797 | 7.766
MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | NO | 14.4995 | 14.4711 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 12.7335 | 12.3307 | 11.9431 | 14.5214 | 14.5049 | 14.4625 | 14.4139 | 14.3662 | 14.3547 | 14.3463 | 14.3381 | 14.3292 | 14.3198 | 14.301 | 12.5505 | 12.0807 | 11.6287 | 14.8851 | 14.8799 | 14.8666 | 14.8513 | 14.8362 | 14.8214 | 14.8069 | 14.7927 | 14.7772 | 14.7609 | 14.7283 | 12.7239 | 12.2834 | 11.8594
| EDZELL STREET | CT |  |  |  | 14.4995 | 14.4711 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 12.8332 | 12.5328 | 12.2447 | 14.5214 | 14.5049 | 14.4625 | 14.4139 | 14.3662 | 14.3547 | 14.3463 | 14.3381 | 14.3292 | 14.3198 | 14.301 | 12.6668 | 12.3164 | 11.9804 | 14.8851 | 14.8799 | 14.8666 | 14.8513 | 14.8362 | 14.8214 | 14.8069 | 14.7927 | 14.7772 | 14.7609 | 14.7283 | 12.8329 | 12.5044 | 12.1893
| EDZELL STREET | LW |  |  |  | 14.5045 | 14.4807 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 12.7335 | 12.3307 | 11.9431 | 14.5243 | 14.5105 | 14.4711 | 14.4227 | 14.3756 | 14.3564 | 14.3477 | 14.3393 | 14.33 | 14.3205 | 14.3015 | 12.5505 | 12.0807 | 11.6287 | 14.886 | 14.8817 | 14.8693 | 14.854 | 14.8392 | 14.8243 | 14.8093 | 14.7947 | 14.7785 | 14.7621 | 14.7292 | 12.7239 | 12.2834 | 11.8594
| EDZELL STREET | ST |  |  |  | 14.5117 | 14.5031 | 14.4832 | 14.4524 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.5284 | 14.5235 | 14.512 | 14.4941 | 14.4728 | 14.4523 | 14.4325 | 14.4131 | 14.3919 | 14.3692 | 14.3555 | 14.3354 | 14.3168 | 14.2989 | 14.8874 | 14.8858 | 14.8822 | 14.8765 | 14.8698 | 14.8634 | 14.8571 | 14.851 | 14.8443 | 14.8372 | 14.8228 | 14.7879 | 14.7557 | 14.7246
| EDZELL STREET | FS |  |  |  | 14.5156 | 14.5143 | 14.5126 | 14.5033 | 14.4925 | 14.4812 | 14.4699 | 14.4554 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.452 | 14.5307 | 14.5299 | 14.529 | 14.5236 | 14.5174 | 14.5108 | 14.5043 | 14.4959 | 14.4874 | 14.4787 | 14.4616 | 14.4196 | 14.3823 | 14.36 | 14.8881 | 14.8878 | 14.8875 | 14.8858 | 14.8839 | 14.8818 | 14.8797 | 14.8771 | 14.8744 | 14.8717 | 14.8663 | 14.8531 | 14.8413 | 14.8306
ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5148 | 12.487 | 12.4417 | 12.3986 | 12.3763 | 12.3534 | 12.3444 | 12.3361 | 12.3272 | 12.3179 | 9.8033 | 9.1017 | 8.6098 | 8.1224 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.8204 | 9.1292 | 8.6446 | 8.1714
| ELGIN | CT |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5157 | 12.4929 | 12.4574 | 12.4204 | 12.3943 | 12.3762 | 12.356 | 12.3458 | 12.3379 | 12.3295 | 12.3112 | 9.4662 | 9.0952 | 8.749 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.4883 | 9.1227 | 8.7816
| ELGIN | LW |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5148 | 12.487 | 12.4417 | 12.3986 | 12.3763 | 12.3534 | 12.3444 | 12.3361 | 12.3272 | 12.3179 | 9.8033 | 9.1017 | 8.6098 | 8.1224 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.8204 | 9.1292 | 8.6446 | 8.1714
| ELGIN | ST |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5374 | 12.5055 | 12.4848 | 12.4614 | 12.4349 | 12.4017 | 12.3849 | 12.3664 | 12.3498 | 12.3428 | 12.3276 | 9.9668 | 9.723 | 9.4945 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.9815 | 9.7413 | 9.5162
| ELGIN | FS |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5415 | 12.5164 | 12.5071 | 12.4963 | 12.4849 | 12.4706 | 12.4557 | 12.4386 | 12.4203 | 12.4026 | 12.3845 | 12.355 | 12.3477 | 12.3438 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263
ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 11.7963 | 11.6951 | 11.5405 | 11.3746 | 11.2122 | 11.0567 | 10.9125 | 10.7717 | 10.6614 | 10.5819 | 10.4286 | 10.1805 | 9.972 | 7.3092 | 10.2803 | 10.2089 | 10.0827 | 9.9439 | 9.8066 | 9.7343 | 9.6674 | 9.6027 | 9.5576 | 9.5303 | 9.4774 | 7.3022 | 6.9611 | 6.5293 | 11.5499 | 11.4738 | 11.3761 | 11.2752 | 11.1779 | 11.0841 | 10.994 | 10.9075 | 10.8524 | 10.825 | 10.7711 | 10.633 | 7.2994 | 6.9117
| ELLIOT DEPOT | CT |  |  |  | 11.7963 | 11.6951 | 11.5405 | 11.3746 | 11.2122 | 11.0567 | 10.9125 | 10.7717 | 10.6614 | 10.5819 | 10.4286 | 10.1805 | 9.972 | 7.3092 | 10.2803 | 10.2089 | 10.0827 | 9.9439 | 9.8066 | 9.7343 | 9.6674 | 9.6027 | 9.5576 | 9.5303 | 9.4774 | 7.3022 | 6.9611 | 6.6097 | 11.5499 | 11.4738 | 11.3761 | 11.2752 | 11.1779 | 11.0841 | 10.994 | 10.9075 | 10.8524 | 10.825 | 10.7711 | 10.633 | 7.2994 | 6.9117
| ELLIOT DEPOT | LW |  |  |  | 11.918 | 11.8849 | 11.8117 | 11.7228 | 11.6317 | 11.5423 | 11.4604 | 11.3784 | 11.2849 | 11.1909 | 11.0025 | 10.7726 | 10.5395 | 7.4094 | 10.3497 | 10.3152 | 10.2265 | 10.1177 | 10.0676 | 10.0418 | 10.0169 | 9.9914 | 9.961 | 9.9302 | 9.8677 | 7.4844 | 7.027 | 6.5293 | 11.6593 | 11.6466 | 11.632 | 11.6155 | 11.5973 | 11.5776 | 11.5566 | 11.5344 | 11.506 | 11.4767 | 11.4166 | 11.2563 | 7.4683 | 6.9182
| ELLIOT DEPOT | ST |  |  |  | 12.0283 | 11.9324 | 11.9084 | 11.8761 | 11.839 | 11.8139 | 11.7936 | 11.7728 | 11.7502 | 11.7242 | 11.6764 | 11.5571 | 11.4401 | 11.311 | 10.4881 | 10.3584 | 10.3304 | 10.2905 | 10.2438 | 10.215 | 10.1927 | 10.1695 | 10.144 | 10.1166 | 10.0775 | 10.0322 | 9.9876 | 9.936 | 11.676 | 11.6717 | 11.6658 | 11.6601 | 11.6546 | 11.6479 | 11.6414 | 11.635 | 11.6284 | 11.6187 | 11.6002 | 11.5487 | 11.4979 | 11.4365
| ELLIOT DEPOT | FS |  |  |  | 12.0591 | 12.0194 | 12.0094 | 11.9903 | 11.97 | 11.9544 | 11.9407 | 11.926 | 11.9115 | 11.8973 | 11.8697 | 11.7954 | 11.7191 | 11.6449 | 10.5352 | 10.4851 | 10.4765 | 10.4578 | 10.4373 | 10.4232 | 10.4117 | 10.3987 | 10.3858 | 10.3733 | 10.3491 | 10.2879 | 10.2274 | 10.1688 | 11.6717 | 11.6658 | 11.66 | 11.6514 | 11.6428 | 11.6344 | 11.6261 | 11.618 | 11.6099 | 11.602 | 11.5864 | 11.5401 | 11.49 | 11.4411
DYCE | ELLON 11 kV | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 22.1258 | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 22.923 | 21.521 | 17.6241 | 17.5552 | 27.9368 | 27.8275 | 27.8023 | 27.7774 | 27.7525 | 27.728 | 27.7015 | 21.9981 | 21.0009 | 18.7808 | 17.1122 | 15.477 | 19.3711 | 19.3494 | 29.8669 | 29.7896 | 29.7126 | 29.636 | 29.5597 | 29.4846 | 29.4427 | 29.4427 | 29.4427 | 20.2596 | 18.5886 | 16.9566
| ELLON 11 kV | CT |  |  |  | 22.1258 | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 32.6069 | 32.6069 | 17.6241 | 17.5651 | 27.9927 | 27.8403 | 27.8222 | 27.8041 | 27.7861 | 27.7683 | 27.7492 | 27.7304 | 27.6926 | 20.6022 | 19.4605 | 18.3447 | 19.3711 | 19.3525 | 29.8845 | 29.8289 | 29.7734 | 29.718 | 29.6627 | 29.6083 | 29.5496 | 29.492 | 29.4427 | 28.7464 | 20.9511 | 19.8185
| ELLON 11 kV | LW |  |  |  | 22.1258 | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 22.923 | 21.521 | 17.6245 | 17.5552 | 27.9368 | 27.8275 | 27.8023 | 27.7774 | 27.7525 | 27.728 | 27.7015 | 21.9981 | 21.0009 | 18.7808 | 17.1122 | 15.477 | 19.3712 | 19.3494 | 29.8669 | 29.7896 | 29.7126 | 29.636 | 29.5597 | 29.4846 | 29.4427 | 29.4427 | 29.4427 | 20.2596 | 18.5886 | 16.9566
| ELLON 11 kV | ST |  |  |  | 22.1258 | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.9438 | 32.9438 | 32.9438 | 17.6444 | 17.6175 | 28.135 | 28.0373 | 27.9193 | 27.843 | 27.835 | 27.8272 | 27.8187 | 27.8106 | 27.7942 | 27.5506 | 27.5118 | 21.7499 | 19.3775 | 19.3691 | 29.9293 | 29.8985 | 29.8613 | 29.8371 | 29.8127 | 29.7887 | 29.7628 | 29.7379 | 29.6877 | 29.2218 | 29.103 | 29.0945
| ELLON 11 kV | FS |  |  |  | 22.1258 | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 17.6567 | 17.6528 | 28.2274 | 28.2006 | 28.1685 | 28.1432 | 28.1176 | 28.0858 | 28.0543 | 28.0238 | 27.9628 | 27.8403 | 27.826 | 27.8125 | 19.3814 | 19.3802 | 29.9585 | 29.95 | 29.9399 | 29.9319 | 29.9239 | 29.9138 | 29.9039 | 29.8943 | 29.8751 | 29.829 | 29.7853 | 29.7438
TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.048407 | 0.04833 | 0.048109 | 0.047838 | 0.047573 | 0.047314 | 0.047166 | 0.047035 | 0.046894 | 0.046754 | 0.046477 | 0.044954 | 0.044954 | 0.044954 | 0.056042 | 0.056004 | 0.055907 | 0.055858 | 0.055809 | 0.055762 | 0.055715 | 0.05567 | 0.055621 | 0.055572 | 0.055476 | 0.054915 | 0.054673 | 0.054673
| EREDINE | CT |  |  |  | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.048407 | 0.048343 | 0.048177 | 0.047987 | 0.047802 | 0.04762 | 0.047443 | 0.047276 | 0.047177 | 0.047079 | 0.046885 | 0.046415 | 0.045942 | 0.045474 | 0.056042 | 0.056011 | 0.05593 | 0.055885 | 0.055851 | 0.055818 | 0.055785 | 0.055753 | 0.055719 | 0.055685 | 0.055618 | 0.055454 | 0.05529 | 0.055127
| EREDINE | LW |  |  |  | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.048407 | 0.04833 | 0.048109 | 0.047838 | 0.047573 | 0.047314 | 0.047166 | 0.047035 | 0.046894 | 0.046754 | 0.046477 | 0.044954 | 0.044954 | 0.044954 | 0.056042 | 0.056004 | 0.055907 | 0.055858 | 0.055809 | 0.055762 | 0.055715 | 0.05567 | 0.055621 | 0.055572 | 0.055476 | 0.054915 | 0.054673 | 0.054673
| EREDINE | ST |  |  |  | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.048429 | 0.048401 | 0.048334 | 0.04823 | 0.048106 | 0.047813 | 0.047526 | 0.047264 | 0.047104 | 0.046948 | 0.046643 | 0.045905 | 0.045177 | 0.044954 | 0.056053 | 0.056039 | 0.056006 | 0.055956 | 0.055907 | 0.055853 | 0.0558 | 0.055749 | 0.055694 | 0.055639 | 0.055533 | 0.055277 | 0.055023 | 0.054771
| EREDINE | FS |  |  |  | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.086331 | 0.048443 | 0.048439 | 0.048434 | 0.048405 | 0.048371 | 0.048275 | 0.048181 | 0.048061 | 0.047943 | 0.047826 | 0.047601 | 0.04717 | 0.046908 | 0.046665 | 0.056059 | 0.056057 | 0.056055 | 0.056041 | 0.056024 | 0.055978 | 0.055932 | 0.055898 | 0.055877 | 0.055855 | 0.055814 | 0.055717 | 0.055625 | 0.055541
INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | NO | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | -0.39488 | -0.40744 | -0.41992 | 0.054007 | 0.053809 | 0.053249 | 0.052566 | 0.051897 | 0.051244 | 0.050602 | 0.050127 | 0.049613 | 0.049105 | 0.048606 | -0.34501 | -0.35911 | -0.37312 | 0.060905 | 0.060809 | 0.060537 | 0.060206 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | -0.43202 | -0.44499 | -0.45873
| ERROGIE | CT |  |  |  | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | -0.39476 | -0.40744 | -0.41992 | 0.054007 | 0.053842 | 0.053422 | 0.052943 | 0.052474 | 0.052014 | 0.051563 | 0.05112 | 0.050642 | 0.050274 | 0.049568 | -0.34487 | -0.35911 | -0.37312 | 0.060906 | 0.060826 | 0.060621 | 0.060389 | 0.060161 | 0.059938 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | -0.4319 | -0.44499 | -0.45873
| ERROGIE | LW |  |  |  | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | -0.39488 | -0.40435 | -0.41362 | 0.054007 | 0.053809 | 0.053249 | 0.052566 | 0.051897 | 0.051244 | 0.050602 | 0.050127 | 0.049613 | 0.049105 | 0.048606 | -0.34501 | -0.35564 | -0.36605 | 0.060905 | 0.060809 | 0.060537 | 0.060206 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | -0.43202 | -0.4418 | -0.45169
| ERROGIE | ST |  |  |  | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | -0.15665 | -0.16034 | -0.16439 | 0.054065 | 0.053991 | 0.05382 | 0.053557 | 0.053244 | 0.052737 | 0.052244 | 0.051759 | 0.051236 | 0.050724 | 0.04994 | -0.15044 | -0.15504 | -0.15959 | 0.060934 | 0.060897 | 0.060814 | 0.060687 | 0.060535 | 0.060289 | 0.060049 | 0.059884 | 0.059884 | 0.059884 | 0.059884 | -0.19144 | -0.19568 | -0.19986
| ERROGIE | FS |  |  |  | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.098615 | 0.0541 | 0.054089 | 0.054075 | 0.054 | 0.053911 | 0.053742 | 0.053577 | 0.053364 | 0.053155 | 0.052947 | 0.052547 | 0.051604 | 0.050702 | 0.050031 | 0.060951 | 0.060945 | 0.060938 | 0.060902 | 0.060859 | 0.060777 | 0.060696 | 0.060593 | 0.060491 | 0.060391 | 0.060197 | 0.059884 | 0.059884 | 0.059884
ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.9852 | 4.6626 | 3.7706 | 3.2952 | 2.834 | 6.3907 | 6.3766 | 6.3363 | 6.2867 | 6.2361 | 6.1944 | 4.8171 | 4.6362 | 4.4405 | 4.2463 | 3.8575 | 2.9679 | 2.395 | 1.8392 | 6.4247 | 6.4056 | 6.361 | 6.3362 | 6.3108 | 6.2855 | 6.2615 | 4.8515 | 4.6609 | 4.4691 | 4.0802 | 3.0948 | 2.5217 | 1.9658
| ERROL | CT |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.6211 | 4.3053 | 4.0003 | 6.3922 | 6.3829 | 6.3588 | 6.3311 | 6.3023 | 6.2733 | 6.2466 | 6.2202 | 6.1964 | 4.9125 | 4.6911 | 3.9929 | 3.6123 | 3.2448 | 6.4267 | 6.414 | 6.3812 | 6.3584 | 6.344 | 6.3294 | 6.316 | 6.3028 | 6.2884 | 6.274 | 4.905 | 4.1172 | 3.7394 | 3.3718
| ERROL | LW |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.9852 | 4.6626 | 3.7706 | 3.2952 | 2.834 | 6.3907 | 6.3766 | 6.3363 | 6.2867 | 6.2361 | 6.1944 | 4.8171 | 4.6362 | 4.4405 | 4.2463 | 3.8575 | 2.9679 | 2.395 | 1.8392 | 6.4247 | 6.4056 | 6.361 | 6.3362 | 6.3108 | 6.2855 | 6.2615 | 4.8515 | 4.6609 | 4.4691 | 4.0802 | 3.0948 | 2.5217 | 1.9658
| ERROL | ST |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.723 | 6.723 | 4.9278 | 6.3947 | 6.3893 | 6.3767 | 6.357 | 6.3324 | 6.3177 | 6.3044 | 6.2913 | 6.2771 | 6.2629 | 6.2347 | 4.7696 | 4.5162 | 4.2699 | 6.4302 | 6.4228 | 6.4056 | 6.3787 | 6.3591 | 6.3517 | 6.345 | 6.3385 | 6.3313 | 6.3242 | 6.31 | 4.9277 | 4.6808 | 4.4408
| ERROL | FS |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.3972 | 6.3965 | 6.3955 | 6.39 | 6.383 | 6.378 | 6.3736 | 6.3679 | 6.3622 | 6.3567 | 6.3457 | 6.3193 | 6.295 | 6.2725 | 6.4336 | 6.4326 | 6.4312 | 6.4237 | 6.4143 | 6.4075 | 6.4014 | 6.3936 | 6.3859 | 6.3784 | 6.3658 | 6.3525 | 6.3403 | 6.329
TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | -9.4449e-06 | 0.025297 | 0.024941 | 0.024032 | 0.023813 | 0.023633 | 0.023456 | 0.023355 | 0.023355 | 0.023355 | 0.023355 | 0.023355 | -0.0089556 | -0.018709 | -0.028364 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | -0.0056325 | -0.015389 | -0.025048
| FINCASTLE | CT |  |  |  | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.025297 | 0.025001 | 0.024238 | 0.023915 | 0.023789 | 0.023665 | 0.023544 | 0.023426 | 0.023355 | 0.023355 | 0.023355 | -0.00015458 | -0.0069822 | -0.013741 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | -0.0036585 | -0.010419
| FINCASTLE | LW |  |  |  | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | -9.4449e-06 | 0.025297 | 0.024941 | 0.024032 | 0.023813 | 0.023633 | 0.023456 | 0.023355 | 0.023355 | 0.023355 | 0.023355 | 0.023355 | -0.0089556 | -0.018709 | -0.028364 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | -0.0056325 | -0.015389 | -0.025048
| FINCASTLE | ST |  |  |  | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.025401 | 0.025269 | 0.02496 | 0.024479 | 0.024029 | 0.023914 | 0.023834 | 0.023756 | 0.023672 | 0.023589 | 0.023427 | 0.023355 | 0.023355 | -0.00046913 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484
| FINCASTLE | FS |  |  |  | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.049621 | 0.025463 | 0.025446 | 0.025424 | 0.025289 | 0.025129 | 0.024943 | 0.024758 | 0.024521 | 0.024288 | 0.024099 | 0.023954 | 0.023799 | 0.023657 | 0.023526 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484 | 0.028484
SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 1.1313 | 1.1312 | 1.131 | 1.1307 | 1.1305 | 1.1303 | 1.1295 | 1.1287 | 1.1279 | 1.127 | 1.1258 | 1.1222 | 1.1187 | 1.1152 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.69342 | 0.69333 | 0.69309 | 0.69279 | 0.69247 | 0.6922 | 0.69128 | 0.69028 | 0.6892 | 0.68817 | 0.68671 | 0.68218 | 0.67777 | 0.67344
| FIRTH | CT |  |  |  | 1.1313 | 1.1312 | 1.1311 | 1.1309 | 1.1307 | 1.1305 | 1.13 | 1.1293 | 1.1286 | 1.128 | 1.1269 | 1.1238 | 1.1213 | 1.1188 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.69342 | 0.69335 | 0.69317 | 0.69295 | 0.69273 | 0.69253 | 0.69182 | 0.69103 | 0.69018 | 0.68933 | 0.68797 | 0.68423 | 0.68105 | 0.678
| FIRTH | LW |  |  |  | 1.1313 | 1.1312 | 1.131 | 1.1307 | 1.1305 | 1.1303 | 1.1295 | 1.1287 | 1.1279 | 1.127 | 1.1258 | 1.1222 | 1.1187 | 1.1152 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.69342 | 0.69333 | 0.69309 | 0.69279 | 0.69247 | 0.6922 | 0.69128 | 0.69028 | 0.6892 | 0.68817 | 0.68671 | 0.68218 | 0.67777 | 0.67344
| FIRTH | ST |  |  |  | 1.1313 | 1.1312 | 1.1312 | 1.1311 | 1.131 | 1.1306 | 1.13 | 1.1294 | 1.1287 | 1.128 | 1.1267 | 1.1248 | 1.1232 | 1.1217 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.69345 | 0.69341 | 0.69334 | 0.69321 | 0.69306 | 0.69265 | 0.69189 | 0.6911 | 0.69022 | 0.68934 | 0.68782 | 0.68539 | 0.68341 | 0.6815
| FIRTH | FS |  |  |  | 1.1313 | 1.1313 | 1.1313 | 1.1312 | 1.1312 | 1.1311 | 1.1309 | 1.1306 | 1.1303 | 1.13 | 1.1296 | 1.1288 | 1.1282 | 1.1277 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.87859 | 0.69346 | 0.69345 | 0.69344 | 0.69341 | 0.69336 | 0.69323 | 0.69294 | 0.69261 | 0.69227 | 0.69192 | 0.69134 | 0.69037 | 0.68963 | 0.68898
THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -2.5759 | -2.576 | -2.5761 | -2.5763 | -2.5765 | -2.5767 | -2.5769 | -2.577 | -2.5772 | -2.5774 | -2.5778 | -2.5787 | -2.58 | -2.5813 | -1.4132 | -1.4139 | -1.4157 | -1.418 | -1.4203 | -1.4225 | -1.4247 | -1.4268 | -1.4291 | -1.4313 | -1.4358 | -1.4468 | -1.4629 | -1.4796
| FLOTTA | CT |  |  |  | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -2.5759 | -2.576 | -2.5761 | -2.5762 | -2.5763 | -2.5765 | -2.5766 | -2.5767 | -2.5768 | -2.577 | -2.5772 | -2.5786 | -2.58 | -2.5813 | -1.4132 | -1.4138 | -1.4152 | -1.4168 | -1.4184 | -1.4199 | -1.4214 | -1.4229 | -1.4245 | -1.4261 | -1.4293 | -1.4461 | -1.4629 | -1.4796
| FLOTTA | LW |  |  |  | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -2.5759 | -2.576 | -2.5761 | -2.5763 | -2.5765 | -2.5767 | -2.5769 | -2.577 | -2.5772 | -2.5774 | -2.5778 | -2.5787 | -2.5796 | -2.5805 | -1.4132 | -1.4139 | -1.4157 | -1.418 | -1.4203 | -1.4225 | -1.4247 | -1.4268 | -1.4291 | -1.4313 | -1.4358 | -1.4468 | -1.4578 | -1.4687
| FLOTTA | ST |  |  |  | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -2.5759 | -2.5759 | -2.576 | -2.576 | -2.5761 | -2.5762 | -2.5763 | -2.5764 | -2.5765 | -2.5766 | -2.5767 | -2.5771 | -2.5775 | -2.5779 | -1.413 | -1.4133 | -1.4138 | -1.4147 | -1.4158 | -1.4168 | -1.4178 | -1.4188 | -1.4199 | -1.4209 | -1.423 | -1.4279 | -1.4327 | -1.4375
| FLOTTA | FS |  |  |  | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -3.3426 | -2.5759 | -2.5759 | -2.5759 | -2.5759 | -2.576 | -2.576 | -2.576 | -2.576 | -2.5761 | -2.5761 | -2.5762 | -2.5763 | -2.5765 | -2.5766 | -1.4129 | -1.4129 | -1.413 | -1.4132 | -1.4135 | -1.4139 | -1.4142 | -1.4147 | -1.4151 | -1.4155 | -1.4163 | -1.4183 | -1.4201 | -1.4218
ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5185 | 16.514 | 16.5103 | 16.505 | 16.5001 | 16.4951 | 16.4901 | 16.4853 | 16.4805 | 16.476 | 16.4671 | 16.4655 | 13.2918 | 12.7833 | 16.9723 | 16.9653 | 16.9478 | 16.9228 | 16.8995 | 16.8759 | 16.8523 | 16.8296 | 16.8071 | 16.7902 | 16.7671 | 16.7671 | 16.7671 | 13.308
| FOCHABERS | CT |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5185 | 16.514 | 16.5103 | 16.5057 | 16.5014 | 16.497 | 16.4926 | 16.4883 | 16.4838 | 16.4796 | 16.4714 | 16.4655 | 13.6387 | 13.2634 | 16.9723 | 16.9653 | 16.948 | 16.9261 | 16.9056 | 16.8849 | 16.8642 | 16.8437 | 16.8229 | 16.8029 | 16.7761 | 16.7671 | 16.7671 | 13.7938
| FOCHABERS | LW |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5194 | 16.5142 | 16.5103 | 16.505 | 16.5001 | 16.4951 | 16.4901 | 16.4853 | 16.4805 | 16.476 | 16.4671 | 16.4655 | 13.2918 | 12.7833 | 16.973 | 16.9661 | 16.9478 | 16.9228 | 16.8995 | 16.8759 | 16.8523 | 16.8296 | 16.8071 | 16.7902 | 16.7671 | 16.7671 | 16.7671 | 13.308
| FOCHABERS | ST |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5217 | 16.5177 | 16.5139 | 16.5114 | 16.5088 | 16.5061 | 16.5033 | 16.5007 | 16.4979 | 16.4953 | 16.4904 | 16.479 | 16.4677 | 16.4655 | 16.9747 | 16.9716 | 16.9648 | 16.9533 | 16.9407 | 16.9278 | 16.9149 | 16.9023 | 16.8894 | 16.8772 | 16.8538 | 16.7999 | 16.7671 | 16.7671
| FOCHABERS | FS |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5235 | 16.5226 | 16.5214 | 16.5168 | 16.5144 | 16.5135 | 16.5125 | 16.5114 | 16.5103 | 16.5093 | 16.5073 | 16.5029 | 16.4989 | 16.4951 | 16.9761 | 16.9754 | 16.9744 | 16.9709 | 16.9674 | 16.9629 | 16.9583 | 16.9528 | 16.9478 | 16.9431 | 16.9338 | 16.9128 | 16.8941 | 16.8759
NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 21.1397 | 20.9325 | 20.6665 | 20.4099 | 20.1625 | 19.9243 | 19.6952 | 19.4754 | 19.3575 | 19.2989 | 19.1837 | 13.7842 | 12.9593 | 12.047 | 18.2987 | 18.0998 | 17.8099 | 17.5071 | 17.2889 | 17.0899 | 16.8997 | 16.7186 | 13.7951 | 13.4681 | 12.8397 | 11.3142 | 10.0873 | 8.7408 | 18.1241 | 17.8982 | 17.5938 | 17.2906 | 17.0006 | 16.7336 | 16.5113 | 13.7112 | 13.3829 | 13.1038 | 12.4512 | 10.7097 | 9.6725 | 8.31
| FORRES | CT |  |  |  | 21.1397 | 20.9325 | 20.6665 | 20.4099 | 20.1625 | 19.9243 | 19.6952 | 19.4754 | 19.3575 | 19.2989 | 19.1837 | 13.7842 | 12.9593 | 12.0649 | 18.2987 | 18.0998 | 17.8099 | 17.5071 | 17.2889 | 17.0899 | 16.8997 | 16.7186 | 13.7951 | 13.4681 | 12.8397 | 11.3142 | 10.3537 | 9.3977 | 18.1241 | 17.8982 | 17.5938 | 17.2906 | 17.0006 | 16.7336 | 16.5113 | 13.7112 | 13.3829 | 13.1038 | 12.4512 | 10.7097 | 9.6725 | 8.6399
| FORRES | LW |  |  |  | 21.4376 | 21.4031 | 21.3632 | 21.3183 | 21.2688 | 21.2152 | 21.158 | 21.0975 | 21.0333 | 20.9671 | 20.831 | 19.8738 | 13.3446 | 12.047 | 18.5294 | 18.4582 | 18.3231 | 18.1523 | 17.9894 | 17.8799 | 17.7899 | 17.7035 | 17.6107 | 17.5218 | 13.4972 | 11.4644 | 10.0873 | 8.7408 | 18.4258 | 18.3723 | 18.2885 | 18.1864 | 18.0843 | 17.986 | 17.9305 | 17.8718 | 17.8095 | 17.7453 | 13.5195 | 11.247 | 9.7689 | 8.31
| FORRES | ST |  |  |  | 21.4832 | 21.4713 | 21.4554 | 21.44 | 21.4249 | 21.4066 | 21.3888 | 21.3715 | 21.3547 | 21.3302 | 21.2831 | 20.8668 | 20.7571 | 20.6403 | 18.6134 | 18.5492 | 18.5011 | 18.433 | 18.3635 | 18.2977 | 18.2363 | 18.1801 | 18.1191 | 18.0466 | 17.9411 | 17.5875 | 17.4445 | 17.3408 | 18.4923 | 18.4573 | 18.4263 | 18.3873 | 18.3479 | 18.3079 | 18.27 | 18.2347 | 18.1976 | 18.1505 | 18.0606 | 17.6479 | 17.5416 | 17.4283
| FORRES | FS |  |  |  | 21.4713 | 21.4554 | 21.4395 | 21.416 | 21.3928 | 21.37 | 21.3474 | 21.3251 | 21.3032 | 21.2815 | 21.2392 | 21.1132 | 20.9899 | 20.8723 | 18.6127 | 18.5932 | 18.5367 | 18.498 | 18.4609 | 18.4238 | 18.3887 | 18.3536 | 18.3183 | 18.2811 | 18.2091 | 18.0188 | 17.8526 | 17.7222 | 18.4838 | 18.4647 | 18.4302 | 18.3979 | 18.3664 | 18.3351 | 18.305 | 18.2749 | 18.2451 | 18.2146 | 18.1554 | 17.9892 | 17.8348 | 17.6916
DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | NO | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 0.85176 | 1.1423 | 1.1389 | 1.1288 | 1.1199 | 1.1177 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 0.8513 | 0.76346 | 0.67456 | 0.58688 | 1.1741 | 1.1725 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 0.89693 | 0.81135 | 0.72242 | 0.63471
| FORSS | CT |  |  |  | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.1423 | 1.1393 | 1.1314 | 1.1238 | 1.1193 | 1.1177 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 0.8454 | 0.77472 | 0.70509 | 1.1741 | 1.1726 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 0.89119 | 0.82235 | 0.75296
| FORSS | LW |  |  |  | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 0.85176 | 1.1424 | 1.1389 | 1.1288 | 1.1199 | 1.1177 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 1.1173 | 0.8513 | 0.76346 | 0.67456 | 0.58688 | 1.1741 | 1.1725 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 0.89693 | 0.81135 | 0.72242 | 0.63471
| FORSS | ST |  |  |  | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.1434 | 1.1422 | 1.1393 | 1.1348 | 1.1294 | 1.1261 | 1.1231 | 1.1202 | 1.1193 | 1.1186 | 1.1173 | 1.1173 | 1.1173 | 0.89837 | 1.1747 | 1.1741 | 1.1727 | 1.1705 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702
| FORSS | FS |  |  |  | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.3449 | 1.144 | 1.1438 | 1.1436 | 1.1423 | 1.1407 | 1.1394 | 1.1381 | 1.1364 | 1.1348 | 1.1331 | 1.13 | 1.124 | 1.1197 | 1.1185 | 1.1749 | 1.1749 | 1.1747 | 1.1741 | 1.1734 | 1.1727 | 1.1721 | 1.1713 | 1.1705 | 1.1702 | 1.1702 | 1.1702 | 1.1702 | 1.1702
BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | NO | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2251 | 6.0103 | 5.802 | 7.2778 | 7.2722 | 7.2606 | 7.2479 | 7.2375 | 7.23 | 7.23 | 7.23 | 6.2909 | 6.224 | 6.0909 | 5.8293 | 5.5698 | 5.3182 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2389 | 5.9777 | 5.7188 | 5.4676
| FORTEVIOT | CT |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2079 | 7.2779 | 7.2733 | 7.2646 | 7.2558 | 7.2488 | 7.2416 | 7.234 | 7.23 | 7.23 | 7.23 | 6.2929 | 6.1278 | 5.9653 | 5.8085 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2757 | 6.1135 | 5.957
| FORTEVIOT | LW |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2251 | 6.0103 | 5.802 | 7.2778 | 7.2722 | 7.2606 | 7.2479 | 7.2375 | 7.23 | 7.23 | 7.23 | 6.2909 | 6.224 | 6.0909 | 5.8293 | 5.5698 | 5.3182 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2389 | 5.9777 | 5.7188 | 5.4676
| FORTEVIOT | ST |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.2789 | 7.2762 | 7.2718 | 7.2665 | 7.2616 | 7.2574 | 7.253 | 7.2485 | 7.2438 | 7.2396 | 7.2314 | 7.23 | 6.2675 | 6.1517 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2986
| FORTEVIOT | FS |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.2797 | 7.2786 | 7.2773 | 7.2754 | 7.2739 | 7.2725 | 7.271 | 7.2693 | 7.2676 | 7.2659 | 7.2627 | 7.2552 | 7.2484 | 7.2421 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719
INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | NO | -0.052069 | -0.13941 | -0.2515 | -0.36103 | -0.47883 | -0.59228 | -0.70138 | -0.80613 | -0.85453 | -0.87916 | -0.92757 | -1.0577 | -1.1762 | -1.2956 | -0.030367 | -0.10116 | -0.19289 | -0.28287 | -0.37778 | -0.4692 | -0.55714 | -0.64159 | -0.68113 | -0.70169 | -0.74212 | -0.85436 | -0.95622 | -1.0587 | -0.048412 | -0.13732 | -0.26579 | -0.38816 | -0.50619 | -0.61987 | -0.7292 | -0.83419 | -0.88308 | -0.90829 | -0.95785 | -1.0921 | -1.2133 | -1.3353
| FOYERS | CT |  |  |  | -0.052069 | -0.13941 | -0.2515 | -0.36103 | -0.47883 | -0.59228 | -0.70138 | -0.80613 | -0.85453 | -0.87916 | -0.92757 | -1.0577 | -1.1762 | -1.2956 | -0.030367 | -0.10116 | -0.19289 | -0.28287 | -0.37778 | -0.4692 | -0.55714 | -0.64159 | -0.68113 | -0.70169 | -0.74212 | -0.85436 | -0.95622 | -1.0587 | -0.048412 | -0.13732 | -0.26579 | -0.38816 | -0.50619 | -0.61987 | -0.7292 | -0.83419 | -0.88308 | -0.90829 | -0.95785 | -1.0921 | -1.2133 | -1.3353
| FOYERS | LW |  |  |  | 0.18514 | 0.17034 | 0.15324 | 0.13399 | 0.11277 | -0.020217 | -0.044349 | -0.069829 | -0.092903 | -0.11826 | -0.18213 | -0.35764 | -0.52788 | -0.70284 | 0.19162 | 0.18286 | 0.17163 | 0.1588 | -0.0033804 | -0.026627 | -0.051018 | -0.076397 | -0.10024 | -0.12461 | -0.17428 | -0.31303 | -0.44999 | -0.59981 | 0.20687 | 0.19139 | 0.17351 | 0.15337 | 0.13118 | -0.022534 | -0.054619 | -0.088131 | -0.11932 | -0.15126 | -0.2165 | -0.3966 | -0.57153 | -0.75108
| FOYERS | ST |  |  |  | 0.20472 | 0.19961 | 0.1928 | 0.18617 | 0.17971 | 0.17186 | 0.16423 | 0.15682 | 0.14972 | 0.13935 | 0.11946 | -0.03504 | -0.074894 | -0.12518 | 0.20256 | 0.19954 | 0.1953 | 0.19087 | 0.18638 | 0.18097 | 0.17571 | 0.17059 | 0.16555 | 0.15874 | -0.0050152 | -0.052695 | -0.096212 | -0.13698 | 0.22734 | 0.222 | 0.21488 | 0.20794 | 0.20119 | 0.19298 | 0.185 | 0.17725 | 0.16982 | 0.15897 | 0.13817 | -0.053083 | -0.10888 | -0.16084
| FOYERS | FS |  |  |  | 0.19961 | 0.1928 | 0.18599 | 0.17591 | 0.16596 | 0.15615 | 0.14647 | 0.13692 | 0.1275 | 0.11822 | -0.010117 | -0.063237 | -0.10969 | -0.15263 | 0.19986 | 0.1961 | 0.19232 | 0.18657 | 0.18085 | 0.1751 | 0.16942 | 0.16371 | 0.15808 | 0.15253 | -0.0047338 | -0.052297 | -0.09422 | -0.13306 | 0.222 | 0.21488 | 0.20775 | 0.19721 | 0.18681 | 0.17654 | 0.16642 | 0.15643 | 0.14659 | 0.13688 | -0.0091383 | -0.062564 | -0.11944 | -0.1721
FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | NO | 45.417 | 45.3555 | 45.2765 | 45.2021 | 45.1303 | 45.0611 | 44.9946 | 44.9308 | 44.8943 | 44.8761 | 44.8404 | 38.0549 | 35.8192 | 34.6174 | 48.8896 | 48.7904 | 48.5996 | 48.3919 | 48.1852 | 47.98 | 47.7754 | 47.5755 | 47.3862 | 47.2164 | 46.8727 | 46.3197 | 45.5841 | 36.836 | 45.7194 | 45.6604 | 45.5846 | 45.5132 | 45.4443 | 45.3779 | 45.3141 | 45.2529 | 45.2178 | 45.2004 | 45.1661 | 36.8441 | 34.3164 | 32.7205
| FRASERBURGH | CT |  |  |  | 45.417 | 45.3555 | 45.2765 | 45.2021 | 45.1303 | 45.0611 | 44.9946 | 44.9308 | 44.8943 | 44.8761 | 44.8404 | 38.0549 | 35.8192 | 34.785 | 48.8896 | 48.7904 | 48.5996 | 48.3919 | 48.1852 | 47.98 | 47.7754 | 47.5755 | 47.3862 | 47.2164 | 46.8727 | 46.3197 | 45.5841 | 37.2533 | 45.7194 | 45.6604 | 45.5846 | 45.5132 | 45.4443 | 45.3779 | 45.3141 | 45.2529 | 45.2178 | 45.2004 | 45.1661 | 36.8441 | 34.3442 | 33.0474
| FRASERBURGH | LW |  |  |  | 45.5055 | 45.4952 | 45.4834 | 45.4701 | 45.4554 | 45.4395 | 45.4225 | 45.4045 | 45.3842 | 45.3632 | 45.3201 | 44.6872 | 35.896 | 34.6174 | 48.9693 | 48.9192 | 48.7918 | 48.6348 | 48.4749 | 48.3129 | 48.1479 | 47.9846 | 47.808 | 47.6364 | 47.2862 | 46.5798 | 45.8112 | 36.836 | 45.8043 | 45.7945 | 45.7831 | 45.7703 | 45.7562 | 45.741 | 45.7247 | 45.7074 | 45.6879 | 45.6678 | 45.6265 | 37.1146 | 34.3164 | 32.7205
| FRASERBURGH | ST |  |  |  | 45.519 | 45.5155 | 45.5108 | 45.5062 | 45.5017 | 45.4963 | 45.491 | 45.4859 | 45.481 | 45.4739 | 45.4602 | 45.164 | 44.5778 | 44.5397 | 49.2332 | 48.98 | 48.9489 | 48.9027 | 48.8471 | 48.7624 | 48.6767 | 48.5927 | 48.5026 | 48.4143 | 48.2357 | 47.5915 | 46.7262 | 46.5536 | 45.8173 | 45.8139 | 45.8094 | 45.805 | 45.8007 | 45.7955 | 45.7904 | 45.7855 | 45.7808 | 45.774 | 45.7609 | 45.4767 | 44.9141 | 37.8728
| FRASERBURGH | FS |  |  |  | 45.5155 | 45.5108 | 45.5061 | 45.4991 | 45.4922 | 45.4854 | 45.4787 | 45.4721 | 45.4656 | 45.4591 | 45.4466 | 45.4092 | 45.37 | 45.332 | 49.2356 | 49.2291 | 48.983 | 48.9629 | 48.9399 | 48.9068 | 48.8732 | 48.8334 | 48.7939 | 48.7558 | 48.6793 | 48.4898 | 48.3066 | 48.1326 | 45.8139 | 45.8094 | 45.8049 | 45.7982 | 45.7916 | 45.7851 | 45.7786 | 45.7723 | 45.766 | 45.7599 | 45.7478 | 45.7119 | 45.6743 | 45.6378
LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | NO | 3.8227 | 3.7473 | 3.6506 | 3.5505 | 3.454 | 3.3611 | 3.2717 | 3.186 | 3.1313 | 3.1041 | 2.9938 | 1.975 | 1.1029 | 0.6694 | 4.6035 | 4.5129 | 4.3648 | 4.2047 | 4.0492 | 3.8919 | 3.7388 | 3.5962 | 3.4754 | 3.3784 | 3.1865 | 2.3213 | 1.5662 | 1.0613 | 4.3683 | 4.2643 | 4.1099 | 3.9457 | 3.7865 | 3.6284 | 3.475 | 3.3307 | 3.219 | 3.1238 | 2.9261 | 1.8711 | 0.96562 | 0.50752
| FRIOCKHEIM | CT |  |  |  | 3.8227 | 3.7473 | 3.6506 | 3.5505 | 3.454 | 3.3611 | 3.2717 | 3.186 | 3.1313 | 3.1041 | 2.9938 | 1.975 | 1.1029 | 0.6694 | 4.6035 | 4.5129 | 4.3648 | 4.2047 | 4.0492 | 3.8919 | 3.7388 | 3.5962 | 3.4754 | 3.3784 | 3.1865 | 2.3213 | 1.5662 | 1.1411 | 4.3683 | 4.2643 | 4.1099 | 3.9457 | 3.7865 | 3.6284 | 3.475 | 3.3307 | 3.219 | 3.1238 | 2.9261 | 1.8711 | 0.96562 | 0.50752
| FRIOCKHEIM | LW |  |  |  | 3.9311 | 3.9186 | 3.9041 | 3.8877 | 3.8697 | 3.8502 | 3.8294 | 3.8074 | 3.7792 | 3.7502 | 3.5368 | 2.4146 | 1.415 | 0.81459 | 4.6995 | 4.6608 | 4.5683 | 4.4564 | 4.3448 | 4.2267 | 4.1081 | 3.9977 | 3.8745 | 3.7514 | 3.5052 | 2.5292 | 1.6447 | 1.0613 | 4.4953 | 4.4624 | 4.393 | 4.3097 | 4.2257 | 4.1365 | 4.0461 | 3.9605 | 3.8406 | 3.7157 | 3.4655 | 2.2997 | 1.2588 | 0.62524
| FRIOCKHEIM | ST |  |  |  | 3.9477 | 3.9434 | 3.9376 | 3.932 | 3.9265 | 3.9199 | 3.9134 | 3.9071 | 3.9005 | 3.891 | 3.8726 | 3.5561 | 3.3134 | 3.1889 | 4.7242 | 4.7137 | 4.6931 | 4.664 | 4.6303 | 4.5871 | 4.5447 | 4.5072 | 4.467 | 4.4241 | 4.3407 | 3.8999 | 3.5278 | 3.3151 | 4.5213 | 4.5119 | 4.4949 | 4.4724 | 4.447 | 4.4147 | 4.3829 | 4.3546 | 4.3242 | 4.2904 | 4.2246 | 3.7484 | 3.3419 | 3.1222
| FRIOCKHEIM | FS |  |  |  | 3.9434 | 3.9376 | 3.9319 | 3.9233 | 3.9149 | 3.9065 | 3.8983 | 3.8902 | 3.8822 | 3.8744 | 3.859 | 3.8131 | 3.7634 | 3.7149 | 4.7232 | 4.7168 | 4.7101 | 4.6927 | 4.6736 | 4.6537 | 4.6338 | 4.6128 | 4.592 | 4.5714 | 4.5316 | 4.429 | 4.3277 | 4.2304 | 4.5181 | 4.5105 | 4.5027 | 4.4862 | 4.4687 | 4.4506 | 4.4328 | 4.4141 | 4.3957 | 4.3776 | 4.3423 | 4.2478 | 4.1519 | 4.0593
KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 11.4702 | 11.4686 | 11.4638 | 11.458 | 11.4523 | 11.4466 | 11.4409 | 10.9612 | 10.9552 | 10.9493 | 10.2658 | 7.2809 | 5.7156 | 5.4259 | 10.8186 | 10.8068 | 10.773 | 10.7314 | 10.7149 | 7.3498 | 7.3038 | 6.8475 | 6.7987 | 6.7507 | 6.0721 | 5.226 | 3.9671 | 3.6386 | 9.871 | 9.8657 | 9.8507 | 9.8321 | 9.8137 | 9.7956 | 9.7775 | 9.2472 | 9.2347 | 9.2225 | 8.4669 | 6.2086 | 4.478 | 4.118
| FYVIE | CT |  |  |  | 11.4703 | 11.469 | 11.4658 | 11.4621 | 11.4583 | 11.4546 | 11.451 | 10.9732 | 10.9693 | 10.9655 | 10.2862 | 7.449 | 5.9604 | 5.8305 | 10.8192 | 10.8102 | 10.7869 | 10.7601 | 10.7335 | 10.7215 | 10.7112 | 6.9447 | 6.913 | 6.882 | 6.237 | 5.4469 | 4.2446 | 4.074 | 9.8712 | 9.8672 | 9.8569 | 9.8449 | 9.8331 | 9.8213 | 9.8095 | 9.2748 | 9.2639 | 9.256 | 8.509 | 6.545 | 4.9007 | 4.6409
| FYVIE | LW |  |  |  | 11.4702 | 11.4686 | 11.4638 | 11.458 | 11.4523 | 11.4466 | 11.4409 | 10.9612 | 10.9552 | 10.9493 | 10.2658 | 7.2809 | 5.7156 | 5.4259 | 10.8186 | 10.8068 | 10.773 | 10.7314 | 10.7149 | 7.3498 | 7.3038 | 6.8475 | 6.7987 | 6.7507 | 6.0721 | 5.226 | 3.9671 | 3.6386 | 9.871 | 9.8657 | 9.8507 | 9.8321 | 9.8137 | 9.7956 | 9.7775 | 9.2472 | 9.2347 | 9.2225 | 8.4669 | 6.2086 | 4.478 | 4.118
| FYVIE | ST |  |  |  | 11.4707 | 11.47 | 11.4685 | 11.4661 | 11.4633 | 11.4607 | 11.4582 | 11.2186 | 11.2159 | 11.2133 | 10.8723 | 10.5041 | 9.8991 | 9.8869 | 10.8219 | 10.8173 | 10.8064 | 10.7894 | 10.7689 | 10.7505 | 10.7322 | 7.2177 | 7.1959 | 7.1746 | 6.8411 | 6.4305 | 5.8161 | 5.7172 | 9.8725 | 9.8704 | 9.8655 | 9.8579 | 9.8488 | 9.8406 | 9.8325 | 9.5629 | 9.5543 | 9.5459 | 9.1599 | 8.7468 | 7.0494 | 6.9038
| FYVIE | FS |  |  |  | 11.471 | 11.4709 | 11.4707 | 11.47 | 11.4692 | 11.4684 | 11.4675 | 11.4664 | 11.4654 | 11.4643 | 11.4623 | 11.4575 | 11.4529 | 11.4486 | 10.8241 | 10.8234 | 10.8224 | 10.8174 | 10.8115 | 10.8054 | 10.7992 | 10.7915 | 10.7839 | 10.7766 | 10.762 | 10.7294 | 10.7166 | 10.7046 | 9.8734 | 9.8731 | 9.8727 | 9.8704 | 9.8678 | 9.8651 | 9.8623 | 9.8589 | 9.8555 | 9.8522 | 9.8457 | 9.8303 | 9.8157 | 9.802
GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | YES | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0013769 | 0.0013673 | 0.0013396 | 0.0013057 | 0.0012774 | 0.0012529 | 0.0012413 | 0.0012357 | 0.0012296 | 0.0012296 | 0.0012296 | 0.0012296 | -0.00019044 | -0.00051228 | 0.0015541 | 0.0015495 | 0.001536 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | -0.00024784
| GARBAT FOREST | CT |  |  |  | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0013769 | 0.0013689 | 0.0013481 | 0.0013244 | 0.0013012 | 0.0012819 | 0.0012651 | 0.0012487 | 0.0012418 | 0.0012376 | 0.0012296 | 0.0012296 | 0.0012296 | -2.4821e-05 | 0.0015541 | 0.0015502 | 0.0015402 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291
| GARBAT FOREST | LW |  |  |  | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0013769 | 0.0013673 | 0.0013396 | 0.0013057 | 0.0012774 | 0.0012529 | 0.0012413 | 0.0012357 | 0.0012296 | 0.0012296 | 0.0012296 | 0.0012296 | -0.00019044 | -0.00051228 | 0.0015541 | 0.0015495 | 0.001536 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | -0.00024784
| GARBAT FOREST | ST |  |  |  | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0013797 | 0.0013761 | 0.0013678 | 0.0013548 | 0.0013393 | 0.0013242 | 0.0013095 | 0.0012952 | 0.0012827 | 0.0012712 | 0.0012488 | 0.0012332 | 0.0012296 | 0.0012296 | 0.0015555 | 0.0015538 | 0.0015497 | 0.0015434 | 0.0015359 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291 | 0.0015291
| GARBAT FOREST | FS |  |  |  | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0022914 | 0.0013814 | 0.0013809 | 0.0013803 | 0.0013767 | 0.0013723 | 0.0013673 | 0.0013623 | 0.0013559 | 0.0013496 | 0.0013435 | 0.0013315 | 0.0013032 | 0.0012807 | 0.0012626 | 0.0015563 | 0.0015561 | 0.0015558 | 0.001554 | 0.0015519 | 0.0015495 | 0.0015471 | 0.001544 | 0.0015409 | 0.0015379 | 0.0015321 | 0.0015291 | 0.0015291 | 0.0015291
STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.0939 | 1.0933 | 1.0915 | 1.0893 | 1.0871 | 1.085 | 1.0813 | 1.0764 | 1.0711 | 1.0659 | 1.0558 | 1.0205 | 0.98732 | 0.98197 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166
| GISLA | CT |  |  |  | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.0939 | 1.0934 | 1.092 | 1.0905 | 1.089 | 1.0875 | 1.086 | 1.0846 | 1.0831 | 1.0815 | 1.0785 | 1.0382 | 1.0049 | 0.98612 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166
| GISLA | LW |  |  |  | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.0939 | 1.0933 | 1.0915 | 1.0893 | 1.0871 | 1.085 | 1.0829 | 1.0809 | 1.0787 | 1.0765 | 1.0722 | 1.0205 | 0.98732 | 0.98197 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166
| GISLA | ST |  |  |  | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.0941 | 1.0939 | 1.0933 | 1.0925 | 1.0915 | 1.0863 | 1.0813 | 1.0764 | 1.0711 | 1.0659 | 1.0558 | 1.0329 | 1.0133 | 0.99742 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166
| GISLA | FS |  |  |  | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.3308 | 1.0942 | 1.0942 | 1.0941 | 1.0939 | 1.0936 | 1.0919 | 1.0903 | 1.0881 | 1.0861 | 1.084 | 1.08 | 1.0706 | 1.0617 | 1.0535 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166 | 0.9166
ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 4.9095 | 4.9091 | 4.9081 | 4.9069 | 4.9058 | 4.9047 | 4.9036 | 4.9025 | 4.9013 | 4.9002 | 4.8979 | 4.895 | 3.4159 | 3.3555 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5079 | 3.4349 | 4.979 | 4.9787 | 4.9779 | 4.977 | 4.9761 | 4.9752 | 4.9743 | 4.9735 | 4.9725 | 4.9716 | 4.9698 | 4.9653 | 3.4229 | 3.3554
| GLASTULLICH | CT |  |  |  | 4.9095 | 4.9091 | 4.9081 | 4.9069 | 4.9058 | 4.9047 | 4.9036 | 4.9025 | 4.9013 | 4.9002 | 4.8979 | 4.895 | 3.4159 | 3.3555 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5079 | 3.4349 | 4.979 | 4.9787 | 4.9779 | 4.977 | 4.9761 | 4.9752 | 4.9743 | 4.9735 | 4.9725 | 4.9716 | 4.9698 | 4.9653 | 3.4229 | 3.3554
| GLASTULLICH | LW |  |  |  | 4.9096 | 4.9096 | 4.9093 | 4.909 | 4.9087 | 4.9084 | 4.9081 | 4.9078 | 4.9075 | 4.9072 | 4.9066 | 4.8984 | 3.4538 | 3.3682 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5537 | 3.4503 | 4.9792 | 4.9791 | 4.9789 | 4.9786 | 4.9784 | 4.9782 | 4.9779 | 4.9777 | 4.9775 | 4.9772 | 4.9767 | 4.9702 | 3.4653 | 3.3696
| GLASTULLICH | ST |  |  |  | 4.9097 | 4.9096 | 4.9096 | 4.9094 | 4.9093 | 4.9086 | 4.9079 | 4.9072 | 4.9064 | 4.9057 | 4.9043 | 4.9008 | 3.9342 | 3.8999 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.9455 | 3.9014 | 4.9792 | 4.9792 | 4.9791 | 4.979 | 4.9789 | 4.9783 | 4.9777 | 4.9772 | 4.9766 | 4.976 | 4.9749 | 4.9721 | 3.963 | 3.9222
| GLASTULLICH | FS |  |  |  | 4.9097 | 4.9097 | 4.9097 | 4.9096 | 4.9096 | 4.9094 | 4.9091 | 4.9088 | 4.9085 | 4.9082 | 4.9077 | 4.9064 | 4.9051 | 4.9038 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.9792 | 4.9792 | 4.9792 | 4.9792 | 4.9791 | 4.9789 | 4.9787 | 4.9785 | 4.9783 | 4.978 | 4.9776 | 4.9765 | 4.9755 | 4.9745
SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | YES | 4.2502 | 4.2501 | 4.2497 | 4.2492 | 4.2488 | 4.2483 | 4.2477 | 4.246 | 4.2449 | 4.2439 | 4.2418 | 4.233 | 4.2218 | 4.2108 | 3.8809 | 3.8793 | 3.8746 | 3.8689 | 3.8633 | 3.8578 | 3.8508 | 3.8342 | 3.8294 | 3.8246 | 3.815 | 3.814 | 3.814 | 3.1999 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.2296
| GLEDFIELD | CT |  |  |  | 4.2502 | 4.2501 | 4.2498 | 4.2495 | 4.2491 | 4.2488 | 4.2485 | 4.2471 | 4.2467 | 4.2463 | 4.2455 | 4.2371 | 4.2288 | 4.2206 | 3.881 | 3.8796 | 3.876 | 3.872 | 3.8681 | 3.8642 | 3.8604 | 3.8429 | 3.8384 | 3.8357 | 3.8318 | 3.814 | 3.814 | 3.814 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572
| GLEDFIELD | LW |  |  |  | 4.2502 | 4.2501 | 4.2497 | 4.2492 | 4.2488 | 4.2483 | 4.2479 | 4.246 | 4.2455 | 4.245 | 4.244 | 4.233 | 4.2218 | 4.2108 | 3.8809 | 3.8793 | 3.8746 | 3.8689 | 3.8633 | 3.8578 | 3.8525 | 3.8343 | 3.8319 | 3.8296 | 3.8252 | 3.814 | 3.814 | 3.1999 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.2296
| GLEDFIELD | ST |  |  |  | 4.2503 | 4.2502 | 4.2501 | 4.2499 | 4.2497 | 4.2487 | 4.2477 | 4.246 | 4.2449 | 4.2439 | 4.2418 | 4.2368 | 4.232 | 4.2273 | 3.8814 | 3.8808 | 3.8794 | 3.8772 | 3.8745 | 3.8625 | 3.8508 | 3.8342 | 3.8294 | 3.8246 | 3.815 | 3.814 | 3.814 | 3.814 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572
| GLEDFIELD | FS |  |  |  | 4.2503 | 4.2503 | 4.2503 | 4.2502 | 4.2501 | 4.2498 | 4.2495 | 4.2488 | 4.2484 | 4.2479 | 4.2471 | 4.2452 | 4.2435 | 4.2418 | 3.8817 | 3.8816 | 3.8815 | 3.8809 | 3.8801 | 3.8762 | 3.8723 | 3.8636 | 3.8585 | 3.8535 | 3.8434 | 3.8305 | 3.8226 | 3.815 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572 | 3.9572
FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | -0.00085013 | 0.0023729 | 0.0023418 | 0.0022562 | 0.0021726 | 0.0021402 | 0.0021274 | 0.0021274 | 0.0021274 | 0.0021274 | 0.0021274 | -0.00014213 | -0.0011836 | -0.0023012 | -0.0033906 | 0.0026843 | 0.0026692 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | -0.00071836 | -0.0018325 | -0.0029223
| GLEN LAOGH | CT |  |  |  | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.002373 | 0.0023471 | 0.0022825 | 0.0022159 | 0.0021616 | 0.0021433 | 0.0021306 | 0.0021274 | 0.0021274 | 0.0021274 | 0.0021274 | -0.00026612 | -0.0010574 | -0.0018399 | 0.0026843 | 0.0026717 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | -0.00059547 | -0.0013711
| GLEN LAOGH | LW |  |  |  | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | -0.00085013 | 0.0023729 | 0.0023418 | 0.0022562 | 0.0021726 | 0.0021402 | 0.0021274 | 0.0021274 | 0.0021274 | 0.0021274 | 0.0021274 | -0.00014213 | -0.0011836 | -0.0023012 | -0.0033906 | 0.0026843 | 0.0026692 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | -0.00071836 | -0.0018325 | -0.0029223
| GLEN LAOGH | ST |  |  |  | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0023821 | 0.00237 | 0.0023435 | 0.0023033 | 0.0022554 | 0.0022151 | 0.0021801 | 0.0021522 | 0.0021433 | 0.0021346 | 0.0021274 | 0.0021274 | 0.0021274 | -0.00040711 | 0.0026887 | 0.0026829 | 0.00267 | 0.0026505 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454
| GLEN LAOGH | FS |  |  |  | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0042611 | 0.0023877 | 0.0023855 | 0.0023828 | 0.0023712 | 0.0023574 | 0.0023416 | 0.0023258 | 0.0023055 | 0.0022857 | 0.0022663 | 0.0022304 | 0.0021638 | 0.0021402 | 0.0021274 | 0.0026915 | 0.0026904 | 0.0026891 | 0.0026834 | 0.0026768 | 0.0026691 | 0.0026614 | 0.0026516 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454 | 0.0026454
KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 4.5563 | 4.5534 | 4.5427 | 4.5323 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.333 | 4.33 | 4.319 | 4.3095 | 4.3058 | 4.3022 | 4.2987 | 4.2953 | 4.2915 | 4.2878 | 4.2805 | 4.2672 | 4.2535 | 3.1548 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
| GLENCOE | CT |  |  |  | 4.5565 | 4.5543 | 4.5467 | 4.5403 | 4.5339 | 4.5277 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.3332 | 4.3309 | 4.3231 | 4.3164 | 4.3101 | 4.3078 | 4.3056 | 4.3033 | 4.3009 | 4.2985 | 4.294 | 4.2839 | 4.2736 | 4.2634 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
| GLENCOE | LW |  |  |  | 4.5563 | 4.5534 | 4.5427 | 4.5323 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.333 | 4.33 | 4.319 | 4.3095 | 4.3058 | 4.3022 | 4.2987 | 4.2953 | 4.2915 | 4.2878 | 4.2805 | 4.2672 | 4.2535 | 3.1548 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
| GLENCOE | ST |  |  |  | 4.5572 | 4.5561 | 4.5522 | 4.5483 | 4.5435 | 4.54 | 4.5365 | 4.5329 | 4.5292 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.3339 | 4.3327 | 4.3288 | 4.3247 | 4.3197 | 4.3162 | 4.3125 | 4.3097 | 4.3084 | 4.3071 | 4.3047 | 4.2987 | 4.2927 | 4.2868 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
| GLENCOE | FS |  |  |  | 4.5577 | 4.5575 | 4.5566 | 4.5555 | 4.5541 | 4.553 | 4.5518 | 4.5503 | 4.5489 | 4.5475 | 4.5447 | 4.5384 | 4.5324 | 4.5266 | 4.3344 | 4.3343 | 4.3333 | 4.3321 | 4.3307 | 4.3295 | 4.3283 | 4.3268 | 4.3253 | 4.3238 | 4.321 | 4.3145 | 4.3095 | 4.3075 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.12735 | 0.12735 | 0.12735 | 0.12735 | -0.002484 | -0.035607 | -0.068154 | -0.10014 | -0.13476 | -0.16916 | -0.23736 | -0.28922 | -0.34169 | -0.39339 | 0.069189 | 0.066313 | 0.066313 | -0.027072 | -0.066831 | -0.10591 | -0.1443 | -0.18204 | -0.22288 | -0.26346 | -0.34392 | -0.40511 | -0.467 | -0.528 | 0.082053 | 0.081028 | 0.08065 | -0.021917 | -0.061689 | -0.10078 | -0.13919 | -0.17693 | -0.21779 | -0.25838 | -0.33887 | -0.40007 | -0.46199 | -0.52301
| GLENDARUEL | CT |  |  |  | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | -0.022474 | 0.071221 | 0.070791 | 0.069695 | 0.068996 | 0.068306 | 0.067627 | 0.066962 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | -0.0062587 | -0.048664 | -0.090414 | 0.082579 | 0.082439 | 0.082229 | 0.081986 | 0.081746 | 0.08151 | 0.081278 | 0.081051 | 0.080805 | 0.08065 | 0.08065 | -0.001097 | -0.043517 | -0.08528
| GLENDARUEL | LW |  |  |  | 0.12735 | 0.12735 | 0.12735 | 0.12735 | -0.002484 | -0.035607 | -0.068154 | -0.10014 | -0.13476 | -0.16916 | -0.23736 | -0.28922 | -0.34169 | -0.39339 | 0.069189 | 0.066313 | 0.066313 | -0.027072 | -0.066831 | -0.10591 | -0.1443 | -0.18204 | -0.22288 | -0.26346 | -0.34392 | -0.40511 | -0.467 | -0.528 | 0.082053 | 0.081028 | 0.08065 | -0.021917 | -0.061689 | -0.10078 | -0.13919 | -0.17693 | -0.21779 | -0.25838 | -0.33887 | -0.40007 | -0.46199 | -0.52301
| GLENDARUEL | ST |  |  |  | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | -0.01558 | -0.038611 | 0.070311 | 0.068939 | 0.066336 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | -0.0045013 | -0.010409 | -0.01621 | -0.027557 | -0.055061 | -0.082281 | -0.10945 | 0.082351 | 0.081966 | 0.08106 | 0.08065 | 0.08065 | 0.08065 | 0.08065 | 0.08065 | -0.0052482 | -0.011052 | -0.022402 | -0.049915 | -0.077145 | -0.10432
| GLENDARUEL | FS |  |  |  | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.12735 | 0.071285 | 0.07102 | 0.070678 | 0.069102 | 0.067746 | 0.067269 | 0.066796 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | 0.066313 | 0.08261 | 0.082481 | 0.082418 | 0.082023 | 0.081551 | 0.081385 | 0.08122 | 0.081008 | 0.080799 | 0.08065 | 0.08065 | 0.08065 | 0.08065 | 0.08065
ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 7.0629 | 7.046 | 7.0002 | 6.9441 | 6.8861 | 6.8255 | 6.7664 | 6.7073 | 6.6433 | 6.5797 | 6.4607 | 6.2852 | 6.1105 | 5.9386 | 7.2186 | 7.1976 | 7.1404 | 7.0704 | 6.9981 | 6.9225 | 6.8488 | 6.7749 | 6.6951 | 6.6159 | 6.4674 | 6.2484 | 6.0304 | 5.8161 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9126 | 6.84 | 6.7672 | 6.6886 | 6.6105 | 6.4642 | 6.2485 | 6.0337 | 5.8225
| GLENDEVON | CT |  |  |  | 7.0646 | 7.0533 | 7.0258 | 6.9943 | 6.9608 | 6.9246 | 6.8899 | 6.8547 | 6.8162 | 6.7768 | 6.7036 | 6.5737 | 6.4503 | 6.3302 | 7.2207 | 7.2066 | 7.1723 | 7.133 | 7.0913 | 7.0461 | 7.0028 | 6.9589 | 6.9108 | 6.8617 | 6.7703 | 6.6083 | 6.4544 | 6.3046 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9011 | 6.8527 | 6.7627 | 6.6031 | 6.4514 | 6.3038
| GLENDEVON | LW |  |  |  | 7.0629 | 7.046 | 7.0002 | 6.9441 | 6.8861 | 6.8255 | 6.7664 | 6.7073 | 6.6433 | 6.5797 | 6.4607 | 6.2852 | 6.1105 | 5.9386 | 7.2186 | 7.1976 | 7.1404 | 7.0704 | 6.9981 | 6.9225 | 6.8488 | 6.7749 | 6.6951 | 6.6159 | 6.4674 | 6.2484 | 6.0304 | 5.8161 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9126 | 6.84 | 6.7672 | 6.6886 | 6.6105 | 6.4642 | 6.2485 | 6.0337 | 5.8225
| GLENDEVON | ST |  |  |  | 7.2121 | 7.0611 | 7.0466 | 7.0244 | 6.9964 | 6.9753 | 6.9552 | 6.9348 | 6.9123 | 6.8891 | 6.8469 | 6.7632 | 6.6859 | 6.61 | 7.4048 | 7.2164 | 7.1983 | 7.1706 | 7.1356 | 7.1093 | 7.0843 | 7.0588 | 7.0307 | 7.0018 | 6.9491 | 6.8447 | 6.7483 | 6.6536 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.8359 | 6.741 | 6.6477
| GLENDEVON | FS |  |  |  | 7.2152 | 7.2139 | 7.2123 | 7.2058 | 7.1975 | 7.1901 | 7.1829 | 7.1742 | 7.1652 | 7.1562 | 7.14 | 7.1072 | 7.0791 | 7.0533 | 7.4086 | 7.407 | 7.405 | 7.3969 | 7.3865 | 7.3772 | 7.3684 | 7.3574 | 7.3462 | 7.335 | 7.3148 | 7.2739 | 7.2388 | 7.2066 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254 | 6.9254
FORT AUGUSTUS | GLENDOE PRIMARY | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5197 | 2.519 | 2.517 | 2.5146 | 2.5122 | 2.5099 | 2.5076 | 2.5048 | 2.5005 | 2.4963 | 2.4881 | 2.4694 | 2.4694 | 1.9441 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 1.9314
| GLENDOE PRIMARY | CT |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5197 | 2.5191 | 2.5176 | 2.5159 | 2.5143 | 2.5126 | 2.5111 | 2.5095 | 2.5078 | 2.5062 | 2.5029 | 2.4707 | 2.4694 | 2.4694 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
| GLENDOE PRIMARY | LW |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5197 | 2.519 | 2.517 | 2.5146 | 2.5122 | 2.5099 | 2.5076 | 2.5054 | 2.503 | 2.5007 | 2.496 | 2.4694 | 2.4694 | 1.9441 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 1.9314
| GLENDOE PRIMARY | ST |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5199 | 2.5196 | 2.519 | 2.5181 | 2.517 | 2.5128 | 2.5088 | 2.5048 | 2.5005 | 2.4963 | 2.4881 | 2.4694 | 2.4694 | 2.4694 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
| GLENDOE PRIMARY | FS |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.52 | 2.5199 | 2.5199 | 2.5196 | 2.5193 | 2.518 | 2.5166 | 2.5149 | 2.5132 | 2.5116 | 2.5083 | 2.5007 | 2.4936 | 2.4869 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | NO | 22.6433 | 31.2866 | 31.1755 | 31.0717 | 30.9716 | 30.8753 | 30.7826 | 30.6937 | 30.6435 | 30.6185 | 30.5694 | 30.2834 | 30.159 | 30.0266 | 20.4718 | 28.6896 | 28.6148 | 28.5547 | 28.4968 | 28.4411 | 28.3874 | 28.336 | 28.3069 | 28.2924 | 28.264 | 28.0985 | 28.0265 | 27.9499 | 22.292 | 30.4743 | 30.3395 | 30.2087 | 30.0831 | 29.9573 | 29.8315 | 29.7102 | 29.6261 | 29.5671 | 29.4557 | 29.0035 | 28.8251 | 28.6931
| GLENEAGLES | CT |  |  |  | 22.6433 | 31.2866 | 31.1755 | 31.0717 | 30.9716 | 30.8753 | 30.7826 | 30.6937 | 30.6435 | 30.6185 | 30.5694 | 30.2834 | 30.159 | 30.0266 | 20.4718 | 28.6896 | 28.6148 | 28.5547 | 28.4968 | 28.4411 | 28.3874 | 28.336 | 28.3069 | 28.2924 | 28.264 | 28.0985 | 28.0265 | 27.9499 | 22.292 | 30.4743 | 30.3395 | 30.2087 | 30.0831 | 29.9573 | 29.8315 | 29.7102 | 29.6261 | 29.5671 | 29.4557 | 29.0035 | 28.8251 | 28.6931
| GLENEAGLES | LW |  |  |  | 22.7678 | 31.4834 | 31.4667 | 31.4479 | 31.4272 | 31.4048 | 31.3809 | 31.3556 | 31.3274 | 31.2983 | 31.2385 | 30.9106 | 30.7269 | 30.53 | 20.5588 | 28.8177 | 28.7901 | 28.7724 | 28.7605 | 28.7475 | 28.7337 | 28.719 | 28.7027 | 28.6859 | 28.6512 | 28.4615 | 28.3552 | 28.2412 | 22.4209 | 30.6765 | 30.6344 | 30.5839 | 30.533 | 30.476 | 30.4125 | 30.3496 | 30.2804 | 30.2101 | 30.0765 | 29.575 | 29.3917 | 29.1952
| GLENEAGLES | ST |  |  |  | 22.7869 | 31.5119 | 31.5052 | 31.4988 | 31.4925 | 31.4848 | 31.4774 | 31.4702 | 31.4634 | 31.4534 | 31.4344 | 31.2987 | 31.2516 | 31.1998 | 20.5801 | 28.8473 | 28.8312 | 28.8177 | 28.8035 | 28.7938 | 28.7895 | 28.7853 | 28.7814 | 28.7756 | 28.7646 | 28.6861 | 28.6589 | 28.6289 | 22.4435 | 30.7141 | 30.6978 | 30.6773 | 30.6558 | 30.6253 | 30.5926 | 30.5606 | 30.5266 | 30.4885 | 30.4172 | 30.1787 | 30.0452 | 29.9105
| GLENEAGLES | FS |  |  |  | 22.7819 | 31.5052 | 31.4986 | 31.4888 | 31.4791 | 31.4695 | 31.4601 | 31.4508 | 31.4416 | 31.4326 | 31.4149 | 31.3622 | 31.3072 | 31.254 | 20.5802 | 28.852 | 28.8421 | 28.8254 | 28.8158 | 28.8041 | 28.7917 | 28.7788 | 28.7688 | 28.7636 | 28.7533 | 28.7228 | 28.691 | 28.6602 | 22.4403 | 30.7121 | 30.7031 | 30.6882 | 30.6735 | 30.6555 | 30.6365 | 30.6166 | 30.5964 | 30.5762 | 30.538 | 30.4435 | 30.3542 | 30.2705
RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | -0.0087959 | -0.019616 | 0.051429 | 0.049961 | 0.048662 | 0.047896 | 0.047822 | 0.047822 | -0.00044977 | -0.0084147 | -0.01702 | -0.025576 | -0.042536 | -0.055403 | -0.068385 | -0.081089 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | -0.0016069 | -0.010215 | -0.018773 | -0.03574 | -0.04861 | -0.061597 | -0.074305
| GLENETIVE | CT |  |  |  | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.051523 | 0.050452 | 0.048947 | 0.048477 | 0.048015 | 0.047822 | 0.047822 | 0.047822 | 0.047822 | 0.047822 | -0.010201 | -0.019173 | -0.028233 | -0.037174 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | -0.0033934 | -0.012369 | -0.021432 | -0.030376
| GLENETIVE | LW |  |  |  | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | -0.0087959 | -0.019616 | 0.051429 | 0.049961 | 0.048662 | 0.047896 | 0.047822 | 0.047822 | -0.00044977 | -0.0084147 | -0.01702 | -0.025576 | -0.042536 | -0.055403 | -0.068385 | -0.081089 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | -0.0016069 | -0.010215 | -0.018773 | -0.03574 | -0.04861 | -0.061597 | -0.074305
| GLENETIVE | ST |  |  |  | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.051861 | 0.051317 | 0.050038 | 0.049003 | 0.04865 | 0.048543 | 0.048438 | 0.048336 | 0.048225 | 0.048116 | 0.047905 | 0.047822 | 0.047822 | 0.047822 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325
| GLENETIVE | FS |  |  |  | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.10161 | 0.052114 | 0.052044 | 0.051954 | 0.051393 | 0.050726 | 0.05049 | 0.050256 | 0.04995 | 0.04966 | 0.049425 | 0.049163 | 0.048916 | 0.048733 | 0.048563 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325 | 0.058325
FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | -0.0078227 | 0.033344 | 0.033236 | 0.032928 | 0.032575 | 0.032381 | 0.032192 | 0.031802 | 0.03133 | 0.030993 | 0.030993 | 0.030993 | 0.030993 | -0.018927 | -0.039095 | 0.038623 | 0.03857 | 0.038501 | 0.038432 | 0.038365 | 0.038299 | 0.038163 | 0.037999 | 0.037823 | 0.037694 | 0.037694 | 0.037694 | -0.016519 | -0.036694
| GLENUIG | CT |  |  |  | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.033344 | 0.033254 | 0.033023 | 0.03276 | 0.032548 | 0.032415 | 0.032285 | 0.032157 | 0.032019 | 0.031882 | 0.031612 | 0.030993 | -0.0054826 | -0.020156 | 0.038623 | 0.038579 | 0.038518 | 0.03847 | 0.038423 | 0.038377 | 0.038331 | 0.038287 | 0.038239 | 0.038191 | 0.038097 | 0.037694 | -0.003071 | -0.017749
| GLENUIG | LW |  |  |  | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | -0.0078227 | 0.033344 | 0.033236 | 0.032928 | 0.032575 | 0.032381 | 0.032192 | 0.032007 | 0.031825 | 0.031629 | 0.031434 | 0.03105 | 0.030993 | -0.018927 | -0.039095 | 0.038623 | 0.03857 | 0.038501 | 0.038432 | 0.038365 | 0.038299 | 0.038234 | 0.038171 | 0.038103 | 0.038035 | 0.037902 | 0.037694 | -0.016519 | -0.036694
| GLENUIG | ST |  |  |  | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.033376 | 0.033335 | 0.033241 | 0.033097 | 0.032925 | 0.032282 | 0.031802 | 0.03133 | 0.030993 | 0.030993 | 0.030993 | 0.030993 | -0.002688 | -0.011636 | 0.038639 | 0.038619 | 0.038573 | 0.038532 | 0.0385 | 0.03833 | 0.038163 | 0.037999 | 0.037823 | 0.037694 | 0.037694 | 0.037694 | -0.00027543 | -0.009226
| GLENUIG | FS |  |  |  | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.05952 | 0.033395 | 0.033389 | 0.033381 | 0.03334 | 0.033292 | 0.032982 | 0.032683 | 0.03244 | 0.032239 | 0.032043 | 0.031659 | 0.030993 | 0.030993 | 0.030993 | 0.038648 | 0.038645 | 0.038641 | 0.038621 | 0.038598 | 0.038511 | 0.038456 | 0.038385 | 0.038315 | 0.038247 | 0.038114 | 0.037803 | 0.037694 | 0.037694
BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9453 | 4.9394 | 4.9258 | 4.9101 | 4.8947 | 4.8808 | 4.8668 | 4.8528 | 4.8377 | 4.8229 | 4.7959 | 4.7673 | 4.7673 | 3.9964 | 5.0588 | 5.0566 | 5.0516 | 5.0458 | 5.0401 | 5.0349 | 5.0297 | 5.0245 | 5.0189 | 5.0134 | 5.0027 | 4.9697 | 4.9353 | 4.9039
| GOLSPIE | CT |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9453 | 4.9394 | 4.9258 | 4.9101 | 4.8947 | 4.8808 | 4.8668 | 4.8528 | 4.8377 | 4.8229 | 4.7959 | 4.7673 | 4.7673 | 3.9964 | 5.0588 | 5.0566 | 5.0516 | 5.0458 | 5.0401 | 5.0349 | 5.0297 | 5.0245 | 5.0189 | 5.0134 | 5.0027 | 4.9697 | 4.9353 | 4.9039
| GOLSPIE | LW |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9475 | 4.9452 | 4.9406 | 4.935 | 4.9296 | 4.9256 | 4.9217 | 4.9179 | 4.9137 | 4.9097 | 4.9018 | 4.7936 | 4.7673 | 4.7673 | 5.0597 | 5.0588 | 5.0571 | 5.055 | 5.053 | 5.0515 | 5.0501 | 5.0486 | 5.0471 | 5.0456 | 5.0427 | 5.0017 | 4.9593 | 4.9179
| GOLSPIE | ST |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9481 | 4.947 | 4.9452 | 4.9427 | 4.94 | 4.931 | 4.9219 | 4.9128 | 4.9031 | 4.8936 | 4.8756 | 4.8321 | 4.7902 | 4.7673 | 5.0599 | 5.0594 | 5.0588 | 5.0579 | 5.0569 | 5.0535 | 5.0501 | 5.0468 | 5.0432 | 5.0396 | 5.033 | 5.0168 | 5.0001 | 4.9836
| GOLSPIE | FS |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9486 | 4.948 | 4.9474 | 4.9465 | 4.9455 | 4.9422 | 4.9389 | 4.9346 | 4.9305 | 4.9264 | 4.9186 | 4.9003 | 4.8827 | 4.8656 | 5.06 | 5.0598 | 5.0596 | 5.0593 | 5.0589 | 5.0577 | 5.0564 | 5.0549 | 5.0533 | 5.0518 | 5.0489 | 5.0421 | 5.0356 | 5.0293
BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0416 | 17.0208 | 16.9612 | 16.8866 | 16.8114 | 16.7515 | 16.7196 | 16.688 | 16.6536 | 16.6197 | 16.5498 | 16.3749 | 16.2158 | 16.2158 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
| GOODLYBURN | CT |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0453 | 17.0338 | 17.0042 | 16.9689 | 16.9327 | 16.8946 | 16.858 | 16.8212 | 16.7811 | 16.7546 | 16.719 | 16.5862 | 16.4579 | 16.3361 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
| GOODLYBURN | LW |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0416 | 17.0208 | 16.9612 | 16.8866 | 16.8114 | 16.7515 | 16.7196 | 16.688 | 16.6536 | 16.6197 | 16.5498 | 16.3749 | 16.2158 | 16.2158 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
| GOODLYBURN | ST |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0483 | 17.0397 | 17.0196 | 16.9882 | 16.95 | 16.9126 | 16.8764 | 16.8405 | 16.8014 | 16.7637 | 16.7298 | 16.6454 | 16.5664 | 16.4917 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
| GOODLYBURN | FS |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.053 | 17.0515 | 17.0494 | 17.0404 | 17.0295 | 17.0174 | 17.0057 | 16.991 | 16.9763 | 16.9619 | 16.9323 | 16.8584 | 16.7906 | 16.7491 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | NO | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 8.0927 | 7.7495 | 7.4069 | 7.0718 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 8.1408 | 8.0102 | 7.8818 | 7.7426 | 7.6041 | 7.3295 | 6.9246 | 6.5205 | 6.1251 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 8.112 | 7.9764 | 7.8415 | 7.574 | 7.1796 | 6.786 | 6.4009
| GOURDIE | CT |  |  |  | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 8.0962 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 8.132 | 7.8628 | 7.595 | 7.3336 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 8.0935 | 7.8326 | 7.578
| GOURDIE | LW |  |  |  | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 8.0927 | 7.7495 | 7.4069 | 7.0718 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 8.1408 | 8.0102 | 7.8818 | 7.7426 | 7.6041 | 7.3295 | 6.9246 | 6.5205 | 6.1251 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 8.112 | 7.9764 | 7.8415 | 7.574 | 7.1796 | 6.786 | 6.4009
| GOURDIE | ST |  |  |  | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 8.0739 | 7.8932 | 7.7152 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 8.1231 | 7.9497
| GOURDIE | FS |  |  |  | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 10.0256 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.6242 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573 | 9.8573
BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 18.1416 | 18.0544 | 17.9424 | 17.8359 | 17.7332 | 17.6343 | 17.5392 | 17.448 | 17.4061 | 17.3853 | 17.3444 | 17.2453 | 14.4557 | 14.074 | 16.3866 | 16.3025 | 16.187 | 16.0739 | 15.9658 | 15.8752 | 15.8192 | 15.7655 | 15.7408 | 15.7286 | 15.7045 | 15.6462 | 13.6918 | 13.1169 | 16.6299 | 16.535 | 16.4132 | 16.2972 | 16.1854 | 16.0778 | 15.9743 | 15.8749 | 15.8294 | 15.8067 | 15.7622 | 15.6543 | 13.5185 | 12.9623
| GRANTOWN | CT |  |  |  | 18.1416 | 18.0544 | 17.9424 | 17.8359 | 17.7332 | 17.6343 | 17.5392 | 17.448 | 17.4061 | 17.3853 | 17.3444 | 17.2453 | 14.4557 | 14.074 | 16.3866 | 16.3025 | 16.187 | 16.0739 | 15.9658 | 15.8752 | 15.8192 | 15.7655 | 15.7408 | 15.7286 | 15.7045 | 15.6462 | 13.7804 | 13.3462 | 16.6299 | 16.535 | 16.4132 | 16.2972 | 16.1854 | 16.0778 | 15.9743 | 15.8749 | 15.8294 | 15.8067 | 15.7622 | 15.6543 | 13.5185 | 13.0579
| GRANTOWN | LW |  |  |  | 18.267 | 18.2525 | 18.2357 | 18.2168 | 18.196 | 18.1734 | 18.1493 | 18.1239 | 18.1007 | 18.0768 | 18.0277 | 17.8969 | 17.7704 | 14.1068 | 16.4886 | 16.4602 | 16.4105 | 16.3526 | 16.2958 | 16.2383 | 16.1802 | 16.1633 | 16.1496 | 16.1356 | 16.1067 | 16.0297 | 13.6918 | 13.1169 | 16.7664 | 16.7506 | 16.7323 | 16.7118 | 16.6891 | 16.6646 | 16.6383 | 16.6106 | 16.5854 | 16.5594 | 16.506 | 16.3636 | 13.5757 | 12.9623
| GRANTOWN | ST |  |  |  | 18.2862 | 18.2812 | 18.2745 | 18.268 | 18.2617 | 18.2539 | 18.2465 | 18.2392 | 18.2322 | 18.222 | 18.2025 | 18.1583 | 18.1193 | 18.0833 | 16.509 | 16.4977 | 16.4808 | 16.4593 | 16.436 | 16.4138 | 16.3916 | 16.3699 | 16.3475 | 16.3232 | 16.2763 | 16.1835 | 16.1606 | 16.1394 | 16.7873 | 16.7819 | 16.7746 | 16.7675 | 16.7606 | 16.7522 | 16.7441 | 16.7362 | 16.7286 | 16.7175 | 16.6962 | 16.6481 | 16.6056 | 16.5665
| GRANTOWN | FS |  |  |  | 18.2812 | 18.2745 | 18.2678 | 18.2579 | 18.2482 | 18.2385 | 18.229 | 18.2197 | 18.2104 | 18.2013 | 18.1835 | 18.1304 | 18.0839 | 18.0408 | 16.5079 | 16.4999 | 16.4925 | 16.4794 | 16.466 | 16.4528 | 16.4397 | 16.4253 | 16.4112 | 16.3973 | 16.3703 | 16.2981 | 16.2322 | 16.1701 | 16.7819 | 16.7746 | 16.7673 | 16.7566 | 16.7459 | 16.7354 | 16.7251 | 16.7149 | 16.7048 | 16.6949 | 16.6755 | 16.6178 | 16.5671 | 16.5202
WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 26.2427 | 26.2221 | 26.1823 | 26.1422 | 26.1157 | 26.0889 | 26.0442 | 25.9987 | 25.95 | 25.9033 | 25.8137 | 25.7228 | 25.6349 | 22.2591 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 22.4405
| GREYFRIARS | CT |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 26.2488 | 26.2416 | 26.2058 | 26.1865 | 26.1795 | 26.1725 | 26.1645 | 26.154 | 26.1434 | 26.1348 | 26.1197 | 26.0495 | 25.9778 | 25.9091 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134
| GREYFRIARS | LW |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 26.2427 | 26.2221 | 26.1823 | 26.1422 | 26.1157 | 26.0899 | 26.0648 | 26.04 | 26.0133 | 25.9867 | 25.9328 | 25.7228 | 25.6349 | 22.2591 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 22.4405
| GREYFRIARS | ST |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 26.2432 | 26.2252 | 26.1941 | 26.1622 | 26.1338 | 26.0889 | 26.0442 | 25.9987 | 25.95 | 25.9033 | 25.8137 | 25.7266 | 25.6731 | 25.6203 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134
| GREYFRIARS | FS |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 26.2517 | 26.2493 | 26.2365 | 26.2103 | 26.2029 | 26.19 | 26.1771 | 26.1608 | 26.145 | 26.1294 | 26.099 | 26.0287 | 25.9613 | 25.8965 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134 | 26.4134
GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309623 | NO | YES | 23.0018 | 22.8431 | 22.6395 | 22.4388 | 22.2452 | 22.0587 | 21.8795 | 21.7075 | 21.6161 | 21.5707 | 21.4815 | 21.2586 | 21.0313 | 20.7924 | 21.8579 | 21.7313 | 21.5688 | 21.4086 | 21.2541 | 21.1053 | 20.9622 | 20.8249 | 20.752 | 20.7158 | 20.6445 | 20.4667 | 20.2853 | 20.0946 | 21.8005 | 21.6411 | 21.4366 | 21.2349 | 21.0404 | 20.8531 | 20.6731 | 20.5002 | 20.4085 | 20.3628 | 20.2732 | 20.0493 | 19.821 | 19.581
| GRUDIE BRIDGE | CT |  |  |  | 23.0018 | 22.8431 | 22.6395 | 22.4388 | 22.2452 | 22.0587 | 21.8795 | 21.7075 | 21.6161 | 21.5707 | 21.4815 | 21.2586 | 21.0313 | 20.7924 | 21.8579 | 21.7313 | 21.5688 | 21.4086 | 21.2541 | 21.1053 | 20.9622 | 20.8249 | 20.752 | 20.7158 | 20.6445 | 20.4667 | 20.2853 | 20.0946 | 21.8005 | 21.6411 | 21.4366 | 21.2349 | 21.0404 | 20.8531 | 20.6731 | 20.5002 | 20.4085 | 20.3628 | 20.2732 | 20.0493 | 19.821 | 19.581
| GRUDIE BRIDGE | LW |  |  |  | 23.2299 | 23.2034 | 23.1729 | 23.1385 | 23.1007 | 23.0596 | 23.0158 | 22.9695 | 22.9208 | 22.8706 | 22.7674 | 22.4924 | 22.1892 | 21.8403 | 22.04 | 22.0189 | 21.9945 | 21.9671 | 21.9369 | 21.9041 | 21.8691 | 21.8322 | 21.7933 | 21.7532 | 21.6709 | 21.4514 | 21.2094 | 20.9309 | 22.0296 | 22.0031 | 21.9724 | 21.9379 | 21.8998 | 21.8586 | 21.8146 | 21.7681 | 21.7191 | 21.6687 | 21.565 | 21.2887 | 20.9842 | 20.6337
| GRUDIE BRIDGE | ST |  |  |  | 23.2648 | 23.2557 | 23.2435 | 23.2317 | 23.2202 | 23.2062 | 23.1925 | 23.1793 | 23.1661 | 23.1469 | 23.1101 | 23.0193 | 22.9347 | 22.8449 | 22.0679 | 22.0606 | 22.0509 | 22.0414 | 22.0322 | 22.0211 | 22.0102 | 21.9996 | 21.9891 | 21.9738 | 21.9444 | 21.8719 | 21.8044 | 21.7327 | 22.0647 | 22.0556 | 22.0434 | 22.0315 | 22.0199 | 22.0058 | 21.9921 | 21.9788 | 21.9656 | 21.9463 | 21.9093 | 21.8181 | 21.7331 | 21.6429
| GRUDIE BRIDGE | FS |  |  |  | 23.2557 | 23.2435 | 23.2314 | 23.2134 | 23.1956 | 23.1781 | 23.1608 | 23.1438 | 23.127 | 23.1104 | 23.078 | 22.9815 | 22.8894 | 22.8022 | 22.0606 | 22.0509 | 22.0412 | 22.0268 | 22.0127 | 21.9987 | 21.9849 | 21.9713 | 21.9579 | 21.9446 | 21.9188 | 21.8418 | 21.7683 | 21.6986 | 22.0556 | 22.0434 | 22.0312 | 22.0131 | 21.9952 | 21.9776 | 21.9603 | 21.9431 | 21.9263 | 21.9096 | 21.877 | 21.7801 | 21.6876 | 21.6
SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.58419 | 0.58309 | 0.5799 | 0.57599 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | -0.067406 | -0.12242 | -0.17815 | -0.23289 | 0.48761 | 0.474 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | -0.02999 | -0.076154 | -0.12202 | -0.21292 | -0.27441 | -0.33671 | -0.3979 | 0 | 0 | 0 | -0.001064 | -0.047644 | -0.093391 | -0.13835 | -0.18256 | -0.2304 | -0.27792 | -0.37211 | -0.43583 | -0.5004 | -0.5638
| GUTCHER | CT |  |  |  | 0.58423 | 0.58336 | 0.5811 | 0.57851 | 0.57597 | 0.57347 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | -0.016801 | -0.058543 | 0.488 | 0.4773 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | -0.0019602 | -0.062033 | -0.10892 | -0.15635 | -0.20301 | 0 | 0 | 0 | 0 | -0.0013074 | -0.031543 | -0.061284 | -0.090506 | -0.12212 | -0.15352 | -0.21576 | -0.26435 | -0.3135 | -0.36185
| GUTCHER | LW |  |  |  | 0.58419 | 0.58309 | 0.5799 | 0.57599 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | 0.57299 | -0.067406 | -0.12242 | -0.17815 | -0.23289 | 0.48761 | 0.474 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | -0.02999 | -0.076154 | -0.12202 | -0.21292 | -0.27441 | -0.33671 | -0.3979 | 0 | 0 | 0 | -0.001064 | -0.047644 | -0.093391 | -0.13835 | -0.18256 | -0.2304 | -0.27792 | -0.37211 | -0.43583 | -0.5004 | -0.5638
| GUTCHER | ST |  |  |  | 0.58453 | 0.58413 | 0.5832 | 0.58175 | 0.58002 | 0.57959 | 0.57916 | 0.57875 | 0.5783 | 0.57786 | 0.57701 | 0.57493 | 0.57299 | 0.57299 | 0.49169 | 0.48683 | 0.47539 | 0.45754 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0.45252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01383 | -0.038801 | -0.063662
| GUTCHER | FS |  |  |  | 0.58471 | 0.58466 | 0.58459 | 0.58417 | 0.58368 | 0.58352 | 0.58337 | 0.58317 | 0.58298 | 0.58278 | 0.58241 | 0.58154 | 0.58073 | 0.57996 | 0.49394 | 0.49329 | 0.49246 | 0.48733 | 0.48125 | 0.47933 | 0.47743 | 0.475 | 0.4726 | 0.47025 | 0.4657 | 0.455 | 0.45252 | 0.45252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 4.2713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 3.6302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 3.9064 | 3.6671 | 3.4328 | 3.6882 | 5.1861 | 5.1801 | 5.1726 | 5.1653 | 5.1581 | 5.151 | 5.144 | 5.1365 | 5.129 | 5.1141 | 5.1134 | 3.7764 | 3.542
| HALKIRK | CT |  |  |  | 4.2713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 3.6302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 3.9823 | 3.8002 | 3.6883 | 5.1868 | 5.1827 | 5.178 | 5.1734 | 5.1689 | 5.1644 | 5.16 | 5.1552 | 5.1505 | 5.1412 | 5.1177 | 5.1134 | 3.9096
| HALKIRK | LW |  |  |  | 4.2713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 3.6302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 3.9064 | 3.6671 | 3.4328 | 3.6882 | 5.1861 | 5.1801 | 5.1726 | 5.1653 | 5.1581 | 5.151 | 5.144 | 5.1365 | 5.129 | 5.1141 | 5.1134 | 3.7764 | 3.542
| HALKIRK | ST |  |  |  | 4.2713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 3.6302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 3.6889 | 5.1881 | 5.1864 | 5.1836 | 5.1803 | 5.1776 | 5.1749 | 5.1723 | 5.1695 | 5.1667 | 5.1612 | 5.148 | 5.1346 | 5.1213
| HALKIRK | FS |  |  |  | 4.2713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 5.7713 | 3.6302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 5.1302 | 3.6892 | 5.1891 | 5.189 | 5.1882 | 5.1873 | 5.1864 | 5.1855 | 5.1844 | 5.1832 | 5.1821 | 5.18 | 5.175 | 5.1702 | 5.1656
ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 23.0173 | 22.9962 | 22.9394 | 22.8661 | 22.7797 | 22.6933 | 22.6117 | 22.5324 | 22.4511 | 22.3695 | 22.2395 | 22.2395 | 22.2395 | 17.8934 | 23.9785 | 23.9521 | 23.881 | 23.7893 | 23.6811 | 23.573 | 23.527 | 23.4906 | 23.4534 | 23.416 | 23.34 | 23.115 | 22.9651 | 22.9651
| HARBOUR | CT |  |  |  | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 23.018 | 23.0012 | 22.9595 | 22.9081 | 22.8451 | 22.782 | 22.7238 | 22.6651 | 22.6027 | 22.5368 | 22.4054 | 22.2395 | 22.2395 | 22.2395 | 23.9794 | 23.9584 | 23.9061 | 23.8418 | 23.763 | 23.6841 | 23.6113 | 23.5514 | 23.5228 | 23.4926 | 23.4325 | 23.2826 | 23.147 | 23.018
| HARBOUR | LW |  |  |  | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 23.0173 | 22.9962 | 22.9394 | 22.8661 | 22.7797 | 22.6933 | 22.6117 | 22.5324 | 22.4511 | 22.3695 | 22.2395 | 22.2395 | 22.2395 | 17.8934 | 23.9785 | 23.9521 | 23.881 | 23.7893 | 23.6811 | 23.573 | 23.527 | 23.4906 | 23.4534 | 23.416 | 23.34 | 23.115 | 22.9651 | 22.9651
| HARBOUR | ST |  |  |  | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 23.0224 | 23.0135 | 22.9933 | 22.9622 | 22.9189 | 22.8617 | 22.8082 | 22.7546 | 22.6971 | 22.637 | 22.5173 | 22.283 | 22.2395 | 22.2395 | 23.9849 | 23.9737 | 23.9484 | 23.9096 | 23.8553 | 23.7838 | 23.7168 | 23.6498 | 23.5778 | 23.5385 | 23.4837 | 23.3764 | 23.282 | 23.1916
| HARBOUR | FS |  |  |  | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 24.5496 | 23.0255 | 23.0228 | 23.0182 | 23.0074 | 22.9921 | 22.9715 | 22.9522 | 22.9295 | 22.9072 | 22.8848 | 22.8394 | 22.7422 | 22.6612 | 22.5914 | 23.9887 | 23.9854 | 23.9796 | 23.966 | 23.9469 | 23.9212 | 23.897 | 23.8686 | 23.8407 | 23.8126 | 23.7559 | 23.6343 | 23.5496 | 23.5177
STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | NO | YES | 29.9492 | 29.8157 | 29.6223 | 29.4353 | 29.2551 | 29.0815 | 28.9146 | 28.7544 | 28.6724 | 28.6314 | 28.5508 | 28.3465 | 28.0068 | 27.7973 | 29.9187 | 29.7984 | 29.6437 | 29.4942 | 29.35 | 29.2112 | 29.0777 | 28.9495 | 28.8837 | 28.8506 | 28.7857 | 28.6162 | 28.3385 | 28.1648 | 29.8785 | 29.7277 | 29.5339 | 29.3465 | 29.1659 | 28.9919 | 28.8247 | 28.6641 | 28.5818 | 28.5405 | 28.4595 | 28.2512 | 27.9073 | 27.6938
| HARRIS GRID | CT |  |  |  | 29.9492 | 29.8157 | 29.6223 | 29.4353 | 29.2551 | 29.0815 | 28.9146 | 28.7544 | 28.6724 | 28.6314 | 28.5508 | 28.3465 | 28.0068 | 27.7973 | 29.9187 | 29.7984 | 29.6437 | 29.4942 | 29.35 | 29.2112 | 29.0777 | 28.9495 | 28.8837 | 28.8506 | 28.7857 | 28.6162 | 28.3385 | 28.1648 | 29.8785 | 29.7277 | 29.5339 | 29.3465 | 29.1659 | 28.9919 | 28.8247 | 28.6641 | 28.5818 | 28.5405 | 28.4595 | 28.2512 | 27.9073 | 27.6938
| HARRIS GRID | LW |  |  |  | 30.2306 | 30.2078 | 30.1814 | 30.1516 | 30.1188 | 29.9962 | 29.9606 | 29.9225 | 29.8836 | 29.8406 | 29.7454 | 29.4833 | 29.065 | 28.7567 | 30.1149 | 30.097 | 30.0813 | 30.0648 | 29.9905 | 29.9585 | 29.9245 | 29.8886 | 29.8522 | 29.8147 | 29.7377 | 29.5204 | 29.1788 | 28.9254 | 30.1244 | 30.1007 | 30.0741 | 30.0445 | 29.9696 | 29.9298 | 29.8874 | 29.8426 | 29.7973 | 29.7506 | 29.6547 | 29.3878 | 28.9651 | 28.6529
| HARRIS GRID | ST |  |  |  | 30.2609 | 30.253 | 30.2425 | 30.2322 | 30.2222 | 30.2101 | 30.1983 | 30.1869 | 30.1757 | 30.1594 | 30.1282 | 29.9672 | 29.8239 | 29.7409 | 30.1396 | 30.1331 | 30.1244 | 30.1159 | 30.1075 | 30.0982 | 30.0907 | 30.0834 | 30.0769 | 30.0675 | 29.9891 | 29.916 | 29.7929 | 29.7235 | 30.1557 | 30.1476 | 30.1366 | 30.1259 | 30.1155 | 30.1027 | 30.091 | 30.0796 | 30.0685 | 30.0523 | 29.9717 | 29.8817 | 29.7296 | 29.6451
| HARRIS GRID | FS |  |  |  | 30.253 | 30.2425 | 30.2319 | 30.2164 | 30.201 | 30.1858 | 30.1709 | 30.1561 | 30.1416 | 30.1273 | 30.0992 | 29.9324 | 29.8547 | 29.7719 | 30.1332 | 30.1246 | 30.1161 | 30.1033 | 30.0927 | 30.0839 | 30.0756 | 30.0673 | 30.0592 | 29.9976 | 29.972 | 29.8961 | 29.8247 | 29.7574 | 30.1476 | 30.1367 | 30.1258 | 30.1097 | 30.0937 | 30.0786 | 30.0637 | 30.049 | 29.993 | 29.9787 | 29.9468 | 29.8526 | 29.764 | 29.6804
THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 6.6507 | 6.517 | 4.9966 | 4.8379 | 4.6849 | 4.5375 | 4.3959 | 4.2408 | 4.0978 | 3.9961 | 3.7953 | 2.9085 | 2.4721 | 2.0303 | 6.1712 | 6.0669 | 5.9355 | 4.8686 | 4.6531 | 4.4442 | 4.2418 | 4.0458 | 3.904 | 3.7953 | 3.5805 | 2.7661 | 2.3108 | 1.853 | 6.1959 | 6.0574 | 5.8999 | 4.8872 | 4.643 | 4.4067 | 4.178 | 3.9571 | 3.8068 | 3.6984 | 3.47 | 2.5214 | 2.0245 | 1.5231
| HASTIGROW | CT |  |  |  | 6.6507 | 6.517 | 4.9966 | 4.8379 | 4.6849 | 4.5375 | 4.3959 | 4.2408 | 4.0978 | 3.9961 | 3.7953 | 2.9085 | 2.4721 | 2.0303 | 6.1712 | 6.0669 | 5.9355 | 4.8686 | 4.6531 | 4.4442 | 4.2418 | 4.0458 | 3.904 | 3.7953 | 3.5805 | 2.7661 | 2.3108 | 1.853 | 6.1959 | 6.0574 | 5.8999 | 4.8872 | 4.643 | 4.4067 | 4.178 | 3.9571 | 3.8068 | 3.6984 | 3.47 | 2.5214 | 2.0245 | 1.5231
| HASTIGROW | LW |  |  |  | 6.8429 | 6.8206 | 6.7949 | 6.7659 | 6.734 | 6.6994 | 6.6625 | 6.6235 | 6.5832 | 6.5417 | 6.4564 | 4.012 | 3.4419 | 2.8403 | 6.331 | 6.3001 | 6.2518 | 6.2121 | 6.1707 | 6.1396 | 6.1102 | 6.0797 | 4.8991 | 4.7917 | 4.5763 | 3.6445 | 3.0532 | 2.4391 | 6.392 | 6.3674 | 6.3358 | 6.2997 | 6.2607 | 6.2191 | 6.1771 | 6.143 | 6.1078 | 4.9397 | 4.7053 | 3.6272 | 2.98 | 2.3024
| HASTIGROW | ST |  |  |  | 6.8723 | 6.8647 | 6.8544 | 6.8444 | 6.8347 | 6.8229 | 6.8114 | 6.8003 | 6.7892 | 6.7731 | 6.7422 | 6.4564 | 6.3867 | 4.8133 | 6.36 | 6.3514 | 6.3376 | 6.321 | 6.3029 | 6.2744 | 6.2573 | 6.2407 | 6.2234 | 6.2027 | 6.168 | 4.849 | 4.6251 | 4.3994 | 6.4227 | 6.4145 | 6.4033 | 6.3919 | 6.3805 | 6.3653 | 6.3505 | 6.3361 | 6.3216 | 6.302 | 6.2643 | 4.9625 | 4.7373 | 4.4949
| HASTIGROW | FS |  |  |  | 6.8647 | 6.8544 | 6.8442 | 6.829 | 6.814 | 6.7993 | 6.7847 | 6.7703 | 6.7562 | 6.7422 | 6.7149 | 6.6336 | 6.5569 | 6.4844 | 6.3548 | 6.3461 | 6.3374 | 6.3226 | 6.3076 | 6.2885 | 6.2697 | 6.249 | 6.2317 | 6.2181 | 6.1915 | 6.1168 | 6.0572 | 6.0066 | 6.415 | 6.4046 | 6.3941 | 6.3783 | 6.3626 | 6.3465 | 6.3307 | 6.3147 | 6.299 | 6.2835 | 6.2532 | 6.1646 | 6.0848 | 6.0215
STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | NO | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 5.9304 | 4.4688 | 4.153 | 7.9958 | 7.9934 | 7.9868 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2452 | 5.721 | 4.4386 | 4.0334 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.8064 | 4.2722 | 3.8965
| HATTON | CT |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 6.0905 | 4.7285 | 4.5099 | 7.9958 | 7.9934 | 7.987 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 5.9264 | 4.7718 | 4.4913 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.9968 | 4.5811 | 4.321
| HATTON | LW |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 5.9304 | 4.4688 | 4.153 | 7.9961 | 7.9938 | 7.9868 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2452 | 5.721 | 4.4386 | 4.0334 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.8064 | 4.2722 | 3.8965
| HATTON | ST |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6205 | 5.6991 | 5.5592 | 8.0262 | 7.9964 | 7.995 | 7.9927 | 7.9897 | 7.9839 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2999 | 5.6827 | 5.5032 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.128 | 5.6203 | 5.4539
| HATTON | FS |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.0264 | 8.0263 | 8.0262 | 8.0256 | 8.0248 | 8.0229 | 8.0211 | 8.0187 | 8.0164 | 8.0141 | 8.0095 | 7.9983 | 7.9876 | 7.98 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953
PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 28.2766 | 28.2127 | 28.1739 | 28.1424 | 28.1191 | 28.0964 | 28.0741 | 28.0521 | 28.0284 | 28.005 | 27.9537 | 27.6654 | 27.5477 | 27.5176 | 27.3939 | 27.3859 | 27.38 | 27.3742 | 27.37 | 27.3658 | 27.3617 | 27.3577 | 27.3534 | 27.3491 | 27.3397 | 27.2868 | 27.2322 | 27.2135
| HAUDAGAIN | CT |  |  |  | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 28.2801 | 28.2281 | 28.1973 | 28.1772 | 28.1637 | 28.1465 | 28.1256 | 28.1087 | 28.0919 | 28.0786 | 28.0535 | 27.8524 | 27.6469 | 27.5562 | 27.3944 | 27.3878 | 27.3839 | 27.3806 | 27.3781 | 27.375 | 27.3712 | 27.3681 | 27.365 | 27.3625 | 27.358 | 27.3211 | 27.2834 | 27.2473
| HAUDAGAIN | LW |  |  |  | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 28.2766 | 28.2127 | 28.1739 | 28.1424 | 28.1191 | 28.0964 | 28.0741 | 28.0521 | 28.0284 | 28.005 | 27.9537 | 27.6654 | 27.5477 | 27.5176 | 27.3939 | 27.3859 | 27.38 | 27.3742 | 27.37 | 27.3658 | 27.3617 | 27.3577 | 27.3534 | 27.3491 | 27.3397 | 27.2868 | 27.2322 | 27.2135
| HAUDAGAIN | ST |  |  |  | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 28.2946 | 28.2586 | 28.2393 | 28.22 | 28.2024 | 28.1694 | 28.138 | 28.1096 | 28.0799 | 28.0529 | 28.0011 | 27.8543 | 27.7085 | 27.5688 | 27.4056 | 27.3917 | 27.3892 | 27.3868 | 27.3846 | 27.3792 | 27.3734 | 27.3682 | 27.3628 | 27.3578 | 27.3484 | 27.3214 | 27.2947 | 27.2691
| HAUDAGAIN | FS |  |  |  | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 30.0755 | 28.3095 | 28.2885 | 28.2804 | 28.2714 | 28.2647 | 28.2503 | 28.2365 | 28.2196 | 28.2029 | 28.1879 | 28.1671 | 28.1199 | 28.0709 | 28.0211 | 27.4211 | 27.3993 | 27.3944 | 27.3933 | 27.3924 | 27.3906 | 27.3889 | 27.3867 | 27.3846 | 27.3826 | 27.3788 | 27.3701 | 27.3611 | 27.352
WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 26.2311 | 26.1617 | 26.0726 | 25.9892 | 25.9088 | 25.8313 | 25.7568 | 25.6853 | 25.6448 | 25.6246 | 25.5849 | 22.6886 | 22.0191 | 21.283 | 25.5575 | 25.4991 | 25.4193 | 25.3425 | 25.2682 | 25.2075 | 25.1609 | 25.1161 | 25.0899 | 25.0761 | 25.0488 | 22.2848 | 21.5786 | 20.8729 | 25.8245 | 25.7518 | 25.6566 | 25.5665 | 25.4796 | 25.3957 | 25.315 | 25.2373 | 25.1909 | 25.1653 | 25.115 | 22.4781 | 21.6484 | 20.818
| HAYTON | CT |  |  |  | 26.2311 | 26.1617 | 26.0726 | 25.9892 | 25.9088 | 25.8313 | 25.7568 | 25.6853 | 25.6448 | 25.6246 | 25.5849 | 25.4897 | 22.6521 | 22.2309 | 25.5575 | 25.4991 | 25.4193 | 25.3425 | 25.2682 | 25.2075 | 25.1609 | 25.1161 | 25.0899 | 25.0761 | 25.0488 | 22.8787 | 22.4306 | 21.9908 | 25.8245 | 25.7518 | 25.6566 | 25.5665 | 25.4796 | 25.3957 | 25.315 | 25.2373 | 25.1909 | 25.1653 | 25.115 | 24.9493 | 22.5835 | 22.0652
| HAYTON | LW |  |  |  | 26.3309 | 26.3193 | 26.3059 | 26.2909 | 26.2743 | 26.2564 | 26.2372 | 26.217 | 26.1942 | 26.1708 | 26.1227 | 22.6886 | 22.0191 | 21.283 | 25.6307 | 25.6073 | 25.5565 | 25.4955 | 25.4609 | 25.4436 | 25.4256 | 25.4071 | 25.3866 | 25.3657 | 25.3282 | 22.2848 | 21.5786 | 20.8729 | 25.9244 | 25.9066 | 25.8761 | 25.8402 | 25.8031 | 25.765 | 25.7259 | 25.686 | 25.642 | 25.5985 | 25.5248 | 22.4781 | 21.6484 | 20.818
| HAYTON | ST |  |  |  | 26.3461 | 26.3421 | 26.3368 | 26.3317 | 26.3266 | 26.3205 | 26.3145 | 26.3087 | 26.3033 | 26.2953 | 26.28 | 26.2385 | 26.2006 | 26.1586 | 25.6799 | 25.6356 | 25.6151 | 25.5858 | 25.5517 | 25.5224 | 25.4937 | 25.4824 | 25.4756 | 25.4674 | 25.4515 | 25.4081 | 25.3717 | 22.6638 | 25.9555 | 25.9343 | 25.9221 | 25.9062 | 25.8885 | 25.872 | 25.8559 | 25.8402 | 25.824 | 25.8054 | 25.7694 | 25.671 | 25.5989 | 25.5249
| HAYTON | FS |  |  |  | 26.3421 | 26.3368 | 26.3315 | 26.3236 | 26.3159 | 26.3082 | 26.3007 | 26.2932 | 26.2858 | 26.2786 | 26.2644 | 26.2222 | 26.1781 | 26.1354 | 25.6802 | 25.6751 | 25.6699 | 25.6579 | 25.645 | 25.6313 | 25.6178 | 25.6022 | 25.5868 | 25.5717 | 25.5424 | 25.4657 | 25.4065 | 25.3746 | 25.9529 | 25.9471 | 25.9412 | 25.9307 | 25.9199 | 25.9089 | 25.898 | 25.8863 | 25.8748 | 25.8634 | 25.8413 | 25.78 | 25.7165 | 25.6543
BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6155 | 4.6151 | 4.6139 | 4.6125 | 4.611 | 4.6097 | 4.6083 | 4.607 | 4.6049 | 4.6028 | 4.6012 | 4.5923 | 4.5821 | 4.5736 | 4.5481 | 4.5479 | 4.5471 | 4.5463 | 4.5454 | 4.5446 | 4.5438 | 4.543 | 4.5418 | 4.5404 | 4.5398 | 4.5398 | 4.5398 | 4.5398
| HELMSDALE | CT |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6155 | 4.6151 | 4.6142 | 4.6132 | 4.6123 | 4.6113 | 4.6103 | 4.6094 | 4.6083 | 4.6073 | 4.6053 | 4.5961 | 4.5882 | 4.5805 | 4.5481 | 4.5479 | 4.5474 | 4.5468 | 4.5462 | 4.5456 | 4.545 | 4.5444 | 4.5438 | 4.5432 | 4.542 | 4.5398 | 4.5398 | 4.5398
| HELMSDALE | LW |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6155 | 4.6151 | 4.6139 | 4.6125 | 4.611 | 4.6097 | 4.6083 | 4.607 | 4.6055 | 4.6041 | 4.6023 | 4.5923 | 4.5821 | 4.5736 | 4.5481 | 4.5479 | 4.5471 | 4.5463 | 4.5454 | 4.5446 | 4.5438 | 4.543 | 4.5421 | 4.5413 | 4.5398 | 4.5398 | 4.5398 | 4.5398
| HELMSDALE | ST |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6156 | 4.6155 | 4.6151 | 4.6145 | 4.6139 | 4.6116 | 4.6094 | 4.6072 | 4.6049 | 4.6028 | 4.6012 | 4.5975 | 4.5937 | 4.5899 | 4.5482 | 4.5481 | 4.5479 | 4.5475 | 4.5471 | 4.5458 | 4.5445 | 4.5432 | 4.5418 | 4.5404 | 4.5398 | 4.5398 | 4.5398 | 4.5398
| HELMSDALE | FS |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6157 | 4.6157 | 4.6156 | 4.6155 | 4.6153 | 4.6144 | 4.6136 | 4.6125 | 4.6114 | 4.6104 | 4.6084 | 4.6036 | 4.6015 | 4.6 | 4.5482 | 4.5482 | 4.5482 | 4.5481 | 4.548 | 4.5475 | 4.547 | 4.5463 | 4.5457 | 4.5451 | 4.5439 | 4.541 | 4.5398 | 4.5398
INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | NO | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 22.3492 | 20.9192 | 29.0968 | 29.0402 | 28.882 | 28.6891 | 28.5005 | 28.3405 | 28.3043 | 28.2681 | 28.2465 | 28.2465 | 28.2465 | 22.0199 | 20.3105 | 18.6235 | 29.7827 | 29.7552 | 29.6783 | 29.5846 | 29.493 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 22.5309 | 20.8015 | 19.1139
| HILTON | CT |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 29.0979 | 29.0513 | 28.9339 | 28.8005 | 28.6696 | 28.5408 | 28.4002 | 28.3303 | 28.3026 | 28.275 | 28.2465 | 28.2465 | 22.5459 | 21.4461 | 29.7832 | 29.7606 | 29.7035 | 29.6387 | 29.5752 | 29.5126 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 21.9374
| HILTON | LW |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 22.3492 | 20.9192 | 29.0968 | 29.0402 | 28.882 | 28.6891 | 28.5005 | 28.3405 | 28.3043 | 28.2681 | 28.2465 | 28.2465 | 28.2465 | 22.0199 | 20.3105 | 18.6235 | 29.7827 | 29.7552 | 29.6783 | 29.5846 | 29.493 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 22.5309 | 20.8015 | 19.1139
| HILTON | ST |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 29.1158 | 29.0927 | 29.0406 | 28.9607 | 28.8657 | 28.7903 | 28.7071 | 28.6236 | 28.5332 | 28.4438 | 28.3308 | 28.2581 | 28.2465 | 28.2465 | 29.7919 | 29.7807 | 29.7554 | 29.7166 | 29.6704 | 29.6338 | 29.5934 | 29.5528 | 29.5089 | 29.4715 | 29.4715 | 29.4715 | 29.4715 | 29.4715
| HILTON | FS |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 29.1293 | 29.1254 | 29.1207 | 29.0991 | 29.0741 | 29.0499 | 29.0218 | 28.9867 | 28.9516 | 28.917 | 28.8476 | 28.6921 | 28.5544 | 28.4241 | 29.7984 | 29.7965 | 29.7943 | 29.7838 | 29.7716 | 29.7599 | 29.7463 | 29.7292 | 29.7121 | 29.6953 | 29.6616 | 29.5861 | 29.5192 | 29.4715
ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 30.3442 | 30.2244 | 30.0607 | 29.8992 | 29.744 | 29.5942 | 29.4489 | 29.3082 | 29.2165 | 29.1678 | 29.0734 | 28.7341 | 28.4466 | 28.1393 | 27.6818 | 27.5505 | 27.2836 | 27.0889 | 26.9059 | 26.8019 | 26.7145 | 26.6299 | 26.5747 | 26.5454 | 26.4884 | 26.2839 | 26.1104 | 22.592 | 29.0687 | 28.9339 | 28.719 | 28.5311 | 28.3518 | 28.1781 | 28.0056 | 27.8349 | 27.7188 | 27.648 | 27.5141 | 27.0327 | 26.6536 | 26.3903
| HUME STREET | CT |  |  |  | 30.3442 | 30.2244 | 30.0607 | 29.8992 | 29.744 | 29.5942 | 29.4489 | 29.3082 | 29.2165 | 29.1678 | 29.0734 | 28.7341 | 28.4466 | 28.1393 | 27.6818 | 27.5505 | 27.2836 | 27.0889 | 26.9059 | 26.8019 | 26.7145 | 26.6299 | 26.5747 | 26.5454 | 26.4884 | 26.2839 | 26.1104 | 22.592 | 29.0687 | 28.9339 | 28.719 | 28.5311 | 28.3518 | 28.1781 | 28.0056 | 27.8349 | 27.7188 | 27.648 | 27.5141 | 27.0327 | 26.6536 | 26.3903
| HUME STREET | LW |  |  |  | 30.5119 | 30.4891 | 30.4511 | 30.4184 | 30.3839 | 30.3474 | 30.309 | 30.2689 | 30.2185 | 30.1669 | 30.0618 | 29.6778 | 29.315 | 28.8797 | 27.826 | 27.776 | 27.6034 | 27.5078 | 27.4183 | 27.33 | 27.2411 | 27.2064 | 27.176 | 27.1449 | 27.0815 | 26.8499 | 26.631 | 22.7813 | 29.2435 | 29.2091 | 29.1205 | 29.0628 | 29.0058 | 28.9479 | 28.8882 | 28.8273 | 28.754 | 28.6795 | 28.5305 | 27.966 | 27.5372 | 27.1565
| HUME STREET | ST |  |  |  | 30.5385 | 30.5303 | 30.5139 | 30.5026 | 30.4916 | 30.4766 | 30.4613 | 30.4456 | 30.4302 | 30.4103 | 30.3728 | 30.2288 | 30.1287 | 30.0116 | 27.8574 | 27.8365 | 27.7548 | 27.7221 | 27.6896 | 27.6349 | 27.5737 | 27.5067 | 27.4462 | 27.3836 | 27.2709 | 27.1819 | 27.1213 | 27.0506 | 29.2743 | 29.2608 | 29.22 | 29.2003 | 29.1807 | 29.1504 | 29.1176 | 29.0826 | 29.05 | 29.0133 | 28.946 | 28.7257 | 28.5529 | 28.3616
| HUME STREET | FS |  |  |  | 30.5324 | 30.5228 | 30.5104 | 30.4962 | 30.4822 | 30.4676 | 30.4531 | 30.4385 | 30.4241 | 30.4099 | 30.3821 | 30.3028 | 30.2179 | 30.1352 | 27.8578 | 27.8434 | 27.8011 | 27.7801 | 27.7602 | 27.7314 | 27.7029 | 27.6718 | 27.641 | 27.6106 | 27.5515 | 27.4071 | 27.2631 | 27.1264 | 29.2699 | 29.2577 | 29.2337 | 29.2158 | 29.1985 | 29.1775 | 29.1568 | 29.1351 | 29.1136 | 29.0925 | 29.0512 | 28.9418 | 28.8284 | 28.7182
KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 18.3003 | 18.2442 | 18.1722 | 18.1049 | 18.04 | 17.9776 | 17.9175 | 17.8598 | 17.8272 | 17.811 | 17.7792 | 14.4958 | 13.1991 | 13.1161 | 16.8882 | 16.8309 | 16.7374 | 16.6587 | 16.5863 | 16.5146 | 16.4435 | 16.3744 | 16.318 | 16.2732 | 16.1817 | 15.9519 | 12.4493 | 11.9275 | 15.7737 | 15.715 | 15.6323 | 15.5513 | 15.4721 | 15.4002 | 15.3462 | 15.2942 | 15.2649 | 15.2503 | 13.6888 | 13.2063 | 11.3324 | 10.8484
| HUNTLY | CT |  |  |  | 18.3003 | 18.2442 | 18.1722 | 18.1049 | 18.04 | 17.9776 | 17.9175 | 17.8598 | 17.8272 | 17.811 | 17.7792 | 14.4958 | 13.1991 | 13.1161 | 16.8882 | 16.8309 | 16.7374 | 16.6587 | 16.5863 | 16.5146 | 16.4435 | 16.3744 | 16.318 | 16.2732 | 16.1817 | 15.9519 | 12.4493 | 11.9275 | 15.7737 | 15.715 | 15.6323 | 15.5513 | 15.4721 | 15.4002 | 15.3462 | 15.2942 | 15.2649 | 15.2503 | 13.6888 | 13.2063 | 11.3324 | 10.8484
| HUNTLY | LW |  |  |  | 18.381 | 18.3717 | 18.3609 | 18.3487 | 18.3353 | 18.3208 | 18.3053 | 18.2889 | 18.2706 | 18.2517 | 18.2129 | 18.1096 | 13.5544 | 13.431 | 16.9525 | 16.9357 | 16.9001 | 16.8558 | 16.8085 | 16.762 | 16.725 | 16.6879 | 16.6477 | 16.6088 | 16.5279 | 16.1521 | 12.6675 | 12.0053 | 15.8513 | 15.8389 | 15.8184 | 15.7938 | 15.7674 | 15.7393 | 15.7096 | 15.6806 | 15.6641 | 15.6471 | 15.6122 | 13.6675 | 11.658 | 11.0227
| HUNTLY | ST |  |  |  | 18.3934 | 18.3901 | 18.3858 | 18.3817 | 18.3776 | 18.3726 | 18.3678 | 18.3631 | 18.3587 | 18.3523 | 18.3399 | 18.3065 | 14.4392 | 14.4068 | 16.9646 | 16.9582 | 16.9459 | 16.9285 | 16.9076 | 16.8563 | 16.8045 | 16.7628 | 16.7255 | 16.6883 | 16.6134 | 16.4298 | 15.9461 | 15.8797 | 15.864 | 15.8595 | 15.8521 | 15.8428 | 15.8323 | 15.81 | 15.7875 | 15.7655 | 15.7434 | 15.7376 | 15.7265 | 15.6964 | 13.2335 | 12.992
| HUNTLY | FS |  |  |  | 18.3901 | 18.3858 | 18.3815 | 18.3752 | 18.3689 | 18.3627 | 18.3566 | 18.3506 | 18.3446 | 18.3387 | 18.3273 | 18.2931 | 18.2575 | 18.223 | 16.9638 | 16.9597 | 16.955 | 16.9458 | 16.9356 | 16.9147 | 16.8937 | 16.8689 | 16.8442 | 16.8203 | 16.7726 | 16.687 | 16.6043 | 16.5257 | 15.8616 | 15.8572 | 15.8526 | 15.8449 | 15.837 | 15.8251 | 15.8132 | 15.8 | 15.7868 | 15.774 | 15.7486 | 15.6844 | 15.6523 | 15.6212
BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 3.9545 | 3.8792 | 3.7822 | 3.2668 | 3.1832 | 3.1028 | 3.0072 | 2.9123 | 2.8521 | 2.8171 | 2.7483 | 2.597 | 2.4347 | 2.2635 | 3.8966 | 3.8521 | 3.8005 | 3.7503 | 3.7018 | 3.655 | 3.2547 | 3.1758 | 3.1241 | 3.0926 | 3.0305 | 2.8985 | 2.7576 | 2.6099 | 3.7558 | 3.6857 | 3.5946 | 3.2875 | 3.187 | 3.0833 | 2.9833 | 2.8872 | 2.8255 | 2.7889 | 2.7168 | 2.5604 | 2.3929 | 2.2167
| INCHBARE | CT |  |  |  | 3.9545 | 3.8792 | 3.7822 | 3.2668 | 3.1832 | 3.1028 | 3.0072 | 2.9123 | 2.8521 | 2.8171 | 2.7483 | 2.597 | 2.4347 | 2.2635 | 3.8966 | 3.8521 | 3.8005 | 3.7503 | 3.7018 | 3.655 | 3.2547 | 3.1758 | 3.1241 | 3.0926 | 3.0305 | 2.8985 | 2.7576 | 2.6099 | 3.7558 | 3.6857 | 3.5946 | 3.2875 | 3.187 | 3.0833 | 2.9833 | 2.8872 | 2.8255 | 2.7889 | 2.7168 | 2.5604 | 2.3929 | 2.2167
| INCHBARE | LW |  |  |  | 4.0624 | 4.0497 | 4.0347 | 4.0178 | 3.9992 | 3.9792 | 3.9578 | 3.9353 | 3.9092 | 3.8823 | 3.8272 | 3.223 | 2.9939 | 2.7424 | 3.9729 | 3.9634 | 3.9515 | 3.9378 | 3.9231 | 3.9073 | 3.8906 | 3.8732 | 3.8531 | 3.837 | 3.8048 | 3.7157 | 3.2041 | 2.9872 | 3.8555 | 3.8434 | 3.8285 | 3.8116 | 3.7933 | 3.7735 | 3.7526 | 3.7307 | 3.7054 | 3.6793 | 3.626 | 3.188 | 2.9515 | 2.6927
| INCHBARE | ST |  |  |  | 4.0789 | 4.0745 | 4.0686 | 4.0628 | 4.057 | 4.05 | 4.0431 | 4.0365 | 4.03 | 4.0208 | 4.003 | 3.9547 | 3.9095 | 3.8584 | 3.9847 | 3.9814 | 3.9768 | 3.972 | 3.9672 | 3.9612 | 3.9554 | 3.9497 | 3.9441 | 3.9366 | 3.922 | 3.8831 | 3.8465 | 3.8117 | 3.8708 | 3.8667 | 3.8609 | 3.855 | 3.8491 | 3.8419 | 3.8352 | 3.8288 | 3.8226 | 3.8136 | 3.7962 | 3.7487 | 3.7044 | 3.6554
| INCHBARE | FS |  |  |  | 4.0747 | 4.0689 | 4.0631 | 4.0546 | 4.0461 | 4.0377 | 4.0294 | 4.0212 | 4.013 | 4.005 | 3.9894 | 3.9431 | 3.8943 | 3.847 | 3.9818 | 3.9777 | 3.9736 | 3.9674 | 3.9612 | 3.9549 | 3.9487 | 3.9425 | 3.9363 | 3.9303 | 3.9185 | 3.8839 | 3.8521 | 3.8262 | 3.867 | 3.8616 | 3.8563 | 3.8483 | 3.8403 | 3.8323 | 3.8243 | 3.8164 | 3.8086 | 3.801 | 3.7859 | 3.7417 | 3.6954 | 3.6505
DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 4.0284 | 3.8994 | 3.1827 | 3.025 | 2.8729 | 2.7265 | 2.5702 | 2.3951 | 2.2777 | 2.2085 | 2.0723 | 1.7105 | 1.3169 | 0.90512 | 3.8074 | 3.7022 | 3.6034 | 3.144 | 2.9803 | 2.8221 | 2.6698 | 2.523 | 2.4215 | 2.3584 | 2.234 | 1.8992 | 1.5385 | 1.1642 | 3.6757 | 3.2146 | 3.0134 | 2.8089 | 2.6112 | 2.4203 | 2.2365 | 2.0597 | 1.9408 | 1.8706 | 1.7324 | 1.3648 | 0.96515 | 0.54138
| INNELLAN | CT |  |  |  | 4.0284 | 3.8994 | 3.1827 | 3.025 | 2.8729 | 2.7265 | 2.5702 | 2.3951 | 2.2777 | 2.2085 | 2.0723 | 1.7105 | 1.3169 | 0.90512 | 3.8074 | 3.7022 | 3.6034 | 3.144 | 2.9803 | 2.8221 | 2.6698 | 2.523 | 2.4215 | 2.3584 | 2.234 | 1.8992 | 1.5385 | 1.1642 | 3.6757 | 3.2146 | 3.0134 | 2.8089 | 2.6112 | 2.4203 | 2.2365 | 2.0597 | 1.9408 | 1.8706 | 1.7324 | 1.3648 | 0.96515 | 0.54138
| INNELLAN | LW |  |  |  | 4.2138 | 4.1924 | 4.1675 | 4.1396 | 4.1088 | 4.0754 | 4.0398 | 4.0022 | 3.9558 | 3.9081 | 3.1576 | 2.7154 | 2.2068 | 1.6329 | 3.9584 | 3.9347 | 3.8969 | 3.8526 | 3.8063 | 3.7751 | 3.7563 | 3.7365 | 3.2983 | 3.2226 | 3.0696 | 2.6591 | 2.1952 | 1.6802 | 3.8592 | 3.8364 | 3.8086 | 3.7769 | 3.7424 | 3.2925 | 3.2247 | 3.1552 | 3.0738 | 2.9912 | 2.8235 | 2.373 | 1.8377 | 1.2376
| INNELLAN | ST |  |  |  | 4.2423 | 4.2348 | 4.225 | 4.2153 | 4.206 | 4.1946 | 4.1835 | 4.1727 | 4.1618 | 4.1459 | 4.1155 | 4.0313 | 3.9501 | 3.1813 | 3.9841 | 3.9758 | 3.9625 | 3.9465 | 3.929 | 3.9099 | 3.8913 | 3.8732 | 3.8543 | 3.8314 | 3.7962 | 3.7519 | 3.2377 | 3.0808 | 3.8885 | 3.8806 | 3.8698 | 3.8588 | 3.8478 | 3.8347 | 3.822 | 3.8097 | 3.7971 | 3.7795 | 3.7456 | 3.1728 | 3.0184 | 2.8479
| INNELLAN | FS |  |  |  | 4.2348 | 4.225 | 4.2151 | 4.2004 | 4.186 | 4.1718 | 4.1577 | 4.1438 | 4.1302 | 4.1167 | 4.0903 | 4.0119 | 3.9279 | 3.2892 | 3.9797 | 3.9713 | 3.9629 | 3.9486 | 3.9341 | 3.9192 | 3.9046 | 3.8892 | 3.8741 | 3.8592 | 3.83 | 3.748 | 3.6974 | 3.6542 | 3.8812 | 3.8711 | 3.861 | 3.8457 | 3.8306 | 3.8157 | 3.8009 | 3.7862 | 3.7717 | 3.7574 | 3.7294 | 3.2809 | 3.1649 | 3.0529
KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.1615 | 13.9905 | 13.6079 | 12.0765 | 11.0994 | 10.3938 | 15.0783 | 15.045 | 14.9453 | 14.858 | 14.846 | 14.846 | 13.7423 | 13.5491 | 13.3404 | 13.1344 | 12.6918 | 11.2127 | 10.1506 | 9.3001 | 13.1392 | 13.0924 | 12.9521 | 12.779 | 12.6075 | 12.4378 | 12.2695 | 12.104 | 11.9252 | 11.7487 | 11.3531 | 9.6994 | 8.5978 | 7.7695
| INSCH | CT |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 13.991 | 12.6825 | 11.9305 | 11.4457 | 15.0783 | 15.0469 | 14.9656 | 14.8774 | 14.8516 | 14.846 | 14.846 | 14.846 | 13.6566 | 13.4993 | 13.1535 | 11.9431 | 11.1521 | 10.5679 | 13.1392 | 13.0951 | 12.9806 | 12.8486 | 12.7178 | 12.5881 | 12.4594 | 12.3329 | 12.1961 | 12.0614 | 11.7502 | 10.4109 | 9.5734 | 9.0043
| INSCH | LW |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.1615 | 13.9905 | 13.6079 | 12.0765 | 11.0994 | 10.3938 | 15.0796 | 15.045 | 14.9453 | 14.858 | 14.846 | 14.846 | 13.7423 | 13.5491 | 13.3404 | 13.1344 | 12.6918 | 11.2127 | 10.1506 | 9.3001 | 13.1411 | 13.0924 | 12.9521 | 12.779 | 12.6075 | 12.4378 | 12.2695 | 12.104 | 11.9252 | 11.7487 | 11.3531 | 9.6994 | 8.5978 | 7.7695
| INSCH | ST |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2156 | 13.8625 | 13.4719 | 13.1556 | 15.0896 | 15.0762 | 15.0448 | 14.9958 | 14.9369 | 14.8882 | 14.8606 | 14.8536 | 14.8461 | 14.846 | 14.8351 | 13.2432 | 12.7595 | 12.3784 | 13.1551 | 13.1362 | 13.0921 | 13.0232 | 12.9402 | 12.8717 | 12.8037 | 12.7371 | 12.6652 | 12.5951 | 12.4356 | 11.6879 | 11.2273 | 10.9008
| INSCH | FS |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 15.0957 | 15.0938 | 15.0912 | 15.0772 | 15.0604 | 15.0445 | 15.0287 | 15.0086 | 14.9888 | 14.9695 | 14.9314 | 14.8607 | 14.8481 | 14.846 | 13.1637 | 13.161 | 13.1574 | 13.1376 | 13.1141 | 13.0917 | 13.0694 | 13.0411 | 13.0133 | 12.9861 | 12.9325 | 12.805 | 12.6848 | 12.5715
BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | NO | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| INVERALMOND | CT |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| INVERALMOND | LW |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| INVERALMOND | ST |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| INVERALMOND | FS |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 2.7404 | 2.6853 | 2.6176 | 2.459 | 2.3842 | 2.3122 | 2.2429 | 2.1764 | 2.1373 | 2.1172 | 2.0777 | 1.9817 | 1.8786 | 1.7691 | 2.8217 | 2.7779 | 2.7321 | 2.485 | 2.4246 | 2.3663 | 2.3103 | 2.2565 | 2.2247 | 2.2081 | 2.1755 | 2.0964 | 2.0116 | 1.9217 | 2.799 | 2.7416 | 2.466 | 2.4049 | 2.3459 | 2.2892 | 2.2346 | 2.1822 | 2.1517 | 2.1361 | 2.1055 | 2.0312 | 1.9365 | 1.826
| INVERARAY | CT |  |  |  | 2.7404 | 2.6853 | 2.6176 | 2.459 | 2.3842 | 2.3122 | 2.2429 | 2.1764 | 2.1373 | 2.1172 | 2.0777 | 1.9817 | 1.8786 | 1.7691 | 2.8217 | 2.7779 | 2.7321 | 2.485 | 2.4246 | 2.3663 | 2.3103 | 2.2565 | 2.2247 | 2.2081 | 2.1755 | 2.0964 | 2.0116 | 1.9217 | 2.799 | 2.7416 | 2.466 | 2.4049 | 2.3459 | 2.2892 | 2.2346 | 2.1822 | 2.1517 | 2.1361 | 2.1055 | 2.0312 | 1.9365 | 1.826
| INVERARAY | LW |  |  |  | 2.8195 | 2.8103 | 2.7997 | 2.7878 | 2.7746 | 2.7604 | 2.7452 | 2.7292 | 2.7108 | 2.6919 | 2.6539 | 2.4357 | 2.2886 | 2.127 | 2.8901 | 2.8817 | 2.8712 | 2.8592 | 2.8462 | 2.8323 | 2.8176 | 2.8022 | 2.7847 | 2.7706 | 2.7429 | 2.4583 | 2.3372 | 2.2046 | 2.8809 | 2.8709 | 2.8583 | 2.844 | 2.8284 | 2.8118 | 2.7942 | 2.7758 | 2.7563 | 2.7384 | 2.7017 | 2.4063 | 2.2956 | 2.1732
| INVERARAY | ST |  |  |  | 2.8316 | 2.8284 | 2.8242 | 2.8201 | 2.8161 | 2.8112 | 2.8065 | 2.8019 | 2.7975 | 2.7911 | 2.7788 | 2.7453 | 2.7143 | 2.6794 | 2.9332 | 2.8978 | 2.8938 | 2.8896 | 2.8853 | 2.8804 | 2.8756 | 2.8709 | 2.8664 | 2.8601 | 2.8479 | 2.8155 | 2.7853 | 2.7589 | 2.9323 | 2.8902 | 2.8853 | 2.8803 | 2.8752 | 2.8693 | 2.8636 | 2.858 | 2.8525 | 2.845 | 2.8305 | 2.7917 | 2.7593 | 2.7263
| INVERARAY | FS |  |  |  | 2.8284 | 2.8242 | 2.82 | 2.8137 | 2.8076 | 2.8015 | 2.7955 | 2.7896 | 2.7838 | 2.778 | 2.7668 | 2.7333 | 2.6982 | 2.6645 | 2.9306 | 2.8944 | 2.8907 | 2.8851 | 2.8796 | 2.8741 | 2.8687 | 2.8633 | 2.8579 | 2.8526 | 2.8423 | 2.812 | 2.782 | 2.7593 | 2.9291 | 2.8861 | 2.8817 | 2.875 | 2.8684 | 2.8618 | 2.8553 | 2.8488 | 2.8424 | 2.8361 | 2.8237 | 2.7874 | 2.7495 | 2.7133
LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | NO | 0.36018 | -0.019495 | -0.09489 | -0.17257 | -0.24749 | -0.31966 | -0.38906 | -0.45571 | -0.49854 | -0.52052 | -0.56372 | -1.2923 | -1.4196 | -1.5563 | 0.25154 | 0.22344 | -0.058466 | -0.12561 | -0.19041 | -0.25286 | -0.31297 | -0.37073 | -0.40898 | -0.42994 | -0.47117 | -1.0912 | -1.2133 | -1.343 | -0.045891 | -0.10725 | -0.18777 | -0.27098 | -0.35127 | -0.42863 | -0.50307 | -0.5746 | -0.62158 | -0.64689 | -0.69666 | -1.4683 | -1.6155 | -1.7724
| INVERARITY | CT |  |  |  | 0.36018 | -0.019495 | -0.09489 | -0.17257 | -0.24749 | -0.31966 | -0.38906 | -0.45571 | -0.49854 | -0.52052 | -0.56372 | -1.2923 | -1.4196 | -1.5563 | 0.25154 | 0.22344 | -0.058466 | -0.12561 | -0.19041 | -0.25286 | -0.31297 | -0.37073 | -0.40898 | -0.42994 | -0.47117 | -1.0912 | -1.2133 | -1.343 | -0.045891 | -0.10725 | -0.18777 | -0.27098 | -0.35127 | -0.42863 | -0.50307 | -0.5746 | -0.62158 | -0.64689 | -0.69666 | -1.4683 | -1.6155 | -1.7724
| INVERARITY | LW |  |  |  | 0.44255 | 0.43182 | 0.41737 | 0.40076 | 0.38299 | 0.36417 | 0.34443 | 0.32389 | -0.0082173 | -0.032261 | -0.081535 | -0.83651 | -1.0052 | -1.2084 | 0.29194 | 0.28726 | 0.28185 | 0.27576 | 0.26905 | 0.26179 | 0.25402 | 0.24582 | -0.010813 | -0.034656 | -0.083244 | -0.74304 | -0.91752 | -1.12 | 0.38368 | 0.3745 | 0.3639 | -0.0061434 | -0.026044 | -0.047011 | -0.068915 | -0.091621 | -0.1195 | -0.14801 | -0.2062 | -1.0214 | -1.2279 | -1.4697
| INVERARITY | ST |  |  |  | 0.45552 | 0.45179 | 0.44636 | 0.44047 | 0.4344 | 0.42593 | 0.41769 | 0.40967 | 0.40121 | 0.39053 | 0.36995 | -0.29147 | -0.33729 | -0.39097 | 0.29813 | 0.29651 | 0.29436 | 0.29226 | 0.29022 | 0.28774 | 0.28533 | 0.28298 | 0.28055 | 0.277 | 0.27019 | -0.26048 | -0.31369 | -0.37338 | 0.39582 | 0.39265 | 0.38843 | 0.38431 | 0.38031 | 0.37544 | 0.37071 | 0.36612 | -0.0086019 | -0.020867 | -0.044523 | -0.42726 | -0.4886 | -0.55806
| INVERARITY | FS |  |  |  | 0.45244 | 0.44799 | 0.44352 | 0.43657 | 0.42962 | 0.42217 | 0.41483 | 0.40727 | 0.39981 | 0.39246 | 0.3781 | 0.337 | -0.017016 | -0.05671 | 0.29652 | 0.29436 | 0.29221 | 0.28902 | 0.28587 | 0.28277 | 0.27971 | 0.27669 | 0.27371 | 0.27078 | 0.26503 | 0.24794 | -0.011319 | -0.049412 | 0.39265 | 0.38843 | 0.3842 | 0.37795 | 0.37178 | 0.3657 | 0.3597 | 0.35378 | -0.0061378 | -0.014261 | -0.030128 | -0.075136 | -0.12253 | -0.16846
INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | NO | 2.4782 | 2.395 | 2.2882 | 2.1868 | 2.0891 | 1.9931 | 1.8958 | 1.8024 | 1.7601 | 1.739 | 1.6977 | 1.5978 | 1.5105 | 1.3948 | 2.473 | 2.3947 | 2.2933 | 2.1966 | 2.1034 | 2.0136 | 1.9272 | 1.8442 | 1.8053 | 1.7849 | 1.7447 | 1.5934 | 1.4519 | 1.3108 | 2.8346 | 2.4322 | 2.3092 | 2.1875 | 2.0701 | 1.957 | 1.8483 | 1.7439 | 1.6955 | 1.6707 | 1.6218 | 1.4607 | 1.3006 | 1.139
| INVERARNIE | CT |  |  |  | 2.4782 | 2.395 | 2.2882 | 2.1868 | 2.0891 | 1.9931 | 1.8958 | 1.8024 | 1.7601 | 1.739 | 1.6977 | 1.5978 | 1.5105 | 1.3948 | 2.473 | 2.3947 | 2.2933 | 2.1966 | 2.1034 | 2.0136 | 1.9272 | 1.8442 | 1.8053 | 1.7849 | 1.7447 | 1.5934 | 1.4519 | 1.3108 | 2.8346 | 2.4322 | 2.3092 | 2.1875 | 2.0701 | 1.957 | 1.8483 | 1.7439 | 1.6955 | 1.6707 | 1.6218 | 1.4607 | 1.3006 | 1.139
| INVERARNIE | LW |  |  |  | 3.1224 | 3.1073 | 3.0877 | 3.0654 | 3.0413 | 3.0155 | 2.4842 | 2.4584 | 2.4349 | 2.4108 | 2.3613 | 2.1599 | 1.928 | 1.6935 | 2.8455 | 2.8329 | 2.8148 | 2.4812 | 2.4368 | 2.3913 | 2.3449 | 2.2977 | 2.2507 | 2.2033 | 2.1079 | 1.885 | 1.6658 | 1.4448 | 2.9513 | 2.9367 | 2.9181 | 2.8969 | 2.8747 | 2.458 | 2.4056 | 2.3522 | 2.2995 | 2.2462 | 2.1386 | 1.8846 | 1.6354 | 1.3836
| INVERARNIE | ST |  |  |  | 3.1411 | 3.1359 | 3.1284 | 3.1205 | 3.1124 | 3.1034 | 3.0946 | 3.0861 | 3.0777 | 3.0664 | 3.0445 | 2.4919 | 2.4521 | 2.4157 | 2.86 | 2.8556 | 2.849 | 2.8414 | 2.8334 | 2.8251 | 2.817 | 2.4965 | 2.4799 | 2.4605 | 2.4232 | 2.3357 | 2.253 | 2.1736 | 2.9695 | 2.9644 | 2.9573 | 2.9498 | 2.9422 | 2.9337 | 2.9253 | 2.9172 | 2.9093 | 2.8988 | 2.4964 | 2.3979 | 2.3054 | 2.217
| INVERARNIE | FS |  |  |  | 3.1365 | 3.1301 | 3.1236 | 3.1137 | 3.1037 | 3.094 | 3.0844 | 3.0747 | 3.0652 | 3.0558 | 3.0375 | 2.4676 | 2.4234 | 2.3827 | 2.8567 | 2.8518 | 2.8468 | 2.8388 | 2.8307 | 2.8228 | 2.815 | 2.8071 | 2.7992 | 2.7915 | 2.4768 | 2.4113 | 2.3529 | 2.2987 | 2.965 | 2.9587 | 2.9524 | 2.9428 | 2.9332 | 2.9237 | 2.9144 | 2.9051 | 2.896 | 2.8869 | 2.8692 | 2.4706 | 2.4017 | 2.3379
FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 6.7367 | 6.7293 | 6.7087 | 6.683 | 6.6566 | 6.6298 | 6.6021 | 6.575 | 6.5458 | 6.518 | 6.4605 | 4.6661 | 2.4909 | 2.3308 | 5.5725 | 5.5631 | 5.537 | 5.5044 | 5.471 | 5.4369 | 5.4018 | 5.3674 | 5.3304 | 5.2951 | 5.2222 | 3.7538 | 2.0039 | 1.8131 | 5.7276 | 5.7276 | 5.7275 | 5.7057 | 5.6833 | 5.6606 | 5.6371 | 5.6141 | 5.5894 | 5.5658 | 5.5171 | 3.7693 | 1.663 | 1.5355
| INVERBERVIE | CT |  |  |  | 6.7369 | 6.7307 | 6.7153 | 6.6971 | 6.6783 | 6.6589 | 6.6388 | 6.6191 | 6.5979 | 6.5778 | 6.5361 | 4.7874 | 2.6688 | 2.5563 | 5.5727 | 5.5649 | 5.5454 | 5.5223 | 5.4984 | 5.4739 | 5.4484 | 5.4233 | 5.3964 | 5.371 | 5.3181 | 3.9076 | 2.2158 | 2.0818 | 5.7276 | 5.7276 | 5.7276 | 5.7176 | 5.7017 | 5.6853 | 5.6682 | 5.6515 | 5.6335 | 5.6165 | 5.5812 | 3.872 | 1.8045 | 1.715
| INVERBERVIE | LW |  |  |  | 6.7367 | 6.7293 | 6.7087 | 6.683 | 6.6566 | 6.6298 | 6.6021 | 6.575 | 6.5458 | 6.518 | 6.4605 | 4.6661 | 2.4909 | 2.3308 | 5.5725 | 5.5631 | 5.537 | 5.5044 | 5.471 | 5.4369 | 5.4018 | 5.3674 | 5.3304 | 5.2951 | 5.2222 | 3.7538 | 2.0039 | 1.8131 | 5.7276 | 5.7276 | 5.7275 | 5.7057 | 5.6833 | 5.6606 | 5.6371 | 5.6141 | 5.5894 | 5.5658 | 5.5171 | 3.7693 | 1.663 | 1.5355
| INVERBERVIE | ST |  |  |  | 6.7389 | 6.736 | 6.7295 | 6.7193 | 6.7068 | 6.6927 | 6.6782 | 6.6639 | 6.6486 | 6.634 | 6.6039 | 5.712 | 4.6411 | 4.5744 | 5.5753 | 5.5716 | 5.5633 | 5.5504 | 5.5346 | 5.5167 | 5.4983 | 5.4802 | 5.4607 | 5.4423 | 5.4041 | 4.6765 | 3.8118 | 3.7272 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7258 | 5.7139 | 5.7016 | 5.6895 | 5.6765 | 5.6642 | 5.6387 | 4.7692 | 3.7228 | 3.6663
| INVERBERVIE | FS |  |  |  | 6.7402 | 6.7396 | 6.7386 | 6.7354 | 6.7316 | 6.7266 | 6.7216 | 6.7155 | 6.7094 | 6.7036 | 6.6917 | 6.663 | 6.6355 | 6.6095 | 5.5769 | 5.5761 | 5.5749 | 5.5709 | 5.566 | 5.5597 | 5.5533 | 5.5456 | 5.5379 | 5.5305 | 5.5155 | 5.4791 | 5.4442 | 5.4112 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7231 | 5.7131 | 5.6887 | 5.6654 | 5.6434
GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | YES | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.058697 | 0.058636 | 0.058467 | 0.05826 | 0.058058 | 0.057543 | 0.05664 | 0.055756 | 0.054835 | 0.054125 | 0.052884 | 0.052267 | 0.052267 | -0.016382 | 0.066143 | 0.066114 | 0.066031 | 0.065931 | 0.065833 | 0.065583 | 0.065144 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | -0.0052812
| INVERBROOM | CT |  |  |  | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.058697 | 0.058646 | 0.058519 | 0.058374 | 0.058232 | 0.058093 | 0.057956 | 0.05782 | 0.057675 | 0.057531 | 0.057248 | 0.052574 | 0.052267 | 0.052267 | 0.066143 | 0.066119 | 0.066057 | 0.065987 | 0.065918 | 0.06585 | 0.065783 | 0.065718 | 0.065647 | 0.065577 | 0.065439 | 0.064996 | 0.064996 | 0.064996
| INVERBROOM | LW |  |  |  | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.058697 | 0.058636 | 0.058467 | 0.05826 | 0.058058 | 0.057861 | 0.057666 | 0.057475 | 0.05727 | 0.057066 | 0.056666 | 0.052267 | 0.052267 | -0.016382 | 0.066143 | 0.066114 | 0.066031 | 0.065931 | 0.065833 | 0.065737 | 0.065643 | 0.06555 | 0.06545 | 0.065351 | 0.065157 | 0.064996 | 0.064996 | -0.0052812
| INVERBROOM | ST |  |  |  | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.058715 | 0.058692 | 0.058639 | 0.05856 | 0.058465 | 0.057543 | 0.05664 | 0.055756 | 0.054835 | 0.054125 | 0.052884 | 0.052267 | 0.052267 | 0.052267 | 0.066152 | 0.066141 | 0.066115 | 0.066077 | 0.066031 | 0.065583 | 0.065144 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | 0.064996 | 0.064996
| INVERBROOM | FS |  |  |  | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.10703 | 0.058726 | 0.058722 | 0.058717 | 0.058694 | 0.058667 | 0.058371 | 0.058077 | 0.057698 | 0.057326 | 0.05696 | 0.056253 | 0.054668 | 0.053481 | 0.052789 | 0.066157 | 0.066155 | 0.066153 | 0.066142 | 0.066129 | 0.065985 | 0.065842 | 0.065658 | 0.065477 | 0.065299 | 0.064996 | 0.064996 | 0.064996 | 0.064996
FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.13692 | 0.13657 | 0.13556 | 0.13431 | 0.13309 | 0.1319 | 0.13072 | 0.12957 | 0.12833 | 0.12736 | 0.12515 | 0.12201 | 0.12201 | -0.021756 | 0.15435 | 0.15418 | 0.15369 | 0.15309 | 0.15249 | 0.15191 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172
| INVERGARRY | CT |  |  |  | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.13692 | 0.13663 | 0.13587 | 0.135 | 0.13415 | 0.13331 | 0.13249 | 0.13168 | 0.13081 | 0.12994 | 0.12823 | 0.1223 | 0.12201 | 0.12201 | 0.15435 | 0.15421 | 0.15384 | 0.15342 | 0.15301 | 0.1526 | 0.1522 | 0.15181 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172
| INVERGARRY | LW |  |  |  | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.13692 | 0.13657 | 0.13556 | 0.13431 | 0.13309 | 0.1319 | 0.13072 | 0.12957 | 0.12833 | 0.12736 | 0.12552 | 0.12201 | 0.12201 | -0.021756 | 0.15435 | 0.15418 | 0.15369 | 0.15309 | 0.15249 | 0.15191 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172
| INVERGARRY | ST |  |  |  | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.13702 | 0.13689 | 0.13659 | 0.13612 | 0.13555 | 0.13392 | 0.13232 | 0.13075 | 0.12906 | 0.1276 | 0.12515 | 0.12251 | 0.12201 | 0.12201 | 0.1544 | 0.15434 | 0.15419 | 0.15396 | 0.15369 | 0.15289 | 0.15212 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172 | 0.15172
| INVERGARRY | FS |  |  |  | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.24985 | 0.13708 | 0.13707 | 0.13704 | 0.13691 | 0.13675 | 0.13621 | 0.13568 | 0.135 | 0.13433 | 0.13367 | 0.13239 | 0.12936 | 0.12692 | 0.1249 | 0.15443 | 0.15442 | 0.15441 | 0.15435 | 0.15427 | 0.15401 | 0.15375 | 0.15342 | 0.15309 | 0.15278 | 0.15215 | 0.15172 | 0.15172 | 0.15172
ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.484 | 14.3407 | 14.191 | 14.0762 | 13.9606 | 13.761 | 13.3856 | 13.0052 | 12.6333 | 16.7234 | 16.6895 | 16.6328 | 16.548 | 16.4781 | 16.4458 | 16.4307 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.7625 | 13.3259 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7333 | 13.565 | 13.3891 | 13.2544 | 13.1186 | 12.8842 | 12.4433 | 11.9965 | 11.5598
| INVERGORDON | CT |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.4468 | 14.3125 | 14.1971 | 14.079 | 13.8835 | 13.5422 | 13.2233 | 12.9127 | 16.7234 | 16.6927 | 16.6432 | 16.571 | 16.5076 | 16.4622 | 16.4419 | 16.4278 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.6539 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.6895 | 13.5319 | 13.3963 | 13.2577 | 13.028 | 12.6272 | 12.2527 | 11.8879
| INVERGORDON | LW |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.484 | 14.3407 | 14.191 | 14.0762 | 13.9606 | 13.761 | 13.3856 | 13.0052 | 12.6333 | 16.7239 | 16.6895 | 16.6328 | 16.548 | 16.4781 | 16.4458 | 16.4307 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.7625 | 13.3259 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7333 | 13.565 | 13.3891 | 13.2544 | 13.1186 | 12.8842 | 12.4433 | 11.9965 | 11.5598
| INVERGORDON | ST |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.4643 | 14.2804 | 14.1176 | 13.9587 | 16.7328 | 16.7182 | 16.7024 | 16.6721 | 16.6361 | 16.6021 | 16.5604 | 16.5238 | 16.4945 | 16.4642 | 16.4437 | 16.4244 | 16.4194 | 16.4194 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7101 | 13.4941 | 13.3029 | 13.1163
| INVERGORDON | FS |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 16.7368 | 16.7287 | 16.7218 | 16.7076 | 16.6919 | 16.6781 | 16.6614 | 16.6419 | 16.6274 | 16.6127 | 16.5869 | 16.5451 | 16.5189 | 16.4941 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265
FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8882 | 17.8552 | 17.8013 | 17.7517 | 17.7101 | 17.6717 | 17.6337 | 17.5961 | 17.5557 | 17.5158 | 17.4379 | 17.0308 | 16.6076 | 16.4507 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.833 | 12.3182
| INVERLOCHY | CT |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8894 | 17.8618 | 17.8201 | 17.7866 | 17.7525 | 17.7211 | 17.6904 | 17.661 | 17.6314 | 17.6029 | 17.5484 | 17.2224 | 16.8805 | 16.5639 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.754
| INVERLOCHY | LW |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8882 | 17.8552 | 17.8013 | 17.7517 | 17.7101 | 17.6717 | 17.6337 | 17.5961 | 17.5557 | 17.5158 | 17.4379 | 17.0308 | 16.6076 | 16.4507 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.833 | 12.3182
| INVERLOCHY | ST |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.9007 | 17.8842 | 17.8639 | 17.8455 | 17.8227 | 17.7775 | 17.7329 | 17.6966 | 17.6587 | 17.6221 | 17.552 | 17.381 | 17.2036 | 17.0279 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506
| INVERLOCHY | FS |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.9104 | 17.9022 | 17.896 | 17.8896 | 17.8824 | 17.8668 | 17.8515 | 17.8323 | 17.8134 | 17.7949 | 17.7595 | 17.6892 | 17.6238 | 17.5603 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506
PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2805 | 6.2587 | 6.2372 | 6.214 | 6.1909 | 6.1452 | 6.0728 | 5.9998 | 5.9278 | 6.5993 | 6.5959 | 6.2808 | 6.2515 | 6.2228 | 6.1946 | 6.167 | 6.1398 | 6.1104 | 6.0812 | 6.0232 | 5.9316 | 5.8391 | 5.748 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2995 | 6.2714 | 6.2438 | 6.2167 | 6.1874 | 6.1582 | 6.1005 | 6.0092 | 5.917 | 5.8261
| INVERNEIL | CT |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.29 | 6.2747 | 6.2582 | 6.2418 | 6.2092 | 6.1622 | 6.1147 | 6.0679 | 6.5993 | 6.5964 | 6.2876 | 6.2668 | 6.2464 | 6.2263 | 6.2066 | 6.1873 | 6.1663 | 6.1455 | 6.1043 | 6.0448 | 5.9846 | 5.9254 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2833 | 6.264 | 6.2432 | 6.2224 | 6.1814 | 6.122 | 6.062 | 6.0029
| INVERNEIL | LW |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2805 | 6.2587 | 6.2372 | 6.214 | 6.1909 | 6.1452 | 6.0728 | 5.9998 | 5.9278 | 6.5994 | 6.5959 | 6.2808 | 6.2515 | 6.2228 | 6.1946 | 6.167 | 6.1398 | 6.1104 | 6.0812 | 6.0232 | 5.9316 | 5.8391 | 5.748 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2995 | 6.2714 | 6.2438 | 6.2167 | 6.1874 | 6.1582 | 6.1005 | 6.0092 | 5.917 | 5.8261
| INVERNEIL | ST |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2688 | 6.2367 | 6.2048 | 6.6004 | 6.5991 | 6.5961 | 6.294 | 6.2807 | 6.2721 | 6.2637 | 6.2555 | 6.2466 | 6.2379 | 6.2209 | 6.1798 | 6.1391 | 6.0987 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2976 | 6.2565 | 6.2161 | 6.1757
| INVERNEIL | FS |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.601 | 6.6008 | 6.6006 | 6.5993 | 6.5977 | 6.5965 | 6.5954 | 6.2998 | 6.2964 | 6.2929 | 6.2863 | 6.2706 | 6.256 | 6.2424 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503
INVERNESS | INVERNESS 11 kV | MINIMUM HEADROOM | NH 65302 42625 | NO | NO | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9648 | 17.9083 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.3534 | 12.612 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.5117 | 12.7779
| INVERNESS 11 kV | CT |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9677 | 17.9215 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.5603 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.728
| INVERNESS 11 kV | LW |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9648 | 17.9083 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.3534 | 12.612 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.5117 | 12.7779
| INVERNESS 11 kV | ST |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9828 | 17.9517 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993
| INVERNESS 11 kV | FS |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9983 | 17.9825 | 17.9616 | 17.9376 | 17.9109 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993
KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 39.9404 | 30.3077 | 29.0246 | 37.6006 | 37.5191 | 37.2855 | 36.9971 | 36.7096 | 36.5114 | 36.3141 | 36.1201 | 35.9107 | 35.7641 | 35.7217 | 35.0347 | 27.8756 | 26.3751 | 38.2902 | 38.2629 | 38.1845 | 38.0878 | 37.9914 | 37.8955 | 37.7996 | 37.7306 | 37.6922 | 37.692 | 37.692 | 29.3566 | 27.6354 | 26.1492
| INVERURIE | CT |  |  |  | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 39.9404 | 39.7509 | 31.0257 | 37.6006 | 37.5307 | 37.3508 | 37.1426 | 36.9345 | 36.7269 | 36.5772 | 36.436 | 36.2837 | 36.1348 | 35.8348 | 35.0347 | 34.9251 | 28.7014 | 38.2902 | 38.2667 | 38.2064 | 38.1366 | 38.0668 | 37.9972 | 37.9275 | 37.8589 | 37.7849 | 37.7333 | 37.692 | 36.4822 | 36.2864 | 28.4671
| INVERURIE | LW |  |  |  | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 39.9404 | 30.3077 | 29.0246 | 37.6011 | 37.5191 | 37.2855 | 36.9971 | 36.7096 | 36.5114 | 36.3141 | 36.1201 | 35.9107 | 35.7641 | 35.7217 | 35.0347 | 27.8756 | 26.3751 | 38.2903 | 38.2629 | 38.1845 | 38.0878 | 37.9914 | 37.8955 | 37.7996 | 37.7306 | 37.6922 | 37.692 | 37.692 | 29.3566 | 27.6354 | 26.1492
| INVERURIE | ST |  |  |  | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 40.5259 | 40.4311 | 40.4311 | 37.6266 | 37.598 | 37.5318 | 37.4287 | 37.3041 | 37.2033 | 37.1018 | 37.0024 | 36.8951 | 36.7918 | 36.622 | 35.7972 | 35.3813 | 35.3421 | 38.2989 | 38.2893 | 38.2671 | 38.2325 | 38.1908 | 38.157 | 38.1229 | 38.0896 | 38.0536 | 38.019 | 37.9492 | 37.1742 | 37.0046 | 36.9892
| INVERURIE | FS |  |  |  | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 41.1113 | 37.6394 | 37.6345 | 37.6278 | 37.5958 | 37.5576 | 37.5238 | 37.4897 | 37.4475 | 37.4057 | 37.3653 | 37.2845 | 37.0911 | 36.9076 | 36.7342 | 38.3032 | 38.3016 | 38.2993 | 38.2886 | 38.2758 | 38.2644 | 38.253 | 38.2389 | 38.2248 | 38.2113 | 38.1842 | 38.1193 | 38.0578 | 37.9997
DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.2334 | 3.1353 | 3.0387 | 3.5241 | 3.5229 | 3.5206 | 3.5184 | 3.5176 | 3.5168 | 3.5161 | 3.516 | 3.516 | 3.516 | 3.516 | 3.1902 | 3.0677 | 2.9455 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.2437 | 3.1216 | 3.0014
| KAMES | CT |  |  |  | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.2537 | 3.1585 | 3.0648 | 3.5242 | 3.5232 | 3.5213 | 3.5193 | 3.5183 | 3.5177 | 3.5172 | 3.5167 | 3.5161 | 3.516 | 3.516 | 3.2154 | 3.097 | 2.9785 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.269 | 3.1505 | 3.0338
| KAMES | LW |  |  |  | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.2334 | 3.1353 | 3.0387 | 3.5241 | 3.5229 | 3.5206 | 3.5184 | 3.5176 | 3.5168 | 3.5161 | 3.516 | 3.516 | 3.516 | 3.516 | 3.1902 | 3.0677 | 2.9455 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.2437 | 3.1216 | 3.0014
| KAMES | ST |  |  |  | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.2882 | 3.2467 | 3.2053 | 3.5251 | 3.5245 | 3.5236 | 3.5224 | 3.5212 | 3.5186 | 3.5176 | 3.5166 | 3.516 | 3.516 | 3.516 | 3.2581 | 3.2066 | 3.1553 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.2602 | 3.2087
| KAMES | FS |  |  |  | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.6497 | 3.5259 | 3.5256 | 3.5253 | 3.5248 | 3.5244 | 3.5234 | 3.5224 | 3.5211 | 3.5199 | 3.5187 | 3.5179 | 3.5161 | 3.516 | 3.516 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041 | 3.6041
KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 19.8759 | 19.7953 | 19.6877 | 19.5824 | 19.4823 | 19.3855 | 19.2921 | 19.202 | 19.1446 | 19.1116 | 19.0468 | 18.7149 | 17.2839 | 17.0862 | 18.1566 | 18.1068 | 18.0403 | 17.9753 | 17.9134 | 17.8537 | 17.7959 | 17.7403 | 17.7048 | 17.6843 | 17.6442 | 17.4387 | 12.9804 | 12.4244 | 17.7675 | 17.6817 | 17.5577 | 17.4323 | 17.3161 | 17.2032 | 17.0931 | 16.9862 | 16.9209 | 16.8869 | 16.8203 | 16.4812 | 13.1201 | 12.5587
| KEITH | CT |  |  |  | 19.8759 | 19.7953 | 19.6877 | 19.5824 | 19.4823 | 19.3855 | 19.2921 | 19.202 | 19.1446 | 19.1116 | 19.0468 | 18.7149 | 17.2839 | 17.0862 | 18.1566 | 18.1068 | 18.0403 | 17.9753 | 17.9134 | 17.8537 | 17.7959 | 17.7403 | 17.7048 | 17.6843 | 17.6442 | 17.4387 | 12.9804 | 12.4244 | 17.7675 | 17.6817 | 17.5577 | 17.4323 | 17.3161 | 17.2032 | 17.0931 | 16.9862 | 16.9209 | 16.8869 | 16.8203 | 16.4812 | 13.1201 | 12.5587
| KEITH | LW |  |  |  | 19.9873 | 19.9721 | 19.9523 | 19.9295 | 19.907 | 19.883 | 19.8578 | 19.8315 | 19.8011 | 19.7699 | 19.7063 | 19.3339 | 17.845 | 17.5762 | 18.2252 | 18.2158 | 18.2036 | 18.1895 | 18.1755 | 18.1607 | 18.1451 | 18.1288 | 18.11 | 18.0908 | 18.0514 | 17.8209 | 13.6501 | 12.9853 | 17.875 | 17.8547 | 17.8237 | 17.7869 | 17.7552 | 17.7223 | 17.6886 | 17.654 | 17.6146 | 17.5745 | 17.4934 | 17.1071 | 15.6041 | 13.229
| KEITH | ST |  |  |  | 20.0049 | 19.9994 | 19.9915 | 19.983 | 19.9755 | 19.9624 | 19.9495 | 19.9367 | 19.9237 | 19.9081 | 19.8782 | 19.7237 | 19.0284 | 18.9478 | 18.2361 | 18.2327 | 18.2278 | 18.2225 | 18.2179 | 18.2097 | 18.2017 | 18.1938 | 18.1856 | 18.176 | 18.1574 | 18.0617 | 17.6327 | 17.5826 | 17.8936 | 17.8854 | 17.8731 | 17.8583 | 17.8463 | 17.8183 | 17.7903 | 17.7627 | 17.7334 | 17.7026 | 17.6599 | 17.502 | 16.8005 | 16.7169
| KEITH | FS |  |  |  | 20.0011 | 19.9947 | 19.9882 | 19.9784 | 19.9692 | 19.9585 | 19.948 | 19.937 | 19.9262 | 19.9156 | 19.8947 | 19.8362 | 19.7761 | 19.7178 | 18.2338 | 18.2298 | 18.2258 | 18.2198 | 18.2141 | 18.2075 | 18.2009 | 18.1941 | 18.1874 | 18.1808 | 18.1679 | 18.1317 | 18.0945 | 18.0584 | 17.8915 | 17.8842 | 17.8764 | 17.8645 | 17.8543 | 17.8388 | 17.8234 | 17.8063 | 17.7894 | 17.7728 | 17.7403 | 17.6557 | 17.5722 | 17.4986
KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 14.4122 | 14.0803 | 15.9077 | 15.8935 | 15.8532 | 15.8184 | 15.7926 | 15.7666 | 15.7403 | 15.7145 | 15.6867 | 15.6597 | 15.6049 | 13.4092 | 13.0117 | 12.6246 | 15.8663 | 15.8626 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.683 | 13.282 | 12.8903
| KEMNAY | CT |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.9089 | 15.8988 | 15.873 | 15.8429 | 15.823 | 15.807 | 15.7907 | 15.7746 | 15.7573 | 15.7407 | 15.7067 | 15.6206 | 13.5848 | 13.3215 | 15.8666 | 15.864 | 15.8574 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.5954
| KEMNAY | LW |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 14.4122 | 14.0803 | 15.9077 | 15.8935 | 15.8532 | 15.8184 | 15.7926 | 15.7666 | 15.7403 | 15.7145 | 15.6867 | 15.6597 | 15.6049 | 13.4092 | 13.0117 | 12.6246 | 15.8663 | 15.8626 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.683 | 13.282 | 12.8903
| KEMNAY | ST |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.9114 | 15.905 | 15.8901 | 15.8671 | 15.8391 | 15.8249 | 15.8128 | 15.8009 | 15.7881 | 15.7758 | 15.7509 | 15.6906 | 15.6321 | 13.713 | 15.8672 | 15.8656 | 15.8618 | 15.8559 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525
| KEMNAY | FS |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.9143 | 15.9132 | 15.9116 | 15.9048 | 15.8966 | 15.889 | 15.8812 | 15.8717 | 15.8622 | 15.8531 | 15.8348 | 15.8119 | 15.7903 | 15.7698 | 15.8679 | 15.8677 | 15.8673 | 15.8655 | 15.8634 | 15.8615 | 15.8595 | 15.8571 | 15.8546 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525
TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.11062 | 0.11038 | 0.10972 | 0.10891 | 0.10811 | 0.10768 | 0.10728 | 0.10689 | 0.10647 | 0.10605 | 0.10522 | 0.10275 | 0.10275 | 0.10275 | 0.12808 | 0.12797 | 0.12774 | 0.12759 | 0.12745 | 0.1273 | 0.12717 | 0.12703 | 0.12688 | 0.12674 | 0.12645 | 0.12522 | 0.12496 | 0.12496
| KENMORE | CT |  |  |  | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.11062 | 0.11042 | 0.10992 | 0.10936 | 0.1088 | 0.10826 | 0.10789 | 0.10762 | 0.10732 | 0.10703 | 0.10644 | 0.10389 | 0.10275 | 0.10275 | 0.12808 | 0.12799 | 0.12778 | 0.12767 | 0.12757 | 0.12747 | 0.12738 | 0.12728 | 0.12718 | 0.12708 | 0.12687 | 0.12598 | 0.12509 | 0.12496
| KENMORE | LW |  |  |  | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.11062 | 0.11038 | 0.10972 | 0.10891 | 0.10811 | 0.10768 | 0.10728 | 0.10689 | 0.10647 | 0.10605 | 0.10522 | 0.10275 | 0.10275 | 0.10275 | 0.12808 | 0.12797 | 0.12774 | 0.12759 | 0.12745 | 0.1273 | 0.12717 | 0.12703 | 0.12688 | 0.12674 | 0.12645 | 0.12522 | 0.12496 | 0.12496
| KENMORE | ST |  |  |  | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.11068 | 0.1106 | 0.1104 | 0.11009 | 0.10971 | 0.10909 | 0.10849 | 0.10798 | 0.10764 | 0.10731 | 0.10667 | 0.10511 | 0.10359 | 0.10275 | 0.12811 | 0.12807 | 0.12797 | 0.12782 | 0.12774 | 0.12763 | 0.12752 | 0.12741 | 0.12729 | 0.12717 | 0.12695 | 0.12641 | 0.12588 | 0.12535
| KENMORE | FS |  |  |  | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.19732 | 0.11072 | 0.11071 | 0.1107 | 0.11061 | 0.11051 | 0.1103 | 0.1101 | 0.10984 | 0.10958 | 0.10933 | 0.10884 | 0.10787 | 0.1073 | 0.10678 | 0.12813 | 0.12813 | 0.12812 | 0.12808 | 0.12803 | 0.12793 | 0.12783 | 0.12776 | 0.12772 | 0.12767 | 0.12758 | 0.12737 | 0.12717 | 0.12699
STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 5.9522 | 5.6262 | 5.6085 | 5.5843 | 5.5573 | 5.5265 | 5.4932 | 5.4603 | 5.4247 | 5.3849 | 5.3025 | 4.8373 | 4.4468 | 4.0559 | 8.0779 | 7.8489 | 7.8364 | 7.8194 | 7.8004 | 7.7819 | 7.7795 | 7.7771 | 7.7745 | 7.7716 | 6.2283 | 5.6547 | 5.1364 | 4.6177 | 8.6312 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 6.1771 | 5.6676 | 5.131
| KEPCULLOCH | CT |  |  |  | 5.9522 | 5.6268 | 5.612 | 5.5926 | 5.5708 | 5.5458 | 5.5186 | 5.4917 | 5.4626 | 5.4299 | 5.362 | 5.0064 | 4.7269 | 4.4462 | 8.0779 | 7.8493 | 7.8389 | 7.8252 | 7.8099 | 7.7924 | 7.7813 | 7.7793 | 7.7772 | 7.7749 | 7.77 | 5.8791 | 5.5082 | 5.1356 | 8.6312 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.3917 | 6.0434 | 5.6668
| KEPCULLOCH | LW |  |  |  | 5.9522 | 5.6262 | 5.6085 | 5.5843 | 5.5573 | 5.5265 | 5.4932 | 5.4603 | 5.4247 | 5.3849 | 5.3025 | 4.8373 | 4.4468 | 4.0559 | 8.0779 | 7.8489 | 7.8364 | 7.8194 | 7.8004 | 7.7819 | 7.7795 | 7.7771 | 7.7745 | 7.7716 | 6.2283 | 5.6547 | 5.1364 | 4.6177 | 8.6312 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 8.4674 | 6.1771 | 5.6676 | 5.131
| KEPCULLOCH | ST |  |  |  | 5.9541 | 5.9514 | 5.945 | 5.9344 | 5.9207 | 5.8908 | 5.8597 | 5.8291 | 5.7958 | 5.7599 | 5.6863 | 5.4476 | 5.2546 | 5.0662 | 8.0792 | 8.0773 | 8.0728 | 8.0654 | 8.0558 | 8.0348 | 8.0129 | 7.9914 | 7.968 | 7.9428 | 7.8911 | 7.7562 | 6.1867 | 5.9366 | 8.6335 | 8.6302 | 8.6224 | 8.6095 | 8.5928 | 8.5563 | 8.5183 | 8.5026 | 8.4952 | 8.4873 | 8.471 | 8.4296 | 8.4296 | 8.4296
| KEPCULLOCH | FS |  |  |  | 5.9552 | 5.9545 | 5.953 | 5.9492 | 5.9445 | 5.9343 | 5.9238 | 5.9116 | 5.8991 | 5.8857 | 5.8584 | 5.7837 | 5.7059 | 5.6253 | 8.08 | 8.0795 | 8.0784 | 8.0758 | 8.0725 | 8.0653 | 8.0579 | 8.0493 | 8.0406 | 8.0312 | 8.012 | 7.9595 | 7.9048 | 7.8482 | 8.6349 | 8.634 | 8.6322 | 8.6276 | 8.6218 | 8.6094 | 8.5965 | 8.5816 | 8.5664 | 8.5501 | 8.5168 | 8.4926 | 8.4753 | 8.4674
TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052
| KERRERA | CT |  |  |  | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052
| KERRERA | LW |  |  |  | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052
| KERRERA | ST |  |  |  | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052
| KERRERA | FS |  |  |  | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.073998 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.041524 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052 | 0.048052
GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | YES | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1011 | 3.9633 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0085 | 3.8643 | 3.7226 | 4.179 | 4.1788 | 4.1782 | 4.1753 | 4.1718 | 4.1684 | 4.1651 | 4.1619 | 4.1583 | 4.1536 | 4.1436 | 4.032 | 3.8728 | 3.7162
| KERRY FALLS | CT |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1031 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0731 | 3.9689 | 3.8664 | 4.179 | 4.1789 | 4.1784 | 4.1772 | 4.1748 | 4.1724 | 4.1701 | 4.1678 | 4.1653 | 4.1629 | 4.158 | 4.1034 | 3.9883 | 3.8751
| KERRY FALLS | LW |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1011 | 3.9633 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0085 | 3.8643 | 3.7226 | 4.179 | 4.1788 | 4.1782 | 4.1753 | 4.1718 | 4.1684 | 4.1651 | 4.1619 | 4.1583 | 4.1548 | 4.1479 | 4.032 | 3.8728 | 3.7162
| KERRY FALLS | ST |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1505 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0801 | 4.0203 | 3.9608 | 4.1791 | 4.179 | 4.1788 | 4.1785 | 4.1782 | 4.1737 | 4.1688 | 4.164 | 4.1588 | 4.1536 | 4.1436 | 4.1111 | 4.045 | 3.9794
| KERRY FALLS | FS |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1791 | 4.1791 | 4.1791 | 4.179 | 4.1789 | 4.1786 | 4.1782 | 4.1767 | 4.1747 | 4.1726 | 4.1687 | 4.1594 | 4.1505 | 4.1422
TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.16316 | 0.16316 | 0.16316 | 0.16316 | -0.0055889 | -0.0202 | -0.034526 | -0.048571 | -0.063772 | -0.078872 | -0.10878 | -0.17861 | -0.2505 | -0.34969 | 0.50755 | 0.50457 | 0.49684 | 0.488 | 0.47933 | 0.47083 | 0.46249 | 0.45432 | 0.44548 | 0.4367 | 0.41929 | 0.37867 | -0.00037878 | -0.11179 | 0.23306 | 0.22933 | 0.22271 | 0.21636 | -0.00050461 | -0.016485 | -0.032154 | -0.047515 | -0.06414 | -0.080654 | -0.11412 | -0.19652 | -0.28137 | -0.39842
| KILCHRENAN | CT |  |  |  | 0.16316 | 0.16316 | 0.16316 | 0.16316 | -0.0055889 | -0.0202 | -0.034526 | -0.048571 | -0.063772 | -0.078872 | -0.10878 | -0.17861 | -0.24902 | -0.31841 | 0.50755 | 0.50457 | 0.49684 | 0.488 | 0.47933 | 0.47083 | 0.46249 | 0.45432 | 0.44548 | 0.4367 | 0.41929 | 0.37867 | 0.35132 | -0.076663 | 0.23306 | 0.22933 | 0.22271 | 0.21636 | -0.00050461 | -0.016485 | -0.032154 | -0.047515 | -0.06414 | -0.080654 | -0.11412 | -0.19652 | -0.27962 | -0.36151
| KILCHRENAN | LW |  |  |  | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | -0.0034224 | -0.012253 | -0.021803 | -0.031287 | -0.050056 | -0.14982 | -0.2505 | -0.34969 | 0.50853 | 0.50693 | 0.50234 | 0.49672 | 0.49122 | 0.48584 | 0.48059 | 0.47545 | 0.4699 | 0.46438 | 0.45346 | 0.39542 | -0.00037878 | -0.11179 | 0.23429 | 0.23229 | 0.22666 | 0.22263 | 0.21868 | 0.21482 | 0.21105 | -0.0077929 | -0.018238 | -0.02861 | -0.049139 | -0.16254 | -0.28137 | -0.39842
| KILCHRENAN | ST |  |  |  | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | -0.0045004 | -0.014312 | -0.033418 | -0.079565 | -0.12504 | -0.1704 | 0.509 | 0.50841 | 0.50702 | 0.50486 | 0.50229 | 0.49665 | 0.49115 | 0.48576 | 0.47996 | 0.47425 | 0.46314 | 0.43629 | 0.40984 | 0.38345 | 0.23487 | 0.23413 | 0.2324 | 0.2297 | 0.22663 | 0.22258 | 0.21863 | 0.21476 | 0.2106 | -0.010046 | -0.030942 | -0.081413 | -0.13331 | -0.18684
| KILCHRENAN | FS |  |  |  | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | 0.16316 | -0.014628 | -0.029434 | 0.50927 | 0.5092 | 0.5091 | 0.50849 | 0.50777 | 0.506 | 0.50424 | 0.50198 | 0.49976 | 0.49759 | 0.49338 | 0.48338 | 0.47407 | 0.46546 | 0.23522 | 0.23512 | 0.235 | 0.23424 | 0.23334 | 0.23112 | 0.22892 | 0.22641 | 0.22481 | 0.22325 | 0.22023 | 0.21305 | -0.01039 | -0.026584
STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 4.7678 | 4.3233 | 3.869 | 3.4129 | 5.9208 | 5.9111 | 5.8849 | 5.8517 | 5.8391 | 4.9416 | 4.8018 | 4.6634 | 4.5136 | 4.3639 | 4.0622 | 3.5404 | 3.007 | 2.4716 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 4.9849 | 4.8451 | 4.7066 | 4.5567 | 4.407 | 4.1052 | 3.5832 | 3.0496 | 2.514
| KILLEARN | CT |  |  |  | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 4.8736 | 4.5341 | 4.1924 | 5.9217 | 5.9149 | 5.8984 | 5.8784 | 5.8575 | 5.8452 | 5.8372 | 4.9679 | 4.8715 | 4.7745 | 4.5781 | 4.1865 | 3.7878 | 3.3867 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 4.9148 | 4.8177 | 4.6212 | 4.2295 | 3.8307 | 3.4294
| KILLEARN | LW |  |  |  | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 4.7678 | 4.3233 | 3.869 | 3.4129 | 5.9208 | 5.9111 | 5.8849 | 5.8517 | 5.8391 | 4.9416 | 4.8018 | 4.6634 | 4.5136 | 4.3639 | 4.0622 | 3.5404 | 3.007 | 2.4716 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 4.9849 | 4.8451 | 4.7066 | 4.5567 | 4.407 | 4.1052 | 3.5832 | 3.0496 | 2.514
| KILLEARN | ST |  |  |  | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 4.8313 | 5.9234 | 5.919 | 5.9094 | 5.8943 | 5.8757 | 5.8644 | 5.8524 | 5.847 | 5.8425 | 5.8378 | 4.9582 | 4.6762 | 4.4029 | 4.1368 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 4.7193 | 4.446 | 4.1798
| KILLEARN | FS |  |  |  | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 6.439 | 5.9254 | 5.9245 | 5.9232 | 5.9189 | 5.9138 | 5.9098 | 5.9056 | 5.9008 | 5.8959 | 5.8909 | 5.8807 | 5.8528 | 5.8412 | 4.9847 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387 | 6.0387
KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 2.3559 | 3.0396 | 3.0363 | 3.0266 | 3.0205 | 3.0153 | 3.0096 | 3.0036 | 2.9977 | 2.9913 | 2.9843 | 2.9746 | 2.4813 | 2.2987 | 2.1167 | 3.1961 | 3.1928 | 3.1832 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4926 | 2.3159
| KILLIN TOWN | CT |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0397 | 3.0369 | 3.0295 | 3.023 | 3.0191 | 3.0148 | 3.0103 | 3.0058 | 3.0009 | 2.9956 | 2.9847 | 2.9672 | 2.4354 | 2.3019 | 3.1962 | 3.1934 | 3.1861 | 3.1768 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4957
| KILLIN TOWN | LW |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 2.3559 | 3.0396 | 3.0363 | 3.0266 | 3.0205 | 3.0153 | 3.0096 | 3.0036 | 2.9977 | 2.9913 | 2.9843 | 2.9746 | 2.4813 | 2.2987 | 2.1167 | 3.1961 | 3.1928 | 3.1832 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4926 | 2.3159
| KILLIN TOWN | ST |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0406 | 3.0392 | 3.036 | 3.0307 | 3.0244 | 3.0196 | 3.0146 | 3.0098 | 3.0044 | 2.9988 | 2.9873 | 2.9715 | 2.9672 | 2.4682 | 3.1971 | 3.1957 | 3.1925 | 3.1873 | 3.1806 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736
| KILLIN TOWN | FS |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0412 | 3.0409 | 3.0403 | 3.0386 | 3.0365 | 3.0318 | 3.027 | 3.0233 | 3.0211 | 3.0187 | 3.014 | 3.0014 | 2.9886 | 2.9759 | 3.1976 | 3.1974 | 3.1968 | 3.1951 | 3.193 | 3.1883 | 3.1835 | 3.1778 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736
TAYNUILT | KILMELFORD PS | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 4.0034 | 3.9837 | 3.9317 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 2.3952 | 1.5276 | 1.3827 | 1.2399 | 4.0642 | 4.0519 | 4.0196 | 3.9969 | 3.993 | 3.9891 | 3.9855 | 2.4821 | 2.4058 | 2.33 | 1.6068 | 0.85661 | 0.6939 | 0.53151 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 2.4506 | 1.5306 | 0.63286 | 0.45814 | 0.286
| KILMELFORD PS | CT |  |  |  | 4.004 | 3.9886 | 3.9517 | 3.9105 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.2445 | 1.789 | 1.7131 | 1.6383 | 4.0646 | 4.055 | 4.032 | 4.0064 | 3.9969 | 3.9944 | 3.992 | 3.9896 | 3.987 | 3.9845 | 1.8427 | 1.1635 | 1.0728 | 0.98342 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 1.7839 | 0.96243 | 0.86506 | 0.76903
| KILMELFORD PS | LW |  |  |  | 4.0034 | 3.9837 | 3.9317 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 3.8984 | 2.3952 | 1.5276 | 1.3827 | 1.2399 | 4.0642 | 4.0519 | 4.0196 | 3.9969 | 3.993 | 3.9891 | 3.9855 | 2.4821 | 2.4058 | 2.33 | 1.6068 | 0.85661 | 0.6939 | 0.53151 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 2.4506 | 1.5306 | 0.63286 | 0.45814 | 0.286
| KILMELFORD PS | ST |  |  |  | 4.009 | 4.0014 | 3.9854 | 3.962 | 3.9346 | 3.9203 | 3.9071 | 3.8984 | 3.8984 | 3.8984 | 3.5714 | 3.2637 | 3.2637 | 3.2637 | 4.0677 | 4.0629 | 4.053 | 4.0384 | 4.0214 | 4.0125 | 4.0043 | 3.9985 | 3.9976 | 3.9967 | 2.4417 | 2.075 | 2.0039 | 1.933 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 2.4761 | 2.0362 | 1.9598 | 1.8837
| KILMELFORD PS | FS |  |  |  | 4.0122 | 4.0104 | 4.0082 | 4.001 | 3.9928 | 3.9878 | 3.9834 | 3.9779 | 3.9725 | 3.9671 | 3.9568 | 3.9331 | 3.9111 | 3.8984 | 4.0696 | 4.0685 | 4.0672 | 4.0627 | 4.0576 | 4.0545 | 4.0518 | 4.0483 | 4.0449 | 4.0416 | 4.0352 | 4.0204 | 4.0068 | 3.9982 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126
TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 1.0143 | 1.0143 | 1.0143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 2.0921 | 2.0063 | 2.0063 | 2.0063 | 0.72665 | 0.72557 | 0.72248 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 2.2411 | 2.0497 | 1.9309 | 1.8138 | 0.75354 | 0.75331 | 0.75265 | 3.2518 | 3.251 | 3.2503 | 3.2495 | 2.4917 | 2.482 | 2.4724 | 1.9365 | 1.7284 | 1.6142 | 1.5016
| KILNINVER | CT |  |  |  | 1.0143 | 1.0143 | 1.0143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 2.0921 | 2.0063 | 2.0063 | 2.0063 | 0.72665 | 0.72575 | 0.72343 | 3.2208 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 2.2702 | 2.1102 | 2.023 | 1.9371 | 0.75354 | 0.75335 | 0.75285 | 3.2523 | 3.2517 | 3.2512 | 3.2507 | 3.2501 | 3.2496 | 2.4947 | 1.9645 | 1.7866 | 1.7027 | 1.6202
| KILNINVER | LW |  |  |  | 1.0143 | 1.0143 | 1.0143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 2.0921 | 2.0063 | 2.0063 | 2.0063 | 0.72665 | 0.72557 | 0.72248 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 2.2411 | 2.0497 | 1.9309 | 1.8138 | 0.75354 | 0.75331 | 0.75265 | 3.2518 | 3.251 | 3.2503 | 3.2495 | 2.4917 | 2.482 | 2.4724 | 1.9365 | 1.7284 | 1.6142 | 1.5016
| KILNINVER | ST |  |  |  | 1.0143 | 1.0143 | 1.0143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 2.326 | 2.2831 | 2.2831 | 2.2831 | 0.72697 | 0.72657 | 0.72563 | 3.2242 | 3.2224 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 2.455 | 2.3666 | 2.3157 | 2.265 | 0.75361 | 0.75353 | 0.75333 | 3.253 | 3.2526 | 3.2518 | 3.2509 | 3.2501 | 2.4972 | 2.4867 | 2.2077 | 2.1107 | 2.0617 | 2.0129
| KILNINVER | FS |  |  |  | 1.0143 | 1.0143 | 1.0143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 3.5143 | 0.72715 | 0.7271 | 0.72703 | 3.2266 | 3.2261 | 3.2248 | 3.2235 | 3.2218 | 3.2202 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 3.2191 | 0.75365 | 0.75364 | 0.75363 | 3.2535 | 3.2534 | 3.2532 | 3.2529 | 3.2525 | 3.2522 | 3.2518 | 3.2511 | 3.2495 | 2.483 | 2.4663
BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9714 | 5.8462 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9764 | 5.8252 | 5.671 | 5.5197 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9394 | 5.7876 | 5.6387
| KILTARLITY | CT |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9932 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9347 | 5.815 | 5.6973 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9293 | 5.8134
| KILTARLITY | LW |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9714 | 5.8462 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9764 | 5.8252 | 5.671 | 5.5197 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9394 | 5.7876 | 5.6387
| KILTARLITY | ST |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9583 | 5.8933 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233
| KILTARLITY | FS |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233
REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | NO | 16.2408 | 16.1748 | 16.0952 | 16.0198 | 15.9469 | 15.8759 | 15.8069 | 15.7415 | 15.7019 | 15.6802 | 15.6375 | 15.5187 | 15.414 | 15.3234 | 14.6781 | 14.6136 | 14.5475 | 14.4832 | 14.4206 | 14.3577 | 14.2976 | 14.2661 | 14.2482 | 14.2393 | 14.2219 | 14.1799 | 14.1351 | 11.4029 | 15.1311 | 15.0577 | 14.9735 | 14.8932 | 14.8153 | 14.7388 | 14.6637 | 14.5934 | 14.5489 | 14.5229 | 14.4715 | 14.3642 | 14.2756 | 14.1813
| KINCORTH | CT |  |  |  | 16.2408 | 16.1748 | 16.0952 | 16.0198 | 15.9469 | 15.8759 | 15.8069 | 15.7415 | 15.7019 | 15.6802 | 15.6375 | 15.5187 | 15.414 | 15.3234 | 14.6781 | 14.6136 | 14.5475 | 14.4832 | 14.4206 | 14.3577 | 14.2976 | 14.2661 | 14.2482 | 14.2393 | 14.2219 | 14.1799 | 14.1351 | 11.4029 | 15.1311 | 15.0577 | 14.9735 | 14.8932 | 14.8153 | 14.7388 | 14.6637 | 14.5934 | 14.5489 | 14.5229 | 14.4715 | 14.3642 | 14.2756 | 14.1813
| KINCORTH | LW |  |  |  | 16.3258 | 16.3082 | 16.2938 | 16.2774 | 16.26 | 16.2416 | 16.2221 | 16.2017 | 16.179 | 16.1557 | 16.1074 | 15.9552 | 15.797 | 15.6624 | 14.7387 | 14.7071 | 14.6893 | 14.6687 | 14.6482 | 14.6271 | 14.6053 | 14.5831 | 14.5586 | 14.5338 | 14.4814 | 14.4018 | 14.3365 | 14.2657 | 15.2173 | 15.1926 | 15.1753 | 15.1554 | 15.1349 | 15.1132 | 15.0906 | 15.0672 | 15.0411 | 15.0145 | 14.9589 | 14.8037 | 14.6742 | 14.5342
| KINCORTH | ST |  |  |  | 16.3397 | 16.332 | 16.3264 | 16.3206 | 16.3146 | 16.3052 | 16.2957 | 16.287 | 16.2784 | 16.2679 | 16.2477 | 16.1924 | 16.1401 | 16.0851 | 14.751 | 14.7346 | 14.7283 | 14.7206 | 14.7119 | 14.6951 | 14.6771 | 14.6618 | 14.6456 | 14.6292 | 14.5972 | 14.5092 | 14.4924 | 14.4739 | 15.2324 | 15.2206 | 15.2141 | 15.2069 | 15.1992 | 15.1861 | 15.1723 | 15.1602 | 15.1478 | 15.134 | 15.1071 | 15.033 | 14.9831 | 14.9464
| KINCORTH | FS |  |  |  | 16.3372 | 16.3302 | 16.3254 | 16.3182 | 16.3109 | 16.303 | 16.2953 | 16.2873 | 16.2795 | 16.2718 | 16.2568 | 16.2143 | 16.17 | 16.1268 | 14.7513 | 14.7401 | 14.7361 | 14.7296 | 14.7229 | 14.7138 | 14.7051 | 14.6955 | 14.6859 | 14.6765 | 14.6588 | 14.6121 | 14.5637 | 14.516 | 15.2305 | 15.2212 | 15.2161 | 15.2083 | 15.2003 | 15.1911 | 15.1821 | 15.1726 | 15.1632 | 15.154 | 15.1362 | 15.0871 | 15.0361 | 14.9861
FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.034548 | 0.034461 | 0.03421 | 0.033905 | 0.03368 | 0.033526 | 0.033375 | 0.033227 | 0.033068 | 0.032909 | 0.032596 | 0.0321 | 0.0321 | 0.0321 | 0.040009 | 0.039967 | 0.039895 | 0.039839 | 0.039784 | 0.039731 | 0.039678 | 0.039627 | 0.039571 | 0.039516 | 0.039407 | 0.039142 | 0.03904 | 0.03904
| KINGAIRLOCH | CT |  |  |  | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.034549 | 0.034476 | 0.034288 | 0.034073 | 0.033864 | 0.033708 | 0.033602 | 0.033498 | 0.033386 | 0.033275 | 0.033056 | 0.032522 | 0.0321 | 0.0321 | 0.040009 | 0.039974 | 0.039909 | 0.03987 | 0.039832 | 0.039794 | 0.039757 | 0.039721 | 0.039682 | 0.039644 | 0.039567 | 0.039382 | 0.039192 | 0.03904
| KINGAIRLOCH | LW |  |  |  | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.034548 | 0.034461 | 0.03421 | 0.033905 | 0.03368 | 0.033526 | 0.033375 | 0.033227 | 0.033068 | 0.032909 | 0.032596 | 0.0321 | 0.0321 | 0.0321 | 0.040009 | 0.039967 | 0.039895 | 0.039839 | 0.039784 | 0.039731 | 0.039678 | 0.039627 | 0.039571 | 0.039516 | 0.039407 | 0.039142 | 0.03904 | 0.03904
| KINGAIRLOCH | ST |  |  |  | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.034574 | 0.034541 | 0.034466 | 0.034348 | 0.034208 | 0.034071 | 0.033938 | 0.033808 | 0.033713 | 0.03364 | 0.033499 | 0.033159 | 0.032821 | 0.032484 | 0.040022 | 0.040006 | 0.039969 | 0.039921 | 0.039895 | 0.03987 | 0.039845 | 0.039822 | 0.039796 | 0.039771 | 0.039721 | 0.039603 | 0.039486 | 0.039368
| KINGAIRLOCH | FS |  |  |  | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.061646 | 0.034589 | 0.034585 | 0.034579 | 0.034546 | 0.034507 | 0.034461 | 0.034416 | 0.034358 | 0.034301 | 0.034245 | 0.034136 | 0.03388 | 0.033698 | 0.03358 | 0.040029 | 0.040027 | 0.040024 | 0.040008 | 0.039989 | 0.039967 | 0.039945 | 0.039922 | 0.039912 | 0.039902 | 0.039882 | 0.039835 | 0.039791 | 0.039749
DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 4.9357 | 4.5811 | 3.2563 | 2.7398 | 2.2347 | 6.4982 | 6.4635 | 6.3634 | 6.3109 | 6.2785 | 4.8718 | 4.6728 | 4.477 | 4.2654 | 4.0566 | 3.6394 | 2.4334 | 1.8257 | 1.2314 | 6.8501 | 6.8455 | 6.8324 | 6.8162 | 6.8001 | 6.7841 | 4.9807 | 4.8011 | 4.607 | 4.4156 | 4.0252 | 2.6339 | 2.0357 | 1.4506
| KINGSEAT | CT |  |  |  | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 4.6253 | 4.2936 | 3.945 | 6.5086 | 6.4968 | 6.4663 | 6.4305 | 6.3942 | 6.3578 | 6.3323 | 6.3227 | 6.3124 | 6.3024 | 6.282 | 4.074 | 3.654 | 3.2438 | 6.8514 | 6.8499 | 6.8459 | 6.8412 | 6.8364 | 6.8317 | 6.8268 | 6.8221 | 6.8169 | 6.8119 | 6.8018 | 4.2177 | 3.8325 | 3.4317
| KINGSEAT | LW |  |  |  | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 4.9357 | 4.5811 | 3.2563 | 2.7398 | 2.2347 | 6.4982 | 6.4635 | 6.3634 | 6.3109 | 6.2785 | 4.8718 | 4.6728 | 4.477 | 4.2654 | 4.0566 | 3.6394 | 2.4334 | 1.8257 | 1.2314 | 6.8501 | 6.8455 | 6.8324 | 6.8162 | 6.8001 | 6.7841 | 4.9807 | 4.8011 | 4.607 | 4.4156 | 4.0252 | 2.6339 | 2.0357 | 1.4506
| KINGSEAT | ST |  |  |  | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 4.9889 | 4.8497 | 4.6154 | 6.6146 | 6.4903 | 6.4521 | 6.3923 | 6.3321 | 6.323 | 6.3138 | 6.3048 | 6.2951 | 6.2857 | 4.9996 | 4.4126 | 4.1319 | 3.8562 | 6.8653 | 6.849 | 6.844 | 6.8362 | 6.8267 | 6.8222 | 6.8176 | 6.8132 | 6.8083 | 6.8036 | 6.7943 | 4.6351 | 4.3777 | 4.1248
| KINGSEAT | FS |  |  |  | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 7.7557 | 6.6223 | 6.6203 | 6.6176 | 6.6028 | 6.5852 | 6.5741 | 6.5629 | 6.5489 | 6.5351 | 6.5216 | 6.4948 | 6.4307 | 6.3699 | 6.3301 | 6.8663 | 6.8661 | 6.8657 | 6.8638 | 6.8615 | 6.86 | 6.8585 | 6.8567 | 6.8549 | 6.8531 | 6.8496 | 6.8412 | 6.8332 | 6.8257
BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 9.5857 | 9.5657 | 9.5212 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.6131 | 8.6037 | 8.5827 | 8.5571 | 8.532 | 8.5064 | 8.4793 | 8.4515 | 8.4215 | 8.3947 | 8.3462 | 8.1889 | 5.6822 | 5.2662 | 8.6415 | 8.6358 | 8.6231 | 8.6076 | 8.5924 | 8.5769 | 8.5605 | 8.5436 | 8.5255 | 8.5092 | 8.4823 | 8.4486 | 5.881 | 5.4712
| KINGUSSIE | CT |  |  |  | 9.5865 | 9.5706 | 9.5383 | 9.5013 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.6135 | 8.606 | 8.5908 | 8.5734 | 8.5561 | 8.5381 | 8.5186 | 8.498 | 8.4755 | 8.4552 | 8.4188 | 8.31 | 6.1444 | 5.8669 | 8.6417 | 8.6372 | 8.628 | 8.6174 | 8.607 | 8.5961 | 8.5843 | 8.5718 | 8.5582 | 8.5459 | 8.5239 | 8.4745 | 6.3359 | 6.063
| KINGUSSIE | LW |  |  |  | 9.5857 | 9.5657 | 9.5212 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.6131 | 8.6037 | 8.5827 | 8.5571 | 8.532 | 8.5064 | 8.4793 | 8.4515 | 8.4215 | 8.3947 | 8.3462 | 8.1889 | 5.6822 | 5.2662 | 8.6415 | 8.6358 | 8.6231 | 8.6076 | 8.5924 | 8.5769 | 8.5605 | 8.5436 | 8.5255 | 8.5092 | 8.4823 | 8.4486 | 5.881 | 5.4712
| KINGUSSIE | ST |  |  |  | 9.5918 | 9.5827 | 9.5668 | 9.5441 | 9.518 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.2213 | 9.2213 | 8.616 | 8.6117 | 8.6042 | 8.5935 | 8.5812 | 8.5637 | 8.5453 | 8.5264 | 8.5056 | 8.4864 | 8.4512 | 8.378 | 8.0942 | 8.0251 | 8.6432 | 8.6406 | 8.6361 | 8.6296 | 8.6222 | 8.6116 | 8.6005 | 8.589 | 8.5764 | 8.5648 | 8.5434 | 8.4991 | 8.2287 | 8.214
| KINGUSSIE | FS |  |  |  | 9.5961 | 9.5926 | 9.5887 | 9.5807 | 9.5721 | 9.559 | 9.545 | 9.528 | 9.5107 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.618 | 8.6163 | 8.6145 | 8.6107 | 8.6067 | 8.6005 | 8.5939 | 8.5859 | 8.5778 | 8.5703 | 8.5565 | 8.5281 | 8.5026 | 8.4786 | 8.6445 | 8.6435 | 8.6424 | 8.6401 | 8.6376 | 8.6339 | 8.6299 | 8.625 | 8.6201 | 8.6156 | 8.6072 | 8.59 | 8.5746 | 8.5601
TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | -0.0085446 | 0.73519 | 0.73417 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | -0.1186
| KINLOCH | CT |  |  |  | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.73519 | 0.73434 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414
| KINLOCH | LW |  |  |  | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | -0.0085446 | 0.73519 | 0.73417 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | -0.1186
| KINLOCH | ST |  |  |  | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.73548 | 0.73511 | 0.73423 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414
| KINLOCH | FS |  |  |  | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.96935 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.88298 | 0.73566 | 0.73561 | 0.73555 | 0.73517 | 0.73471 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414 | 0.73414
TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 2.7949 | 2.793 | 2.7873 | 2.7807 | 2.7781 | 2.7772 | 2.7762 | 2.7753 | 2.7743 | 2.7733 | 2.7713 | 2.7713 | 2.4806 | 2.4053 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.4439
| KINLOCH RANNOCH | CT |  |  |  | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 2.7949 | 2.7933 | 2.7891 | 2.7842 | 2.7799 | 2.7784 | 2.7776 | 2.777 | 2.7763 | 2.7756 | 2.7742 | 2.7713 | 2.7713 | 2.7713 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309
| KINLOCH RANNOCH | LW |  |  |  | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 2.7949 | 2.793 | 2.7873 | 2.7807 | 2.7781 | 2.7772 | 2.7762 | 2.7753 | 2.7743 | 2.7733 | 2.7713 | 2.7713 | 2.4806 | 2.4053 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.4439
| KINLOCH RANNOCH | ST |  |  |  | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 2.7955 | 2.7948 | 2.7931 | 2.7904 | 2.7872 | 2.7829 | 2.7794 | 2.7783 | 2.7776 | 2.777 | 2.7758 | 2.7727 | 2.7713 | 2.7713 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309
| KINLOCH RANNOCH | FS |  |  |  | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 3.0764 | 2.7958 | 2.7957 | 2.7956 | 2.7949 | 2.794 | 2.7925 | 2.7911 | 2.7893 | 2.7875 | 2.7858 | 2.7824 | 2.7782 | 2.7771 | 2.7761 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309 | 2.8309
GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | YES | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.5425 | -0.59396 | -0.64473 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.5273 | -0.53215 | -0.53692 | -0.5416 | -0.54667 | -0.55172 | -0.5617 | -0.62096 | -0.68098 | -0.7402 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474
| KINLOCHEWE | CT |  |  |  | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.55283 | -0.58943 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52304 | -0.52641 | -0.52973 | -0.53299 | -0.53653 | -0.54005 | -0.54703 | -0.58969 | -0.63302 | -0.6757 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474
| KINLOCHEWE | LW |  |  |  | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.5425 | -0.59396 | -0.64473 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.5273 | -0.53215 | -0.53692 | -0.5416 | -0.54667 | -0.55172 | -0.5617 | -0.62096 | -0.68098 | -0.7402 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474
| KINLOCHEWE | ST |  |  |  | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.53088 | -0.55239 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.5228 | -0.52805 | -0.5332 | -0.53877 | -0.54425 | -0.55495 | -0.58093 | -0.60675 | -0.6325 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474
| KINLOCHEWE | FS |  |  |  | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52391 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.52274 | -0.5269 | -0.53686 | -0.54624 | -0.55505 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474 | -0.60474
KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0463 | 3.0451 | 3.0421 | 3.0384 | 3.0347 | 3.0311 | 3.0275 | 3.0239 | 3.0201 | 3.0163 | 3.009 | 2.9647 | 2.9529 | 2.9529 | 3.0485 | 3.0481 | 3.0471 | 3.0458 | 3.0446 | 3.0434 | 3.0422 | 3.041 | 3.0397 | 3.0384 | 3.036 | 3.0212 | 3.0054 | 3.0046
| KINLOCHLEVEN | CT |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0463 | 3.0451 | 3.0423 | 3.0391 | 3.036 | 3.0329 | 3.0298 | 3.0268 | 3.0235 | 3.0202 | 3.0139 | 2.9824 | 2.9529 | 2.9529 | 3.0485 | 3.0481 | 3.0472 | 3.0461 | 3.0451 | 3.044 | 3.043 | 3.042 | 3.0408 | 3.0398 | 3.0376 | 3.0271 | 3.0156 | 3.0046
| KINLOCHLEVEN | LW |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0464 | 3.0452 | 3.0421 | 3.0384 | 3.0347 | 3.0311 | 3.0275 | 3.0239 | 3.0201 | 3.0163 | 3.009 | 2.9647 | 2.9529 | 2.9529 | 3.0485 | 3.0481 | 3.0471 | 3.0458 | 3.0446 | 3.0434 | 3.0422 | 3.041 | 3.0397 | 3.0384 | 3.036 | 3.0212 | 3.0054 | 3.0046
| KINLOCHLEVEN | ST |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0467 | 3.0463 | 3.0453 | 3.0438 | 3.0421 | 3.0379 | 3.0337 | 3.0296 | 3.0252 | 3.0209 | 3.0126 | 2.9921 | 2.9703 | 2.9529 | 3.0487 | 3.0485 | 3.0482 | 3.0477 | 3.0471 | 3.0457 | 3.0443 | 3.0429 | 3.0414 | 3.04 | 3.0372 | 3.0303 | 3.023 | 3.0158
| KINLOCHLEVEN | FS |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.047 | 3.0469 | 3.0467 | 3.0463 | 3.0458 | 3.0444 | 3.043 | 3.0412 | 3.0395 | 3.0378 | 3.0344 | 3.0266 | 3.0188 | 3.011 | 3.0487 | 3.0487 | 3.0486 | 3.0485 | 3.0483 | 3.0479 | 3.0474 | 3.0468 | 3.0462 | 3.0456 | 3.0445 | 3.0419 | 3.0393 | 3.0367
FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.029793 | 0.029735 | 0.029569 | 0.029366 | 0.029167 | 0.029036 | 0.028936 | 0.028812 | 0.028623 | 0.028437 | 0.028073 | 0.027673 | 0.027673 | -0.00032654 | 0.034496 | 0.034468 | 0.034407 | 0.03437 | 0.034333 | 0.034298 | 0.034263 | 0.03422 | 0.034154 | 0.034089 | 0.033963 | 0.033656 | 0.033656 | 0.033656
| KINLOCHMOIDART | CT |  |  |  | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.029793 | 0.029745 | 0.029621 | 0.029478 | 0.029339 | 0.029203 | 0.029087 | 0.029019 | 0.028945 | 0.028871 | 0.028726 | 0.027673 | 0.027673 | 0.027673 | 0.034496 | 0.034472 | 0.034416 | 0.03439 | 0.034365 | 0.03434 | 0.034316 | 0.034292 | 0.034266 | 0.03424 | 0.03419 | 0.033709 | 0.033656 | 0.033656
| KINLOCHMOIDART | LW |  |  |  | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.029793 | 0.029735 | 0.029569 | 0.029366 | 0.029167 | 0.029036 | 0.028936 | 0.028838 | 0.028733 | 0.028628 | 0.02842 | 0.027673 | 0.027673 | -0.00032654 | 0.034496 | 0.034468 | 0.034407 | 0.03437 | 0.034333 | 0.034298 | 0.034263 | 0.034229 | 0.034192 | 0.034156 | 0.034083 | 0.033656 | 0.033656 | 0.033656
| KINLOCHMOIDART | ST |  |  |  | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.02981 | 0.029789 | 0.029739 | 0.029661 | 0.029568 | 0.029221 | 0.028988 | 0.028812 | 0.028623 | 0.028437 | 0.028073 | 0.027673 | 0.027673 | 0.027673 | 0.034504 | 0.034493 | 0.034469 | 0.034431 | 0.034407 | 0.034343 | 0.034281 | 0.03422 | 0.034154 | 0.034089 | 0.033963 | 0.033656 | 0.033656 | 0.033656
| KINLOCHMOIDART | FS |  |  |  | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.053144 | 0.02982 | 0.029817 | 0.029814 | 0.029792 | 0.029766 | 0.029649 | 0.029537 | 0.029392 | 0.029248 | 0.029109 | 0.028964 | 0.028629 | 0.028317 | 0.02802 | 0.034509 | 0.034507 | 0.034506 | 0.034495 | 0.034482 | 0.034426 | 0.034401 | 0.034375 | 0.034348 | 0.034323 | 0.034273 | 0.034156 | 0.034047 | 0.033944
ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 16.3435 | 16.3428 | 16.341 | 16.3388 | 16.3365 | 16.3343 | 16.3321 | 16.33 | 16.3279 | 16.3258 | 16.3216 | 16.3047 | 13.7739 | 13.7739 | 15.0863 | 15.082 | 15.0709 | 15.0573 | 15.0439 | 13.78 | 13.7531 | 13.7273 | 13.701 | 13.6749 | 13.6231 | 13.4163 | 12.5241 | 12.3172 | 14.7971 | 14.794 | 14.786 | 14.7763 | 13.7966 | 13.7734 | 13.7504 | 13.7282 | 13.7057 | 13.6833 | 13.639 | 13.4618 | 12.3781 | 12.1989
| KINLOSS | CT |  |  |  | 16.3437 | 16.3433 | 16.3425 | 16.3416 | 16.3406 | 16.3397 | 16.3387 | 16.3378 | 16.3369 | 16.336 | 16.3342 | 16.3253 | 13.7739 | 13.7739 | 15.0871 | 15.0849 | 15.0799 | 15.0743 | 15.0686 | 15.0628 | 15.057 | 15.0514 | 15.046 | 15.0405 | 13.7787 | 13.6692 | 12.8669 | 12.7595 | 14.7977 | 14.7961 | 14.7925 | 14.7885 | 14.7844 | 14.7803 | 14.7761 | 14.7721 | 14.7682 | 13.7908 | 13.7723 | 13.6784 | 12.6809 | 12.586
| KINLOSS | LW |  |  |  | 16.3435 | 16.3428 | 16.341 | 16.3388 | 16.3365 | 16.3343 | 16.3321 | 16.33 | 16.3279 | 16.3258 | 16.3216 | 16.3047 | 13.7739 | 13.7739 | 15.0863 | 15.082 | 15.0709 | 15.0573 | 15.0439 | 13.78 | 13.7531 | 13.7273 | 13.701 | 13.6749 | 13.6231 | 13.4163 | 12.5241 | 12.3172 | 14.7971 | 14.794 | 14.786 | 14.7763 | 13.7966 | 13.7734 | 13.7504 | 13.7282 | 13.7057 | 13.6833 | 13.639 | 13.4618 | 12.3781 | 12.1989
| KINLOSS | ST |  |  |  | 16.3437 | 16.3434 | 16.3426 | 16.3415 | 16.3401 | 16.3383 | 16.3365 | 16.3347 | 16.3328 | 16.331 | 16.3274 | 16.3189 | 14.1678 | 14.1678 | 15.0873 | 15.0851 | 15.0806 | 15.0738 | 15.0657 | 15.0545 | 15.0434 | 13.7843 | 13.7615 | 13.739 | 13.6952 | 13.5911 | 13.1487 | 13.0454 | 14.7978 | 14.7963 | 14.793 | 14.7881 | 14.7823 | 14.7743 | 13.7958 | 13.7771 | 13.7576 | 13.7382 | 13.7008 | 13.6116 | 13.0718 | 12.9834
| KINLOSS | FS |  |  |  | 16.3439 | 16.3438 | 16.3437 | 16.3434 | 16.343 | 16.3424 | 16.3418 | 16.3411 | 16.3404 | 16.3397 | 16.3383 | 16.3352 | 16.3324 | 16.3297 | 15.0882 | 15.0877 | 15.0872 | 15.0851 | 15.0828 | 15.0792 | 15.0756 | 15.0712 | 15.067 | 15.0629 | 15.0548 | 13.7913 | 13.7567 | 13.7232 | 14.7985 | 14.7981 | 14.7977 | 14.7963 | 14.7946 | 14.792 | 14.7894 | 14.7863 | 14.7833 | 14.7803 | 14.7745 | 13.783 | 13.7534 | 13.7247
BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | NO | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 7.6258 | 9.3844 | 9.3653 | 9.3145 | 9.2504 | 9.1996 | 9.1933 | 9.187 | 7.3245 | 7.192 | 7.0554 | 6.7807 | 6.1282 | 5.528 | 4.9301 | 9.8327 | 9.8295 | 9.8209 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 6.7925 | 6.1851 | 5.5802
| KIPPEN | CT |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 10.6285 | 9.3845 | 9.3682 | 9.3294 | 9.2832 | 9.2359 | 9.1998 | 9.1951 | 9.1905 | 9.1855 | 7.3175 | 7.1144 | 6.6232 | 6.1863 | 5.75 | 9.8327 | 9.83 | 9.8234 | 9.8157 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 7.2933 | 6.8512 | 6.4097
| KIPPEN | LW |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 7.6258 | 9.3844 | 9.3653 | 9.3145 | 9.2504 | 9.1996 | 9.1933 | 9.187 | 7.3245 | 7.192 | 7.0554 | 6.7807 | 6.1282 | 5.528 | 4.9301 | 9.8327 | 9.8295 | 9.8209 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 6.7925 | 6.1851 | 5.5802
| KIPPEN | ST |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6664 | 10.6664 | 10.6664 | 9.3897 | 9.3814 | 9.364 | 9.3363 | 9.3024 | 9.2762 | 9.2493 | 9.2231 | 9.2005 | 9.1977 | 9.192 | 7.2203 | 6.9332 | 6.6514 | 9.8336 | 9.8322 | 9.8293 | 9.8246 | 9.8189 | 9.8145 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.7733 | 9.7733 | 7.3305
| KIPPEN | FS |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 9.3935 | 9.3918 | 9.39 | 9.382 | 9.3723 | 9.3636 | 9.3547 | 9.3441 | 9.3333 | 9.322 | 9.2993 | 9.2394 | 9.199 | 9.1932 | 9.8342 | 9.8339 | 9.8336 | 9.8323 | 9.8306 | 9.8292 | 9.8277 | 9.8259 | 9.8241 | 9.8222 | 9.8184 | 9.8111 | 9.8111 | 9.8111
THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 47.2665 | 47.2632 | 47.2538 | 47.2421 | 47.2304 | 47.2186 | 47.2075 | 47.1967 | 47.1836 | 47.1713 | 47.1468 | 37.3768 | 36.3773 | 35.3796 | 44.23 | 44.2129 | 44.1638 | 44.1024 | 44.0413 | 43.9797 | 43.9219 | 43.8653 | 43.7971 | 43.7327 | 43.6046 | 35.2371 | 34.0636 | 32.8922 | 42.9351 | 42.926 | 42.8999 | 42.8674 | 42.835 | 42.8023 | 42.7716 | 42.7416 | 42.7054 | 42.6712 | 42.6032 | 36.8681 | 35.7251 | 34.5841
| KIRKWALL | CT |  |  |  | 47.2665 | 47.2634 | 47.2556 | 47.2464 | 47.2372 | 47.2279 | 47.2193 | 47.2108 | 47.2005 | 47.1908 | 47.1716 | 45.2531 | 37.1556 | 36.4161 | 44.23 | 44.214 | 44.1731 | 44.1252 | 44.0771 | 44.0284 | 43.9833 | 43.9391 | 43.8853 | 43.8347 | 43.7341 | 35.8454 | 34.9774 | 34.1091 | 42.9351 | 42.9266 | 42.9049 | 42.8795 | 42.8539 | 42.8281 | 42.8041 | 42.7807 | 42.7522 | 42.7253 | 42.6719 | 37.0659 | 36.6151 | 35.7694
| KIRKWALL | LW |  |  |  | 47.2665 | 47.2632 | 47.2538 | 47.2421 | 47.2304 | 47.2186 | 47.2075 | 47.1967 | 47.1836 | 47.1713 | 47.1468 | 37.3768 | 36.3773 | 35.3796 | 44.2303 | 44.2129 | 44.1638 | 44.1024 | 44.0413 | 43.9797 | 43.9219 | 43.8653 | 43.7971 | 43.7327 | 43.6046 | 35.2371 | 34.0636 | 32.8922 | 42.9352 | 42.926 | 42.8999 | 42.8674 | 42.835 | 42.8023 | 42.7716 | 42.7416 | 42.7054 | 42.6712 | 42.6032 | 36.8681 | 35.7251 | 34.5841
| KIRKWALL | ST |  |  |  | 48.0326 | 48.0313 | 47.2639 | 47.2593 | 47.2538 | 47.2449 | 47.2365 | 47.2283 | 47.2186 | 47.2095 | 47.1915 | 46.223 | 46.1797 | 46.1363 | 44.6462 | 44.6396 | 44.2164 | 44.1926 | 44.164 | 44.1173 | 44.0733 | 44.0304 | 43.9799 | 43.9321 | 43.838 | 37.1657 | 36.6347 | 36.1018 | 43.6448 | 43.6413 | 42.9279 | 42.9153 | 42.9001 | 42.8753 | 42.852 | 42.8292 | 42.8024 | 42.777 | 42.7271 | 41.7509 | 41.6309 | 41.5106
| KIRKWALL | FS |  |  |  | 48.0336 | 48.0333 | 48.033 | 48.0315 | 48.0299 | 48.027 | 48.0242 | 48.0207 | 48.017 | 48.0135 | 48.0066 | 47.9897 | 47.9738 | 47.9582 | 44.6515 | 44.6501 | 44.6481 | 44.6406 | 44.6321 | 44.6168 | 44.6024 | 44.5841 | 44.5647 | 44.5463 | 44.5101 | 44.422 | 44.3388 | 44.2574 | 43.6477 | 43.6469 | 43.6458 | 43.6419 | 43.6373 | 43.6292 | 43.6216 | 43.6119 | 43.6016 | 43.5918 | 43.5726 | 43.5258 | 43.4817 | 43.4385
BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 1.9468 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 1.9637 | 1.805 | 2.7951 | 2.7947 | 2.7935 | 2.7919 | 2.7904 | 2.7889 | 2.7873 | 2.7843 | 2.7811 | 2.7779 | 2.7718 | 2.744 | 1.9791 | 1.8267
| KISHORNHILL | CT |  |  |  | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 1.9007 | 2.7951 | 2.7948 | 2.7938 | 2.7928 | 2.7917 | 2.7907 | 2.7897 | 2.7887 | 2.7876 | 2.7865 | 2.7843 | 2.7542 | 2.7235 | 1.9186
| KISHORNHILL | LW |  |  |  | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 1.9468 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 1.9637 | 1.805 | 2.7951 | 2.7947 | 2.7935 | 2.7919 | 2.7904 | 2.7889 | 2.7875 | 2.786 | 2.7845 | 2.7829 | 2.7799 | 2.744 | 1.9791 | 1.8267
| KISHORNHILL | ST |  |  |  | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.7952 | 2.7951 | 2.7947 | 2.7941 | 2.7935 | 2.7903 | 2.7873 | 2.7843 | 2.7811 | 2.7779 | 2.7718 | 2.7568 | 2.7418 | 2.7269
| KISHORNHILL | FS |  |  |  | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.4124 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.3535 | 2.7953 | 2.7953 | 2.7953 | 2.7951 | 2.7949 | 2.7939 | 2.7929 | 2.7916 | 2.7903 | 2.789 | 2.7866 | 2.7807 | 2.7753 | 2.7701
BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 6.512 | 6.4091 | 5.2766 | 5.1486 | 5.0252 | 4.9062 | 4.792 | 4.6823 | 3.9978 | 3.9716 | 3.9201 | 3.7935 | 3.5821 | 3.3556 | 6.1197 | 6.042 | 4.9414 | 4.8441 | 4.7557 | 4.6727 | 4.5929 | 4.5164 | 3.9513 | 3.9204 | 3.8596 | 3.6456 | 3.4345 | 3.2214 | 6.146 | 6.0532 | 4.9341 | 4.8191 | 4.7082 | 3.9411 | 3.8051 | 3.6744 | 3.6063 | 3.5686 | 3.4946 | 3.2474 | 3.0047 | 2.7591
| KYLE | CT |  |  |  | 6.512 | 6.4091 | 5.2766 | 5.1486 | 5.0252 | 4.9062 | 4.792 | 4.6823 | 3.9978 | 3.9716 | 3.9201 | 3.7935 | 3.5821 | 3.3556 | 6.1197 | 6.042 | 4.9414 | 4.8441 | 4.7557 | 4.6727 | 4.5929 | 4.5164 | 3.9513 | 3.9204 | 3.8596 | 3.6456 | 3.4345 | 3.2214 | 6.146 | 6.0532 | 4.9341 | 4.8191 | 4.7082 | 3.9411 | 3.8051 | 3.6744 | 3.6063 | 3.5686 | 3.4946 | 3.2474 | 3.0047 | 2.7591
| KYLE | LW |  |  |  | 6.6597 | 6.6423 | 5.6218 | 5.5987 | 5.5733 | 5.5459 | 5.5167 | 5.4859 | 5.4559 | 5.4251 | 5.3619 | 5.1865 | 5.0062 | 3.9754 | 6.2301 | 6.2164 | 5.1991 | 5.1797 | 5.1586 | 5.136 | 5.1121 | 5.087 | 5.0624 | 5.0372 | 4.9856 | 4.8436 | 3.9732 | 3.6694 | 6.2794 | 6.2639 | 5.2461 | 5.226 | 5.2038 | 5.1798 | 5.1542 | 5.1271 | 5.1009 | 5.0738 | 5.0182 | 4.8701 | 3.7255 | 3.3739
| KYLE | ST |  |  |  | 6.6828 | 6.6767 | 5.6686 | 5.6606 | 5.6527 | 5.6426 | 5.6328 | 5.6232 | 5.6138 | 5.6006 | 5.5752 | 5.5154 | 5.4608 | 5.4069 | 6.2484 | 6.2436 | 5.2369 | 5.2301 | 5.2231 | 5.2129 | 5.203 | 5.1934 | 5.1837 | 5.1712 | 5.1472 | 5.0902 | 5.0368 | 4.9924 | 6.2998 | 6.2945 | 5.2874 | 5.2805 | 5.2737 | 5.2655 | 5.2575 | 5.2498 | 5.2423 | 5.2313 | 5.2102 | 5.1607 | 5.1158 | 5.0717
| KYLE | FS |  |  |  | 6.6772 | 6.6693 | 5.6614 | 5.6496 | 5.6379 | 5.6263 | 5.6147 | 5.6032 | 5.5919 | 5.5808 | 5.559 | 5.4946 | 5.4359 | 5.3811 | 6.2451 | 6.239 | 5.233 | 5.2238 | 5.2148 | 5.2052 | 5.1957 | 5.186 | 5.1765 | 5.1671 | 5.1488 | 5.0959 | 5.0475 | 5.0021 | 6.2945 | 6.2874 | 5.2803 | 5.2697 | 5.2594 | 5.2491 | 5.239 | 5.229 | 5.2192 | 5.2095 | 5.1905 | 5.1341 | 5.0828 | 5.0348
LAIRG | LAIRG GRID | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 3.1353 | 3.0347 | 2.4921 | 2.3362 | 2.1856 | 2.0403 | 1.9002 | 1.7654 | 1.6922 | 1.6486 | 1.5627 | 1.3541 | 1.1525 | 0.94789 | 2.9125 | 2.472 | 2.338 | 2.2058 | 2.0779 | 1.9544 | 1.8352 | 1.7203 | 1.6541 | 1.6117 | 1.5279 | 1.3252 | 1.1272 | 0.92754 | 2.9254 | 2.4916 | 2.3284 | 2.1682 | 2.0133 | 1.8637 | 1.7194 | 1.5805 | 1.5027 | 1.4546 | 1.3596 | 1.1293 | 0.90564 | 0.6794
| LAIRG GRID | CT |  |  |  | 3.1353 | 3.0347 | 2.4921 | 2.3362 | 2.1856 | 2.0403 | 1.9002 | 1.7654 | 1.6922 | 1.6486 | 1.5627 | 1.3541 | 1.1525 | 0.94789 | 2.9125 | 2.472 | 2.338 | 2.2058 | 2.0779 | 1.9544 | 1.8352 | 1.7203 | 1.6541 | 1.6117 | 1.5279 | 1.3252 | 1.1272 | 0.92754 | 2.9254 | 2.4916 | 2.3284 | 2.1682 | 2.0133 | 1.8637 | 1.7194 | 1.5805 | 1.5027 | 1.4546 | 1.3596 | 1.1293 | 0.90564 | 0.6794
| LAIRG GRID | LW |  |  |  | 3.2799 | 3.2632 | 3.2438 | 3.222 | 3.198 | 3.172 | 3.1442 | 3.1148 | 3.0866 | 3.0576 | 2.998 | 2.2962 | 2.0275 | 1.7444 | 3.0205 | 3.0076 | 2.9916 | 2.9734 | 2.9535 | 2.9322 | 2.9095 | 2.8858 | 2.4756 | 2.4421 | 2.3726 | 2.1179 | 1.8581 | 1.5877 | 3.0566 | 3.0413 | 3.0234 | 3.0031 | 2.9809 | 2.9568 | 2.9311 | 2.904 | 2.878 | 2.4672 | 2.3843 | 2.0941 | 1.7985 | 1.489
| LAIRG GRID | ST |  |  |  | 3.3021 | 3.2963 | 3.2886 | 3.2811 | 3.2738 | 3.2649 | 3.2563 | 3.2479 | 3.2397 | 3.2278 | 3.205 | 3.1518 | 3.1038 | 3.0571 | 3.0371 | 3.0326 | 3.0265 | 3.0202 | 3.014 | 3.0047 | 2.9956 | 2.9868 | 2.978 | 2.9664 | 2.9441 | 2.4584 | 2.3663 | 2.2755 | 3.0767 | 3.0714 | 3.0644 | 3.0574 | 3.0506 | 3.0418 | 3.0334 | 3.0251 | 3.0171 | 3.0056 | 2.9836 | 2.9322 | 2.4108 | 2.3107
| LAIRG GRID | FS |  |  |  | 3.2963 | 3.2886 | 3.2809 | 3.2695 | 3.2582 | 3.2471 | 3.2361 | 3.2253 | 3.2147 | 3.2042 | 3.1836 | 3.1224 | 3.0671 | 3.0155 | 3.0329 | 3.0272 | 3.0214 | 3.0128 | 3.0042 | 2.9951 | 2.9861 | 2.9769 | 2.9679 | 2.9591 | 2.9417 | 2.8913 | 2.4482 | 2.3853 | 3.0715 | 3.0645 | 3.0575 | 3.0472 | 3.0369 | 3.0266 | 3.0165 | 3.0064 | 2.9965 | 2.9867 | 2.9676 | 2.9109 | 2.4759 | 2.401
MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 4.2964 | 4.1495 | 2.9158 | 2.7429 | 2.5762 | 2.4157 | 2.2613 | 2.1132 | 2.0348 | 1.9958 | 1.9193 | 1.5403 | 0.93596 | 0.5743 | 3.8017 | 3.7329 | 2.8329 | 2.6408 | 2.4547 | 2.2747 | 2.1008 | 1.9328 | 1.8228 | 1.7475 | 1.5989 | 1.1949 | 0.66199 | 0.32089 | 4.0701 | 3.9384 | 2.9536 | 2.7184 | 2.4907 | 2.2708 | 2.0585 | 1.8538 | 1.7256 | 1.6425 | 1.4788 | 1.0115 | 0.37776 | -0.0071831
| LATHERON | CT |  |  |  | 4.2964 | 4.1495 | 2.9158 | 2.7429 | 2.5762 | 2.4157 | 2.2613 | 2.1132 | 2.0348 | 1.9958 | 1.9193 | 1.5403 | 0.93596 | 0.5743 | 3.8017 | 3.7329 | 2.8329 | 2.6408 | 2.4547 | 2.2747 | 2.1008 | 1.9328 | 1.8228 | 1.7475 | 1.5989 | 1.1949 | 0.66199 | 0.32089 | 4.0701 | 3.9384 | 2.9536 | 2.7184 | 2.4907 | 2.2708 | 2.0585 | 1.8538 | 1.7256 | 1.6425 | 1.4788 | 1.0115 | 0.37776 | -0.0071831
| LATHERON | LW |  |  |  | 4.5053 | 4.4797 | 4.4478 | 4.4115 | 4.372 | 4.3297 | 4.285 | 4.238 | 4.1886 | 4.1379 | 4.0341 | 2.704 | 2.0555 | 1.5499 | 3.926 | 3.9111 | 3.8931 | 3.8726 | 3.8503 | 3.8262 | 2.9977 | 2.9306 | 2.8592 | 2.7868 | 2.6408 | 2.1587 | 1.5297 | 1.0686 | 4.2648 | 4.2415 | 4.2147 | 4.1844 | 4.1511 | 4.115 | 4.0764 | 4.0357 | 3.9929 | 2.974 | 2.8088 | 2.2539 | 1.5092 | 0.98174
| LATHERON | ST |  |  |  | 4.5376 | 4.5288 | 4.5166 | 4.5041 | 4.4915 | 4.4763 | 4.4614 | 4.447 | 4.4324 | 4.4124 | 4.3739 | 4.2335 | 4.0247 | 2.9377 | 3.9452 | 3.9401 | 3.9331 | 3.926 | 3.919 | 3.9105 | 3.9022 | 3.8942 | 3.8861 | 3.8748 | 3.853 | 2.8993 | 2.6537 | 2.5038 | 4.2955 | 4.2875 | 4.2768 | 4.2664 | 4.2562 | 4.2439 | 4.2319 | 4.2203 | 4.2087 | 4.1918 | 4.1594 | 4.0357 | 2.817 | 2.652
| LATHERON | FS |  |  |  | 4.5295 | 4.5183 | 4.5072 | 4.4902 | 4.4734 | 4.4565 | 4.4398 | 4.4231 | 4.4067 | 4.3905 | 4.3588 | 4.2657 | 4.1771 | 4.0931 | 3.9403 | 3.9337 | 3.927 | 3.917 | 3.9071 | 3.8973 | 3.8876 | 3.8779 | 3.8684 | 3.859 | 3.8406 | 3.7863 | 2.9538 | 2.8572 | 4.2875 | 4.2768 | 4.2661 | 4.2503 | 4.2346 | 4.2192 | 4.204 | 4.189 | 4.1742 | 4.1596 | 4.1311 | 4.0462 | 3.9654 | 3.8888
FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 4.8821 | 3.953 | 3.4927 | 8.3074 | 8.2908 | 8.2427 | 8.183 | 8.1234 | 8.0641 | 8.0049 | 7.9467 | 7.8839 | 7.8256 | 4.8977 | 3.496 | 2.5934 | 2.0374 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 4.9341 | 4.8249 | 4.7134 | 4.4686 | 2.7752 | 1.7654 | 1.2251
| LAURENCEKIRK | CT |  |  |  | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 7.7799 | 4.4714 | 4.1342 | 8.3074 | 8.293 | 8.2556 | 8.2122 | 8.1689 | 8.1256 | 8.0823 | 8.0396 | 7.9936 | 7.9486 | 7.8579 | 3.9708 | 3.2196 | 2.8122 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 4.9373 | 4.7797 | 3.2366 | 2.374 | 1.9781
| LAURENCEKIRK | LW |  |  |  | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 4.8821 | 3.953 | 3.4927 | 8.3076 | 8.2908 | 8.2427 | 8.183 | 8.1234 | 8.0641 | 8.0049 | 7.9467 | 7.8839 | 7.8256 | 4.8977 | 3.496 | 2.5934 | 2.0374 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 4.9341 | 4.8249 | 4.7134 | 4.4686 | 2.7752 | 1.7654 | 1.2251
| LAURENCEKIRK | ST |  |  |  | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.3025 | 8.0934 | 8.0934 | 8.3613 | 8.3047 | 8.2876 | 8.2609 | 8.2286 | 8.203 | 8.1774 | 8.1523 | 8.1251 | 8.0988 | 8.0463 | 4.9277 | 4.5069 | 4.2582 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 4.308 | 3.857 | 3.6153
| LAURENCEKIRK | FS |  |  |  | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.825 | 8.3647 | 8.3635 | 8.362 | 8.3541 | 8.3446 | 8.3363 | 8.3279 | 8.3173 | 8.3069 | 8.2968 | 8.2767 | 8.2286 | 8.183 | 8.14 | 6.4843 | 6.484 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839 | 6.4839
STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0.89156 | 0.7947 | 0.67038 | -0.036026 | -0.14863 | -0.28872 | -0.43087 | -0.56784 | -0.64476 | -0.69527 | -0.79492 | -1.0677 | -1.3734 | -1.6324 | 0.8132 | 0.7443 | 0.66911 | -0.048823 | -0.18394 | -0.31466 | -0.44103 | -0.56305 | -0.63857 | -0.69307 | -0.80071 | -1.0875 | -1.4009 | -1.6756 | 0.59607 | 0.5044 | 0.38552 | -0.14065 | -0.30075 | -0.45552 | -0.60498 | -0.74912 | -0.8339 | -0.89226 | -1.0074 | -1.311 | -1.6475 | -1.9362
| LAXAY | CT |  |  |  | 0.89156 | 0.7947 | 0.67038 | -0.036026 | -0.14863 | -0.28872 | -0.43087 | -0.56784 | -0.64476 | -0.69527 | -0.79492 | -1.0677 | -1.3734 | -1.6324 | 0.8132 | 0.7443 | 0.66911 | -0.048823 | -0.18394 | -0.31466 | -0.44103 | -0.56305 | -0.63857 | -0.69307 | -0.80071 | -1.0875 | -1.4009 | -1.6756 | 0.59607 | 0.5044 | 0.38552 | -0.14065 | -0.30075 | -0.45552 | -0.60498 | -0.74912 | -0.8339 | -0.89226 | -1.0074 | -1.311 | -1.6475 | -1.9362
| LAXAY | LW |  |  |  | 1.0308 | 1.0147 | 0.99605 | 0.97506 | 0.95193 | 0.92688 | 0.90012 | 0.87186 | 0.84612 | 0.81962 | 0.76513 | -0.24745 | -0.63739 | -0.98 | 0.91745 | 0.9033 | 0.88322 | 0.85998 | 0.83941 | 0.82426 | 0.80807 | 0.79098 | 0.77541 | 0.75938 | -0.067452 | -0.4285 | -0.82246 | -1.1787 | 0.73749 | 0.71897 | 0.69536 | 0.66959 | 0.64563 | 0.6199 | 0.59262 | 0.56397 | 0.53751 | 0.51034 | -0.09492 | -0.47942 | -0.90658 | -1.2854
| LAXAY | ST |  |  |  | 1.0521 | 1.0466 | 1.0392 | 1.0319 | 1.0249 | 1.0163 | 1.008 | 0.99994 | 0.9923 | 0.98115 | 0.95975 | 0.91089 | 0.84797 | 0.80885 | 0.9343 | 0.93001 | 0.92413 | 0.91819 | 0.9123 | 0.90072 | 0.88942 | 0.87842 | 0.86735 | 0.85709 | 0.84415 | 0.81459 | -0.040244 | -0.16903 | 0.76086 | 0.75482 | 0.74668 | 0.73863 | 0.73072 | 0.71846 | 0.70652 | 0.69491 | 0.68407 | 0.67199 | 0.64878 | 0.59531 | -0.041295 | -0.1741
| LAXAY | FS |  |  |  | 1.0466 | 1.0392 | 1.0317 | 1.0208 | 1.0099 | 0.99921 | 0.98866 | 0.97825 | 0.96799 | 0.95788 | 0.93808 | 0.87917 | 0.82685 | 0.77827 | 0.93018 | 0.92456 | 0.91891 | 0.90993 | 0.90091 | 0.89123 | 0.88169 | 0.87176 | 0.86198 | 0.85236 | 0.83354 | 0.7954 | 0.76375 | 0.73436 | 0.75492 | 0.74694 | 0.73894 | 0.72672 | 0.71457 | 0.70212 | 0.68984 | 0.67742 | 0.6652 | 0.65508 | 0.63528 | 0.57712 | 0.52532 | 0.47721
COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | -0.44056 | -0.68786 | -1.0053 | -1.3108 | -1.6053 | -1.8889 | -2.1616 | -2.4234 | -2.5264 | -2.6171 | -2.8514 | -4.6484 | -5.8254 | -6.262 | -0.29013 | -0.42424 | -0.60035 | -0.91046 | -1.2554 | -1.5888 | -1.9108 | -2.2214 | -2.3895 | -2.5088 | -2.7444 | -4.2902 | -5.3351 | -5.78 | -0.74959 | -1.0477 | -1.4528 | -1.8573 | -2.2706 | -2.67 | -3.0556 | -3.4273 | -3.6227 | -3.7583 | -4.0259 | -5.8831 | -7.1237 | -7.6265
| LEOCH | CT |  |  |  | -0.44056 | -0.68786 | -1.0053 | -1.3108 | -1.6053 | -1.8889 | -2.1616 | -2.4234 | -2.5264 | -2.6171 | -2.8514 | -4.6484 | -5.8254 | -6.262 | -0.29013 | -0.42424 | -0.60035 | -0.91046 | -1.2554 | -1.5888 | -1.9108 | -2.2214 | -2.3895 | -2.5088 | -2.7444 | -4.2902 | -5.3351 | -5.78 | -0.74959 | -1.0477 | -1.4528 | -1.8573 | -2.2706 | -2.67 | -3.0556 | -3.4273 | -3.6227 | -3.7583 | -4.0259 | -5.8831 | -7.1237 | -7.6265
| LEOCH | LW |  |  |  | -0.08501 | -0.1262 | -0.17378 | -0.22736 | -0.28641 | -0.35037 | -0.4187 | -0.49085 | -0.5472 | -0.70758 | -1.0556 | -3.0331 | -4.3923 | -5.02 | -0.097306 | -0.11964 | -0.14545 | -0.17451 | -0.20653 | -0.37386 | -0.55775 | -0.743 | -0.92324 | -1.1043 | -1.4672 | -3.197 | -4.4272 | -5.064 | -0.34811 | -0.42043 | -0.54798 | -0.73478 | -0.93635 | -1.1411 | -1.3485 | -1.558 | -1.7597 | -1.9626 | -2.3697 | -4.4348 | -5.8849 | -6.6059
| LEOCH | ST |  |  |  | -0.030533 | -0.044745 | -0.063695 | -0.082155 | -0.10012 | -0.12197 | -0.1432 | -0.16382 | -0.18384 | -0.21307 | -0.26913 | -0.93364 | -1.3526 | -1.5839 | -0.067762 | -0.07547 | -0.085747 | -0.095758 | -0.1055 | -0.11735 | -0.12887 | -0.14005 | -0.15091 | -0.16676 | -0.19716 | -0.98575 | -1.5458 | -1.7899 | -0.27895 | -0.30495 | -0.34955 | -0.40641 | -0.46972 | -0.52523 | -0.58819 | -0.64959 | -0.71328 | -0.78685 | -0.92919 | -1.8832 | -2.5447 | -2.8174
| LEOCH | FS |  |  |  | -0.044745 | -0.063695 | -0.082646 | -0.1107 | -0.13838 | -0.1657 | -0.19264 | -0.21921 | -0.24541 | -0.27123 | -0.32178 | -0.47219 | -0.58854 | -0.69195 | -0.07547 | -0.085747 | -0.096024 | -0.11124 | -0.12625 | -0.14106 | -0.15567 | -0.17008 | -0.18429 | -0.1983 | -0.22571 | -0.30728 | -0.37038 | -0.48581 | -0.29056 | -0.31345 | -0.33672 | -0.37894 | -0.42265 | -0.46215 | -0.50114 | -0.54205 | -0.58236 | -0.62205 | -0.69958 | -0.92664 | -1.128 | -1.3111
NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 2.9962 | 2.9145 | 2.8093 | 2.7097 | 1.8881 | 0.95517 | 0.84584 | 0.74072 | 0.68902 | 0.65928 | 0.60077 | 0.38444 | 0.21486 | 0.04399 | 2.576 | 2.5241 | 2.455 | 2.3887 | 1.9671 | 1.2158 | 1.1244 | 1.0365 | 0.9915 | 0.96433 | 0.91083 | 0.7049 | 0.53619 | 0.36863 | 2.8015 | 2.72 | 2.6143 | 2.5139 | 1.9088 | 0.96139 | 0.84979 | 0.74248 | 0.68932 | 0.65846 | 0.59773 | 0.37144 | 0.19246 | 0.014404
| LETHEN | CT |  |  |  | 2.9962 | 2.9145 | 2.8093 | 2.7097 | 1.8881 | 0.95517 | 0.84584 | 0.74072 | 0.68902 | 0.65928 | 0.60077 | 0.38444 | 0.21486 | 0.04399 | 2.576 | 2.5241 | 2.455 | 2.3887 | 1.9671 | 1.2158 | 1.1244 | 1.0365 | 0.9915 | 0.96433 | 0.91083 | 0.7049 | 0.53619 | 0.36863 | 2.8015 | 2.72 | 2.6143 | 2.5139 | 1.9088 | 0.96139 | 0.84979 | 0.74248 | 0.68932 | 0.65846 | 0.59773 | 0.37144 | 0.19246 | 0.014404
| LETHEN | LW |  |  |  | 3.1132 | 3.0993 | 3.0827 | 3.0639 | 3.0433 | 1.5182 | 1.4809 | 1.4425 | 1.4062 | 1.3692 | 1.2942 | 1.0038 | 0.75333 | 0.49527 | 2.6479 | 2.6372 | 2.6208 | 2.6017 | 2.5817 | 1.6656 | 1.6311 | 1.5957 | 1.5617 | 1.5272 | 1.4574 | 1.1764 | 0.92273 | 0.66964 | 2.9176 | 2.9032 | 2.8848 | 2.8638 | 2.8411 | 1.5315 | 1.4928 | 1.4528 | 1.415 | 1.3765 | 1.2983 | 0.99358 | 0.72724 | 0.44618
| LETHEN | ST |  |  |  | 3.134 | 3.1264 | 3.1199 | 3.1134 | 3.107 | 3.0987 | 3.0906 | 3.0828 | 3.0751 | 3.0646 | 3.0442 | 2.9861 | 2.95 | 2.9178 | 2.684 | 2.6559 | 2.65 | 2.6432 | 2.6359 | 2.6235 | 2.6115 | 2.5998 | 2.5876 | 2.5738 | 2.547 | 2.4879 | 2.4681 | 1.9556 | 2.9439 | 2.9307 | 2.9236 | 2.9163 | 2.9089 | 2.8984 | 2.8883 | 2.8783 | 2.8685 | 2.8557 | 2.8312 | 2.7607 | 2.7098 | 2.6627
| LETHEN | FS |  |  |  | 3.1293 | 3.1231 | 3.1168 | 3.1075 | 3.0982 | 3.0889 | 3.0797 | 3.0705 | 3.0614 | 3.0525 | 3.035 | 2.9835 | 2.9388 | 2.8976 | 2.6809 | 2.6755 | 2.6701 | 2.6622 | 2.6556 | 2.6476 | 2.6397 | 2.6311 | 2.6227 | 2.6144 | 2.5983 | 2.5538 | 2.5143 | 2.4776 | 2.9394 | 2.9332 | 2.9269 | 2.9174 | 2.9079 | 2.898 | 2.8881 | 2.8781 | 2.8683 | 2.8586 | 2.8395 | 2.7846 | 2.7365 | 2.6921
GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | YES | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0027585 | 0.0027489 | 0.0027213 | 0.0026874 | 0.0026543 | 0.0026219 | 0.0025902 | 0.0025654 | 0.00254 | 0.0025149 | 0.0024843 | 0.0024593 | 0.0024593 | 0.0024593 | 0.0031106 | 0.0031059 | 0.0030925 | 0.003076 | 0.0030599 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582
| LETTEREWE | CT |  |  |  | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0027586 | 0.0027505 | 0.0027298 | 0.0027061 | 0.0026829 | 0.0026602 | 0.0026381 | 0.0026164 | 0.002593 | 0.0025732 | 0.0025384 | 0.0024817 | 0.0024613 | 0.0024593 | 0.0031106 | 0.0031067 | 0.0030966 | 0.0030851 | 0.0030738 | 0.0030628 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582
| LETTEREWE | LW |  |  |  | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0027585 | 0.0027489 | 0.0027213 | 0.0026874 | 0.0026543 | 0.0026219 | 0.0025902 | 0.0025654 | 0.00254 | 0.0025149 | 0.0024843 | 0.0024593 | 0.0024593 | 0.0024593 | 0.0031106 | 0.0031059 | 0.0030925 | 0.003076 | 0.0030599 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582
| LETTEREWE | ST |  |  |  | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0027614 | 0.0027578 | 0.0027494 | 0.0027365 | 0.002721 | 0.0027059 | 0.0026912 | 0.0026769 | 0.0026614 | 0.0026462 | 0.0026166 | 0.002555 | 0.0025026 | 0.0024807 | 0.0031119 | 0.0031102 | 0.0031062 | 0.0030999 | 0.0030923 | 0.003085 | 0.0030779 | 0.0030709 | 0.0030634 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582 | 0.0030582
| LETTEREWE | FS |  |  |  | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.0045827 | 0.002763 | 0.0027626 | 0.002762 | 0.0027583 | 0.002754 | 0.002749 | 0.002744 | 0.0027376 | 0.0027313 | 0.0027251 | 0.0027132 | 0.0026848 | 0.0026587 | 0.0026347 | 0.0031128 | 0.0031125 | 0.0031122 | 0.0031105 | 0.0031084 | 0.0031059 | 0.0031035 | 0.0031004 | 0.0030974 | 0.0030944 | 0.0030885 | 0.0030748 | 0.0030621 | 0.0030582
ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9534 | 4.7799 | 4.6006 | 4.425 | 5.7532 | 5.7385 | 5.7099 | 5.6846 | 5.6601 | 4.9612 | 4.9224 | 4.8843 | 4.8428 | 4.8014 | 4.7201 | 4.4975 | 4.2674 | 4.0422 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.982 | 4.9454 | 4.9094 | 4.8741 | 4.8356 | 4.7973 | 4.7219 | 4.5155 | 4.3022 | 4.0934
| LHANBRYDE | CT |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9217 | 4.7965 | 4.6738 | 5.7536 | 5.7413 | 5.719 | 5.7019 | 5.6848 | 5.6671 | 4.9814 | 4.9515 | 4.9212 | 4.8918 | 4.8351 | 4.6794 | 4.5188 | 4.3614 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9927 | 4.9641 | 4.9364 | 4.9083 | 4.8811 | 4.8285 | 4.6842 | 4.5353 | 4.3893
| LHANBRYDE | LW |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9534 | 4.7799 | 4.6006 | 4.425 | 5.7532 | 5.7385 | 5.7099 | 5.6846 | 5.6601 | 4.9612 | 4.9224 | 4.8843 | 4.8428 | 4.8014 | 4.7201 | 4.4975 | 4.2674 | 4.0422 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.982 | 4.9454 | 4.9094 | 4.8741 | 4.8356 | 4.7973 | 4.7219 | 4.5155 | 4.3022 | 4.0934
| LHANBRYDE | ST |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9656 | 4.8855 | 5.7576 | 5.7505 | 5.7398 | 5.7307 | 5.7197 | 5.7061 | 5.6918 | 5.678 | 5.6639 | 4.9847 | 4.9423 | 4.8396 | 4.7357 | 4.633 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9879 | 4.9672 | 4.9279 | 4.8327 | 4.7363 | 4.6411
| LHANBRYDE | FS |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7607 | 5.7574 | 5.754 | 5.751 | 5.7475 | 5.7431 | 5.7388 | 5.7335 | 5.7283 | 5.7231 | 5.7132 | 5.691 | 5.6705 | 4.9849 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9979 | 4.9674
FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.43697 | 0.43573 | 0.43253 | 0.42886 | 0.42525 | 0.42171 | 0.41822 | 0.4148 | 0.4111 | 0.40742 | 0.40012 | 0.39595 | 0.39552 | 0.39508 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652
| LIDDESDALE | CT |  |  |  | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.43697 | 0.43573 | 0.43253 | 0.42886 | 0.42525 | 0.42171 | 0.41822 | 0.4148 | 0.4111 | 0.40742 | 0.40012 | 0.39595 | 0.39552 | 0.39508 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652
| LIDDESDALE | LW |  |  |  | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.43768 | 0.43763 | 0.4375 | 0.43733 | 0.43717 | 0.43701 | 0.43685 | 0.4367 | 0.43653 | 0.43637 | 0.43604 | 0.4292 | 0.42228 | 0.41549 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652
| LIDDESDALE | ST |  |  |  | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.4377 | 0.43768 | 0.43764 | 0.43757 | 0.4375 | 0.43688 | 0.43629 | 0.4357 | 0.43507 | 0.43445 | 0.43323 | 0.4303 | 0.42739 | 0.42449 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652
| LIDDESDALE | FS |  |  |  | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.59487 | 0.4377 | 0.4377 | 0.4377 | 0.43768 | 0.43766 | 0.43746 | 0.43726 | 0.437 | 0.43675 | 0.43651 | 0.43602 | 0.43489 | 0.43384 | 0.43283 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 0.44652
KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 2.0987 | 2.0278 | 1.9282 | 1.8306 | 1.7361 | 1.6448 | 1.5565 | 1.4713 | 1.4131 | 1.3743 | 1.2976 | 0.86018 | -0.021668 | -0.20946 | 2.1075 | 2.046 | 1.9564 | 1.8675 | 1.7814 | 1.6979 | 1.6172 | 1.5392 | 1.483 | 1.443 | 1.364 | 0.96699 | 0.19964 | 0.01065 | 2.1885 | 2.1207 | 2.0208 | 1.9175 | 1.8173 | 1.7204 | 1.6266 | 1.536 | 1.4713 | 1.4259 | 1.3361 | 0.87422 | -0.054751 | -0.27996
| LIMEHILLOCKS | CT |  |  |  | 2.0987 | 2.0278 | 1.9282 | 1.8306 | 1.7361 | 1.6448 | 1.5565 | 1.4713 | 1.4131 | 1.3743 | 1.2976 | 0.86018 | -0.021668 | -0.20946 | 2.1075 | 2.046 | 1.9564 | 1.8675 | 1.7814 | 1.6979 | 1.6172 | 1.5392 | 1.483 | 1.443 | 1.364 | 0.96699 | 0.19964 | 0.01065 | 2.1885 | 2.1207 | 2.0208 | 1.9175 | 1.8173 | 1.7204 | 1.6266 | 1.536 | 1.4713 | 1.4259 | 1.3361 | 0.87422 | -0.054751 | -0.27996
| LIMEHILLOCKS | LW |  |  |  | 2.1929 | 2.1781 | 2.1538 | 2.1253 | 2.0956 | 2.0648 | 2.0331 | 2.0007 | 1.9647 | 1.9281 | 1.8539 | 1.366 | 0.41997 | 0.16153 | 2.1867 | 2.1727 | 2.1479 | 2.1185 | 2.0882 | 2.0571 | 2.0254 | 1.9931 | 1.9574 | 1.9213 | 1.8482 | 1.4012 | 0.57225 | 0.31637 | 2.2814 | 2.2682 | 2.2468 | 2.2133 | 2.1789 | 2.1434 | 2.1072 | 2.0703 | 2.0294 | 1.9881 | 1.9044 | 1.3852 | 0.40786 | 0.10186
| LIMEHILLOCKS | ST |  |  |  | 2.2084 | 2.2033 | 2.1952 | 2.1854 | 2.1748 | 2.1596 | 2.1447 | 2.1302 | 2.1152 | 2.0981 | 2.0648 | 1.849 | 1.4183 | 1.3332 | 2.2001 | 2.1953 | 2.1873 | 2.1773 | 2.1661 | 2.1497 | 2.1337 | 2.1181 | 2.1019 | 2.0838 | 2.0488 | 1.8513 | 1.4752 | 1.3869 | 2.2963 | 2.2918 | 2.2849 | 2.2771 | 2.2681 | 2.2497 | 2.2316 | 2.214 | 2.1957 | 2.1753 | 2.1356 | 1.9063 | 1.4652 | 1.365
| LIMEHILLOCKS | FS |  |  |  | 2.2053 | 2.2002 | 2.195 | 2.1863 | 2.1774 | 2.167 | 2.1568 | 2.1458 | 2.135 | 2.1243 | 2.1035 | 2.046 | 1.988 | 1.9321 | 2.1978 | 2.1934 | 2.189 | 2.1812 | 2.1731 | 2.1632 | 2.1535 | 2.1427 | 2.1321 | 2.1217 | 2.1014 | 2.0465 | 1.9915 | 1.9388 | 2.293 | 2.288 | 2.283 | 2.2748 | 2.2666 | 2.2576 | 2.2486 | 2.2393 | 2.2281 | 2.2162 | 2.1928 | 2.1296 | 2.0661 | 2.0052
ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.4807 | 22.4805 | 22.48 | 22.4793 | 22.4786 | 22.478 | 22.4773 | 22.4767 | 22.4761 | 22.4751 | 22.4732 | 22.4648 | 22.4614 | 22.4609 | 22.5036 | 22.5035 | 22.5033 | 22.5029 | 22.5026 | 22.5023 | 22.502 | 22.5017 | 22.5014 | 22.5009 | 22.5001 | 22.5001 | 22.5001 | 22.5001
| LOCH CARNAN | CT |  |  |  | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.4807 | 22.4806 | 22.4801 | 22.4797 | 22.4792 | 22.4787 | 22.4783 | 22.4779 | 22.4774 | 22.4769 | 22.476 | 22.468 | 22.4626 | 22.4611 | 22.5036 | 22.5036 | 22.5034 | 22.5031 | 22.5029 | 22.5027 | 22.5025 | 22.5023 | 22.502 | 22.5018 | 22.5014 | 22.5001 | 22.5001 | 22.5001
| LOCH CARNAN | LW |  |  |  | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.4807 | 22.4805 | 22.48 | 22.4793 | 22.4786 | 22.478 | 22.4773 | 22.4767 | 22.4761 | 22.4754 | 22.4741 | 22.4648 | 22.4614 | 22.4609 | 22.5036 | 22.5035 | 22.5033 | 22.5029 | 22.5026 | 22.5023 | 22.502 | 22.5017 | 22.5014 | 22.5011 | 22.5004 | 22.5001 | 22.5001 | 22.5001
| LOCH CARNAN | ST |  |  |  | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.4808 | 22.4807 | 22.4805 | 22.4803 | 22.48 | 22.479 | 22.478 | 22.4771 | 22.4761 | 22.4751 | 22.4732 | 22.4688 | 22.4653 | 22.4627 | 22.5037 | 22.5036 | 22.5036 | 22.5034 | 22.5033 | 22.5028 | 22.5023 | 22.5019 | 22.5014 | 22.5009 | 22.5001 | 22.5001 | 22.5001 | 22.5001
| LOCH CARNAN | FS |  |  |  | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.6295 | 22.4808 | 22.4808 | 22.4808 | 22.4807 | 22.4806 | 22.4803 | 22.48 | 22.4796 | 22.4792 | 22.4788 | 22.478 | 22.4762 | 22.4746 | 22.473 | 22.5037 | 22.5037 | 22.5037 | 22.5036 | 22.5036 | 22.5034 | 22.5033 | 22.5031 | 22.5029 | 22.5027 | 22.5023 | 22.5015 | 22.5007 | 22.5001
GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | YES | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49987 | 0.49959 | 0.50069 | 0.50068 | 0.50065 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49989 | 0.49956 | 0.49924 | 0.49892 | 0.50078 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.4997 | 0.49937 | 0.49905
| LOCH GLASCARNOCH | CT |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50069 | 0.50068 | 0.50066 | 0.50064 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49986 | 0.49963 | 0.49941 | 0.50078 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.49999 | 0.49977 | 0.49954
| LOCH GLASCARNOCH | LW |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49987 | 0.49959 | 0.50069 | 0.50068 | 0.50065 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49989 | 0.49956 | 0.49924 | 0.49892 | 0.50078 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.4997 | 0.49937 | 0.49905
| LOCH GLASCARNOCH | ST |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50069 | 0.50069 | 0.50068 | 0.50066 | 0.50065 | 0.50064 | 0.50063 | 0.50062 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.49999 | 0.49985 | 0.50078 | 0.50078 | 0.50077 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.49998
| LOCH GLASCARNOCH | FS |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50069 | 0.50069 | 0.50069 | 0.50069 | 0.50068 | 0.50068 | 0.50067 | 0.50067 | 0.50066 | 0.50065 | 0.50064 | 0.50062 | 0.50062 | 0.50061 | 0.50078 | 0.50078 | 0.50078 | 0.50078 | 0.50077 | 0.50077 | 0.50077 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076
FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.6315 | 0.63136 | 0.63095 | 0.63044 | 0.62995 | 0.62946 | 0.62899 | 0.62852 | 0.62801 | 0.62751 | 0.62652 | 0.62406 | 0.6215 | 0.61899 | 0.53945 | 0.53939 | 0.53923 | 0.53904 | 0.53885 | 0.53867 | 0.53849 | 0.53831 | 0.53812 | 0.53793 | 0.53755 | 0.53662 | 0.53564 | 0.53469
| LOCHALINE | CT |  |  |  | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.6315 | 0.63138 | 0.63108 | 0.63072 | 0.63038 | 0.63003 | 0.6297 | 0.62937 | 0.62901 | 0.62866 | 0.62796 | 0.62626 | 0.62446 | 0.62268 | 0.53945 | 0.5394 | 0.53928 | 0.53915 | 0.53902 | 0.53889 | 0.53876 | 0.53863 | 0.5385 | 0.53836 | 0.5381 | 0.53745 | 0.53677 | 0.53609
| LOCHALINE | LW |  |  |  | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.6315 | 0.63136 | 0.63095 | 0.63044 | 0.62995 | 0.62946 | 0.62899 | 0.62852 | 0.62801 | 0.62751 | 0.62652 | 0.62406 | 0.6215 | 0.61899 | 0.53945 | 0.53939 | 0.53923 | 0.53904 | 0.53885 | 0.53867 | 0.53849 | 0.53831 | 0.53812 | 0.53793 | 0.53755 | 0.53662 | 0.53564 | 0.53469
| LOCHALINE | ST |  |  |  | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.63155 | 0.63149 | 0.63137 | 0.63117 | 0.63094 | 0.63072 | 0.6305 | 0.63028 | 0.63004 | 0.62981 | 0.62937 | 0.62828 | 0.62716 | 0.62605 | 0.53946 | 0.53944 | 0.53939 | 0.53932 | 0.53923 | 0.53915 | 0.53906 | 0.53898 | 0.53889 | 0.5388 | 0.53863 | 0.53822 | 0.5378 | 0.53737
| LOCHALINE | FS |  |  |  | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.53947 | 0.63157 | 0.63156 | 0.63155 | 0.6315 | 0.63143 | 0.63136 | 0.63128 | 0.63119 | 0.63109 | 0.631 | 0.63082 | 0.6304 | 0.62998 | 0.62959 | 0.53947 | 0.53947 | 0.53946 | 0.53944 | 0.53942 | 0.53939 | 0.53936 | 0.53933 | 0.53929 | 0.53925 | 0.53919 | 0.53902 | 0.53887 | 0.53872
TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.67382 | 0.67346 | 0.67243 | 0.67117 | 0.66994 | 0.66873 | 0.66755 | 0.6664 | 0.66515 | 0.66391 | 0.66146 | 0.65419 | 0.64686 | 0.63963 | 0.49633 | 0.4947 | 0.48999 | 0.48422 | 0.47857 | 0.47305 | 0.46764 | 0.46236 | 0.45664 | 0.45096 | 0.43973 | 0.42302 | 0.41082 | 0.40254 | 0.52606 | 0.52528 | 0.52302 | 0.52026 | 0.51756 | 0.51491 | 0.51233 | 0.5098 | 0.50706 | 0.50434 | 0.49897 | 0.48302 | 0.46938 | 0.46938
| LOCHDONHEAD | CT |  |  |  | 0.67382 | 0.67352 | 0.67275 | 0.67187 | 0.67101 | 0.67016 | 0.66934 | 0.66853 | 0.66766 | 0.66679 | 0.66507 | 0.65797 | 0.65081 | 0.64374 | 0.49633 | 0.49498 | 0.49145 | 0.48741 | 0.48346 | 0.47959 | 0.47581 | 0.47211 | 0.46811 | 0.46414 | 0.45628 | 0.42932 | 0.41739 | 0.40562 | 0.52606 | 0.52541 | 0.52372 | 0.52179 | 0.5199 | 0.51804 | 0.51624 | 0.51447 | 0.51255 | 0.51065 | 0.50689 | 0.49131 | 0.47561 | 0.46938
| LOCHDONHEAD | LW |  |  |  | 0.67382 | 0.67346 | 0.67243 | 0.67117 | 0.66994 | 0.66873 | 0.66755 | 0.6664 | 0.66515 | 0.66391 | 0.66146 | 0.65419 | 0.64686 | 0.63963 | 0.49633 | 0.4947 | 0.48999 | 0.48422 | 0.47857 | 0.47305 | 0.46764 | 0.46236 | 0.45664 | 0.45096 | 0.43973 | 0.42302 | 0.41082 | 0.40254 | 0.52606 | 0.52528 | 0.52302 | 0.52026 | 0.51756 | 0.51491 | 0.51233 | 0.5098 | 0.50706 | 0.50434 | 0.49897 | 0.48302 | 0.46938 | 0.46938
| LOCHDONHEAD | ST |  |  |  | 0.67392 | 0.67379 | 0.67348 | 0.673 | 0.67242 | 0.67174 | 0.67108 | 0.67043 | 0.66973 | 0.66904 | 0.6677 | 0.66448 | 0.66132 | 0.65817 | 0.49681 | 0.49621 | 0.49479 | 0.49258 | 0.48995 | 0.48683 | 0.48379 | 0.48082 | 0.47762 | 0.47446 | 0.46832 | 0.45356 | 0.4391 | 0.42965 | 0.52629 | 0.526 | 0.52532 | 0.52426 | 0.523 | 0.52151 | 0.52005 | 0.51863 | 0.5171 | 0.51559 | 0.51265 | 0.50558 | 0.49867 | 0.49175
| LOCHDONHEAD | FS |  |  |  | 0.67398 | 0.67396 | 0.67394 | 0.67381 | 0.67365 | 0.67342 | 0.6732 | 0.67291 | 0.67263 | 0.67235 | 0.67181 | 0.67054 | 0.66936 | 0.66827 | 0.49709 | 0.49701 | 0.49692 | 0.4963 | 0.49556 | 0.49453 | 0.4935 | 0.49219 | 0.49089 | 0.48962 | 0.48715 | 0.48132 | 0.47591 | 0.47094 | 0.52642 | 0.52638 | 0.52634 | 0.52604 | 0.52569 | 0.52519 | 0.5247 | 0.52407 | 0.52345 | 0.52285 | 0.52166 | 0.51887 | 0.51629 | 0.51391
KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1043 | 2.999 | 2.874 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.6344 | 2.4257 | 2.6569 | 2.6503 | 2.6173 | 2.5757 | 2.5345 | 2.4936 | 2.4531 | 2.4134 | 2.3704 | 2.3272 | 2.2413 | 2.0376 | 1.8316 | 1.6283
| LOCHEARNHEAD | CT |  |  |  | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.113 | 3.0335 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7038 | 2.6569 | 2.6516 | 2.6284 | 2.5997 | 2.5712 | 2.5429 | 2.5148 | 2.4872 | 2.4574 | 2.4274 | 2.3675 | 2.212 | 2.0546 | 1.8991
| LOCHEARNHEAD | LW |  |  |  | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1043 | 2.999 | 2.874 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.6344 | 2.4257 | 2.6569 | 2.6503 | 2.6173 | 2.5757 | 2.5345 | 2.4936 | 2.4531 | 2.4134 | 2.3704 | 2.3272 | 2.2413 | 2.0376 | 1.8316 | 1.6283
| LOCHEARNHEAD | ST |  |  |  | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.6588 | 2.6563 | 2.6505 | 2.6352 | 2.6157 | 2.597 | 2.5786 | 2.5605 | 2.541 | 2.5215 | 2.4832 | 2.3884 | 2.295 | 2.2023
| LOCHEARNHEAD | FS |  |  |  | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 3.1288 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.7285 | 2.6599 | 2.6596 | 2.6591 | 2.6565 | 2.6534 | 2.65 | 2.6446 | 2.637 | 2.6294 | 2.622 | 2.6073 | 2.5716 | 2.5375 | 2.5049
LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | NO | 26.4586 | 26.4504 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 25.759 | 25.753 | 25.7221 | 25.7013 | 25.6814 | 25.6606 | 25.6385 | 25.617 | 25.5921 | 25.5651 | 25.5109 | 25.4568 | 25.436 | 25.4167 | 25.7915 | 25.7862 | 25.7816 | 25.7785 | 25.7756 | 25.7725 | 25.7692 | 25.766 | 25.7623 | 25.7583 | 25.7538 | 25.7538 | 25.7538 | 25.7538
| LOCHEE | CT |  |  |  | 26.4587 | 26.4521 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 25.7591 | 25.7542 | 25.7293 | 25.7153 | 25.7017 | 25.6879 | 25.6737 | 25.6581 | 25.6429 | 25.6234 | 25.5841 | 25.4736 | 25.4585 | 25.4446 | 25.7916 | 25.7864 | 25.7827 | 25.7806 | 25.7786 | 25.7765 | 25.7744 | 25.7721 | 25.7698 | 25.767 | 25.7611 | 25.7538 | 25.7538 | 25.7538
| LOCHEE | LW |  |  |  | 26.4586 | 26.4504 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 25.759 | 25.753 | 25.7221 | 25.7013 | 25.6814 | 25.6606 | 25.6385 | 25.617 | 25.5921 | 25.5651 | 25.5109 | 25.4568 | 25.436 | 25.4167 | 25.7915 | 25.7862 | 25.7816 | 25.7785 | 25.7756 | 25.7725 | 25.7692 | 25.766 | 25.7623 | 25.7583 | 25.7538 | 25.7538 | 25.7538 | 25.7538
| LOCHEE | ST |  |  |  | 26.461 | 26.4578 | 26.4392 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 25.7607 | 25.7584 | 25.7448 | 25.7368 | 25.7274 | 25.715 | 25.7023 | 25.6888 | 25.6753 | 25.6589 | 25.626 | 25.5465 | 25.481 | 25.4672 | 25.7939 | 25.7907 | 25.785 | 25.7838 | 25.7824 | 25.7805 | 25.7787 | 25.7767 | 25.7747 | 25.7722 | 25.7673 | 25.7555 | 25.7538 | 25.7538
| LOCHEE | FS |  |  |  | 26.4624 | 26.4618 | 26.4548 | 26.4514 | 26.4477 | 26.4418 | 26.436 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 26.4292 | 25.7618 | 25.7614 | 25.7562 | 25.7537 | 25.751 | 25.7467 | 25.7424 | 25.7372 | 25.7315 | 25.7254 | 25.7131 | 25.6826 | 25.6578 | 25.6366 | 25.7954 | 25.7948 | 25.7876 | 25.7863 | 25.7859 | 25.7853 | 25.7846 | 25.7838 | 25.783 | 25.7821 | 25.7803 | 25.7757 | 25.7721 | 25.7689
PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.5029 | 12.9647 | 12.4351 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6321 | 13.5294 | 13.4274 | 13.2259 | 12.2942 | 11.6356 | 10.9875 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.635 | 13.5503 | 13.4673 | 13.3773 | 13.2793 | 13.0743 | 12.0717 | 11.4015 | 10.7422
| LOCHGILPHEAD | CT |  |  |  | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.6275 | 13.3665 | 12.9937 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6903 | 13.5973 | 13.5064 | 13.3291 | 12.5907 | 12.1272 | 11.6711 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.5946 | 13.5183 | 13.4368 | 13.3571 | 13.1793 | 12.3733 | 11.9018 | 11.4377
| LOCHGILPHEAD | LW |  |  |  | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.5029 | 12.9647 | 12.4351 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6321 | 13.5294 | 13.4274 | 13.2259 | 12.2942 | 11.6356 | 10.9875 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.635 | 13.5503 | 13.4673 | 13.3773 | 13.2793 | 13.0743 | 12.0717 | 11.4015 | 10.7422
| LOCHGILPHEAD | ST |  |  |  | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.7748 | 13.7748 | 13.7748 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.3169 | 13.0285 | 12.7414 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.5689 | 13.1396 | 12.8461 | 12.554
| LOCHGILPHEAD | FS |  |  |  | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.9222 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6936 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6382 | 13.6045
CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.6339 | 1.6336 | 1.6325 | 1.6312 | 1.6299 | 1.6287 | 1.6275 | 1.6263 | 1.625 | 1.6237 | 1.6212 | 1.6067 | 1.5921 | 1.5785 | 1.9859 | 1.9858 | 1.9856 | 1.9853 | 1.985 | 1.9848 | 1.9845 | 1.9843 | 1.984 | 1.9837 | 1.9832 | 1.9801 | 1.9771 | 1.9771
| LOCHGOILHEAD | CT |  |  |  | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.6339 | 1.6336 | 1.6328 | 1.6319 | 1.631 | 1.6302 | 1.6293 | 1.6285 | 1.6276 | 1.6267 | 1.6249 | 1.6105 | 1.5959 | 1.5816 | 1.9859 | 1.9858 | 1.9857 | 1.9855 | 1.9853 | 1.9851 | 1.9849 | 1.9847 | 1.9845 | 1.9843 | 1.984 | 1.9809 | 1.9777 | 1.9771
| LOCHGOILHEAD | LW |  |  |  | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.6339 | 1.6336 | 1.6325 | 1.6312 | 1.6299 | 1.6287 | 1.6275 | 1.6263 | 1.625 | 1.6237 | 1.6212 | 1.6067 | 1.5921 | 1.5785 | 1.9859 | 1.9858 | 1.9856 | 1.9853 | 1.985 | 1.9848 | 1.9845 | 1.9843 | 1.984 | 1.9837 | 1.9832 | 1.9801 | 1.9771 | 1.9771
| LOCHGOILHEAD | ST |  |  |  | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.634 | 1.6339 | 1.6336 | 1.6331 | 1.6325 | 1.6311 | 1.6298 | 1.6285 | 1.6271 | 1.6258 | 1.6231 | 1.6167 | 1.6103 | 1.604 | 1.9859 | 1.9859 | 1.9858 | 1.9857 | 1.9856 | 1.9853 | 1.985 | 1.9847 | 1.9844 | 1.9841 | 1.9836 | 1.9822 | 1.9808 | 1.9795
| LOCHGOILHEAD | FS |  |  |  | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.1264 | 1.6341 | 1.6341 | 1.6341 | 1.6339 | 1.6337 | 1.6333 | 1.6329 | 1.6323 | 1.6318 | 1.6312 | 1.6302 | 1.6277 | 1.6253 | 1.6232 | 1.9859 | 1.9859 | 1.9859 | 1.9859 | 1.9858 | 1.9858 | 1.9857 | 1.9855 | 1.9854 | 1.9853 | 1.9851 | 1.9845 | 1.9841 | 1.9836
GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | YES | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.85077 | 0.84852 | 0.84271 | 0.83606 | 0.82953 | 0.82313 | 0.81683 | 0.81064 | 0.80395 | 0.79731 | 0.78417 | 0.77378 | 0.77378 | 0.77378 | 0.9189 | 0.91594 | 0.90829 | 0.89954 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132
| LOCHINVER | CT |  |  |  | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.85077 | 0.84852 | 0.84271 | 0.83606 | 0.82953 | 0.82313 | 0.81683 | 0.81064 | 0.80395 | 0.79731 | 0.78417 | 0.77378 | 0.77378 | 0.77378 | 0.9189 | 0.91594 | 0.90829 | 0.89954 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132 | 0.89132
| LOCHINVER | LW |  |  |  | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.85172 | 0.85093 | 0.8487 | 0.84598 | 0.84331 | 0.84071 | 0.83815 | 0.83564 | 0.83294 | 0.83026 | 0.82497 | 0.78791 | 0.77378 | 0.77378 | 0.92015 | 0.91911 | 0.91617 | 0.91259 | 0.90908 | 0.90566 | 0.90229 | 0.89898 | 0.89542 | 0.8919 | 0.89132 | 0.89132 | 0.89132 | 0.89132
| LOCHINVER | ST |  |  |  | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.85196 | 0.85166 | 0.85097 | 0.84993 | 0.84868 | 0.84569 | 0.84277 | 0.83991 | 0.83683 | 0.8338 | 0.82791 | 0.81363 | 0.79926 | 0.78497 | 0.92046 | 0.92007 | 0.91917 | 0.91779 | 0.91614 | 0.91222 | 0.90837 | 0.90461 | 0.90055 | 0.89657 | 0.89132 | 0.89132 | 0.89132 | 0.89132
| LOCHINVER | FS |  |  |  | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.78358 | 0.8521 | 0.85205 | 0.85199 | 0.85169 | 0.85134 | 0.85023 | 0.84913 | 0.84772 | 0.84633 | 0.84498 | 0.84234 | 0.83612 | 0.83021 | 0.82462 | 0.92064 | 0.92058 | 0.92051 | 0.92011 | 0.91965 | 0.91819 | 0.91674 | 0.91488 | 0.91305 | 0.91127 | 0.90781 | 0.89962 | 0.89184 | 0.89132
LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | NO | 36.0963 | 36.0906 | 36.0801 | 36.0669 | 36.0534 | 36.0395 | 36.0251 | 36.0143 | 36.0024 | 35.9902 | 35.9673 | 35.8548 | 35.8407 | 35.8407 | 30.4244 | 30.3683 | 30.2642 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1235 | 30.1235 | 30.1235 | 32.5836 | 32.5669 | 32.5359 | 32.4973 | 32.4576 | 32.4165 | 32.3743 | 32.3426 | 32.3074 | 32.2717 | 32.2043 | 32.0499 | 32.0499 | 32.0499
| LOCHSIDE | CT |  |  |  | 36.0963 | 36.0906 | 36.0801 | 36.0669 | 36.0534 | 36.0395 | 36.0251 | 36.0143 | 36.0024 | 35.9902 | 35.9673 | 35.8548 | 35.8407 | 35.8407 | 30.4244 | 30.3683 | 30.2642 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1235 | 30.1235 | 30.1235 | 32.5836 | 32.5669 | 32.5359 | 32.4973 | 32.4576 | 32.4165 | 32.3743 | 32.3426 | 32.3074 | 32.2717 | 32.2043 | 32.0499 | 32.0499 | 32.0499
| LOCHSIDE | LW |  |  |  | 36.0971 | 36.0921 | 36.0836 | 36.0719 | 36.0599 | 36.0475 | 36.0345 | 36.026 | 36.0169 | 36.0078 | 35.99 | 35.8652 | 35.8407 | 35.8407 | 30.4323 | 30.3835 | 30.2989 | 30.1838 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.1235 | 30.1235 | 30.1235 | 32.586 | 32.5714 | 32.5462 | 32.512 | 32.4767 | 32.4402 | 32.402 | 32.377 | 32.3501 | 32.3235 | 32.2711 | 32.0499 | 32.0499 | 32.0499
| LOCHSIDE | ST |  |  |  | 36.1136 | 36.0966 | 36.0941 | 36.09 | 36.085 | 36.0777 | 36.0701 | 36.0649 | 36.0591 | 36.0531 | 36.0422 | 35.9835 | 35.96 | 35.9362 | 30.5951 | 30.4273 | 30.4032 | 30.3625 | 30.3133 | 30.2412 | 30.1664 | 30.1625 | 30.1625 | 30.1625 | 30.1625 | 30.143 | 30.143 | 30.143 | 32.7432 | 32.5845 | 32.5773 | 32.5652 | 32.5505 | 32.529 | 32.5067 | 32.4914 | 32.4742 | 32.4567 | 32.4245 | 32.317 | 32.2478 | 32.178
| LOCHSIDE | FS |  |  |  | 36.1146 | 36.1135 | 36.098 | 36.0963 | 36.0944 | 36.0917 | 36.0889 | 36.0865 | 36.0842 | 36.0818 | 36.0774 | 36.0674 | 36.0586 | 36.0501 | 30.6051 | 30.5947 | 30.4417 | 30.425 | 30.4061 | 30.3792 | 30.3512 | 30.3279 | 30.3047 | 30.2816 | 30.2379 | 30.1625 | 30.1625 | 30.1625 | 32.7553 | 32.7428 | 32.5888 | 32.5838 | 32.5782 | 32.5702 | 32.5618 | 32.5549 | 32.5479 | 32.5411 | 32.5281 | 32.4988 | 32.4727 | 32.4478
BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 5.653 | 5.653 | 5.653 | 5.653 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 2.4674 | 2.4071 | 4.8812 | 4.8793 | 4.8736 | 4.8667 | 2.3599 | 2.3533 | 2.3468 | 2.3405 | 2.3337 | 2.3269 | 2.3135 | 2.2426 | 2.1711 | 2.1007 | 4.6783 | 4.6765 | 4.6712 | 4.6649 | 2.1586 | 2.1525 | 2.1465 | 2.1407 | 2.1344 | 2.1281 | 2.1157 | 2.0503 | 1.9844 | 1.9194
| LOGIE PERT | CT |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 2.4769 | 4.8812 | 4.8796 | 4.8753 | 4.8705 | 2.3658 | 2.3611 | 2.3566 | 2.3522 | 2.3474 | 2.3426 | 2.3332 | 2.2829 | 2.2322 | 2.1822 | 4.6783 | 4.6768 | 4.6728 | 4.6684 | 2.164 | 2.1597 | 2.1555 | 2.1515 | 2.147 | 2.1427 | 2.134 | 2.0875 | 2.0408 | 1.9946
| LOGIE PERT | LW |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 2.4674 | 2.4071 | 4.8812 | 4.8793 | 4.8736 | 4.8667 | 2.3599 | 2.3533 | 2.3468 | 2.3405 | 2.3337 | 2.3269 | 2.3135 | 2.2426 | 2.1711 | 2.1007 | 4.6783 | 4.6765 | 4.6712 | 4.6649 | 2.1586 | 2.1525 | 2.1465 | 2.1407 | 2.1344 | 2.1281 | 2.1157 | 2.0503 | 1.9844 | 1.9194
| LOGIE PERT | ST |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 4.8818 | 4.8811 | 4.8794 | 4.8767 | 2.3735 | 2.367 | 2.3606 | 2.3543 | 2.3475 | 2.3409 | 2.3279 | 2.2966 | 2.2657 | 2.2349 | 4.6788 | 4.6781 | 4.6766 | 4.6741 | 2.1712 | 2.1651 | 2.1592 | 2.1534 | 2.1472 | 2.141 | 2.1291 | 2.1002 | 2.0717 | 2.0433
| LOGIE PERT | FS |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 3.153 | 4.8822 | 4.8821 | 4.8819 | 4.8812 | 2.3803 | 2.3781 | 2.376 | 2.3733 | 2.3706 | 2.3679 | 2.3628 | 2.3506 | 2.3393 | 2.3288 | 4.6791 | 4.679 | 4.6789 | 4.6782 | 2.1774 | 2.1754 | 2.1735 | 2.1709 | 2.1684 | 2.166 | 2.1613 | 2.15 | 2.1396 | 2.1299
MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | NO | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6737 | 27.6533 | 27.6027 | 27.5366 | 27.481 | 27.4241 | 27.3661 | 27.3209 | 27.3143 | 27.3074 | 27.2937 | 27.0006 | 26.965 | 26.9311 | 27.3744 | 27.3645 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 22.7507 | 22.1008
| LONGHAUGH | CT |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6745 | 27.6589 | 27.6241 | 27.5804 | 27.5454 | 27.5099 | 27.475 | 27.4401 | 27.4011 | 27.3577 | 27.3167 | 27.0317 | 27.0037 | 26.9773 | 27.3748 | 27.3673 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 26.9245 | 26.9245
| LONGHAUGH | LW |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6737 | 27.6533 | 27.6027 | 27.5366 | 27.481 | 27.4241 | 27.3661 | 27.3209 | 27.3143 | 27.3074 | 27.2937 | 27.0006 | 26.965 | 26.9311 | 27.3744 | 27.3645 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 22.7507 | 22.1008
| LONGHAUGH | ST |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.3637 | 28.3637 | 28.3637 | 27.6791 | 27.6695 | 27.6504 | 27.6194 | 27.5887 | 27.5596 | 27.531 | 27.5026 | 27.471 | 27.4366 | 27.367 | 27.1821 | 27.1668 | 27.1524 | 27.3771 | 27.3724 | 27.3631 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.1406 | 27.1406 | 27.1406
| LONGHAUGH | FS |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 27.6836 | 27.681 | 27.6783 | 27.6691 | 27.6615 | 27.6519 | 27.6423 | 27.6301 | 27.6174 | 27.6042 | 27.5779 | 27.5132 | 27.4577 | 27.4081 | 27.3792 | 27.378 | 27.3767 | 27.3722 | 27.3685 | 27.3638 | 27.3592 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568
ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8172 | 17.8091 | 17.7891 | 17.7648 | 17.7404 | 17.7161 | 17.6917 | 17.6674 | 17.6407 | 17.6138 | 17.5592 | 17.4819 | 17.4819 | 13.6983 | 18.0045 | 18.0011 | 17.9928 | 17.9826 | 17.9725 | 17.9623 | 17.9522 | 17.942 | 17.9309 | 17.9197 | 17.897 | 17.8031 | 17.8031 | 17.8031
| LOSSIEMOUTH | CT |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8183 | 17.8134 | 17.8028 | 17.7908 | 17.7785 | 17.7659 | 17.7531 | 17.74 | 17.7254 | 17.7103 | 17.679 | 17.535 | 17.4819 | 17.4819 | 18.0049 | 18.0029 | 17.9985 | 17.9935 | 17.9884 | 17.9831 | 17.9778 | 17.9723 | 17.9662 | 17.9599 | 17.9469 | 17.8869 | 17.8279 | 17.8031
| LOSSIEMOUTH | LW |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8172 | 17.8091 | 17.7891 | 17.7648 | 17.7404 | 17.7161 | 17.6917 | 17.6674 | 17.6407 | 17.6138 | 17.5592 | 17.4819 | 17.4819 | 13.6983 | 18.0045 | 18.0011 | 17.9928 | 17.9826 | 17.9725 | 17.9623 | 17.9522 | 17.942 | 17.9309 | 17.9197 | 17.897 | 17.8031 | 17.8031 | 17.8031
| LOSSIEMOUTH | ST |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8196 | 17.8162 | 17.8097 | 17.8002 | 17.7888 | 17.7677 | 17.7467 | 17.7257 | 17.7027 | 17.6796 | 17.6332 | 17.5311 | 17.4819 | 17.4819 | 18.0055 | 18.0041 | 18.0014 | 17.9974 | 17.9926 | 17.9838 | 17.9751 | 17.9663 | 17.9568 | 17.9471 | 17.9278 | 17.8853 | 17.8444 | 17.8044
| LOSSIEMOUTH | FS |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8211 | 17.82 | 17.8189 | 17.8157 | 17.812 | 17.8049 | 17.7978 | 17.7888 | 17.7798 | 17.7708 | 17.7528 | 17.7094 | 17.6726 | 17.6391 | 18.0061 | 18.0057 | 18.0052 | 18.0038 | 18.0023 | 17.9993 | 17.9964 | 17.9926 | 17.9889 | 17.9851 | 17.9777 | 17.9596 | 17.9442 | 17.9302
BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0.32615 | -0.11133 | -0.33642 | -0.58825 | -0.83732 | -1.0772 | -1.3078 | -1.5293 | -1.6534 | -1.716 | -1.839 | -2.1881 | -2.5603 | -2.9529 | 0.42904 | -0.045731 | -0.24162 | -0.43924 | -0.63149 | -0.81868 | -1.0042 | -1.1823 | -1.2826 | -1.3337 | -1.4341 | -1.739 | -2.0585 | -2.3921 | -0.0099636 | -0.2111 | -0.47081 | -0.73044 | -0.98082 | -1.2219 | -1.4538 | -1.6765 | -1.8014 | -1.8646 | -1.989 | -2.3499 | -2.7287 | -3.1256
| LOWER OLLACH | CT |  |  |  | 0.32615 | -0.11133 | -0.33642 | -0.58825 | -0.83732 | -1.0772 | -1.3078 | -1.5293 | -1.6534 | -1.716 | -1.839 | -2.1881 | -2.5603 | -2.9529 | 0.42904 | -0.045731 | -0.24162 | -0.43924 | -0.63149 | -0.81868 | -1.0042 | -1.1823 | -1.2826 | -1.3337 | -1.4341 | -1.739 | -2.0585 | -2.3921 | -0.0099636 | -0.2111 | -0.47081 | -0.73044 | -0.98082 | -1.2219 | -1.4538 | -1.6765 | -1.8014 | -1.8646 | -1.989 | -2.3499 | -2.7287 | -3.1256
| LOWER OLLACH | LW |  |  |  | 0.58437 | 0.55445 | 0.5199 | 0.48099 | 0.43811 | 0.39165 | 0.34203 | 0.28963 | -0.028139 | -0.086352 | -0.2113 | -0.64371 | -1.1354 | -1.7005 | 0.59384 | 0.57464 | 0.5523 | 0.52711 | 0.4994 | 0.46941 | 0.43741 | 0.40364 | -0.00044395 | -0.054352 | -0.16484 | -0.53229 | -0.94429 | -1.4118 | 0.47329 | 0.44715 | 0.41696 | 0.38295 | 0.34548 | 0.30489 | -0.0086445 | -0.070308 | -0.13834 | -0.20829 | -0.3518 | -0.79678 | -1.2949 | -1.866
| LOWER OLLACH | ST |  |  |  | 0.62393 | 0.61361 | 0.59985 | 0.58644 | 0.57339 | 0.55753 | 0.54211 | 0.52713 | 0.51205 | 0.49002 | 0.44778 | 0.34069 | -0.082579 | -0.23629 | 0.61912 | 0.61249 | 0.60362 | 0.59493 | 0.58644 | 0.57557 | 0.565 | 0.55473 | 0.54433 | 0.52952 | 0.50109 | 0.42947 | -0.10851 | -0.24165 | 0.50786 | 0.49884 | 0.48682 | 0.4751 | 0.4637 | 0.44984 | 0.43636 | 0.42327 | 0.41009 | 0.39084 | 0.35393 | -0.080655 | -0.22793 | -0.38651
| LOWER OLLACH | FS |  |  |  | 0.61361 | 0.59985 | 0.58609 | 0.56571 | 0.54561 | 0.52577 | 0.50621 | 0.48691 | 0.46789 | 0.44913 | 0.41242 | 0.30319 | -0.063162 | -0.18417 | 0.61255 | 0.60376 | 0.59497 | 0.58193 | 0.56905 | 0.55615 | 0.54342 | 0.53079 | 0.51835 | 0.50608 | 0.48207 | 0.41098 | -0.055739 | -0.15523 | 0.49884 | 0.48682 | 0.47479 | 0.45699 | 0.43942 | 0.42209 | 0.40499 | 0.38813 | 0.3715 | 0.35511 | 0.32303 | -0.067752 | -0.20002 | -0.32607
KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | -0.13561 | -0.13748 | 0.0059666 | 0.0058836 | 0.0056688 | 0.0056172 | 0.0055751 | 0.0055339 | 0.005508 | 0.005508 | 0.005508 | 0.005508 | 0.005508 | -0.0020364 | -0.11397 | -0.11607 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | -0.0012527 | -0.14102 | -0.14308
| LUBNAIG | CT |  |  |  | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | -0.13334 | -0.13465 | 0.0059666 | 0.0058974 | 0.0057188 | 0.005641 | 0.0056115 | 0.0055827 | 0.0055545 | 0.0055269 | 0.005508 | 0.005508 | 0.005508 | 0.005508 | -0.11142 | -0.11289 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | -0.13867 | -0.14002
| LUBNAIG | LW |  |  |  | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | -0.13561 | -0.13748 | 0.0059666 | 0.0058836 | 0.0056688 | 0.0056172 | 0.0055751 | 0.0055339 | 0.005508 | 0.005508 | 0.005508 | 0.005508 | 0.005508 | -0.0020364 | -0.11397 | -0.11607 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | -0.0012527 | -0.14102 | -0.14308
| LUBNAIG | ST |  |  |  | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | -0.06246 | -0.063277 | 0.0059909 | 0.0059601 | 0.0058879 | 0.0057758 | 0.0056682 | 0.0056408 | 0.0056221 | 0.0056038 | 0.0055842 | 0.0055648 | 0.0055271 | 0.005508 | -0.053844 | -0.054761 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | -0.067232 | -0.068086
| LUBNAIG | FS |  |  |  | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.011703 | 0.0060052 | 0.0060013 | 0.0059962 | 0.0059647 | 0.0059273 | 0.0058839 | 0.0058409 | 0.0057855 | 0.0057312 | 0.0056863 | 0.0056503 | 0.005614 | 0.0055807 | 0.0055502 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176 | 0.0067176
LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | NO | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8754 | 11.3973 | 10.9153 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 11.8297 | 10.4735 | 9.9247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.6941 | 11.217 | 9.6493 | 9.0832
| LUNANHEAD | CT |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.212 | 11.8504 | 11.4834 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.2129 | 10.9893 | 10.5716 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 11.6123 | 10.1815 | 9.7505
| LUNANHEAD | LW |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8754 | 11.3973 | 10.9153 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 11.8297 | 10.4735 | 9.9247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.6941 | 11.217 | 9.6493 | 9.0832
| LUNANHEAD | ST |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.6099 | 13.1881 | 13.0983 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.6158 | 12.3355 | 12.0984 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.4384 | 11.7311 | 11.4865
| LUNANHEAD | FS |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247
PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | -0.0044771 | -0.010279 | 0.010481 | 0.010336 | 0.0101 | 0.0098326 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | -0.0008915 | -0.0077869 | -0.014717 | -0.021563 | 0.012178 | 0.012152 | 0.012076 | 0.011982 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | -0.00012929 | -0.007027 | -0.01396 | -0.020807
| LUSSAGIVEN | CT |  |  |  | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | -0.00072434 | -0.0059109 | 0.010481 | 0.010361 | 0.010167 | 0.0099802 | 0.0097971 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | -0.0040957 | -0.01029 | -0.016409 | 0.012178 | 0.012156 | 0.012099 | 0.012034 | 0.01197 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | -0.0033345 | -0.0095311 | -0.015652
| LUSSAGIVEN | LW |  |  |  | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | -0.0044771 | -0.010279 | 0.010481 | 0.010336 | 0.0101 | 0.0098326 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | -0.0008915 | -0.0077869 | -0.014717 | -0.021563 | 0.012178 | 0.012152 | 0.012076 | 0.011982 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | -0.00012929 | -0.007027 | -0.01396 | -0.020807
| LUSSAGIVEN | ST |  |  |  | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.010523 | 0.010469 | 0.010344 | 0.01022 | 0.010098 | 0.0099292 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | 0.0097919 | -0.0025615 | -0.0055814 | 0.012197 | 0.012176 | 0.012153 | 0.012117 | 0.012075 | 0.012016 | 0.011959 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | 0.011909 | -0.0017998 | -0.0048207
| LUSSAGIVEN | FS |  |  |  | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.018805 | 0.010548 | 0.010541 | 0.010532 | 0.010477 | 0.010412 | 0.010307 | 0.010248 | 0.010177 | 0.010107 | 0.010039 | 0.0099067 | 0.0097919 | 0.0097919 | 0.0097919 | 0.012209 | 0.012205 | 0.012201 | 0.012177 | 0.012166 | 0.012146 | 0.012127 | 0.012102 | 0.012078 | 0.012054 | 0.012008 | 0.011909 | 0.011909 | 0.011909
LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | NO | 13.7259 | 13.7189 | 13.6981 | 13.6726 | 13.6481 | 13.6227 | 13.5966 | 13.571 | 13.5421 | 13.5115 | 13.4498 | 13.2652 | 13.2371 | 13.2188 | 12.5119 | 12.5036 | 12.4789 | 12.4523 | 12.429 | 12.405 | 12.3802 | 12.3575 | 12.3367 | 12.3147 | 12.2704 | 12.1185 | 12.0992 | 12.0878 | 12.6075 | 12.5999 | 12.5773 | 12.5497 | 12.5231 | 12.4956 | 12.4673 | 12.4395 | 12.4082 | 12.3849 | 12.3675 | 12.3068 | 12.25 | 12.211
| LYNDHURST | CT |  |  |  | 13.7259 | 13.7192 | 13.7019 | 13.6821 | 13.6628 | 13.6435 | 13.6251 | 13.607 | 13.5869 | 13.5634 | 13.5149 | 13.3468 | 13.2522 | 13.238 | 12.5119 | 12.5038 | 12.4834 | 12.4613 | 12.4429 | 12.4246 | 12.4071 | 12.3901 | 12.371 | 12.352 | 12.3171 | 12.1964 | 12.1086 | 12.0998 | 12.6075 | 12.6002 | 12.5814 | 12.56 | 12.539 | 12.5181 | 12.4981 | 12.4786 | 12.4568 | 12.4313 | 12.3858 | 12.3383 | 12.2942 | 12.2526
| LYNDHURST | LW |  |  |  | 13.7263 | 13.7189 | 13.6981 | 13.6726 | 13.6481 | 13.6227 | 13.5966 | 13.571 | 13.5421 | 13.5115 | 13.4498 | 13.2652 | 13.2371 | 13.2188 | 12.5123 | 12.5036 | 12.4789 | 12.4523 | 12.429 | 12.405 | 12.3802 | 12.3575 | 12.3367 | 12.3147 | 12.2704 | 12.1185 | 12.0992 | 12.0878 | 12.6079 | 12.5999 | 12.5773 | 12.5497 | 12.5231 | 12.4956 | 12.4673 | 12.4395 | 12.4082 | 12.3849 | 12.3675 | 12.3068 | 12.25 | 12.211
| LYNDHURST | ST |  |  |  | 13.7285 | 13.7257 | 13.7193 | 13.7094 | 13.6977 | 13.6812 | 13.6655 | 13.6501 | 13.6331 | 13.6138 | 13.5746 | 13.4796 | 13.396 | 13.3249 | 12.5148 | 12.5115 | 12.504 | 12.4923 | 12.4785 | 12.4604 | 12.4455 | 12.4309 | 12.4147 | 12.3965 | 12.36 | 12.2918 | 12.2318 | 12.1752 | 12.6103 | 12.6072 | 12.6003 | 12.5896 | 12.5769 | 12.5591 | 12.542 | 12.5253 | 12.5068 | 12.486 | 12.4434 | 12.3759 | 12.3522 | 12.33
| LYNDHURST | FS |  |  |  | 13.7297 | 13.7293 | 13.7287 | 13.7258 | 13.7226 | 13.7171 | 13.7116 | 13.7046 | 13.6972 | 13.6896 | 13.6744 | 13.6365 | 13.6039 | 13.575 | 12.5164 | 12.5158 | 12.5151 | 12.5117 | 12.5079 | 12.5014 | 12.4949 | 12.4866 | 12.4779 | 12.4689 | 12.4539 | 12.418 | 12.3871 | 12.3603 | 12.6117 | 12.6112 | 12.6105 | 12.6074 | 12.6039 | 12.5979 | 12.592 | 12.5843 | 12.5764 | 12.5681 | 12.5516 | 12.5105 | 12.4752 | 12.4438
THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | -0.76384 | -0.80066 | -0.83715 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | -0.63173 | -0.67843 | -0.72472 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | -0.80984 | -0.85364 | -0.89705
| LYNESS | CT |  |  |  | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | -0.74689 | -0.77438 | -0.80158 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | -0.61024 | -0.64509 | -0.6796 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | -0.78969 | -0.82238 | -0.85473
| LYNESS | LW |  |  |  | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | -0.76384 | -0.80066 | -0.83715 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | -0.63173 | -0.67843 | -0.72472 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | -0.80984 | -0.85364 | -0.89705
| LYNESS | ST |  |  |  | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | -0.33251 | -0.34822 | -0.3639 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | -0.28652 | -0.30644 | -0.32633 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | -0.37035 | -0.38903 | -0.40768
| LYNESS | FS |  |  |  | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.34812 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.32462 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523 | 0.42523
STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.019685 | 0.019617 | 0.019423 | 0.019186 | 0.018955 | 0.018728 | 0.018506 | 0.018326 | 0.018149 | 0.017973 | 0.017735 | 0.017548 | -0.0017229 | -0.0082484 | 0.022196 | 0.022164 | 0.022069 | 0.021954 | 0.021842 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | -0.0044502
| MAARUIG | CT |  |  |  | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.019685 | 0.019629 | 0.019483 | 0.019317 | 0.019155 | 0.018996 | 0.018841 | 0.01869 | 0.018526 | 0.018381 | 0.018138 | 0.017548 | 0.017548 | -0.0022228 | 0.022196 | 0.022169 | 0.022098 | 0.022018 | 0.021939 | 0.021862 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822
| MAARUIG | LW |  |  |  | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.019685 | 0.019617 | 0.019423 | 0.019186 | 0.018955 | 0.018728 | 0.018506 | 0.018326 | 0.018149 | 0.017973 | 0.017735 | 0.017548 | -0.0017229 | -0.0082484 | 0.022196 | 0.022164 | 0.022069 | 0.021954 | 0.021842 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | -0.0044502
| MAARUIG | ST |  |  |  | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.019704 | 0.019679 | 0.019621 | 0.01953 | 0.019422 | 0.01913 | 0.018846 | 0.018567 | 0.018309 | 0.018085 | 0.017742 | 0.017548 | 0.017548 | 0.017548 | 0.022206 | 0.022194 | 0.022165 | 0.022121 | 0.022068 | 0.021927 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822 | 0.021822
| MAARUIG | FS |  |  |  | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.035936 | 0.019716 | 0.019713 | 0.019709 | 0.019683 | 0.019653 | 0.019555 | 0.019458 | 0.019335 | 0.019215 | 0.019097 | 0.018868 | 0.01835 | 0.017965 | 0.017732 | 0.022211 | 0.02221 | 0.022208 | 0.022195 | 0.022181 | 0.022133 | 0.022086 | 0.022027 | 0.021968 | 0.021911 | 0.021822 | 0.021822 | 0.021822 | 0.021822
LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | NO | 19.5555 | 19.464 | 19.3327 | 19.2084 | 19.0934 | 18.9822 | 18.8745 | 18.7695 | 18.7013 | 18.6551 | 18.5637 | 18.3657 | 18.172 | 14.2622 | 17.8863 | 17.8388 | 17.7777 | 17.7226 | 17.6695 | 17.6184 | 17.5692 | 17.522 | 17.4965 | 17.4839 | 14.9894 | 14.0933 | 13.2237 | 12.3824 | 18.0135 | 17.9068 | 17.7749 | 17.6707 | 17.5701 | 17.4733 | 17.3802 | 17.2909 | 17.2427 | 17.2188 | 17.1717 | 14.2111 | 13.3083 | 12.4385
| MACALPINE ROAD | CT |  |  |  | 19.5555 | 19.464 | 19.3327 | 19.2084 | 19.0934 | 18.9822 | 18.8745 | 18.7695 | 18.7013 | 18.6551 | 18.5637 | 18.3657 | 18.172 | 14.7088 | 17.8863 | 17.8388 | 17.7777 | 17.7226 | 17.6695 | 17.6184 | 17.5692 | 17.522 | 17.4965 | 17.4839 | 17.459 | 14.4536 | 13.7903 | 13.1503 | 18.0135 | 17.9068 | 17.7749 | 17.6707 | 17.5701 | 17.4733 | 17.3802 | 17.2909 | 17.2427 | 17.2188 | 17.1717 | 14.4028 | 13.7203 | 13.0592
| MACALPINE ROAD | LW |  |  |  | 19.6764 | 19.653 | 19.6051 | 19.5479 | 19.4955 | 19.4415 | 19.386 | 19.3298 | 19.2687 | 19.2061 | 19.0798 | 18.8978 | 18.7197 | 14.2622 | 17.9547 | 17.9468 | 17.9377 | 17.9273 | 17.916 | 17.9037 | 17.8905 | 17.8767 | 17.8618 | 17.8466 | 14.9894 | 14.0933 | 13.2237 | 12.3824 | 18.1387 | 18.1138 | 18.0777 | 18.0582 | 18.0367 | 18.0134 | 17.9885 | 17.9623 | 17.9342 | 17.9053 | 17.846 | 14.2111 | 13.3083 | 12.4385
| MACALPINE ROAD | ST |  |  |  | 19.6977 | 19.6895 | 19.6722 | 19.6502 | 19.6296 | 19.6127 | 19.596 | 19.579 | 19.5618 | 19.5412 | 19.501 | 19.3996 | 19.3093 | 19.219 | 17.9652 | 17.9625 | 17.9588 | 17.9553 | 17.9518 | 17.9476 | 17.9435 | 17.9396 | 17.936 | 17.9307 | 17.9206 | 17.8935 | 17.8695 | 17.8442 | 18.1714 | 18.1528 | 18.135 | 18.1124 | 18.1045 | 18.0966 | 18.0888 | 18.0813 | 18.0745 | 18.0645 | 18.0454 | 17.9942 | 17.9488 | 17.9008
| MACALPINE ROAD | FS |  |  |  | 19.6944 | 19.6875 | 19.6787 | 19.6638 | 19.6501 | 19.6375 | 19.6249 | 19.6117 | 19.5985 | 19.5852 | 19.5592 | 19.487 | 19.416 | 19.3487 | 17.9625 | 17.9588 | 17.9552 | 17.9498 | 17.9445 | 17.9392 | 17.934 | 17.9289 | 17.9239 | 17.9189 | 17.9092 | 17.8802 | 17.8504 | 17.8216 | 18.1737 | 18.1646 | 18.1469 | 18.125 | 18.1104 | 18.0969 | 18.0835 | 18.0695 | 18.0554 | 18.0422 | 18.0238 | 17.969 | 17.9126 | 17.858
#N/A | MACDUFF NEW | MINIMUM HEADROOM | #N/A | NO | #N/A | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | CT |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | LW |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | ST |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| MACDUFF NEW | FS |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.1913 | 4.1855 | 4.1706 | 4.1535 | 4.1366 | 4.1201 | 4.1039 | 4.0879 | 4.0726 | 4.0713 | 4.0686 | 3.2799 | 3.1676 | 3.0572 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683
| MACHRIE | CT |  |  |  | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.1913 | 4.1855 | 4.1706 | 4.1535 | 4.1366 | 4.1201 | 4.1039 | 4.0879 | 4.0726 | 4.0713 | 4.0686 | 3.2799 | 3.1676 | 3.0572 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683
| MACHRIE | LW |  |  |  | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.1944 | 4.1938 | 4.192 | 4.1898 | 4.1876 | 4.1855 | 4.1834 | 4.1814 | 4.1792 | 4.177 | 4.1727 | 4.0802 | 4.066 | 3.198 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683
| MACHRIE | ST |  |  |  | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.1946 | 4.1944 | 4.1938 | 4.193 | 4.192 | 4.1837 | 4.1756 | 4.1676 | 4.1591 | 4.1507 | 4.1343 | 4.0945 | 4.0714 | 4.0683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683
| MACHRIE | FS |  |  |  | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.5951 | 4.1947 | 4.1947 | 4.1947 | 4.1944 | 4.1941 | 4.1914 | 4.1887 | 4.1852 | 4.1818 | 4.1785 | 4.172 | 4.1566 | 4.1423 | 4.1288 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683 | 4.1683
FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 7.4771
| MALLAIG | CT |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
| MALLAIG | LW |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 7.4771
| MALLAIG | ST |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
| MALLAIG | FS |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6211 | 0.90447 | -1.2818 | -1.4086 | 3.7056 | 3.6875 | 3.6391 | 3.5767 | 3.5146 | 3.4528 | 3.3912 | 3.3308 | 3.2656 | 3.2015 | 3.073 | 2.3539 | 0.53442 | 0.25977 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.3886 | -0.57195 | -0.83575
| MARNOCH | CT |  |  |  | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 0.94841 | -1.2299 | -1.349 | 3.7056 | 3.6875 | 3.6407 | 3.5867 | 3.5329 | 3.4795 | 3.4263 | 3.374 | 3.3176 | 3.2622 | 3.151 | 2.4491 | 0.64681 | 0.38895 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.3886 | -0.46615 | -0.71168
| MARNOCH | LW |  |  |  | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6211 | 0.90447 | -1.2818 | -1.4086 | 3.7075 | 3.6898 | 3.6391 | 3.5767 | 3.5146 | 3.4528 | 3.3912 | 3.3308 | 3.2656 | 3.2015 | 3.073 | 2.3539 | 0.53442 | 0.25977 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.3886 | -0.57195 | -0.83575
| MARNOCH | ST |  |  |  | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.3855 | 0.37869 | 0.3241 | 3.7141 | 3.7099 | 3.7002 | 3.6851 | 3.6668 | 3.6418 | 3.6169 | 3.5924 | 3.566 | 3.5405 | 3.4895 | 3.1463 | 2.2564 | 2.1382 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.6279 | 0.79034 | 0.79034
| MARNOCH | FS |  |  |  | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 3.7159 | 3.7149 | 3.7136 | 3.7073 | 3.6998 | 3.6913 | 3.6828 | 3.6721 | 3.6616 | 3.6515 | 3.6312 | 3.5828 | 3.5371 | 3.4941 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672 | 1.8672
BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 4.5769 | 3.8754 | 3.5861 | 3.291 | 3.0056 | 2.7296 | 2.4632 | 2.1754 | 2.0062 | 1.8945 | 1.6712 | 1.2675 | 0.8549 | 0.42714 | 3.9765 | 3.8096 | 3.5672 | 3.3173 | 3.0753 | 2.8411 | 2.6145 | 2.3589 | 2.2052 | 2.096 | 1.877 | 1.5139 | 1.1459 | 0.76184 | 3.9382 | 3.7293 | 3.4368 | 3.1383 | 2.8484 | 2.564 | 2.2892 | 1.9879 | 1.8093 | 1.6882 | 1.4457 | 1.0212 | 0.58855 | 0.14103
| MARYBANK | CT |  |  |  | 4.5769 | 3.8754 | 3.5861 | 3.291 | 3.0056 | 2.7296 | 2.4632 | 2.1754 | 2.0062 | 1.8945 | 1.6712 | 1.2675 | 0.8549 | 0.42714 | 3.9765 | 3.8096 | 3.5672 | 3.3173 | 3.0753 | 2.8411 | 2.6145 | 2.3589 | 2.2052 | 2.096 | 1.877 | 1.5139 | 1.1459 | 0.76184 | 3.9382 | 3.7293 | 3.4368 | 3.1383 | 2.8484 | 2.564 | 2.2892 | 1.9879 | 1.8093 | 1.6882 | 1.4457 | 1.0212 | 0.58855 | 0.14103
| MARYBANK | LW |  |  |  | 4.8205 | 4.7923 | 4.7597 | 4.723 | 3.9385 | 3.8082 | 3.6758 | 3.504 | 3.3574 | 3.2095 | 2.913 | 2.4109 | 1.8622 | 1.2495 | 4.8385 | 4.8107 | 4.7574 | 3.8892 | 3.7556 | 3.6209 | 3.4852 | 3.3038 | 3.1545 | 3.0044 | 2.705 | 2.2501 | 1.7589 | 1.2197 | 4.6953 | 4.6671 | 4.6306 | 3.9012 | 3.7566 | 3.6101 | 3.462 | 3.2669 | 3.1032 | 2.9384 | 2.6088 | 2.0776 | 1.5 | 0.85998
| MARYBANK | ST |  |  |  | 4.8579 | 4.8481 | 4.8351 | 4.8225 | 4.8102 | 4.7952 | 4.7807 | 4.7665 | 4.7523 | 4.7316 | 3.9891 | 3.8021 | 3.6265 | 3.4415 | 4.8627 | 4.8528 | 4.8351 | 4.8118 | 4.7854 | 4.7696 | 4.7543 | 3.9521 | 3.921 | 3.8845 | 3.8115 | 3.6358 | 3.471 | 3.2991 | 4.7302 | 4.7204 | 4.7066 | 4.6919 | 4.6769 | 4.6618 | 4.6471 | 3.975 | 3.9402 | 3.8985 | 3.8154 | 3.6143 | 3.4255 | 3.2276
| MARYBANK | FS |  |  |  | 4.8481 | 4.8351 | 4.8222 | 4.8029 | 4.784 | 4.7653 | 4.7468 | 4.7286 | 4.7106 | 4.6929 | 4.6583 | 3.9674 | 3.8299 | 3.6992 | 4.8594 | 4.8516 | 4.8437 | 4.8285 | 4.8125 | 4.7997 | 4.7872 | 4.7698 | 4.7567 | 4.7438 | 3.9728 | 3.8498 | 3.7333 | 3.6226 | 4.7217 | 4.7097 | 4.6976 | 4.6791 | 4.6607 | 4.6431 | 4.6257 | 4.6076 | 4.5906 | 4.5738 | 3.9658 | 3.8201 | 3.6805 | 3.5459
LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | NO | 18.1662 | 17.9012 | 17.557 | 14.3862 | 14.0939 | 13.8123 | 13.5417 | 13.2819 | 13.1807 | 13.1304 | 12.9357 | 11.6244 | 10.9764 | 10.3425 | 13.7717 | 13.5167 | 13.1411 | 12.758 | 12.3887 | 12.0378 | 11.6967 | 11.3641 | 11.1626 | 11.0067 | 10.7084 | 9.4683 | 8.7449 | 8.0343 | 13.4462 | 13.129 | 12.68 | 12.2293 | 11.7948 | 11.3805 | 10.979 | 10.589 | 10.3722 | 10.2047 | 9.8836 | 8.4549 | 7.694 | 6.9482
| MARYTON | CT |  |  |  | 18.1662 | 17.9012 | 17.557 | 14.3862 | 14.0939 | 13.8123 | 13.5417 | 13.2819 | 13.1807 | 13.1304 | 12.9357 | 11.6244 | 10.9764 | 10.3425 | 13.7717 | 13.5167 | 13.1411 | 12.758 | 12.3887 | 12.0378 | 11.6967 | 11.3641 | 11.1626 | 11.0067 | 10.7084 | 9.4683 | 8.7449 | 8.0343 | 13.4462 | 13.129 | 12.68 | 12.2293 | 11.7948 | 11.3805 | 10.979 | 10.589 | 10.3722 | 10.2047 | 9.8836 | 8.4549 | 7.694 | 6.9482
| MARYTON | LW |  |  |  | 18.543 | 18.496 | 18.436 | 18.3671 | 18.2928 | 18.2141 | 18.131 | 18.044 | 17.9734 | 17.9095 | 17.7854 | 13.3555 | 12.4456 | 11.5433 | 15.6263 | 15.6012 | 15.5723 | 13.6559 | 13.4613 | 13.2728 | 13.0823 | 12.8902 | 12.702 | 12.5125 | 12.1408 | 10.6126 | 9.5973 | 8.5906 | 15.693 | 13.774 | 13.6182 | 13.4288 | 13.2372 | 13.0458 | 12.8393 | 12.6304 | 12.4297 | 12.2272 | 11.8287 | 10.0965 | 9.0283 | 7.969
| MARYTON | ST |  |  |  | 18.6173 | 18.5854 | 18.5623 | 18.538 | 18.5136 | 18.4841 | 18.4553 | 18.4271 | 18.399 | 18.3613 | 18.2892 | 17.8759 | 17.7763 | 14.526 | 15.6594 | 15.6507 | 15.6392 | 15.628 | 15.6171 | 15.6038 | 13.7182 | 13.6233 | 13.5219 | 13.4133 | 13.2087 | 12.5236 | 12.0909 | 11.6785 | 15.7518 | 15.7365 | 15.716 | 13.7754 | 13.6982 | 13.6063 | 13.5156 | 13.4253 | 13.3296 | 13.2217 | 13.0048 | 12.2294 | 11.7771 | 11.3515
| MARYTON | FS |  |  |  | 18.6028 | 18.5705 | 18.55 | 18.5187 | 18.4877 | 18.4566 | 18.4259 | 18.3949 | 18.3645 | 18.3344 | 18.2757 | 18.1047 | 17.9715 | 17.8528 | 15.6507 | 15.6392 | 15.6277 | 15.6106 | 15.5938 | 15.5772 | 15.5608 | 15.5447 | 15.5288 | 13.7845 | 13.6776 | 13.4038 | 13.1725 | 12.9595 | 15.7365 | 15.716 | 15.6956 | 15.6654 | 15.6355 | 13.7541 | 13.7 | 13.6403 | 13.5814 | 13.5232 | 13.4109 | 13.1151 | 12.8697 | 12.644
STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | NO | 6.4264 | 6.3467 | 6.2443 | 6.1448 | 6.0488 | 5.9564 | 5.8676 | 5.7824 | 5.7317 | 5.7065 | 5.657 | 4.505 | 3.0228 | 2.6496 | 6.003 | 5.9188 | 5.7917 | 5.6612 | 5.5339 | 5.4098 | 5.2887 | 5.1715 | 5.0811 | 5.0139 | 4.8797 | 3.8421 | 2.6016 | 2.2087 | 6.5273 | 6.4533 | 6.3572 | 6.2634 | 6.1729 | 6.0856 | 5.9881 | 5.8482 | 5.7442 | 5.6703 | 5.5228 | 4.2509 | 2.7143 | 2.2829
| MAUD | CT |  |  |  | 6.4264 | 6.3467 | 6.2443 | 6.1448 | 6.0488 | 5.9564 | 5.8676 | 5.7824 | 5.7317 | 5.7065 | 5.657 | 4.505 | 3.0228 | 2.6496 | 6.003 | 5.9188 | 5.7917 | 5.6612 | 5.5339 | 5.4098 | 5.2887 | 5.1715 | 5.0811 | 5.0139 | 4.8797 | 3.8421 | 2.6016 | 2.2087 | 6.5273 | 6.4533 | 6.3572 | 6.2634 | 6.1729 | 6.0856 | 5.9881 | 5.8482 | 5.7442 | 5.6703 | 5.5228 | 4.2509 | 2.7143 | 2.2829
| MAUD | LW |  |  |  | 6.5412 | 6.5279 | 6.5125 | 6.4952 | 6.4762 | 6.4555 | 6.4335 | 6.4102 | 6.3828 | 6.3545 | 6.2964 | 5.0872 | 3.4853 | 2.9743 | 6.1045 | 6.0785 | 6.0241 | 5.9584 | 5.8912 | 5.8227 | 5.753 | 5.6831 | 5.6057 | 5.5287 | 5.3724 | 4.2276 | 2.8637 | 2.3343 | 6.6325 | 6.6194 | 6.6029 | 6.584 | 6.5635 | 6.5415 | 6.5183 | 6.494 | 6.4424 | 6.3579 | 6.1861 | 4.7981 | 3.1246 | 2.5387
| MAUD | ST |  |  |  | 6.5587 | 6.5542 | 6.548 | 6.5421 | 6.5363 | 6.5292 | 6.5224 | 6.5157 | 6.5092 | 6.4997 | 6.4814 | 6.0534 | 5.4659 | 5.2892 | 6.1787 | 6.1147 | 6.097 | 6.0724 | 6.0439 | 6.0067 | 5.9698 | 5.9337 | 5.8953 | 5.8552 | 5.7761 | 5.2499 | 4.6339 | 4.4395 | 6.6521 | 6.6443 | 6.6379 | 6.6313 | 6.6246 | 6.6163 | 6.6081 | 6.6002 | 6.5922 | 6.5816 | 6.5611 | 5.9988 | 5.2401 | 5.0313
| MAUD | FS |  |  |  | 6.5542 | 6.548 | 6.5419 | 6.5329 | 6.5239 | 6.5151 | 6.5064 | 6.4979 | 6.4894 | 6.4811 | 6.4648 | 6.4162 | 6.3649 | 6.315 | 6.1772 | 6.171 | 6.1097 | 6.0961 | 6.0814 | 6.0633 | 6.0452 | 6.0246 | 6.0042 | 5.9844 | 5.9452 | 5.8436 | 5.7427 | 5.6462 | 6.6481 | 6.6424 | 6.6334 | 6.6248 | 6.6162 | 6.6075 | 6.5989 | 6.5902 | 6.5817 | 6.5733 | 6.5569 | 6.5088 | 6.4584 | 6.4095
MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.45895 | 0.45895 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | -0.066349 | -0.14016 | 1.4441 | 1.444 | 1.3856 | 1.3851 | 1.3847 | 1.3842 | 1.3838 | 1.3834 | 1.3829 | 1.3825 | 1.3816 | 1.373 | 1.3644 | 1.3559 | 2.0041 | 2.004 | 1.9093 | 1.9089 | 1.9084 | 1.908 | 1.9075 | 1.9071 | 1.9066 | 1.9062 | 1.9053 | 1.8967 | 1.888 | 1.8794
| MELVICH | CT |  |  |  | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 1.4441 | 1.444 | 1.4437 | 1.4434 | 1.4431 | 1.4428 | 1.4425 | 1.4422 | 1.4419 | 1.4415 | 1.4409 | 1.4346 | 1.4282 | 1.4219 | 2.0041 | 2.004 | 2.0037 | 2.0034 | 2.0031 | 2.0028 | 2.0025 | 2.0022 | 2.0018 | 2.0015 | 2.0009 | 1.9945 | 1.988 | 1.9817
| MELVICH | LW |  |  |  | 0.45895 | 0.45895 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | 0.36801 | -0.066349 | -0.14016 | 1.4441 | 1.444 | 1.3856 | 1.3851 | 1.3847 | 1.3842 | 1.3838 | 1.3834 | 1.3829 | 1.3825 | 1.3816 | 1.373 | 1.3644 | 1.3559 | 2.0041 | 2.004 | 1.9093 | 1.9089 | 1.9084 | 1.908 | 1.9075 | 1.9071 | 1.9066 | 1.9062 | 1.9053 | 1.8967 | 1.888 | 1.8794
| MELVICH | ST |  |  |  | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 1.4442 | 1.4441 | 1.444 | 1.4438 | 1.4436 | 1.443 | 1.4423 | 1.4416 | 1.4409 | 1.4403 | 1.4389 | 1.4357 | 1.4324 | 1.4292 | 2.0042 | 2.0041 | 2.004 | 2.0038 | 2.0036 | 2.0029 | 2.0023 | 2.0016 | 2.0009 | 2.0002 | 1.9989 | 1.9956 | 1.9923 | 1.9891
| MELVICH | FS |  |  |  | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 0.45895 | 1.4442 | 1.4442 | 1.4442 | 1.4441 | 1.4441 | 1.4439 | 1.4436 | 1.4434 | 1.4431 | 1.4428 | 1.4423 | 1.441 | 1.4398 | 1.4387 | 2.0042 | 2.0042 | 2.0042 | 2.0041 | 2.0041 | 2.0039 | 2.0036 | 2.0033 | 2.0031 | 2.0028 | 2.0023 | 2.001 | 1.9998 | 1.9987
CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | NO | 29.3038 | 29.1955 | 29.0382 | 28.884 | 28.7468 | 28.6127 | 28.4821 | 28.3601 | 28.2852 | 28.2319 | 28.059 | 27.7961 | 27.5438 | 27.2882 | 25.4015 | 25.3599 | 25.3065 | 25.2583 | 25.2117 | 25.167 | 25.1239 | 25.0826 | 25.0602 | 25.0491 | 24.995 | 24.9443 | 18.2818 | 17.112 | 23.7519 | 23.6652 | 23.5539 | 23.4533 | 23.3564 | 23.263 | 23.1732 | 23.0871 | 23.0405 | 23.0174 | 22.9045 | 22.7988 | 18.4633 | 17.248
| MENZIESHILL | CT |  |  |  | 29.3038 | 29.1955 | 29.0382 | 28.884 | 28.7468 | 28.6127 | 28.4821 | 28.3601 | 28.2852 | 28.2319 | 28.059 | 27.7961 | 27.5438 | 27.2941 | 25.4015 | 25.3599 | 25.3065 | 25.2583 | 25.2117 | 25.167 | 25.1239 | 25.0826 | 25.0602 | 25.0491 | 24.995 | 24.9443 | 24.8927 | 18.9373 | 23.7519 | 23.6652 | 23.5539 | 23.4533 | 23.3564 | 23.263 | 23.1732 | 23.0871 | 23.0405 | 23.0174 | 22.9045 | 22.7988 | 22.6913 | 18.9463
| MENZIESHILL | LW |  |  |  | 29.4301 | 29.3889 | 29.3065 | 29.2056 | 29.1187 | 29.0293 | 28.9528 | 28.8835 | 28.8075 | 28.7292 | 28.5046 | 28.0716 | 27.6343 | 27.2882 | 25.4613 | 25.4544 | 25.4464 | 25.4374 | 25.4275 | 25.4167 | 25.4052 | 25.3931 | 25.3801 | 25.3667 | 25.3069 | 25.2337 | 18.2818 | 17.112 | 23.8766 | 23.8622 | 23.8455 | 23.8267 | 23.806 | 23.7836 | 23.7596 | 23.7343 | 23.7072 | 23.6794 | 23.5547 | 23.402 | 18.4633 | 17.248
| MENZIESHILL | ST |  |  |  | 29.456 | 29.4376 | 29.4038 | 29.3566 | 29.3117 | 29.2641 | 29.2168 | 29.1697 | 29.1197 | 29.0653 | 28.9492 | 28.7568 | 28.5816 | 28.4092 | 25.4705 | 25.4681 | 25.4649 | 25.4618 | 25.4588 | 25.4551 | 25.4516 | 25.4481 | 25.4449 | 25.4403 | 25.4153 | 25.3916 | 25.3705 | 25.3483 | 23.8957 | 23.8907 | 23.8841 | 23.8776 | 23.8713 | 23.8637 | 23.8562 | 23.849 | 23.8424 | 23.8328 | 23.7806 | 23.7312 | 23.6873 | 23.641
| MENZIESHILL | FS |  |  |  | 29.4564 | 29.4457 | 29.4338 | 29.4114 | 29.3919 | 29.3694 | 29.347 | 29.3215 | 29.2959 | 29.27 | 29.2192 | 29.0871 | 28.9627 | 28.854 | 25.4681 | 25.4649 | 25.4617 | 25.457 | 25.4524 | 25.4478 | 25.4432 | 25.4388 | 25.4344 | 25.43 | 25.4215 | 25.3962 | 25.3701 | 25.3449 | 23.8907 | 23.8841 | 23.8775 | 23.8676 | 23.8579 | 23.8483 | 23.8389 | 23.8296 | 23.8204 | 23.8113 | 23.7936 | 23.7408 | 23.6864 | 23.6339
KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 1.9167 | 1.8358 | 1.7321 | 1.6312 | 1.5334 | 1.438 | 1.3462 | 1.2581 | 1.2057 | 0.35091 | 0.2393 | -0.55074 | -1.2866 | -1.5728 | 1.7397 | 1.6583 | 1.5398 | 1.4196 | 1.3019 | 1.1854 | 1.0727 | 0.96376 | 0.88465 | 0.17296 | 0.064218 | -0.60827 | -1.238 | -1.5695 | 1.7537 | 1.6504 | 1.5058 | 1.3609 | 1.2205 | 1.0847 | 0.95334 | 0.82666 | 0.73865 | -0.15039 | -0.26416 | -1.0628 | -1.8069 | -2.0982
| METHLICK | CT |  |  |  | 1.9167 | 1.8358 | 1.7321 | 1.6312 | 1.5334 | 1.438 | 1.3462 | 1.2581 | 1.2057 | 0.35091 | 0.2393 | -0.55074 | -1.2866 | -1.5728 | 1.7397 | 1.6583 | 1.5398 | 1.4196 | 1.3019 | 1.1854 | 1.0727 | 0.96376 | 0.88465 | 0.17296 | 0.064218 | -0.60827 | -1.238 | -1.5092 | 1.7537 | 1.6504 | 1.5058 | 1.3609 | 1.2205 | 1.0847 | 0.95334 | 0.82666 | 0.73865 | -0.15039 | -0.26416 | -1.0628 | -1.8069 | -2.0982
| METHLICK | LW |  |  |  | 2.0329 | 2.0194 | 2.0039 | 1.9863 | 1.967 | 1.9461 | 1.9238 | 1.9002 | 1.8164 | 0.90458 | 0.73095 | -0.15831 | -1.015 | -1.4415 | 1.8388 | 1.8091 | 1.744 | 1.6653 | 1.586 | 1.5062 | 1.426 | 1.3457 | 1.2569 | 0.53642 | 0.35896 | -0.41523 | -1.1641 | -1.5695 | 1.8869 | 1.8558 | 1.7936 | 1.7189 | 1.643 | 1.5659 | 1.4879 | 1.4093 | 1.3216 | 0.40198 | 0.22443 | -0.6757 | -1.5431 | -1.9771
| METHLICK | ST |  |  |  | 2.0507 | 2.046 | 2.0398 | 2.0338 | 2.0279 | 2.0208 | 2.0139 | 2.0071 | 2.0005 | 1.6339 | 1.6153 | 1.3054 | 0.93982 | 0.79606 | 1.8598 | 1.8492 | 1.8285 | 1.7995 | 1.7659 | 1.7393 | 1.7132 | 1.6876 | 1.6606 | 1.3193 | 1.2623 | 0.91567 | 0.59471 | 0.45044 | 1.9122 | 1.9012 | 1.881 | 1.8536 | 1.8224 | 1.7966 | 1.7713 | 1.7466 | 1.7208 | 1.276 | 1.2195 | 0.80972 | 0.43953 | 0.29271
| METHLICK | FS |  |  |  | 2.046 | 2.0398 | 2.0336 | 2.0245 | 2.0154 | 2.0065 | 1.9977 | 1.989 | 1.9805 | 1.972 | 1.9555 | 1.9063 | 1.8543 | 1.8037 | 1.8587 | 1.8524 | 1.8458 | 1.8311 | 1.8152 | 1.8008 | 1.7866 | 1.7706 | 1.7549 | 1.7395 | 1.7094 | 1.629 | 1.5485 | 1.4715 | 1.9094 | 1.9014 | 1.8932 | 1.8768 | 1.8594 | 1.8434 | 1.8275 | 1.8103 | 1.7932 | 1.7765 | 1.7438 | 1.6546 | 1.564 | 1.477
SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.60063 | 0.60012 | 0.59867 | 0.59684 | 0.59501 | 0.59244 | 0.58642 | 0.58054 | 0.57421 | 0.56803 | 0.55601 | 0.49156 | 0.43729 | 0.4291 | 0.48459 | 0.48411 | 0.48397 | 0.48386 | 0.48375 | 0.48359 | 0.48323 | 0.48287 | 0.48249 | 0.48211 | 0.48139 | 0.47749 | 0.47309 | 0.47309
| MID YELL | CT |  |  |  | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.60064 | 0.60021 | 0.59911 | 0.59782 | 0.59651 | 0.59532 | 0.59412 | 0.59293 | 0.59169 | 0.59052 | 0.58819 | 0.51826 | 0.44766 | 0.43543 | 0.48459 | 0.48419 | 0.484 | 0.48392 | 0.48384 | 0.48377 | 0.48369 | 0.48362 | 0.48355 | 0.48348 | 0.48334 | 0.4791 | 0.47483 | 0.47309
| MID YELL | LW |  |  |  | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.60063 | 0.60012 | 0.59867 | 0.59684 | 0.59501 | 0.59332 | 0.59163 | 0.58996 | 0.5882 | 0.58653 | 0.5832 | 0.49156 | 0.43729 | 0.4291 | 0.48459 | 0.48411 | 0.48397 | 0.48386 | 0.48375 | 0.48365 | 0.48354 | 0.48344 | 0.48334 | 0.48323 | 0.48303 | 0.47749 | 0.47309 | 0.47309
| MID YELL | ST |  |  |  | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.60079 | 0.60059 | 0.60014 | 0.59941 | 0.59854 | 0.59244 | 0.58642 | 0.58054 | 0.57421 | 0.56803 | 0.55601 | 0.52679 | 0.49788 | 0.4691 | 0.48473 | 0.48455 | 0.48412 | 0.48401 | 0.48396 | 0.48359 | 0.48323 | 0.48287 | 0.48249 | 0.48211 | 0.48139 | 0.47962 | 0.47787 | 0.47613
| MID YELL | FS |  |  |  | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.52965 | 0.60088 | 0.60085 | 0.6008 | 0.60058 | 0.60033 | 0.59804 | 0.59577 | 0.59285 | 0.59001 | 0.58721 | 0.5818 | 0.56904 | 0.55709 | 0.54584 | 0.48481 | 0.48478 | 0.48474 | 0.48454 | 0.4843 | 0.48393 | 0.48379 | 0.48362 | 0.48344 | 0.48328 | 0.48295 | 0.48218 | 0.48145 | 0.48077
KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 3.413 | 3.3657 | 3.3187 | 3.2724 | 3.2225 | 3.1731 | 3.0745 | 2.4536 | 1.2165 | 1.0079 | 4.5894 | 4.5745 | 4.5311 | 4.4773 | 3.4238 | 3.3708 | 3.3182 | 3.2665 | 3.2105 | 3.1553 | 3.0449 | 2.4811 | 1.4245 | 1.1742 | 4.5083 | 4.5083 | 4.4874 | 4.4536 | 3.42 | 3.3867 | 3.3537 | 3.3212 | 3.2703 | 3.216 | 3.1077 | 2.4597 | 1.1863 | 0.95694
| MIDMAR | CT |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 3.4565 | 3.4527 | 3.4266 | 3.401 | 3.3733 | 3.346 | 3.2912 | 2.7487 | 1.5906 | 1.4596 | 4.5912 | 4.5815 | 4.5562 | 4.5268 | 3.4975 | 3.4682 | 3.4391 | 3.4104 | 3.3793 | 3.3488 | 3.2875 | 2.8114 | 1.8433 | 1.6966 | 4.5083 | 4.5083 | 4.5032 | 4.4848 | 3.4663 | 3.448 | 3.4296 | 3.4116 | 3.3921 | 3.3729 | 3.3344 | 2.784 | 1.5975 | 1.4534
| MIDMAR | LW |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 3.413 | 3.3657 | 3.3187 | 3.2724 | 3.2225 | 3.1731 | 3.0745 | 2.4536 | 1.2165 | 1.0079 | 4.5894 | 4.5745 | 4.5311 | 4.4773 | 3.4238 | 3.3708 | 3.3182 | 3.2665 | 3.2105 | 3.1553 | 3.0449 | 2.4811 | 1.4245 | 1.1742 | 4.5083 | 4.5083 | 4.4874 | 4.4536 | 3.42 | 3.3867 | 3.3537 | 3.3212 | 3.2703 | 3.216 | 3.1077 | 2.4597 | 1.1863 | 0.95694
| MIDMAR | ST |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4467 | 3.4254 | 3.4046 | 3.3633 | 3.0582 | 2.4474 | 2.3499 | 4.5938 | 4.5882 | 4.5749 | 4.5541 | 3.5289 | 3.5062 | 3.4837 | 3.4616 | 3.4377 | 3.4144 | 3.3682 | 3.0923 | 2.5726 | 2.4635 | 4.5083 | 4.5083 | 4.5083 | 4.5019 | 3.486 | 3.4718 | 3.4576 | 3.4438 | 3.4288 | 3.4141 | 3.3851 | 3.107 | 2.4788 | 2.3716
| MIDMAR | FS |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4565 | 3.4324 | 3.4002 | 4.5963 | 4.5956 | 4.5946 | 4.5887 | 3.5817 | 3.5747 | 3.5677 | 3.5587 | 3.5499 | 3.5413 | 3.5243 | 3.4838 | 3.4455 | 3.4094 | 4.5083 | 4.5083 | 4.5083 | 4.5083 | 3.5083 | 3.5083 | 3.5083 | 3.5048 | 3.4993 | 3.4939 | 3.4832 | 3.4577 | 3.4337 | 3.411
BRIDGE OF DUN | MILL RD MONTROSE | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 13.6238 | 13.6105 | 13.5726 | 13.5668 | 13.5612 | 13.5557 | 13.5503 | 13.545 | 13.5393 | 13.5337 | 13.5225 | 13.4832 | 13.4448 | 13.4448 | 14.7409 | 14.7327 | 14.7092 | 14.6807 | 14.6529 | 14.6257 | 14.6092 | 14.6001 | 14.5902 | 14.5804 | 14.561 | 14.4928 | 14.4252 | 14.3736
| MILL RD MONTROSE | CT |  |  |  | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 13.6238 | 13.6128 | 13.5844 | 13.5701 | 13.5661 | 13.5623 | 13.5585 | 13.5548 | 13.5508 | 13.5469 | 13.5391 | 13.5124 | 13.4857 | 13.4591 | 14.7409 | 14.7341 | 14.7166 | 14.6967 | 14.6773 | 14.6583 | 14.6397 | 14.6216 | 14.6102 | 14.6034 | 14.5898 | 14.5435 | 14.4973 | 14.451
| MILL RD MONTROSE | LW |  |  |  | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 13.6238 | 13.6105 | 13.5726 | 13.5668 | 13.5612 | 13.5557 | 13.5503 | 13.545 | 13.5393 | 13.5337 | 13.5225 | 13.4832 | 13.4448 | 13.4448 | 14.7409 | 14.7327 | 14.7092 | 14.6807 | 14.6529 | 14.6257 | 14.6092 | 14.6001 | 14.5902 | 14.5804 | 14.561 | 14.4928 | 14.4252 | 14.3736
| MILL RD MONTROSE | ST |  |  |  | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 13.6277 | 13.6228 | 13.6113 | 13.5939 | 13.5731 | 13.5689 | 13.5652 | 13.5616 | 13.5577 | 13.5539 | 13.5465 | 13.5281 | 13.5102 | 13.4921 | 14.7433 | 14.7402 | 14.7332 | 14.7224 | 14.7096 | 14.691 | 14.6728 | 14.6551 | 14.6359 | 14.6171 | 14.6027 | 14.5707 | 14.5397 | 14.5083
| MILL RD MONTROSE | FS |  |  |  | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 14.3398 | 13.63 | 13.6292 | 13.6282 | 13.6232 | 13.6173 | 13.6075 | 13.5977 | 13.5853 | 13.573 | 13.5712 | 13.5683 | 13.5612 | 13.5547 | 13.5485 | 14.7447 | 14.7442 | 14.7436 | 14.7405 | 14.7369 | 14.7308 | 14.7248 | 14.7171 | 14.7095 | 14.7021 | 14.6877 | 14.6531 | 14.6209 | 14.6061
ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 22.8372 | 22.5375 | 22.1529 | 21.7752 | 21.4111 | 21.0604 | 20.7233 | 20.3997 | 20.2595 | 20.1898 | 20.0529 | 14.4229 | 12.5399 | 11.1373 | 18.2497 | 18.0564 | 17.818 | 17.6013 | 17.3992 | 17.212 | 13.4118 | 12.9498 | 12.6434 | 12.4003 | 11.9259 | 10.2805 | 7.9316 | 6.158 | 19.1773 | 18.8898 | 18.5207 | 18.1583 | 17.8089 | 17.4724 | 13.7212 | 13.1828 | 12.8385 | 12.5725 | 12.0531 | 10.3131 | 8.0348 | 6.1457
| MILNATHORT | CT |  |  |  | 22.8372 | 22.5375 | 22.1529 | 21.7752 | 21.4111 | 21.0604 | 20.7233 | 20.3997 | 20.2595 | 20.1898 | 20.0529 | 14.4229 | 12.5399 | 11.4147 | 18.2497 | 18.0564 | 17.818 | 17.6013 | 17.3992 | 17.212 | 13.4118 | 12.9498 | 12.6434 | 12.4003 | 11.9259 | 10.3711 | 8.5553 | 7.3561 | 19.1773 | 18.8898 | 18.5207 | 18.1583 | 17.8089 | 17.4724 | 13.7212 | 13.1828 | 12.8385 | 12.5725 | 12.0531 | 10.3131 | 8.2652 | 6.9764
| MILNATHORT | LW |  |  |  | 23.268 | 23.2181 | 23.1604 | 23.0955 | 23.024 | 22.9464 | 22.8637 | 22.7762 | 22.7014 | 22.6244 | 22.466 | 21.7211 | 12.7859 | 11.1373 | 18.5263 | 18.4739 | 18.4108 | 18.3589 | 18.3178 | 18.2733 | 18.2258 | 18.1757 | 13.6264 | 13.2097 | 12.3787 | 10.2805 | 7.9316 | 6.158 | 19.5909 | 19.5429 | 19.4875 | 19.4252 | 19.3566 | 19.2822 | 19.2028 | 19.1189 | 19.0471 | 18.9731 | 12.9417 | 10.6507 | 8.0348 | 6.1457
| MILNATHORT | ST |  |  |  | 23.334 | 23.3168 | 23.2938 | 23.2715 | 23.2497 | 23.2232 | 23.1975 | 23.1725 | 23.1477 | 23.1116 | 23.0423 | 22.7355 | 22.2658 | 22.153 | 18.5811 | 18.5535 | 18.5191 | 18.4894 | 18.4574 | 18.4322 | 18.4174 | 18.4031 | 18.3888 | 18.3681 | 18.3283 | 18.1523 | 12.9046 | 12.1694 | 19.6562 | 19.6392 | 19.6165 | 19.5944 | 19.5732 | 19.5478 | 19.5231 | 19.4991 | 19.4754 | 19.4407 | 19.3742 | 19.0797 | 13.4458 | 12.6669
| MILNATHORT | FS |  |  |  | 23.3168 | 23.2938 | 23.2709 | 23.2369 | 23.2033 | 23.1702 | 23.1376 | 23.1054 | 23.0736 | 23.0423 | 22.9811 | 22.7988 | 22.6507 | 22.5168 | 18.5758 | 18.5556 | 18.5353 | 18.4979 | 18.4685 | 18.4432 | 18.4182 | 18.3925 | 18.3675 | 18.3428 | 18.2945 | 18.1886 | 18.1036 | 18.0268 | 19.6392 | 19.6165 | 19.5938 | 19.5609 | 19.5287 | 19.4969 | 19.4656 | 19.4347 | 19.4043 | 19.3742 | 19.3155 | 19.1406 | 18.9984 | 18.8699
MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | NO | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.7509 | 15.7386 | 15.7038 | 15.6611 | 15.6199 | 15.5776 | 15.5475 | 15.5363 | 15.5237 | 15.5106 | 15.5091 | 15.5091 | 15.5091 | 13.5149 | 15.7548 | 15.75 | 15.7363 | 15.7195 | 15.7032 | 15.6866 | 15.6696 | 15.6542 | 15.6421 | 15.6293 | 15.6071 | 15.6071 | 15.6071 | 13.5683
| MILTON OF CRAIGIE | CT |  |  |  | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.7521 | 15.7437 | 15.7223 | 15.6979 | 15.6739 | 15.65 | 15.6272 | 15.6049 | 15.5799 | 15.5543 | 15.5354 | 15.5091 | 15.5091 | 15.5091 | 15.7553 | 15.752 | 15.7435 | 15.7339 | 15.7245 | 15.7151 | 15.7061 | 15.6974 | 15.6875 | 15.6758 | 15.6534 | 15.6071 | 15.6071 | 15.6071
| MILTON OF CRAIGIE | LW |  |  |  | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.7509 | 15.7386 | 15.7038 | 15.6611 | 15.6199 | 15.5776 | 15.5475 | 15.5363 | 15.5237 | 15.5106 | 15.5091 | 15.5091 | 15.5091 | 13.5149 | 15.7548 | 15.75 | 15.7363 | 15.7195 | 15.7032 | 15.6866 | 15.6696 | 15.6542 | 15.6421 | 15.6293 | 15.6071 | 15.6071 | 15.6071 | 13.5683
| MILTON OF CRAIGIE | ST |  |  |  | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.7547 | 15.7503 | 15.7402 | 15.7248 | 15.7063 | 15.6847 | 15.664 | 15.6438 | 15.6213 | 15.5959 | 15.55 | 15.5167 | 15.5091 | 15.5091 | 15.7563 | 15.7546 | 15.7506 | 15.7445 | 15.7373 | 15.7287 | 15.7206 | 15.7127 | 15.7038 | 15.6938 | 15.6733 | 15.6353 | 15.6071 | 15.6071
| MILTON OF CRAIGIE | FS |  |  |  | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 24.9794 | 15.7567 | 15.756 | 15.7551 | 15.7506 | 15.7456 | 15.7387 | 15.7319 | 15.7231 | 15.7139 | 15.7042 | 15.6851 | 15.637 | 15.5959 | 15.5618 | 15.7571 | 15.7568 | 15.7564 | 15.7547 | 15.7527 | 15.75 | 15.7473 | 15.7438 | 15.7402 | 15.7364 | 15.7289 | 15.71 | 15.6938 | 15.6795
STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | NO | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.0625 | 12.5524 | 17.9792 | 17.9653 | 17.927 | 17.8781 | 17.8291 | 17.7802 | 17.7409 | 17.7351 | 17.7289 | 17.7228 | 17.7106 | 13.3746 | 12.035 | 11.4389 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 10.9795 | 10.3729
| MINTLAW | CT |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.4361 | 13.0484 | 17.9792 | 17.9653 | 17.9297 | 17.8884 | 17.847 | 17.8057 | 17.7641 | 17.7399 | 17.7347 | 17.7296 | 17.7192 | 13.6723 | 12.4781 | 12.0185 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 11.2269 | 10.9627
| MINTLAW | LW |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.0625 | 12.5524 | 17.9804 | 17.9665 | 17.927 | 17.8781 | 17.8291 | 17.7802 | 17.7409 | 17.7351 | 17.7289 | 17.7228 | 17.7106 | 13.3746 | 12.035 | 11.4389 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 10.9795 | 10.3729
| MINTLAW | ST |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.4425 | 14.4553 | 14.4553 | 18.0186 | 17.9813 | 17.9721 | 17.9578 | 17.9405 | 17.9172 | 17.8937 | 17.8707 | 17.846 | 17.8221 | 17.774 | 17.4135 | 17.1454 | 17.1322 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.4532 | 12.076 | 12.076
| MINTLAW | FS |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.0204 | 18.0196 | 17.9852 | 17.9807 | 17.9753 | 17.9673 | 17.9592 | 17.9491 | 17.9392 | 17.9296 | 17.9105 | 17.8647 | 17.8212 | 17.7801 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251
BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 22.6435 | 22.5551 | 22.4417 | 22.3243 | 22.2112 | 22.1022 | 21.9974 | 21.8968 | 21.8326 | 21.8007 | 21.738 | 21.5771 | 21.298 | 21.0976 | 17.8886 | 17.7818 | 17.6359 | 17.509 | 17.4278 | 17.3512 | 17.278 | 17.2077 | 17.1593 | 17.1311 | 17.0764 | 16.9814 | 16.8212 | 13.5029 | 18.3771 | 18.2872 | 18.1717 | 18.0523 | 17.9371 | 17.8262 | 17.7195 | 17.6171 | 17.5518 | 17.5193 | 17.4555 | 17.2918 | 17.0127 | 13.6229
| MONTROSE NORTH | CT |  |  |  | 22.6435 | 22.5551 | 22.4417 | 22.3243 | 22.2112 | 22.1022 | 21.9974 | 21.8968 | 21.8326 | 21.8007 | 21.738 | 21.5771 | 21.298 | 21.0976 | 17.8886 | 17.7818 | 17.6359 | 17.509 | 17.4278 | 17.3512 | 17.278 | 17.2077 | 17.1593 | 17.1311 | 17.0764 | 16.9814 | 16.8212 | 13.5029 | 18.3771 | 18.2872 | 18.1717 | 18.0523 | 17.9371 | 17.8262 | 17.7195 | 17.6171 | 17.5518 | 17.5193 | 17.4555 | 17.2918 | 17.0127 | 13.6229
| MONTROSE NORTH | LW |  |  |  | 22.7705 | 22.7558 | 22.7388 | 22.7197 | 22.6986 | 22.6757 | 22.6513 | 22.6255 | 22.5925 | 22.5584 | 22.4885 | 22.302 | 21.9742 | 21.6841 | 17.994 | 17.9461 | 17.8794 | 17.7997 | 17.7359 | 17.7076 | 17.6849 | 17.6616 | 17.6332 | 17.6043 | 17.5454 | 17.3974 | 17.2092 | 13.5521 | 18.5064 | 18.4914 | 18.4741 | 18.4546 | 18.4332 | 18.4099 | 18.385 | 18.3588 | 18.3252 | 18.2905 | 18.2193 | 18.0296 | 17.6959 | 17.4007
| MONTROSE NORTH | ST |  |  |  | 22.79 | 22.7849 | 22.7782 | 22.7716 | 22.7651 | 22.7573 | 22.7498 | 22.7424 | 22.7347 | 22.7235 | 22.7019 | 22.642 | 22.5362 | 22.4646 | 18.0167 | 17.995 | 17.972 | 17.9417 | 17.9067 | 17.861 | 17.8189 | 17.7803 | 17.7562 | 17.7393 | 17.7155 | 17.6545 | 17.5654 | 17.4975 | 18.5262 | 18.521 | 18.5141 | 18.5074 | 18.5009 | 18.493 | 18.4852 | 18.4777 | 18.4699 | 18.4585 | 18.4365 | 18.3756 | 18.2679 | 18.195
| MONTROSE NORTH | FS |  |  |  | 22.7849 | 22.7782 | 22.7714 | 22.7614 | 22.7515 | 22.7417 | 22.7321 | 22.7226 | 22.7132 | 22.704 | 22.6859 | 22.6322 | 22.574 | 22.5171 | 18.0172 | 18.0034 | 17.9936 | 17.9767 | 17.9585 | 17.9367 | 17.9171 | 17.8946 | 17.8724 | 17.8506 | 17.8088 | 17.7029 | 17.6503 | 17.6068 | 18.521 | 18.5141 | 18.5073 | 18.4971 | 18.487 | 18.4771 | 18.4673 | 18.4576 | 18.4481 | 18.4387 | 18.4203 | 18.3656 | 18.3063 | 18.2484
TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | NO | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 2.4498 | 3.4606 | 3.4567 | 3.4454 | 3.4315 | 3.4242 | 3.4231 | 3.422 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 2.2833 | 1.9064 | 1.6556 | 3.4476 | 3.447 | 3.4453 | 3.4433 | 3.4412 | 3.4392 | 3.4372 | 3.4352 | 3.433 | 3.4309 | 3.4267 | 3.4117 | 2.1491 | 1.8955
| MOSSAT | CT |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 3.67 | 3.4606 | 3.4573 | 3.4486 | 3.4386 | 3.4286 | 3.4243 | 3.4235 | 3.4227 | 3.4218 | 3.4217 | 3.4217 | 2.4158 | 2.1156 | 1.9553 | 3.4476 | 3.4471 | 3.4458 | 3.4443 | 3.4429 | 3.4414 | 3.4399 | 3.4385 | 3.4369 | 3.4354 | 3.4323 | 3.4161 | 2.3563 | 2.2019
| MOSSAT | LW |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 2.4498 | 3.4606 | 3.4567 | 3.4454 | 3.4315 | 3.4242 | 3.4231 | 3.422 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 2.2833 | 1.9064 | 1.6556 | 3.4476 | 3.447 | 3.4453 | 3.4433 | 3.4412 | 3.4392 | 3.4372 | 3.4352 | 3.433 | 3.4309 | 3.4267 | 3.4117 | 2.1491 | 1.8955
| MOSSAT | ST |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.7647 | 3.7647 | 3.4618 | 3.4603 | 3.4568 | 3.4513 | 3.4447 | 3.4298 | 3.424 | 3.4228 | 3.4217 | 3.4217 | 3.4217 | 2.4435 | 2.269 | 2.164 | 3.4478 | 3.4476 | 3.447 | 3.4462 | 3.4452 | 3.443 | 3.4408 | 3.4387 | 3.4364 | 3.4341 | 3.4297 | 3.4189 | 3.3138 | 2.4315
| MOSSAT | FS |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.4625 | 3.4622 | 3.4619 | 3.4603 | 3.4584 | 3.4535 | 3.4487 | 3.4425 | 3.4364 | 3.4304 | 3.4243 | 3.422 | 3.4217 | 3.4217 | 3.4479 | 3.4478 | 3.4478 | 3.4476 | 3.4473 | 3.4466 | 3.4458 | 3.4449 | 3.444 | 3.4431 | 3.4414 | 3.4373 | 3.4334 | 3.4298
THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 17.4491 | 17.3481 | 17.2184 | 17.0936 | 16.9733 | 16.8574 | 16.746 | 16.6391 | 16.5877 | 16.5621 | 16.5118 | 16.3887 | 14.8368 | 14.5143 | 16.9239 | 16.8362 | 16.7189 | 16.6042 | 16.4931 | 16.3859 | 16.2823 | 16.1824 | 16.1119 | 16.0615 | 15.9975 | 15.9297 | 14.8004 | 14.4741 | 17.0708 | 16.9605 | 16.8162 | 16.6764 | 16.5413 | 16.411 | 16.2855 | 16.1832 | 16.1294 | 16.0994 | 16.047 | 14.7112 | 14.3664 | 14.0242
| MOUNT PLEASANT | CT |  |  |  | 17.4491 | 17.3481 | 17.2184 | 17.0936 | 16.9733 | 16.8574 | 16.746 | 16.6391 | 16.5877 | 16.5621 | 16.5118 | 16.3887 | 14.8368 | 14.5143 | 16.9239 | 16.8362 | 16.7189 | 16.6042 | 16.4931 | 16.3859 | 16.2823 | 16.1824 | 16.1119 | 16.0615 | 15.9975 | 15.9297 | 14.8004 | 14.4741 | 17.0708 | 16.9605 | 16.8162 | 16.6764 | 16.5413 | 16.411 | 16.2855 | 16.1832 | 16.1294 | 16.0994 | 16.047 | 14.7112 | 14.3664 | 14.0242
| MOUNT PLEASANT | LW |  |  |  | 17.5944 | 17.5776 | 17.5582 | 17.5363 | 17.5121 | 17.486 | 17.4581 | 17.4286 | 17.4005 | 17.3715 | 17.3119 | 17.1531 | 16.9924 | 14.9376 | 17.0448 | 17.0263 | 16.9972 | 16.9629 | 16.9266 | 16.8889 | 16.8497 | 16.8093 | 16.7492 | 16.6867 | 16.6017 | 16.3507 | 16.2622 | 14.6774 | 17.2265 | 17.206 | 17.1779 | 17.1454 | 17.1104 | 17.0734 | 17.0345 | 16.994 | 16.9433 | 16.8907 | 16.8069 | 16.6316 | 14.9218 | 14.435
| MOUNT PLEASANT | ST |  |  |  | 17.6167 | 17.6109 | 17.6031 | 17.5956 | 17.5883 | 17.5793 | 17.5707 | 17.5622 | 17.5541 | 17.5421 | 17.5192 | 17.466 | 17.4181 | 17.3718 | 17.0652 | 17.0597 | 17.0519 | 17.0436 | 17.0348 | 17.0106 | 16.9868 | 16.9634 | 16.9279 | 16.8882 | 16.833 | 16.6991 | 16.5843 | 16.4809 | 17.2515 | 17.2449 | 17.2358 | 17.2266 | 17.2172 | 17.1982 | 17.1796 | 17.1613 | 17.1365 | 17.107 | 17.0621 | 16.9548 | 16.902 | 16.8546
| MOUNT PLEASANT | FS |  |  |  | 17.6109 | 17.6031 | 17.5954 | 17.5839 | 17.5726 | 17.5615 | 17.5505 | 17.5396 | 17.5289 | 17.5183 | 17.4977 | 17.4362 | 17.3808 | 17.3292 | 17.0606 | 17.0541 | 17.0475 | 17.0374 | 17.0273 | 17.0126 | 16.998 | 16.9821 | 16.9619 | 16.9414 | 16.9103 | 16.8252 | 16.7477 | 16.6746 | 17.2454 | 17.237 | 17.2286 | 17.216 | 17.2035 | 17.1885 | 17.1737 | 17.1582 | 17.1404 | 17.1225 | 17.0925 | 17.0076 | 16.9306 | 16.8583
BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.698 | 30.6647 | 30.5928 | 30.539 | 30.5229 | 30.5089 | 30.495 | 30.4768 | 30.457 | 30.4373 | 30.3974 | 30.3128 | 30.2477 | 30.1839 | 31.2558 | 31.2453 | 31.2227 | 31.195 | 31.1671 | 31.1428 | 31.1187 | 31.0871 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
| MUIR OF ORD | CT |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.6992 | 30.6718 | 30.6179 | 30.5563 | 30.5368 | 30.5268 | 30.5167 | 30.503 | 30.4879 | 30.473 | 30.4421 | 30.3816 | 30.3304 | 30.281 | 31.2562 | 31.2476 | 31.2306 | 31.2112 | 31.1911 | 31.1739 | 31.1564 | 31.1325 | 31.1063 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
| MUIR OF ORD | LW |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.698 | 30.6647 | 30.5928 | 30.539 | 30.5229 | 30.5089 | 30.495 | 30.4768 | 30.457 | 30.4373 | 30.3974 | 30.3128 | 30.2477 | 30.1839 | 31.2558 | 31.2453 | 31.2227 | 31.195 | 31.1671 | 31.1428 | 31.1187 | 31.0871 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
| MUIR OF ORD | ST |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.7117 | 30.6969 | 30.6728 | 30.6381 | 30.5961 | 30.5618 | 30.543 | 30.5342 | 30.5245 | 30.5148 | 30.4946 | 30.4582 | 30.4294 | 30.4015 | 31.2601 | 31.2555 | 31.2479 | 31.2369 | 31.2237 | 31.2129 | 31.2019 | 31.1867 | 31.1698 | 31.1531 | 31.1181 | 31.0812 | 31.0812 | 31.0812
| MUIR OF ORD | FS |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.7217 | 30.7157 | 30.7103 | 30.698 | 30.6842 | 30.6723 | 30.6604 | 30.6401 | 30.6193 | 30.5987 | 30.5558 | 30.5309 | 30.5189 | 30.5091 | 31.2633 | 31.2614 | 31.2597 | 31.2558 | 31.2515 | 31.2477 | 31.244 | 31.2376 | 31.231 | 31.2245 | 31.211 | 31.1809 | 31.1601 | 31.1431
BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1403 | 7.1346 | 7.1309 | 7.1264 | 7.1221 | 7.1179 | 7.1137 | 7.1087 | 7.1031 | 7.1016 | 7.0987 | 7.0852 | 5.9765 | 5.7904 | 7.3634 | 7.3616 | 7.3604 | 7.359 | 7.3577 | 7.3563 | 7.355 | 7.3534 | 7.3507 | 7.3481 | 7.343 | 7.3195 | 7.2898 | 7.2805
| MUIREND | CT |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1405 | 7.1357 | 7.1329 | 7.1299 | 7.1268 | 7.1232 | 7.1192 | 7.116 | 7.1125 | 7.1094 | 7.1037 | 7.093 | 7.0818 | 7.0707 | 7.3635 | 7.3619 | 7.3611 | 7.3601 | 7.3591 | 7.358 | 7.3568 | 7.3557 | 7.3546 | 7.3537 | 7.3517 | 7.3331 | 7.3136 | 7.2945
| MUIREND | LW |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1403 | 7.1346 | 7.1309 | 7.1264 | 7.1221 | 7.1179 | 7.1137 | 7.1096 | 7.1051 | 7.1033 | 7.1017 | 7.0852 | 5.9765 | 5.7904 | 7.3634 | 7.3616 | 7.3604 | 7.359 | 7.3577 | 7.3563 | 7.355 | 7.3537 | 7.3523 | 7.3509 | 7.3482 | 7.3195 | 7.2898 | 7.2805
| MUIREND | ST |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.142 | 7.1389 | 7.1377 | 7.1361 | 7.134 | 7.1254 | 7.1168 | 7.1087 | 7.1031 | 7.1016 | 7.0987 | 7.0915 | 7.084 | 7.0767 | 7.3639 | 7.3629 | 7.3626 | 7.3621 | 7.3614 | 7.3587 | 7.356 | 7.3534 | 7.3507 | 7.3481 | 7.343 | 7.3305 | 7.3176 | 7.3048
| MUIREND | FS |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1433 | 7.1415 | 7.1413 | 7.1406 | 7.1399 | 7.1371 | 7.1344 | 7.1309 | 7.1274 | 7.1241 | 7.1176 | 7.1036 | 7.101 | 7.0984 | 7.3644 | 7.3638 | 7.3637 | 7.3635 | 7.3633 | 7.3624 | 7.3615 | 7.3604 | 7.3593 | 7.3583 | 7.3563 | 7.3515 | 7.3469 | 7.3424
NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 23.6127 | 23.6069 | 23.591 | 23.5787 | 23.5667 | 23.5549 | 23.5426 | 23.5293 | 23.5161 | 23.5029 | 23.4779 | 23.437 | 23.437 | 23.437 | 19.6835 | 19.6295 | 19.5122 | 19.4479 | 19.3848 | 19.3233 | 19.2592 | 19.1896 | 19.1204 | 19.0515 | 18.9208 | 18.5168 | 18.1742 | 13.7154 | 20.0575 | 20.048 | 20.0227 | 20.0031 | 19.9837 | 19.9649 | 19.9453 | 19.924 | 19.9028 | 19.8817 | 19.8417 | 19.718 | 19.5885 | 19.4623
| NAIRN CENTRAL | CT |  |  |  | 23.6127 | 23.6073 | 23.5935 | 23.5837 | 23.574 | 23.5642 | 23.5531 | 23.5409 | 23.5298 | 23.5187 | 23.4979 | 23.4383 | 23.437 | 23.437 | 19.6835 | 19.6331 | 19.5248 | 19.474 | 19.4232 | 19.3717 | 19.3141 | 19.2504 | 19.1919 | 19.1341 | 19.0256 | 18.7139 | 18.3867 | 18.1742 | 20.0575 | 20.0487 | 20.0266 | 20.011 | 19.9955 | 19.9797 | 19.9621 | 19.9426 | 19.9247 | 19.907 | 19.8738 | 19.7783 | 19.6782 | 19.5798
| NAIRN CENTRAL | LW |  |  |  | 23.6129 | 23.6069 | 23.591 | 23.5787 | 23.5667 | 23.5549 | 23.5426 | 23.5293 | 23.5161 | 23.5029 | 23.4779 | 23.437 | 23.437 | 23.437 | 19.6848 | 19.6295 | 19.5122 | 19.4479 | 19.3848 | 19.3233 | 19.2592 | 19.1896 | 19.1204 | 19.0515 | 18.9208 | 18.5168 | 18.1742 | 13.7154 | 20.0577 | 20.048 | 20.0227 | 20.0031 | 19.9837 | 19.9649 | 19.9453 | 19.924 | 19.9028 | 19.8817 | 19.8417 | 19.718 | 19.5885 | 19.4623
| NAIRN CENTRAL | ST |  |  |  | 23.6149 | 23.6121 | 23.6056 | 23.6011 | 23.5955 | 23.5885 | 23.5808 | 23.5723 | 23.5644 | 23.5566 | 23.5422 | 23.5085 | 23.4737 | 23.4393 | 19.7032 | 19.6774 | 19.618 | 19.5762 | 19.5356 | 19.499 | 19.4585 | 19.414 | 19.3728 | 19.3323 | 19.2572 | 19.081 | 18.8987 | 18.719 | 20.0609 | 20.0564 | 20.046 | 20.0388 | 20.0299 | 20.0187 | 20.0063 | 19.9927 | 19.98 | 19.9677 | 19.9447 | 19.8907 | 19.8349 | 19.7799
| NAIRN CENTRAL | FS |  |  |  | 23.6305 | 23.6152 | 23.6129 | 23.6114 | 23.6097 | 23.6072 | 23.6047 | 23.6013 | 23.5982 | 23.5951 | 23.5893 | 23.5766 | 23.5641 | 23.5519 | 19.846 | 19.7056 | 19.6848 | 19.6712 | 19.6555 | 19.633 | 19.6095 | 19.5787 | 19.5501 | 19.5336 | 19.503 | 19.4366 | 19.3716 | 19.3077 | 20.1245 | 20.0613 | 20.0577 | 20.0553 | 20.0526 | 20.0487 | 20.0446 | 20.0392 | 20.0342 | 20.0293 | 20.0199 | 19.9996 | 19.9797 | 19.9601
STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | NO | 5.0737 | 5.0211 | 4.9535 | 4.8905 | 4.8297 | 4.7712 | 4.7149 | 4.6609 | 4.6303 | 4.6151 | 4.5853 | 4.371 | 3.9365 | 3.8142 | 5.1187 | 5.0946 | 5.0632 | 5.0336 | 5.005 | 4.9276 | 4.8477 | 4.7703 | 4.7123 | 4.6692 | 4.5825 | 4.2309 | 3.6732 | 3.4065 | 4.9323 | 4.8634 | 4.7628 | 4.6627 | 4.5645 | 4.4686 | 4.3748 | 4.284 | 4.2177 | 4.1699 | 4.0739 | 3.6674 | 3.0079 | 2.7125
| NEW PITSLIGO | CT |  |  |  | 5.0737 | 5.0211 | 4.9535 | 4.8905 | 4.8297 | 4.7712 | 4.7149 | 4.6609 | 4.6303 | 4.6151 | 4.5853 | 4.371 | 3.9365 | 3.8142 | 5.1187 | 5.0946 | 5.0632 | 5.0336 | 5.005 | 4.9276 | 4.8477 | 4.7703 | 4.7123 | 4.6692 | 4.5825 | 4.2309 | 3.6732 | 3.4065 | 4.9323 | 4.8634 | 4.7628 | 4.6627 | 4.5645 | 4.4686 | 4.3748 | 4.284 | 4.2177 | 4.1699 | 4.0739 | 3.6674 | 3.0079 | 2.7125
| NEW PITSLIGO | LW |  |  |  | 5.1494 | 5.1406 | 5.1305 | 5.1191 | 5.1065 | 5.0929 | 5.0784 | 5.063 | 5.0458 | 5.0282 | 4.9918 | 4.7521 | 4.2831 | 4.1238 | 5.1528 | 5.1485 | 5.1428 | 5.1363 | 5.1292 | 5.1216 | 5.1135 | 5.1051 | 5.066 | 5.0151 | 4.9114 | 4.4917 | 3.8584 | 3.5093 | 5.0206 | 5.0029 | 4.9674 | 4.923 | 4.8764 | 4.828 | 4.7781 | 4.7276 | 4.6723 | 4.6171 | 4.5046 | 4.0216 | 3.273 | 2.8859
| NEW PITSLIGO | ST |  |  |  | 5.161 | 5.1579 | 5.1539 | 5.15 | 5.1461 | 5.1415 | 5.137 | 5.1326 | 5.1285 | 5.1224 | 5.1109 | 5.0081 | 4.8009 | 4.7496 | 5.1622 | 5.1568 | 5.1549 | 5.153 | 5.1512 | 5.1484 | 5.1456 | 5.1429 | 5.1402 | 5.1367 | 5.1299 | 5.0573 | 4.7888 | 4.6607 | 5.1242 | 5.0339 | 5.0283 | 5.0217 | 5.0141 | 4.9927 | 4.9712 | 4.9499 | 4.9275 | 4.9034 | 4.8553 | 4.6515 | 4.3289 | 4.1874
| NEW PITSLIGO | FS |  |  |  | 5.1579 | 5.1539 | 5.1499 | 5.1439 | 5.138 | 5.1322 | 5.1265 | 5.1208 | 5.1152 | 5.1097 | 5.099 | 5.067 | 5.0336 | 5.0012 | 5.1608 | 5.159 | 5.1531 | 5.1503 | 5.1476 | 5.1447 | 5.1419 | 5.139 | 5.1362 | 5.1334 | 5.128 | 5.1121 | 5.0956 | 5.0797 | 5.1214 | 5.1177 | 5.0242 | 5.0152 | 5.0057 | 4.9938 | 4.9818 | 4.9686 | 4.9553 | 4.9423 | 4.9165 | 4.8466 | 4.7762 | 4.7083
DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.057313 | 0.05715 | 0.056679 | 0.056104 | 0.055767 | 0.055477 | 0.055193 | 0.054916 | 0.054616 | 0.054319 | 0.05373 | 0.053258 | 0.053258 | -0.012366 | 0.066377 | 0.066298 | 0.066177 | 0.066072 | 0.065969 | 0.065868 | 0.065769 | 0.065673 | 0.065568 | 0.065465 | 0.06526 | 0.064773 | 0.064773 | -0.0082225
| NEWTON | CT |  |  |  | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.057313 | 0.057177 | 0.056824 | 0.056421 | 0.056027 | 0.05582 | 0.055621 | 0.055428 | 0.055218 | 0.055009 | 0.054597 | 0.053258 | 0.053258 | -0.012366 | 0.066377 | 0.066311 | 0.066204 | 0.06613 | 0.066058 | 0.065987 | 0.065918 | 0.065851 | 0.065778 | 0.065705 | 0.065562 | 0.064773 | 0.064773 | -0.0082225
| NEWTON | LW |  |  |  | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.057313 | 0.05715 | 0.056679 | 0.056104 | 0.055767 | 0.055477 | 0.055193 | 0.054916 | 0.054616 | 0.054319 | 0.05373 | 0.053258 | 0.053258 | 0.053258 | 0.066377 | 0.066298 | 0.066177 | 0.066072 | 0.065969 | 0.065868 | 0.065769 | 0.065673 | 0.065568 | 0.065465 | 0.06526 | 0.064773 | 0.064773 | 0.064773
| NEWTON | ST |  |  |  | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.057361 | 0.057301 | 0.057159 | 0.056938 | 0.056675 | 0.056409 | 0.056149 | 0.055954 | 0.05581 | 0.055669 | 0.055394 | 0.054734 | 0.054089 | 0.053442 | 0.0664 | 0.066371 | 0.066302 | 0.066225 | 0.066176 | 0.066128 | 0.06608 | 0.066034 | 0.065984 | 0.065935 | 0.065839 | 0.065609 | 0.065385 | 0.06516
| NEWTON | FS |  |  |  | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.10228 | 0.057389 | 0.057382 | 0.057372 | 0.05731 | 0.057236 | 0.057147 | 0.05706 | 0.056947 | 0.056836 | 0.056728 | 0.056517 | 0.056017 | 0.055774 | 0.055551 | 0.066414 | 0.06641 | 0.066405 | 0.066375 | 0.06634 | 0.066297 | 0.066254 | 0.066226 | 0.066206 | 0.066186 | 0.066147 | 0.066056 | 0.065971 | 0.065893
REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | NO | 23.2964 | 23.284 | 23.2486 | 23.205 | 23.1617 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 13.4636 | 12.4206 | 19.6333 | 19.5411 | 19.2852 | 19.1339 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 13.3951 | 12.3028 | 10.9398 | 8.946 | 7.608 | 20.0486 | 20.0251 | 19.9575 | 19.8742 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.2164 | 11.8887 | 9.7313 | 8.428
| NEWTONHILL | CT |  |  |  | 23.2964 | 23.2859 | 23.2589 | 23.2278 | 23.197 | 23.1664 | 23.1359 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.3773 | 22.3773 | 19.6333 | 19.5552 | 19.3536 | 19.179 | 19.1182 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 12.8752 | 11.3207 | 10.4136 | 20.0486 | 20.0287 | 19.9772 | 19.9179 | 19.859 | 19.8005 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.7739 | 12.0444 | 11.1608
| NEWTONHILL | LW |  |  |  | 23.2964 | 23.284 | 23.2486 | 23.205 | 23.1617 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 13.4636 | 12.4206 | 19.6335 | 19.5411 | 19.2852 | 19.1339 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 13.3951 | 12.3028 | 10.9398 | 8.946 | 7.608 | 20.0487 | 20.0251 | 19.9575 | 19.8742 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.2164 | 11.8887 | 9.7313 | 8.428
| NEWTONHILL | ST |  |  |  | 23.3223 | 23.2954 | 23.2845 | 23.2676 | 23.2473 | 23.2368 | 23.2263 | 23.216 | 23.2049 | 23.1942 | 23.1727 | 23.1354 | 22.7563 | 22.7563 | 19.827 | 19.6259 | 19.545 | 19.4187 | 19.2775 | 19.214 | 19.176 | 19.1557 | 19.1339 | 19.1127 | 19.0703 | 19.0587 | 18.8394 | 18.8394 | 20.0981 | 20.0467 | 20.0261 | 19.9938 | 19.955 | 19.935 | 19.915 | 19.8954 | 19.8741 | 19.8536 | 19.8126 | 19.7932 | 19.4015 | 19.4015
| NEWTONHILL | FS |  |  |  | 23.3244 | 23.3237 | 23.3005 | 23.2955 | 23.2896 | 23.2861 | 23.2827 | 23.2784 | 23.2741 | 23.27 | 23.2618 | 23.2422 | 23.2236 | 23.206 | 19.8428 | 19.8375 | 19.6642 | 19.627 | 19.5826 | 19.557 | 19.5311 | 19.499 | 19.4672 | 19.4364 | 19.3751 | 19.2464 | 19.1706 | 19.1359 | 20.1021 | 20.1008 | 20.0565 | 20.047 | 20.0357 | 20.0291 | 20.0225 | 20.0143 | 20.0062 | 19.9983 | 19.9827 | 19.9452 | 19.9097 | 19.8762
ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 7.9671 | 7.9671 | 7.967 | 7.967 | 7.967 | 7.9669 | 7.9669 | 7.9669 | 7.9668 | 7.9668 | 7.9667 | 7.9665 | 7.9664 | 7.9662
| NIGG | CT |  |  |  | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 7.9671 | 7.9671 | 7.967 | 7.967 | 7.967 | 7.967 | 7.9669 | 7.9669 | 7.9669 | 7.9669 | 7.9668 | 7.9667 | 7.9666 | 7.9664
| NIGG | LW |  |  |  | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 7.9671 | 7.9671 | 7.967 | 7.967 | 7.967 | 7.9669 | 7.9669 | 7.9669 | 7.9668 | 7.9668 | 7.9667 | 7.9665 | 7.9664 | 7.9662
| NIGG | ST |  |  |  | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.967 | 7.967 | 7.967 | 7.967 | 7.967 | 7.967 | 7.9669 | 7.9668 | 7.9668 | 7.9667
| NIGG | FS |  |  |  | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.0523 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 8.1433 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.9671 | 7.967 | 7.967 | 7.967 | 7.967 | 7.967 | 7.9669
CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | NO | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 18.2437 | 18.2262 | 18.1951 | 18.1639 | 18.1333 | 18.1027 | 18.0726 | 18.0492 | 18.0321 | 18.0149 | 17.9803 | 17.8752 | 17.7724 | 17.7067 | 18.1274 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257
| NINEWELLS | CT |  |  |  | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 18.245 | 18.2318 | 18.2118 | 18.1948 | 18.1774 | 18.1591 | 18.1401 | 18.122 | 18.1033 | 18.0845 | 18.0513 | 17.9758 | 17.9023 | 17.8316 | 18.1285 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257
| NINEWELLS | LW |  |  |  | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 18.2437 | 18.2262 | 18.1951 | 18.1639 | 18.1333 | 18.1027 | 18.0726 | 18.0492 | 18.0321 | 18.0149 | 17.9803 | 17.8752 | 17.7724 | 17.7067 | 18.1274 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257
| NINEWELLS | ST |  |  |  | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 18.248 | 18.2392 | 18.2271 | 18.2139 | 18.1977 | 18.1785 | 18.1591 | 18.1405 | 18.121 | 18.1016 | 18.0631 | 18.0104 | 17.9636 | 17.9182 | 18.1313 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257
| NINEWELLS | FS |  |  |  | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 19.4771 | 18.2514 | 18.2477 | 18.2449 | 18.241 | 18.2365 | 18.2302 | 18.2241 | 18.2165 | 18.2089 | 18.2013 | 18.1865 | 18.1514 | 18.1194 | 18.0901 | 18.1343 | 18.131 | 18.1284 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257 | 18.1257
THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.023607 | 0.023489 | 0.023151 | 0.022734 | 0.022325 | 0.021972 | 0.021677 | 0.02139 | 0.021267 | 0.021191 | 0.021063 | 0.021063 | 0.021063 | -0.001247 | 0.026632 | 0.026575 | 0.026411 | 0.026208 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193
| NORTH HOY | CT |  |  |  | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.023608 | 0.023509 | 0.023255 | 0.022962 | 0.022673 | 0.022387 | 0.022118 | 0.021915 | 0.021686 | 0.021463 | 0.021256 | 0.021063 | 0.021063 | 0.021063 | 0.026633 | 0.026585 | 0.026461 | 0.026319 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193
| NORTH HOY | LW |  |  |  | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.023607 | 0.023489 | 0.023151 | 0.022734 | 0.022325 | 0.021972 | 0.021677 | 0.02139 | 0.021267 | 0.021191 | 0.021063 | 0.021063 | 0.021063 | -0.001247 | 0.026632 | 0.026575 | 0.026411 | 0.026208 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193
| NORTH HOY | ST |  |  |  | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.023642 | 0.023598 | 0.023494 | 0.023332 | 0.023139 | 0.022949 | 0.022767 | 0.02259 | 0.022389 | 0.022196 | 0.021894 | 0.021298 | 0.021137 | 0.021063 | 0.026649 | 0.026628 | 0.026577 | 0.026499 | 0.026405 | 0.026313 | 0.026224 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193 | 0.026193
| NORTH HOY | FS |  |  |  | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.043134 | 0.023663 | 0.023656 | 0.023647 | 0.023601 | 0.023546 | 0.023482 | 0.02342 | 0.023341 | 0.023261 | 0.023183 | 0.023031 | 0.022665 | 0.022325 | 0.022036 | 0.026659 | 0.026656 | 0.026652 | 0.026629 | 0.026603 | 0.026572 | 0.026542 | 0.026503 | 0.026464 | 0.026426 | 0.026352 | 0.026193 | 0.026193 | 0.026193
PERSLEY | NORTHFIELD | MINIMUM HEADROOM | NJ 90728 08364 | NO | NO | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4477 | 17.4424 | 17.4301 | 17.4162 | 17.4025 | 17.389 | 17.3755 | 17.3621 | 17.3477 | 17.3336 | 17.301 | 17.0727 | 16.9037 | 16.9037 | 16.712 | 16.7099 | 16.7051 | 16.6996 | 16.6942 | 16.6889 | 16.6836 | 16.6783 | 16.6726 | 16.6671 | 16.6543 | 16.5751 | 16.5142 | 16.479
| NORTHFIELD | CT |  |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4477 | 17.4424 | 17.4301 | 17.4162 | 17.4025 | 17.389 | 17.3755 | 17.3621 | 17.3477 | 17.3336 | 17.3052 | 17.0867 | 16.9107 | 16.9037 | 16.712 | 16.7099 | 16.7051 | 16.6996 | 16.6942 | 16.6889 | 16.6836 | 16.6783 | 16.6726 | 16.6671 | 16.6559 | 16.5786 | 16.5216 | 16.479
| NORTHFIELD | LW |  |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4484 | 17.4436 | 17.4319 | 17.4177 | 17.4038 | 17.3902 | 17.3767 | 17.3633 | 17.349 | 17.3351 | 17.301 | 17.0727 | 16.9037 | 16.9037 | 16.7123 | 16.7104 | 16.7058 | 16.7002 | 16.6947 | 16.6894 | 16.684 | 16.6788 | 16.6732 | 16.6677 | 16.6543 | 16.5751 | 16.5142 | 16.479
| NORTHFIELD | ST |  |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4503 | 17.449 | 17.447 | 17.4443 | 17.4411 | 17.425 | 17.4091 | 17.3935 | 17.3766 | 17.3601 | 17.3276 | 17.2244 | 17.1218 | 17.0326 | 16.713 | 16.7125 | 16.7117 | 16.7106 | 16.7094 | 16.7031 | 16.6968 | 16.6907 | 16.684 | 16.6775 | 16.6648 | 16.6241 | 16.5876 | 16.5631
| NORTHFIELD | FS |  |  |  | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 14.55 | 17.4507 | 17.4502 | 17.4496 | 17.4478 | 17.4458 | 17.4399 | 17.434 | 17.4265 | 17.4191 | 17.4119 | 17.398 | 17.3641 | 17.3269 | 17.2877 | 16.7132 | 16.713 | 16.7127 | 16.712 | 16.7113 | 16.7089 | 16.7066 | 16.7036 | 16.7007 | 16.6979 | 16.6924 | 16.6791 | 16.6645 | 16.649
BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.2451 | 1.2371 | 1.2241 | 1.2202 | 1.2163 | 1.2126 | 1.2088 | 1.2052 | 1.2013 | 1.1973 | 1.1896 | 1.174 | -0.053022 | -0.22682 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | -0.13414 | -0.30741
| NOSTIE BRIDGE | CT |  |  |  | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.2451 | 1.2371 | 1.2241 | 1.2202 | 1.2163 | 1.2126 | 1.2088 | 1.2052 | 1.2013 | 1.1973 | 1.1896 | 1.174 | -0.053022 | -0.22682 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | -0.13414 | -0.30741
| NOSTIE BRIDGE | LW |  |  |  | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.248 | 1.2444 | 1.2341 | 1.2249 | 1.2229 | 1.2208 | 1.2189 | 1.2169 | 1.2148 | 1.2127 | 1.2086 | 1.1875 | 1.166 | -0.20268 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | -0.047751 | -0.28334
| NOSTIE BRIDGE | ST |  |  |  | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.2491 | 1.2477 | 1.2446 | 1.2398 | 1.234 | 1.2252 | 1.2234 | 1.2217 | 1.2198 | 1.2179 | 1.2143 | 1.2056 | 1.1969 | 1.1882 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323
| NOSTIE BRIDGE | FS |  |  |  | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.2497 | 1.2495 | 1.2493 | 1.2479 | 1.2463 | 1.2427 | 1.2391 | 1.2345 | 1.23 | 1.2256 | 1.2242 | 1.2208 | 1.2176 | 1.2146 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323 | 1.1323
TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 32.4189 | 32.4082 | 32.3818 | 32.3497 | 32.3178 | 32.286 | 32.2552 | 32.2272 | 32.1969 | 32.1669 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 28.9446 | 28.8605 | 28.6546 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 20.9516 | 29.2906 | 29.2656 | 29.2042 | 29.1294 | 29.055 | 28.9808 | 28.909 | 28.8437 | 28.7732 | 28.7032 | 28.6484 | 28.6484 | 21.9519 | 20.6967
| OBAN | CT |  |  |  | 32.4191 | 32.41 | 32.3896 | 32.3665 | 32.3431 | 32.3196 | 32.2969 | 32.2763 | 32.2539 | 32.2316 | 32.1882 | 32.1389 | 32.1389 | 32.1389 | 28.946 | 28.8746 | 28.7156 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 29.291 | 29.2697 | 29.2224 | 29.1684 | 29.1139 | 29.059 | 29.0061 | 28.9582 | 28.9061 | 28.854 | 28.7529 | 28.6484 | 28.6484 | 28.6484
| OBAN | LW |  |  |  | 32.4189 | 32.4082 | 32.3818 | 32.3497 | 32.3178 | 32.286 | 32.2552 | 32.2272 | 32.1969 | 32.1669 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 28.9446 | 28.8605 | 28.6546 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 20.9516 | 29.2906 | 29.2656 | 29.2042 | 29.1294 | 29.055 | 28.9808 | 28.909 | 28.8437 | 28.7732 | 28.7032 | 28.6484 | 28.6484 | 21.9519 | 20.6967
| OBAN | ST |  |  |  | 32.4677 | 32.4187 | 32.4099 | 32.3968 | 32.381 | 32.3672 | 32.354 | 32.3423 | 32.3295 | 32.3168 | 32.2927 | 32.2359 | 32.1802 | 32.1389 | 29.3259 | 28.9427 | 28.8742 | 28.7718 | 28.6481 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 29.4042 | 29.29 | 29.2696 | 29.2391 | 29.2023 | 29.1701 | 29.1394 | 29.112 | 29.0822 | 29.0526 | 28.9963 | 28.864 | 28.7342 | 28.6484
| OBAN | FS |  |  |  | 32.4709 | 32.4695 | 32.4361 | 32.4321 | 32.4276 | 32.4228 | 32.4182 | 32.4131 | 32.408 | 32.403 | 32.3934 | 32.3713 | 32.351 | 32.332 | 29.3512 | 29.3404 | 29.0787 | 29.0476 | 29.0121 | 28.975 | 28.9393 | 28.899 | 28.8591 | 28.8202 | 28.7452 | 28.5865 | 28.5811 | 28.5811 | 29.4118 | 29.4085 | 29.3306 | 29.3213 | 29.3107 | 29.2997 | 29.289 | 29.277 | 29.2651 | 29.2535 | 29.2312 | 29.1797 | 29.1323 | 29.0881
MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | NO | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0785 | 14.0542 | 14.0173 | 13.9723 | 13.9354 | 13.897 | 13.8573 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
| OLD CRAIGIE ROAD | CT |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.081 | 14.0643 | 14.0456 | 14.0242 | 14.0084 | 13.991 | 13.973 | 13.9562 | 13.9373 | 13.9146 | 13.8672 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
| OLD CRAIGIE ROAD | LW |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0785 | 14.0542 | 14.0173 | 13.9723 | 13.9354 | 13.897 | 13.8573 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
| OLD CRAIGIE ROAD | ST |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0833 | 14.0709 | 14.0573 | 14.0376 | 14.0185 | 13.987 | 13.9555 | 13.9254 | 13.8922 | 13.8567 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
| OLD CRAIGIE ROAD | FS |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0868 | 14.0813 | 14.0784 | 14.0719 | 14.0666 | 14.0562 | 14.0461 | 14.0333 | 14.02 | 14.0063 | 13.9793 | 13.9137 | 13.857 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 10.5377 | 10.5342 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.2755 | 5.0028 | 4.4639 | 7.1669 | 7.1649 | 7.159 | 7.1517 | 7.1175 | 6.9633 | 6.8089 | 6.6569 | 6.4925 | 6.3313 | 6.0069 | 4.2525 | 3.0501 | 2.4174 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2941 | 7.142 | 6.9897 | 6.8396 | 6.6775 | 6.5184 | 6.1984 | 4.1198 | 2.7474 | 2.1145
| OLDMELDRUM | CT |  |  |  | 10.538 | 10.5355 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.9235 | 5.876 | 5.5072 | 7.1671 | 7.1656 | 7.1619 | 7.1575 | 7.1531 | 7.1487 | 7.1151 | 7.0224 | 6.9222 | 6.8245 | 6.6265 | 5.0742 | 4.0754 | 3.6424 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2917 | 7.2003 | 7.1015 | 7.0051 | 6.8097 | 4.9417 | 3.7729 | 3.3398
| OLDMELDRUM | LW |  |  |  | 10.5377 | 10.5342 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.2755 | 5.0028 | 4.4639 | 7.1669 | 7.1649 | 7.159 | 7.1517 | 7.1175 | 6.9633 | 6.8089 | 6.6569 | 6.4925 | 6.3313 | 6.0069 | 4.2525 | 3.0501 | 2.4174 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2941 | 7.142 | 6.9897 | 6.8396 | 6.6775 | 6.5184 | 6.1984 | 4.1198 | 2.7474 | 2.1145
| OLDMELDRUM | ST |  |  |  | 10.5467 | 10.5369 | 10.5332 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 7.5582 | 7.2409 | 7.2387 | 7.1722 | 7.1665 | 7.1643 | 7.1609 | 7.1567 | 7.1539 | 7.1511 | 7.1483 | 7.1371 | 7.0757 | 6.9523 | 6.0968 | 5.5253 | 5.2373 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3134 | 7.2529 | 7.1311 | 6.1264 | 5.4778 | 5.1897
| OLDMELDRUM | FS |  |  |  | 10.5474 | 10.5472 | 10.5388 | 10.5374 | 10.5357 | 10.5342 | 10.5326 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 7.1726 | 7.1725 | 7.1676 | 7.1667 | 7.1658 | 7.1649 | 7.1639 | 7.1628 | 7.1617 | 7.1606 | 7.1583 | 7.153 | 7.1479 | 7.0917 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2686
THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.6864 | 17.604 | 14.6128 | 17.3165 | 17.3059 | 17.277 | 17.2262 | 17.1913 | 17.1569 | 17.1232 | 17.0718 | 17.0198 | 16.9738 | 16.8775 | 16.7181 | 14.5938 | 14.003 | 17.3203 | 17.318 | 17.3118 | 17.3009 | 17.2934 | 17.2861 | 17.2789 | 17.2679 | 17.256 | 17.2438 | 17.2184 | 16.9641 | 14.5174 | 13.9696
| ORMLIE | CT |  |  |  | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.6864 | 17.604 | 17.604 | 17.3166 | 17.3077 | 17.286 | 17.2473 | 17.223 | 17.1992 | 17.1754 | 17.1357 | 17.0912 | 17.0477 | 16.9676 | 16.7181 | 16.671 | 14.674 | 17.3203 | 17.3184 | 17.3137 | 17.3054 | 17.3002 | 17.2951 | 17.29 | 17.2816 | 17.272 | 17.2627 | 17.2422 | 17.0074 | 14.984 | 14.5916
| ORMLIE | LW |  |  |  | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.6864 | 17.604 | 14.6128 | 17.3165 | 17.3059 | 17.277 | 17.2262 | 17.1913 | 17.1569 | 17.1232 | 17.0718 | 17.0198 | 16.9738 | 16.8775 | 16.7181 | 14.5938 | 14.003 | 17.3203 | 17.318 | 17.3118 | 17.3009 | 17.2934 | 17.2861 | 17.2789 | 17.2679 | 17.256 | 17.2438 | 17.2184 | 16.9641 | 14.5174 | 13.9696
| ORMLIE | ST |  |  |  | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.779 | 17.7379 | 17.7379 | 17.3197 | 17.3155 | 17.3065 | 17.2836 | 17.2674 | 17.2353 | 17.2036 | 17.1617 | 17.115 | 17.0691 | 16.9831 | 16.7773 | 16.7475 | 16.7475 | 17.3209 | 17.32 | 17.3181 | 17.3132 | 17.3097 | 17.3029 | 17.2961 | 17.2871 | 17.2771 | 17.2673 | 17.2463 | 17.1192 | 17.0451 | 17.0103
| ORMLIE | FS |  |  |  | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.8717 | 17.3216 | 17.3208 | 17.3198 | 17.3112 | 17.3064 | 17.2958 | 17.285 | 17.2675 | 17.2498 | 17.2319 | 17.1944 | 17.1221 | 17.0606 | 17.0093 | 17.3213 | 17.3212 | 17.321 | 17.3191 | 17.3181 | 17.3158 | 17.3135 | 17.3098 | 17.306 | 17.3021 | 17.2941 | 17.2786 | 17.2655 | 17.2532
DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 3.4181 | 3.4177 | 3.4168 | 3.4155 | 3.4144 | 3.4132 | 3.4121 | 3.411 | 3.4098 | 3.4086 | 3.4062 | 3.3952 | 3.3842 | 3.3733 | 3.2338 | 3.2321 | 3.2297 | 3.2293 | 3.2289 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008
| OTTER FERRY | CT |  |  |  | 3.4181 | 3.4178 | 3.4171 | 3.4162 | 3.4154 | 3.4146 | 3.4138 | 3.413 | 3.4122 | 3.4113 | 3.4097 | 3.4014 | 3.3929 | 3.3847 | 3.2338 | 3.2324 | 3.2298 | 3.2295 | 3.2293 | 3.229 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008
| OTTER FERRY | LW |  |  |  | 3.4181 | 3.4177 | 3.4168 | 3.4155 | 3.4144 | 3.4132 | 3.4121 | 3.411 | 3.4098 | 3.4086 | 3.4062 | 3.3952 | 3.3842 | 3.3733 | 3.2338 | 3.2321 | 3.2297 | 3.2293 | 3.2289 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008
| OTTER FERRY | ST |  |  |  | 3.4182 | 3.4181 | 3.4178 | 3.4173 | 3.4167 | 3.4157 | 3.4148 | 3.4138 | 3.4128 | 3.4118 | 3.4098 | 3.4051 | 3.4005 | 3.3959 | 3.2343 | 3.2337 | 3.2322 | 3.23 | 3.2297 | 3.2294 | 3.2291 | 3.2288 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2287 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008
| OTTER FERRY | FS |  |  |  | 3.4182 | 3.4182 | 3.4182 | 3.4181 | 3.4179 | 3.4176 | 3.4173 | 3.4168 | 3.4164 | 3.416 | 3.4152 | 3.4134 | 3.4116 | 3.41 | 3.2346 | 3.2345 | 3.2344 | 3.2337 | 3.233 | 3.2314 | 3.2299 | 3.2297 | 3.2296 | 3.2295 | 3.2292 | 3.2287 | 3.2287 | 3.2287 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008 | 3.2008
GLENAGNES | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 52.6634 | 52.6617 | 52.6572 | 52.6493 | 52.6451 | 52.6409 | 52.6368 | 52.6328 | 52.6285 | 52.6241 | 52.6155 | 52.5945 | 52.574 | 52.5539 | 51.3305 | 51.3226 | 51.3013 | 51.2639 | 51.2439 | 51.2242 | 51.205 | 51.1862 | 51.1657 | 51.1449 | 51.1043 | 51.0141 | 50.9775 | 50.9416
| OVERGATE | CT |  |  |  | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 52.6634 | 52.662 | 52.6585 | 52.6523 | 52.6494 | 52.6465 | 52.6436 | 52.6403 | 52.6366 | 52.6333 | 52.6271 | 52.6125 | 52.5983 | 52.5845 | 51.3305 | 51.3239 | 51.3072 | 51.2779 | 51.2644 | 51.2509 | 51.237 | 51.2215 | 51.2039 | 51.1885 | 51.1591 | 51.0902 | 51.0231 | 50.9961
| OVERGATE | LW |  |  |  | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 52.6634 | 52.6617 | 52.6572 | 52.6493 | 52.6451 | 52.6409 | 52.6368 | 52.6328 | 52.6285 | 52.6241 | 52.6155 | 52.5945 | 52.574 | 52.5539 | 51.3305 | 51.3226 | 51.3013 | 51.2639 | 51.2439 | 51.2242 | 51.205 | 51.1862 | 51.1657 | 51.1449 | 51.1043 | 51.0141 | 50.9775 | 50.9416
| OVERGATE | ST |  |  |  | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 52.6719 | 52.663 | 52.6613 | 52.6575 | 52.6556 | 52.6535 | 52.6514 | 52.6491 | 52.6464 | 52.6441 | 52.6397 | 52.6295 | 52.6199 | 52.6104 | 51.3707 | 51.3287 | 51.3208 | 51.3028 | 51.2938 | 51.284 | 51.274 | 51.2629 | 51.2503 | 51.2393 | 51.2185 | 51.1704 | 51.1249 | 51.0801
| OVERGATE | FS |  |  |  | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 49.9028 | 52.6721 | 52.6683 | 52.6679 | 52.6663 | 52.6657 | 52.665 | 52.6642 | 52.6633 | 52.6623 | 52.6614 | 52.6596 | 52.6556 | 52.652 | 52.6488 | 51.3717 | 51.3538 | 51.3518 | 51.3445 | 51.3417 | 51.3381 | 51.3345 | 51.3299 | 51.3256 | 51.3212 | 51.3126 | 51.2937 | 51.2768 | 51.2616
CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | -0.0019453 | 0.0086639 | 0.0086158 | 0.0084774 | 0.0083081 | 0.0081425 | 0.0080157 | 0.0078959 | 0.0078175 | 0.007787 | 0.0077569 | 0.0077318 | -0.001295 | -0.0063952 | -0.011412 | 0.0097752 | 0.0097519 | 0.0096846 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | -0.0046913 | -0.0097096
| OVERSCAIG | CT |  |  |  | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.0086639 | 0.0086239 | 0.00852 | 0.0084015 | 0.0082856 | 0.0081723 | 0.0080768 | 0.0079949 | 0.0079063 | 0.0078269 | 0.0077851 | 0.0077318 | -0.0028739 | -0.0066419 | 0.0097752 | 0.0097558 | 0.0097054 | 0.0096478 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | -0.0012201 | -0.0049381
| OVERSCAIG | LW |  |  |  | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | -0.0019453 | 0.0086639 | 0.0086158 | 0.0084774 | 0.0083081 | 0.0081425 | 0.0080157 | 0.0078959 | 0.0078175 | 0.007787 | 0.0077569 | 0.0077318 | -0.001295 | -0.0063952 | -0.011412 | 0.0097752 | 0.0097519 | 0.0096846 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | -0.0046913 | -0.0097096
| OVERSCAIG | ST |  |  |  | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.0086779 | 0.0086601 | 0.0086184 | 0.0085535 | 0.0084761 | 0.0082502 | 0.0080527 | 0.0078897 | 0.0078017 | 0.0077602 | 0.0077318 | 0.0077318 | -0.00078919 | -0.0029298 | 0.0097821 | 0.0097734 | 0.0097531 | 0.0097216 | 0.009684 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | -0.0012746
| OVERSCAIG | FS |  |  |  | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.015833 | 0.0086862 | 0.0086839 | 0.008681 | 0.0086628 | 0.0086411 | 0.0085673 | 0.0084932 | 0.0083983 | 0.0083049 | 0.0082132 | 0.0080569 | 0.0078081 | 0.0077375 | 0.0077318 | 0.0097861 | 0.009785 | 0.0097835 | 0.0097747 | 0.0097642 | 0.0097283 | 0.0096923 | 0.0096462 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148 | 0.0096148
KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | NO | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.0205 | 7.0161 | 7.0034 | 6.9877 | 6.9722 | 6.9568 | 6.9415 | 6.9265 | 6.9145 | 5.9897 | 5.8705 | 5.6205 | 5.3689 | 5.1223 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 5.8092 | 5.5565 | 5.3088
| PARK | CT |  |  |  | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.0219 | 7.0205 | 7.0168 | 7.0126 | 7.0083 | 7.004 | 6.9996 | 6.9953 | 6.9907 | 6.9862 | 6.9771 | 6.9362 | 5.9928 | 5.843 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101
| PARK | LW |  |  |  | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.0205 | 7.0161 | 7.0034 | 6.9877 | 6.9722 | 6.9568 | 6.9415 | 6.9265 | 6.9145 | 5.9897 | 5.8705 | 5.6205 | 5.3689 | 5.1223 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 5.8092 | 5.5565 | 5.3088
| PARK | ST |  |  |  | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.0215 | 7.0193 | 7.0141 | 7.006 | 6.9962 | 6.9899 | 6.9836 | 6.9774 | 6.9707 | 6.9642 | 6.9513 | 6.92 | 5.9711 | 5.8581 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101
| PARK | FS |  |  |  | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.7748 | 7.0226 | 7.0223 | 7.0219 | 7.0199 | 7.0175 | 7.0154 | 7.0133 | 7.0107 | 7.0082 | 7.0057 | 7.0008 | 6.9891 | 6.978 | 6.9676 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101 | 7.101
ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | YES | YES | 3.7367 | 3.7361 | 3.7344 | 3.7324 | 3.7304 | 3.7284 | 3.7265 | 3.7245 | 3.7224 | 3.7203 | 3.717 | 3.717 | 3.717 | 3.717 | 3.3472 | 3.3444 | 3.3367 | 3.3273 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4514 | 2.2954 | 3.3225 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 2.3734
| PEDDIESTON | CT |  |  |  | 3.7367 | 3.7361 | 3.7347 | 3.7331 | 3.7315 | 3.73 | 3.7284 | 3.7269 | 3.7251 | 3.7234 | 3.7201 | 3.717 | 3.717 | 3.717 | 3.3472 | 3.3445 | 3.338 | 3.3306 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4684 | 3.3225 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
| PEDDIESTON | LW |  |  |  | 3.7367 | 3.7361 | 3.7344 | 3.7324 | 3.7304 | 3.7284 | 3.7265 | 3.7245 | 3.7224 | 3.7203 | 3.717 | 3.717 | 3.717 | 3.717 | 3.3473 | 3.3444 | 3.3367 | 3.3273 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4514 | 2.2954 | 3.3227 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 2.3734
| PEDDIESTON | ST |  |  |  | 3.7368 | 3.7364 | 3.7354 | 3.734 | 3.7323 | 3.7311 | 3.7298 | 3.7286 | 3.7273 | 3.726 | 3.7234 | 3.7177 | 3.717 | 3.717 | 3.3476 | 3.3457 | 3.3413 | 3.3346 | 3.3267 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3231 | 3.3205 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
| PEDDIESTON | FS |  |  |  | 3.737 | 3.7369 | 3.7369 | 3.7366 | 3.7363 | 3.7359 | 3.7355 | 3.735 | 3.7345 | 3.734 | 3.733 | 3.7308 | 3.7288 | 3.7268 | 3.3485 | 3.3483 | 3.348 | 3.3469 | 3.3456 | 3.3438 | 3.3419 | 3.3395 | 3.3371 | 3.3347 | 3.3301 | 3.3266 | 3.3266 | 3.3266 | 3.3242 | 3.3239 | 3.3236 | 3.3221 | 3.3204 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
PETERHEAD GRANGE | PETERHEAD GRANGE 11kV | MINIMUM HEADROOM | NK 11738 46516 | NO | NO | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 31.0518 | 30.9888 | 30.8225 | 30.6065 | 30.424 | 30.2944 | 30.1682 | 30.1682 | 30.1682 | 30.1682 | 30.1682 | 29.7538 | 21.6385 | 20.3397 | 30.9068 | 30.8954 | 30.865 | 30.8256 | 30.786 | 30.7464 | 30.7064 | 30.6671 | 30.6247 | 30.5834 | 30.4999 | 29.7514 | 22.0629 | 20.7666
| PETERHEAD GRANGE 11kV | CT |  |  |  | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 31.0518 | 30.9888 | 30.8272 | 30.6396 | 30.4607 | 30.3482 | 30.2348 | 30.1682 | 30.1682 | 30.1682 | 30.1682 | 29.7538 | 22.4019 | 21.2924 | 30.9068 | 30.8954 | 30.8659 | 30.8317 | 30.7973 | 30.7628 | 30.7281 | 30.6939 | 30.6571 | 30.6213 | 30.5488 | 29.7514 | 22.8249 | 21.7175
| PETERHEAD GRANGE 11kV | LW |  |  |  | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 31.0582 | 30.9967 | 30.8225 | 30.6065 | 30.424 | 30.2944 | 30.1682 | 30.1682 | 30.1682 | 30.1682 | 30.1682 | 29.7538 | 21.6385 | 20.3397 | 30.908 | 30.8968 | 30.865 | 30.8256 | 30.786 | 30.7464 | 30.7064 | 30.6671 | 30.6247 | 30.5834 | 30.4999 | 29.7514 | 22.0629 | 20.7666
| PETERHEAD GRANGE 11kV | ST |  |  |  | 33.2848 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.9156 | 32.9156 | 32.9156 | 31.5031 | 31.0638 | 31.0261 | 30.9674 | 30.8959 | 30.812 | 30.7268 | 30.6431 | 30.5529 | 30.47 | 30.3652 | 29.961 | 29.961 | 29.961 | 30.9892 | 30.909 | 30.9021 | 30.8914 | 30.8784 | 30.8631 | 30.8475 | 30.8323 | 30.8158 | 30.8001 | 30.768 | 30.3647 | 30.2895 | 30.2167
| PETERHEAD GRANGE 11kV | FS |  |  |  | 33.2856 | 33.2852 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 31.5102 | 31.5067 | 31.0788 | 31.0585 | 31.034 | 31.0053 | 30.976 | 30.9402 | 30.9046 | 30.8705 | 30.8016 | 30.6358 | 30.4775 | 30.387 | 30.9905 | 30.9898 | 30.9118 | 30.9081 | 30.9036 | 30.8984 | 30.893 | 30.8865 | 30.88 | 30.8738 | 30.8612 | 30.8309 | 30.8021 | 30.7747
PETERHEAD GRANGE | PHEAD NORTH ST | MINIMUM HEADROOM | NK 13470 46450 | NO | NO | 27.1514 | 27.1505 | 27.148 | 27.1448 | 27.1416 | 27.1384 | 27.1352 | 27.132 | 27.1286 | 27.1253 | 27.1185 | 27.1004 | 27.0823 | 27.0647 | 26.0776 | 26.0708 | 26.0518 | 26.0281 | 26.0043 | 25.9803 | 25.956 | 25.9322 | 25.9066 | 25.882 | 25.8316 | 25.6962 | 25.6501 | 25.6391 | 26.2751 | 26.2641 | 26.2333 | 26.195 | 26.1563 | 26.1174 | 26.0781 | 26.0395 | 25.9981 | 25.9581 | 25.9102 | 25.8015 | 25.6931 | 25.5871
| PHEAD NORTH ST | CT |  |  |  | 27.1514 | 27.1507 | 27.1488 | 27.1465 | 27.1442 | 27.1419 | 27.1395 | 27.1372 | 27.1348 | 27.1324 | 27.1275 | 27.1141 | 27.1008 | 27.0878 | 26.0777 | 26.072 | 26.0576 | 26.0408 | 26.0237 | 26.0064 | 25.9888 | 25.9715 | 25.953 | 25.9352 | 25.8987 | 25.7986 | 25.6991 | 25.6535 | 26.2752 | 26.2661 | 26.2427 | 26.2154 | 26.1877 | 26.1597 | 26.1312 | 26.1032 | 26.0731 | 26.0443 | 25.9851 | 25.8837 | 25.8038 | 25.7258
| PHEAD NORTH ST | LW |  |  |  | 27.1514 | 27.1505 | 27.148 | 27.1448 | 27.1416 | 27.1384 | 27.1352 | 27.132 | 27.1286 | 27.1253 | 27.1185 | 27.1004 | 27.0823 | 27.0647 | 26.0776 | 26.0708 | 26.0518 | 26.0281 | 26.0043 | 25.9803 | 25.956 | 25.9322 | 25.9066 | 25.882 | 25.8316 | 25.6962 | 25.6501 | 25.6391 | 26.2751 | 26.2641 | 26.2333 | 26.195 | 26.1563 | 26.1174 | 26.0781 | 26.0395 | 25.9981 | 25.9581 | 25.9102 | 25.8015 | 25.6931 | 25.5871
| PHEAD NORTH ST | ST |  |  |  | 27.1517 | 27.1513 | 27.1505 | 27.1493 | 27.1478 | 27.1461 | 27.1444 | 27.1427 | 27.1409 | 27.1392 | 27.1357 | 27.1273 | 27.1192 | 27.1114 | 26.0796 | 26.0769 | 26.0709 | 26.0615 | 26.0501 | 26.0375 | 26.0248 | 26.0123 | 25.9989 | 25.986 | 25.9599 | 25.8971 | 25.837 | 25.7785 | 26.2784 | 26.2741 | 26.2642 | 26.249 | 26.2305 | 26.2102 | 26.1895 | 26.1693 | 26.1475 | 26.1267 | 26.0843 | 25.9826 | 25.9145 | 25.8676
| PHEAD NORTH ST | FS |  |  |  | 27.1519 | 27.1518 | 27.1517 | 27.1513 | 27.1509 | 27.1503 | 27.1497 | 27.149 | 27.1482 | 27.1476 | 27.1462 | 27.1428 | 27.1396 | 27.1367 | 26.0808 | 26.0803 | 26.0795 | 26.0767 | 26.0733 | 26.069 | 26.0646 | 26.0591 | 26.0538 | 26.0486 | 26.0382 | 26.0131 | 25.9894 | 25.9673 | 26.2803 | 26.2795 | 26.2783 | 26.2737 | 26.2682 | 26.2612 | 26.254 | 26.2452 | 26.2365 | 26.2281 | 26.2112 | 26.1706 | 26.1322 | 26.0964
FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 15.4958 | 15.4917 | 15.4812 | 15.4727 | 15.4563 | 15.4379 | 15.4174 | 15.4005 | 15.3824 | 15.3688 | 15.355 | 15.3138 | 15.273 | 15.2514 | 14.1035 | 14.0905 | 14.0573 | 14.0305 | 13.9785 | 13.9204 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6909 | 14.6846 | 14.6685 | 14.6554 | 14.6302 | 14.602 | 14.5704 | 14.5445 | 14.5167 | 14.4957 | 14.4747 | 14.4555 | 14.4555 | 14.4555
| PINEGROVE | CT |  |  |  | 15.4959 | 15.4924 | 15.4836 | 15.4771 | 15.4636 | 15.4482 | 15.4314 | 15.4165 | 15.4 | 15.3849 | 15.3671 | 15.3327 | 15.3057 | 15.2802 | 14.1037 | 14.0928 | 14.0649 | 14.0444 | 14.0015 | 13.9528 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.691 | 14.6857 | 14.6722 | 14.6622 | 14.6413 | 14.6177 | 14.5919 | 14.569 | 14.5438 | 14.5204 | 14.4932 | 14.4555 | 14.4555 | 14.4555
| PINEGROVE | LW |  |  |  | 15.4958 | 15.4917 | 15.4812 | 15.4727 | 15.4563 | 15.4379 | 15.4174 | 15.4005 | 15.3824 | 15.3688 | 15.355 | 15.3138 | 15.273 | 15.2514 | 14.1035 | 14.0905 | 14.0573 | 14.0305 | 13.9785 | 13.9204 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6909 | 14.6846 | 14.6685 | 14.6554 | 14.6302 | 14.602 | 14.5704 | 14.5445 | 14.5167 | 14.4957 | 14.4747 | 14.4555 | 14.4555 | 14.4555
| PINEGROVE | ST |  |  |  | 15.4965 | 15.4943 | 15.489 | 15.485 | 15.4759 | 15.4638 | 15.4508 | 15.4391 | 15.426 | 15.4135 | 15.3974 | 15.3726 | 15.354 | 15.3361 | 14.1058 | 14.0988 | 14.082 | 14.0692 | 14.0405 | 14.0023 | 13.9612 | 13.9242 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.692 | 14.6886 | 14.6804 | 14.6742 | 14.6603 | 14.6417 | 14.6218 | 14.6038 | 14.5836 | 14.5645 | 14.5397 | 14.5017 | 14.473 | 14.4555
| PINEGROVE | FS |  |  |  | 15.4971 | 15.4959 | 15.4933 | 15.4915 | 15.4875 | 15.4825 | 15.4771 | 15.4723 | 15.467 | 15.4625 | 15.4564 | 15.446 | 15.4394 | 15.4332 | 14.1075 | 14.1038 | 14.0957 | 14.0898 | 14.0772 | 14.0614 | 14.0444 | 14.0292 | 14.0124 | 13.9982 | 13.9789 | 13.946 | 13.925 | 13.915 | 14.6928 | 14.691 | 14.6871 | 14.6842 | 14.6781 | 14.6704 | 14.6622 | 14.6548 | 14.6467 | 14.6397 | 14.6304 | 14.6144 | 14.6042 | 14.5947
TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 7.7282 | 7.7274 | 7.7252 | 7.7225 | 7.9572 | 7.9542 | 7.9513 | 7.9482 | 7.945 | 7.9417 | 7.9365 | 7.9281 | 7.9281 | 6.0201 | 7.3638 | 7.3597 | 7.3481 | 7.3336 | 7.8686 | 7.853 | 7.8391 | 7.8312 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 6.1829 | 5.8273 | 7.8036 | 7.7946 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| PITLOCHRY | CT |  |  |  | 7.7282 | 7.7275 | 7.7258 | 7.7239 | 7.9593 | 7.9571 | 7.9549 | 7.9526 | 7.95 | 7.9474 | 7.9433 | 7.9281 | 7.9281 | 6.2901 | 7.3639 | 7.3604 | 7.3514 | 7.3409 | 7.8799 | 7.8683 | 7.8566 | 7.8443 | 7.8359 | 7.829 | 7.8272 | 7.8272 | 7.8272 | 6.1514 | 7.8036 | 7.7961 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| PITLOCHRY | LW |  |  |  | 7.7282 | 7.7274 | 7.7252 | 7.7225 | 7.9572 | 7.9542 | 7.9513 | 7.9482 | 7.945 | 7.9417 | 7.9365 | 7.9281 | 7.9281 | 6.0201 | 7.3638 | 7.3597 | 7.3481 | 7.3336 | 7.8686 | 7.853 | 7.8391 | 7.8312 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 6.1829 | 5.8273 | 7.8036 | 7.7946 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| PITLOCHRY | ST |  |  |  | 7.7284 | 7.728 | 7.7273 | 7.7261 | 7.9623 | 7.9593 | 7.9563 | 7.9533 | 7.95 | 7.9466 | 7.9409 | 7.9281 | 7.9281 | 7.9281 | 7.3648 | 7.3631 | 7.359 | 7.353 | 7.8957 | 7.8798 | 7.8641 | 7.8481 | 7.8358 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8057 | 7.8019 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| PITLOCHRY | FS |  |  |  | 7.7285 | 7.7284 | 7.7282 | 7.7278 | 7.9649 | 7.9638 | 7.9628 | 7.9615 | 7.9602 | 7.9589 | 7.9567 | 7.9513 | 7.9466 | 7.9422 | 7.3654 | 7.3649 | 7.364 | 7.3619 | 7.9096 | 7.9041 | 7.8986 | 7.8918 | 7.885 | 7.8781 | 7.8661 | 7.8394 | 7.8272 | 7.8272 | 7.807 | 7.8059 | 7.8039 | 7.7995 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 1.978 | 1.784 | 1.5816 | 3.5948 | 3.583 | 3.5543 | 3.5212 | 3.4883 | 3.4578 | 3.4276 | 3.3978 | 3.3655 | 3.3335 | 3.2709 | 2.3488 | 2.0808 | 1.8012 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5661 | 1.5231 | 1.4783
| POLLACHAR | CT |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 1.978 | 1.784 | 1.5932 | 3.5948 | 3.583 | 3.5543 | 3.5212 | 3.4883 | 3.4578 | 3.4276 | 3.3978 | 3.3655 | 3.3335 | 3.2709 | 2.3488 | 2.0808 | 1.8172 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5661 | 1.5231 | 1.4809
| POLLACHAR | LW |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.0766 | 1.827 | 1.5816 | 3.5995 | 3.595 | 3.5844 | 3.5715 | 3.5583 | 3.5476 | 3.5372 | 3.527 | 3.5159 | 3.505 | 3.4833 | 2.485 | 2.1402 | 1.8012 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5879 | 1.5327 | 1.4783
| POLLACHAR | ST |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.5656 | 2.5237 | 2.442 | 3.6007 | 3.5987 | 3.5951 | 3.5898 | 3.5834 | 3.5595 | 3.5358 | 3.5126 | 3.4874 | 3.4627 | 3.4153 | 2.9723 | 2.8588 | 2.7458 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.9883 | 1.9823 | 1.9642
| POLLACHAR | FS |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 3.6014 | 3.6007 | 3.6 | 3.5982 | 3.5961 | 3.5874 | 3.5788 | 3.5677 | 3.5568 | 3.5461 | 3.5254 | 3.4767 | 3.4312 | 3.3886 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664
FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.0083224 | 0.0082722 | 0.0081397 | 0.0080494 | 0.0079608 | 0.0078742 | 0.007789 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | -0.0012819 | 0.0096489 | 0.0096321 | 0.0096063 | 0.0095749 | 0.009544 | 0.0095139 | 0.0094843 | 0.0094552 | 0.0094239 | 0.009423 | 0.009423 | 0.009423 | 0.009423 | -0.00067898
| POOR HOUSE | CT |  |  |  | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.0083226 | 0.0082806 | 0.0081745 | 0.0080992 | 0.0080369 | 0.007976 | 0.0079159 | 0.0078567 | 0.007793 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.009649 | 0.0096337 | 0.0096143 | 0.0095922 | 0.0095705 | 0.0095493 | 0.0095284 | 0.0095078 | 0.0094857 | 0.0094637 | 0.009423 | 0.009423 | 0.009423 | 0.009423
| POOR HOUSE | LW |  |  |  | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.0083224 | 0.0082722 | 0.0081397 | 0.0080494 | 0.0079608 | 0.0078742 | 0.007789 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0077479 | -0.0012819 | 0.0096489 | 0.0096321 | 0.0096063 | 0.0095749 | 0.009544 | 0.0095139 | 0.0094843 | 0.0094552 | 0.0094239 | 0.009423 | 0.009423 | 0.009423 | 0.009423 | -0.00067898
| POOR HOUSE | ST |  |  |  | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.0083373 | 0.0083181 | 0.0082748 | 0.0082086 | 0.008139 | 0.0080985 | 0.0080586 | 0.0080194 | 0.0079773 | 0.007936 | 0.007856 | 0.0077479 | 0.0077479 | 0.0077479 | 0.0096561 | 0.0096468 | 0.0096326 | 0.0096205 | 0.0096061 | 0.0095919 | 0.0095781 | 0.0095644 | 0.0095498 | 0.0095354 | 0.0095076 | 0.0094402 | 0.009423 | 0.009423
| POOR HOUSE | FS |  |  |  | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.014879 | 0.0083462 | 0.0083431 | 0.0083392 | 0.0083203 | 0.0082979 | 0.008272 | 0.0082462 | 0.0082131 | 0.0081807 | 0.0081491 | 0.0081167 | 0.0080405 | 0.0079654 | 0.0078929 | 0.0096605 | 0.0096589 | 0.0096571 | 0.0096479 | 0.009637 | 0.0096321 | 0.0096274 | 0.0096213 | 0.0096154 | 0.0096096 | 0.0095983 | 0.0095718 | 0.0095457 | 0.0095204
PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | YES | 3.4082 | 3.4048 | 3.3948 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0636 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 2.4055 | 3.2507 | 3.2497 | 3.2466 | 3.2428 | 3.2392 | 3.2356 | 3.232 | 3.2286 | 3.2249 | 3.2219 | 3.2219 | 3.2219 | 3.1811 | 2.4613
| PORT ASKAIG | CT |  |  |  | 3.4082 | 3.4053 | 3.3978 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0636 | 3.0626 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 3.0378 | 3.2507 | 3.2498 | 3.2475 | 3.2449 | 3.2423 | 3.2398 | 3.2374 | 3.235 | 3.2323 | 3.2298 | 3.2246 | 3.2219 | 3.1811 | 3.1811
| PORT ASKAIG | LW |  |  |  | 3.4082 | 3.4048 | 3.3948 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0636 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 2.4055 | 3.2507 | 3.2497 | 3.2466 | 3.2428 | 3.2392 | 3.2356 | 3.232 | 3.2286 | 3.2249 | 3.2219 | 3.2219 | 3.2219 | 3.1811 | 2.4613
| PORT ASKAIG | ST |  |  |  | 3.4092 | 3.4079 | 3.4049 | 3.4003 | 3.3947 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3693 | 3.3693 | 3.0639 | 3.0635 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.05 | 3.05 | 3.251 | 3.2506 | 3.2497 | 3.2483 | 3.2466 | 3.2436 | 3.2408 | 3.238 | 3.235 | 3.232 | 3.2263 | 3.2219 | 3.2015 | 3.2015
| PORT ASKAIG | FS |  |  |  | 3.4098 | 3.4097 | 3.4095 | 3.4081 | 3.4066 | 3.4035 | 3.4004 | 3.3964 | 3.3925 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.0641 | 3.0641 | 3.064 | 3.0636 | 3.0631 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.2512 | 3.2512 | 3.2511 | 3.2507 | 3.2502 | 3.2493 | 3.2483 | 3.2471 | 3.2459 | 3.2447 | 3.2425 | 3.2371 | 3.2321 | 3.2274
PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.7214 | 7.7214 | 7.7214 | 7.2434 | 7.2328 | 7.2148 | 7.1956 | 7.1775 | 7.1621 | 7.147 | 7.1324 | 7.1276 | 7.1276 | 7.1276 | 6.9723 | 6.9723 | 6.9723 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 6.8208 | 6.8208 | 6.8208
| PORT ELLEN | CT |  |  |  | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.7214 | 7.7214 | 7.7214 | 7.2435 | 7.2346 | 7.2206 | 7.2069 | 7.1938 | 7.1824 | 7.1702 | 7.1584 | 7.1459 | 7.1341 | 7.1276 | 6.9723 | 6.9723 | 6.9723 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 6.8208 | 6.8208 | 6.8208
| PORT ELLEN | LW |  |  |  | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.7214 | 7.7214 | 7.7214 | 7.2434 | 7.2328 | 7.2148 | 7.1956 | 7.1775 | 7.1621 | 7.147 | 7.1324 | 7.1276 | 7.1276 | 7.1276 | 6.9723 | 6.9723 | 6.9723 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 6.8208 | 6.8208 | 6.8208
| PORT ELLEN | ST |  |  |  | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.8604 | 7.8604 | 7.8604 | 7.246 | 7.2407 | 7.2339 | 7.226 | 7.2173 | 7.2021 | 7.1865 | 7.1714 | 7.1552 | 7.1397 | 7.1276 | 7.05 | 7.05 | 7.05 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 6.9644 | 6.9644 | 6.9644
| PORT ELLEN | FS |  |  |  | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.9993 | 7.2478 | 7.2453 | 7.2434 | 7.2405 | 7.2376 | 7.2324 | 7.2272 | 7.2207 | 7.2143 | 7.208 | 7.1959 | 7.1683 | 7.1427 | 7.1276 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108 | 7.108
DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 10.363 | 10.2767 | 10.166 | 10.0608 | 9.9594 | 9.8617 | 9.7678 | 9.6777 | 9.6367 | 9.6163 | 9.5762 | 9.4794 | 9.3944 | 9.3085 | 10.0872 | 9.992 | 9.8364 | 9.7349 | 9.6594 | 9.6045 | 9.5516 | 9.5009 | 9.4778 | 9.4663 | 9.4438 | 9.3893 | 9.3415 | 9.2931 | 10.1653 | 10.0652 | 9.9352 | 9.8134 | 9.6951 | 9.5804 | 9.473 | 9.3579 | 9.3056 | 9.2752 | 9.2224 | 9.1215 | 9.0331 | 7.3552
| PORTREE | CT |  |  |  | 10.363 | 10.2767 | 10.166 | 10.0608 | 9.9594 | 9.8617 | 9.7678 | 9.6777 | 9.6367 | 9.6163 | 9.5762 | 9.4794 | 9.3944 | 9.3085 | 10.0872 | 9.992 | 9.8364 | 9.7349 | 9.6594 | 9.6045 | 9.5516 | 9.5009 | 9.4778 | 9.4663 | 9.4438 | 9.3893 | 9.3415 | 9.2931 | 10.1653 | 10.0652 | 9.9352 | 9.8134 | 9.6951 | 9.5804 | 9.473 | 9.3579 | 9.3056 | 9.2752 | 9.2224 | 9.1215 | 9.0331 | 7.3552
| PORTREE | LW |  |  |  | 10.487 | 10.4727 | 10.4561 | 10.4374 | 10.4168 | 10.3945 | 10.3706 | 10.3454 | 10.3227 | 10.2993 | 10.2511 | 10.1227 | 9.9995 | 9.872 | 10.1983 | 10.1702 | 10.0954 | 10.0344 | 9.9684 | 9.9043 | 9.8909 | 9.8767 | 9.8639 | 9.8507 | 9.8236 | 9.7514 | 9.6821 | 9.6103 | 10.3026 | 10.2815 | 10.2478 | 10.22 | 10.1896 | 10.1569 | 10.127 | 10.0823 | 10.053 | 10.023 | 9.9626 | 9.7913 | 9.6631 | 9.5303
| PORTREE | ST |  |  |  | 10.5061 | 10.5011 | 10.4945 | 10.488 | 10.4818 | 10.4741 | 10.4667 | 10.4595 | 10.4527 | 10.4426 | 10.4233 | 10.3799 | 10.3416 | 10.3068 | 10.2188 | 10.2069 | 10.1697 | 10.1435 | 10.1137 | 10.0654 | 10.0299 | 9.9507 | 9.9371 | 9.9314 | 9.9206 | 9.8961 | 9.8746 | 9.855 | 10.3249 | 10.3168 | 10.2984 | 10.2854 | 10.2744 | 10.2589 | 10.2459 | 10.2252 | 10.2118 | 10.1949 | 10.1628 | 10.0924 | 10.0288 | 9.9829
| PORTREE | FS |  |  |  | 10.5011 | 10.4945 | 10.4879 | 10.4781 | 10.4684 | 10.4589 | 10.4495 | 10.4402 | 10.4311 | 10.4221 | 10.4044 | 10.352 | 10.3061 | 10.2637 | 10.2175 | 10.2083 | 10.1876 | 10.1691 | 10.1495 | 10.1243 | 10.1053 | 10.0679 | 10.0463 | 10.0252 | 9.9827 | 9.8815 | 9.8546 | 9.8308 | 10.3204 | 10.312 | 10.2996 | 10.2855 | 10.271 | 10.2556 | 10.2436 | 10.2286 | 10.2165 | 10.2045 | 10.181 | 10.1154 | 10.0582 | 10.0051
MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 2.431 | 1.273 | 1.2389 | 4.8742 | 4.874 | 4.8734 | 4.8726 | 4.8717 | 4.8709 | 4.87 | 4.8691 | 4.8682 | 4.8673 | 4.8655 | 2.9967 | 1.7618 | 1.6011 | 6.2459 | 6.2454 | 6.2439 | 6.2421 | 6.2402 | 6.2382 | 6.2361 | 6.2341 | 6.232 | 4.9957 | 4.9741 | 2.6218 | 1.2006 | 1.0866
| PORTSOY | CT |  |  |  | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 2.431 | 1.273 | 1.273 | 4.8742 | 4.874 | 4.8735 | 4.873 | 4.8724 | 4.8717 | 4.8711 | 4.8704 | 4.8697 | 4.8691 | 4.8677 | 3.0454 | 1.8223 | 1.6731 | 6.2459 | 6.2455 | 6.2444 | 6.243 | 6.2416 | 6.2402 | 6.2386 | 6.2371 | 6.2355 | 6.234 | 6.2308 | 2.6564 | 1.2435 | 1.1377
| PORTSOY | LW |  |  |  | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 2.431 | 1.273 | 1.2389 | 4.8742 | 4.874 | 4.8734 | 4.8726 | 4.8717 | 4.8709 | 4.87 | 4.8691 | 4.8682 | 4.8673 | 4.8655 | 2.9967 | 1.7618 | 1.6011 | 6.2459 | 6.2454 | 6.2439 | 6.2421 | 6.2402 | 6.2382 | 6.2361 | 6.2341 | 6.232 | 4.9957 | 4.9741 | 2.6218 | 1.2006 | 1.0866
| PORTSOY | ST |  |  |  | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 3.4233 | 2.8443 | 2.8443 | 4.8743 | 4.8742 | 4.874 | 4.8736 | 4.8732 | 4.8725 | 4.8717 | 4.871 | 4.8702 | 4.8694 | 4.8679 | 4.0558 | 3.4606 | 3.4026 | 6.2461 | 6.2459 | 6.2454 | 6.2446 | 6.2437 | 6.242 | 6.2402 | 6.2385 | 6.2366 | 6.2348 | 6.2312 | 3.8402 | 3.1455 | 3.1043
| PORTSOY | FS |  |  |  | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.4155 | 4.8743 | 4.8743 | 4.8743 | 4.8742 | 4.874 | 4.8737 | 4.8734 | 4.8731 | 4.8727 | 4.8723 | 4.8716 | 4.8699 | 4.8683 | 4.8667 | 6.2462 | 6.2461 | 6.246 | 6.2458 | 6.2455 | 6.2448 | 6.2441 | 6.2432 | 6.2424 | 6.2416 | 6.2399 | 6.236 | 6.2322 | 4.9892
WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7792 | 16.755 | 16.6859 | 16.601 | 16.5177 | 16.4357 | 16.3551 | 16.2759 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 10.9361 | 9.4537 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 10.7216 | 9.2329
| QUEENS LANE NORTH | CT |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7818 | 16.7657 | 16.7247 | 16.6777 | 16.6315 | 16.586 | 16.5411 | 16.497 | 16.4493 | 16.402 | 16.3079 | 16.2069 | 16.2069 | 16.2069 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
| QUEENS LANE NORTH | LW |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7792 | 16.755 | 16.6859 | 16.601 | 16.5177 | 16.4357 | 16.3551 | 16.2759 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 10.9361 | 9.4537 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 10.7216 | 9.2329
| QUEENS LANE NORTH | ST |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.783 | 16.7677 | 16.7325 | 16.6776 | 16.6118 | 16.5546 | 16.4985 | 16.4436 | 16.3842 | 16.3259 | 16.2119 | 16.2069 | 16.2069 | 16.2069 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
| QUEENS LANE NORTH | FS |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7916 | 16.7886 | 16.7865 | 16.7746 | 16.7605 | 16.743 | 16.7257 | 16.7035 | 16.6817 | 16.6602 | 16.6187 | 16.5196 | 16.4234 | 16.3303 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
QUOICH | QUOICH PRIMARY | MINIMUM HEADROOM | NH 11700 01900 | YES | YES | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.9188 | -2.9189 | -2.9191 | -2.9195 | -2.9198 | -2.9201 | -2.9205 | -2.9208 | -2.9211 | -2.9214 | -2.9221 | -2.9241 | -2.9262 | -2.9282
| QUOICH PRIMARY | CT |  |  |  | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.9188 | -2.9189 | -2.9191 | -2.9193 | -2.9195 | -2.9198 | -2.92 | -2.9202 | -2.9204 | -2.9207 | -2.9211 | -2.9224 | -2.9236 | -2.9248
| QUOICH PRIMARY | LW |  |  |  | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.9188 | -2.9189 | -2.9191 | -2.9195 | -2.9198 | -2.9201 | -2.9205 | -2.9208 | -2.9211 | -2.9214 | -2.9221 | -2.9241 | -2.9262 | -2.9282
| QUOICH PRIMARY | ST |  |  |  | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.9187 | -2.9188 | -2.9189 | -2.919 | -2.9191 | -2.9193 | -2.9195 | -2.9197 | -2.9199 | -2.9201 | -2.9205 | -2.9214 | -2.9223 | -2.9232
| QUOICH PRIMARY | FS |  |  |  | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.9547 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.8886 | -2.9187 | -2.9187 | -2.9187 | -2.9188 | -2.9188 | -2.9189 | -2.9189 | -2.919 | -2.9191 | -2.9192 | -2.9193 | -2.9197 | -2.92 | -2.9203
FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.013116 | 0.013106 | 0.013079 | 0.013045 | 0.013012 | 0.012979 | 0.012948 | 0.012917 | 0.012883 | 0.01285 | 0.012795 | 0.012711 | 0.012626 | 0.012543 | 0.015181 | 0.015176 | 0.015163 | 0.015146 | 0.015139 | 0.015133 | 0.015127 | 0.015121 | 0.015115 | 0.015109 | 0.015097 | 0.015068 | 0.015038 | 0.015009
| RAHOY | CT |  |  |  | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.013116 | 0.013108 | 0.013087 | 0.013064 | 0.01304 | 0.013018 | 0.012996 | 0.012974 | 0.01295 | 0.012927 | 0.012881 | 0.012787 | 0.012728 | 0.012669 | 0.015181 | 0.015177 | 0.015167 | 0.015155 | 0.015144 | 0.01514 | 0.015136 | 0.015132 | 0.015127 | 0.015123 | 0.015115 | 0.015094 | 0.015074 | 0.015053
| RAHOY | LW |  |  |  | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.013116 | 0.013106 | 0.013079 | 0.013045 | 0.013012 | 0.012979 | 0.012948 | 0.012917 | 0.012883 | 0.01285 | 0.012795 | 0.012711 | 0.012626 | 0.012543 | 0.015181 | 0.015176 | 0.015163 | 0.015146 | 0.015139 | 0.015133 | 0.015127 | 0.015121 | 0.015115 | 0.015109 | 0.015097 | 0.015068 | 0.015038 | 0.015009
| RAHOY | ST |  |  |  | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.013119 | 0.013115 | 0.013107 | 0.013094 | 0.013078 | 0.013063 | 0.013049 | 0.013034 | 0.013019 | 0.013004 | 0.012974 | 0.012903 | 0.012834 | 0.012784 | 0.015182 | 0.015181 | 0.015177 | 0.01517 | 0.015163 | 0.015155 | 0.015148 | 0.015143 | 0.01514 | 0.015137 | 0.015132 | 0.015119 | 0.015106 | 0.015093
| RAHOY | FS |  |  |  | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.023382 | 0.013121 | 0.01312 | 0.013119 | 0.013116 | 0.013112 | 0.013106 | 0.013102 | 0.013095 | 0.013089 | 0.013083 | 0.013071 | 0.013042 | 0.013016 | 0.012992 | 0.015183 | 0.015183 | 0.015183 | 0.015181 | 0.015179 | 0.015176 | 0.015174 | 0.015171 | 0.015168 | 0.015165 | 0.015159 | 0.015145 | 0.015139 | 0.015135
INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | NO | 31.4905 | 31.3898 | 31.2604 | 31.1362 | 31.0164 | 30.9011 | 30.7902 | 30.6837 | 30.6329 | 30.6076 | 30.5579 | 30.4369 | 30.326 | 30.2122 | 31.456 | 31.3307 | 31.1901 | 31.0373 | 30.9054 | 30.7756 | 30.6519 | 30.5316 | 30.4228 | 30.3546 | 30.2243 | 29.7697 | 29.3047 | 29.1582 | 31.2715 | 31.1439 | 30.9788 | 30.8075 | 30.6514 | 30.4995 | 30.3644 | 30.2371 | 30.1598 | 30.1168 | 30.0336 | 29.7866 | 29.6476 | 29.5314
| RAIGMORE | CT |  |  |  | 31.4905 | 31.3898 | 31.2604 | 31.1362 | 31.0164 | 30.9011 | 30.7902 | 30.6837 | 30.6329 | 30.6076 | 30.5579 | 30.4369 | 30.326 | 30.2122 | 31.456 | 31.3307 | 31.1901 | 31.0373 | 30.9054 | 30.7756 | 30.6519 | 30.5316 | 30.4228 | 30.3546 | 30.2243 | 29.7697 | 29.3047 | 29.1582 | 31.2715 | 31.1439 | 30.9788 | 30.8075 | 30.6514 | 30.4995 | 30.3644 | 30.2371 | 30.1598 | 30.1168 | 30.0336 | 29.7866 | 29.6476 | 29.5314
| RAIGMORE | LW |  |  |  | 31.6354 | 31.6186 | 31.5992 | 31.5774 | 31.5534 | 31.5273 | 31.4994 | 31.4701 | 31.4422 | 31.4135 | 31.3545 | 31.1972 | 31.039 | 30.8686 | 31.5635 | 31.4906 | 31.3864 | 31.2703 | 31.1768 | 31.0845 | 30.9997 | 30.9149 | 30.8021 | 30.7128 | 30.5369 | 29.8923 | 29.6426 | 29.5432 | 31.4212 | 31.3759 | 31.3142 | 31.2332 | 31.1692 | 31.1178 | 31.0675 | 31.0158 | 30.9564 | 30.9038 | 30.7982 | 30.5254 | 30.3664 | 30.1951
| RAIGMORE | ST |  |  |  | 31.6576 | 31.6518 | 31.6441 | 31.6366 | 31.6293 | 31.6204 | 31.6117 | 31.6033 | 31.5952 | 31.5833 | 31.5605 | 31.5077 | 31.4604 | 31.4148 | 31.5918 | 31.5551 | 31.5122 | 31.4432 | 31.3811 | 31.3192 | 31.26 | 31.2018 | 31.1254 | 31.0634 | 30.9457 | 30.6677 | 30.3869 | 30.1105 | 31.4497 | 31.4287 | 31.4035 | 31.3663 | 31.3324 | 31.29 | 31.2495 | 31.2189 | 31.1876 | 31.1578 | 31.1011 | 30.968 | 30.8385 | 30.7441
| RAIGMORE | FS |  |  |  | 31.6518 | 31.6441 | 31.6364 | 31.6249 | 31.6137 | 31.6025 | 31.5916 | 31.5807 | 31.5701 | 31.5595 | 31.5389 | 31.4777 | 31.4226 | 31.3714 | 31.5977 | 31.5774 | 31.5633 | 31.5326 | 31.5072 | 31.4741 | 31.4436 | 31.4076 | 31.3654 | 31.3373 | 31.2832 | 31.1519 | 31.0285 | 30.9098 | 31.4484 | 31.4337 | 31.4218 | 31.3997 | 31.3801 | 31.3571 | 31.3354 | 31.3113 | 31.2844 | 31.261 | 31.2156 | 31.0981 | 31.0126 | 30.9319
ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 5.8042 | 5.718 | 5.6075 | 5.493 | 5.3827 | 3.9694 | 3.8744 | 3.7701 | 3.6815 | 3.6263 | 3.5179 | 2.6396 | 1.8727 | 1.5346 | 3.6303 | 3.5445 | 3.4268 | 3.3066 | 3.1902 | 3.0769 | 2.966 | 2.8597 | 2.781 | 2.7286 | 2.626 | 1.884 | 1.229 | 0.91078 | 3.6135 | 3.5059 | 3.3608 | 3.2121 | 3.0684 | 2.9288 | 2.7928 | 2.6623 | 2.569 | 2.5104 | 2.3953 | 1.4756 | 0.6714 | 0.31286
| REDFORD | CT |  |  |  | 5.8042 | 5.718 | 5.6075 | 5.493 | 5.3827 | 3.9694 | 3.8744 | 3.7701 | 3.6815 | 3.6263 | 3.5179 | 2.6396 | 1.8727 | 1.5346 | 3.6303 | 3.5445 | 3.4268 | 3.3066 | 3.1902 | 3.0769 | 2.966 | 2.8597 | 2.781 | 2.7286 | 2.626 | 1.884 | 1.229 | 0.91078 | 3.6135 | 3.5059 | 3.3608 | 3.2121 | 3.0684 | 2.9288 | 2.7928 | 2.6623 | 2.569 | 2.5104 | 2.3953 | 1.4756 | 0.6714 | 0.31286
| REDFORD | LW |  |  |  | 5.928 | 5.9137 | 5.8971 | 5.8785 | 5.8579 | 5.8356 | 5.8118 | 5.7867 | 5.7545 | 5.7213 | 5.6531 | 3.2307 | 2.3703 | 1.8981 | 3.7313 | 3.7008 | 3.6504 | 3.5953 | 3.5397 | 3.4836 | 3.4268 | 3.3698 | 3.3039 | 3.2375 | 3.1041 | 2.2899 | 1.5443 | 1.1038 | 3.7474 | 3.7144 | 3.6623 | 3.6052 | 3.5469 | 3.4876 | 3.4273 | 3.3662 | 3.2947 | 3.2224 | 3.0765 | 2.0816 | 1.178 | 0.67768
| REDFORD | ST |  |  |  | 5.947 | 5.9421 | 5.9355 | 5.929 | 5.9228 | 5.9152 | 5.9078 | 5.9006 | 5.8931 | 5.8821 | 5.8611 | 5.5246 | 3.7874 | 3.6382 | 3.8864 | 3.7365 | 3.7175 | 3.6951 | 3.6695 | 3.6438 | 3.6178 | 3.5929 | 3.5667 | 3.5383 | 3.4838 | 3.1172 | 2.8065 | 2.6593 | 3.8973 | 3.7568 | 3.737 | 3.7141 | 3.6884 | 3.6621 | 3.6356 | 3.6101 | 3.5834 | 3.5535 | 3.4961 | 3.0468 | 2.671 | 2.5118
| REDFORD | FS |  |  |  | 5.9421 | 5.9355 | 5.9289 | 5.9191 | 5.9094 | 5.8999 | 5.8905 | 5.8813 | 5.8722 | 5.8632 | 5.8456 | 5.7932 | 5.7364 | 5.681 | 3.8846 | 3.8759 | 3.8683 | 3.8559 | 3.8427 | 3.8284 | 3.8144 | 3.7989 | 3.7836 | 3.7685 | 3.7392 | 3.6616 | 3.5828 | 3.5069 | 3.894 | 3.8838 | 3.8746 | 3.8599 | 3.8446 | 3.8283 | 3.8123 | 3.7948 | 3.7776 | 3.7607 | 3.7278 | 3.6389 | 3.5474 | 3.459
BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5079 | 14.2533 | 13.9903 | 13.4563 | 12.2407 | 11.5069 | 10.9159 | 15.5566 | 15.5312 | 15.4677 | 15.3869 | 15.3169 | 13.5556 | 13.2914 | 13.0129 | 12.7118 | 12.4009 | 11.7714 | 10.341 | 9.4776 | 8.7822 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.5222 | 13.2217 | 12.9114 | 12.2831 | 10.8555 | 9.9937 | 9.2995
| REDGORTON | CT |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.4207 | 13.9682 | 13.2645 | 12.8166 | 12.4051 | 15.558 | 15.5384 | 15.4921 | 15.4356 | 15.3739 | 15.3169 | 13.6267 | 13.4106 | 13.1696 | 12.9097 | 12.3748 | 11.5457 | 11.0187 | 10.5344 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.6787 | 13.4193 | 12.8854 | 12.0578 | 11.5318 | 11.0485
| REDGORTON | LW |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5079 | 14.2533 | 13.9903 | 13.4563 | 12.2407 | 11.5069 | 10.9159 | 15.5566 | 15.5312 | 15.4677 | 15.3869 | 15.3169 | 13.5556 | 13.2914 | 13.0129 | 12.7118 | 12.4009 | 11.7714 | 10.341 | 9.4776 | 8.7822 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.5222 | 13.2217 | 12.9114 | 12.2831 | 10.8555 | 9.9937 | 9.2995
| REDGORTON | ST |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5118 | 14.0255 | 13.7352 | 13.4668 | 15.5641 | 15.5526 | 15.5279 | 15.4926 | 15.4499 | 15.4012 | 15.3494 | 13.78 | 13.6054 | 13.4152 | 13.0175 | 12.4425 | 12.0995 | 11.7837 | 15.5549 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.5268 | 12.9529 | 12.6106 | 12.2954
| REDGORTON | FS |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 15.569 | 15.5641 | 15.5558 | 15.5414 | 15.525 | 15.5059 | 15.4855 | 15.4618 | 15.4365 | 15.4096 | 15.3541 | 13.6035 | 13.3813 | 13.2544 | 15.5566 | 15.5549 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.7633
REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | NO | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.5136 | 43.428 | 43.232 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 35.7687 | 34.5977 | 33.4469 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 36.6348 | 35.4634 | 34.3122
| REDMOSS | CT |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.5192 | 43.4549 | 43.3232 | 43.1789 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 36.0048 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
| REDMOSS | LW |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.5136 | 43.428 | 43.232 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 35.7687 | 34.5977 | 33.4469 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 36.6348 | 35.4634 | 34.3122
| REDMOSS | ST |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.7644 | 43.5016 | 43.4329 | 43.3337 | 43.2151 | 43.1658 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
| REDMOSS | FS |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.7826 | 43.7685 | 43.5288 | 43.4944 | 43.455 | 43.4231 | 43.3901 | 43.3512 | 43.3103 | 43.2676 | 43.2025 | 43.1537 | 43.1537 | 43.1537 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 1.0579 | 1.0553 | 1.0478 | 1.0386 | 1.0296 | 1.0208 | 1.0122 | 1.0038 | 0.99468 | 0.98565 | 0.96781 | 0.94029 | 0.94029 | 0.94029 | 1.0019 | 1.0017 | 1.0012 | 1.0005 | 0.9999 | 0.99928 | 0.99867 | 0.99807 | 0.99742 | 0.99678 | 0.99552 | 0.98834 | 0.98106 | 0.97389 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003
| RHICONICH | CT |  |  |  | 1.0579 | 1.0558 | 1.0501 | 1.0437 | 1.0374 | 1.0312 | 1.0252 | 1.0192 | 1.0128 | 1.0065 | 0.99397 | 0.94029 | 0.94029 | 0.94029 | 1.0019 | 1.0017 | 1.0013 | 1.0009 | 1.0004 | 1 | 0.99958 | 0.99916 | 0.99871 | 0.99826 | 0.99737 | 0.9909 | 0.98431 | 0.97784 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003
| RHICONICH | LW |  |  |  | 1.0579 | 1.0553 | 1.0478 | 1.0386 | 1.0296 | 1.0208 | 1.0122 | 1.0038 | 0.99468 | 0.98565 | 0.96781 | 0.94029 | 0.94029 | 0.94029 | 1.0019 | 1.0017 | 1.0012 | 1.0005 | 0.9999 | 0.99928 | 0.99867 | 0.99807 | 0.99742 | 0.99678 | 0.99552 | 0.98834 | 0.98106 | 0.97389 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003
| RHICONICH | ST |  |  |  | 1.0587 | 1.0577 | 1.0555 | 1.0519 | 1.0477 | 1.0385 | 1.0294 | 1.0206 | 1.011 | 1.0017 | 0.98342 | 0.94029 | 0.94029 | 0.94029 | 1.002 | 1.0019 | 1.0017 | 1.0015 | 1.0012 | 1.0005 | 0.99988 | 0.99926 | 0.99858 | 0.99792 | 0.99663 | 0.9935 | 0.99038 | 0.98728 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003
| RHICONICH | FS |  |  |  | 1.0592 | 1.059 | 1.0589 | 1.0579 | 1.0567 | 1.0536 | 1.0506 | 1.0467 | 1.0428 | 1.039 | 1.0317 | 1.0145 | 0.99824 | 0.98292 | 1.002 | 1.002 | 1.002 | 1.0019 | 1.0018 | 1.0016 | 1.0014 | 1.0011 | 1.0008 | 1.0006 | 1 | 0.99883 | 0.99768 | 0.99659 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003 | 1.2003
DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 30.8965 | 30.8009 | 30.6782 | 30.5665 | 30.4588 | 30.3551 | 30.2554 | 30.1597 | 30.1074 | 30.0814 | 30.0304 | 29.9108 | 29.7881 | 29.6583 | 28.9842 | 28.8805 | 28.7237 | 28.5757 | 28.4307 | 28.2884 | 28.1523 | 28.0206 | 27.9201 | 27.8329 | 27.7144 | 27.5543 | 27.4432 | 27.3681 | 29.6103 | 29.4984 | 29.3435 | 29.1999 | 29.0604 | 28.9248 | 28.7947 | 28.6694 | 28.5873 | 28.5456 | 28.4932 | 28.3705 | 28.2469 | 28.1174
| ROSEBANK STREET | CT |  |  |  | 30.8965 | 30.8009 | 30.6782 | 30.5665 | 30.4588 | 30.3551 | 30.2554 | 30.1597 | 30.1074 | 30.0814 | 30.0304 | 29.9108 | 29.7881 | 29.6583 | 28.9842 | 28.8805 | 28.7237 | 28.5757 | 28.4307 | 28.2884 | 28.1523 | 28.0206 | 27.9201 | 27.8329 | 27.7144 | 27.5543 | 27.4432 | 27.3681 | 29.6103 | 29.4984 | 29.3435 | 29.1999 | 29.0604 | 28.9248 | 28.7947 | 28.6694 | 28.5873 | 28.5456 | 28.4932 | 28.3705 | 28.2469 | 28.1174
| ROSEBANK STREET | LW |  |  |  | 31.034 | 31.0181 | 30.9997 | 30.9789 | 30.9561 | 30.9314 | 30.905 | 30.8771 | 30.8469 | 30.8159 | 30.7521 | 30.5821 | 30.391 | 30.1958 | 29.0967 | 29.0541 | 28.9661 | 28.8684 | 28.7719 | 28.6719 | 28.5687 | 28.4659 | 28.3515 | 28.2319 | 28.1288 | 27.9027 | 27.7921 | 27.6791 | 29.7537 | 29.7229 | 29.6688 | 29.6086 | 29.5475 | 29.4836 | 29.417 | 29.3622 | 29.3313 | 29.2994 | 29.234 | 29.0595 | 28.8633 | 28.663
| ROSEBANK STREET | ST |  |  |  | 31.0551 | 31.0496 | 31.0422 | 31.0351 | 31.0281 | 31.0197 | 31.0115 | 31.0035 | 30.9962 | 30.9855 | 30.965 | 30.91 | 30.8608 | 30.8083 | 29.1292 | 29.1086 | 29.0698 | 29.0201 | 28.9612 | 28.8832 | 28.8081 | 28.7348 | 28.6563 | 28.5698 | 28.3974 | 28.1996 | 28.0898 | 28.0336 | 29.7829 | 29.7695 | 29.7462 | 29.7177 | 29.685 | 29.6422 | 29.6009 | 29.5606 | 29.5183 | 29.4735 | 29.4525 | 29.396 | 29.3456 | 29.2917
| ROSEBANK STREET | FS |  |  |  | 31.0496 | 31.0422 | 31.0349 | 31.0241 | 31.0134 | 31.0028 | 30.9924 | 30.9821 | 30.972 | 30.962 | 30.9424 | 30.8843 | 30.8241 | 30.766 | 29.1393 | 29.1285 | 29.1174 | 29.0964 | 29.0745 | 29.0439 | 29.0138 | 28.9777 | 28.9411 | 28.9042 | 28.8317 | 28.6456 | 28.4745 | 28.3169 | 29.7842 | 29.7742 | 29.7642 | 29.7471 | 29.7296 | 29.7081 | 29.6869 | 29.6629 | 29.6388 | 29.6147 | 29.5672 | 29.4403 | 29.3192 | 29.2483
KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3145 | 6.3113 | 6.3029 | 6.2921 | 6.2814 | 6.2721 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 4.9718 | 4.7484 | 7.7642 | 7.761 | 7.7529 | 7.7425 | 7.7321 | 7.7231 | 7.7142 | 7.7054 | 7.6956 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896
| ROTHES | CT |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3145 | 6.3113 | 6.3029 | 6.2921 | 6.2814 | 6.2721 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 4.9718 | 4.7484 | 7.7642 | 7.761 | 7.7529 | 7.7425 | 7.7321 | 7.7231 | 7.7142 | 7.7054 | 7.6956 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896
| ROTHES | LW |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3158 | 6.3143 | 6.3103 | 6.3042 | 6.2978 | 6.2929 | 6.2882 | 6.2835 | 6.2784 | 6.2734 | 6.2655 | 6.2655 | 6.2655 | 4.81 | 7.7654 | 7.764 | 7.7601 | 7.7542 | 7.748 | 7.7433 | 7.7387 | 7.7342 | 7.7292 | 7.7243 | 7.7146 | 7.6896 | 7.6896 | 7.6896
| ROTHES | ST |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3175 | 6.3158 | 6.3148 | 6.3125 | 6.3098 | 6.3057 | 6.3018 | 6.2978 | 6.2934 | 6.289 | 6.2807 | 6.2655 | 6.2655 | 6.2655 | 7.7658 | 7.7654 | 7.7644 | 7.7622 | 7.7596 | 7.7557 | 7.7519 | 7.748 | 7.7437 | 7.7395 | 7.7314 | 7.7124 | 7.6932 | 7.6896
| ROTHES | FS |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3182 | 6.3179 | 6.3175 | 6.3153 | 6.3143 | 6.3128 | 6.3114 | 6.3095 | 6.3076 | 6.3058 | 6.3023 | 6.2941 | 6.2866 | 6.2793 | 7.766 | 7.7659 | 7.7658 | 7.7649 | 7.764 | 7.7625 | 7.7611 | 7.7593 | 7.7575 | 7.7558 | 7.7524 | 7.7445 | 7.7372 | 7.7301
DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5976 | 26.5862 | 26.5558 | 26.5301 | 26.5099 | 26.4901 | 26.4707 | 26.4516 | 26.431 | 26.4196 | 26.4196 | 26.4196 | 26.4196 | 23.6937 | 27.0126 | 27.0086 | 27.003 | 26.9959 | 26.9888 | 26.9819 | 26.9752 | 26.9686 | 26.9614 | 26.9543 | 26.9428 | 26.9428 | 26.9428 | 23.882
| ROTHESAY | CT |  |  |  | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5976 | 26.5862 | 26.5564 | 26.5331 | 26.5155 | 26.4983 | 26.4814 | 26.4648 | 26.4469 | 26.4291 | 26.4196 | 26.4196 | 26.4196 | 26.4196 | 27.0126 | 27.0086 | 27.0031 | 26.9969 | 26.9908 | 26.9848 | 26.9789 | 26.9732 | 26.9669 | 26.9607 | 26.9485 | 26.9428 | 26.9428 | 26.9428
| ROTHESAY | LW |  |  |  | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5988 | 26.5878 | 26.5558 | 26.5301 | 26.5099 | 26.4901 | 26.4707 | 26.4516 | 26.431 | 26.4196 | 26.4196 | 26.4196 | 26.4196 | 23.6937 | 27.0132 | 27.0089 | 27.003 | 26.9959 | 26.9888 | 26.9819 | 26.9752 | 26.9686 | 26.9614 | 26.9543 | 26.9428 | 26.9428 | 26.9428 | 23.882
| ROTHESAY | ST |  |  |  | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.6029 | 26.5988 | 26.5893 | 26.5745 | 26.5568 | 26.5374 | 26.5238 | 26.5106 | 26.4964 | 26.4824 | 26.4551 | 26.4196 | 26.4196 | 26.4196 | 27.0151 | 27.0132 | 27.0092 | 27.0064 | 27.0032 | 26.9984 | 26.9937 | 26.9891 | 26.9841 | 26.9793 | 26.9698 | 26.9468 | 26.9428 | 26.9428
| ROTHESAY | FS |  |  |  | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.5536 | 26.6054 | 26.6048 | 26.6041 | 26.5998 | 26.5949 | 26.5858 | 26.5769 | 26.5654 | 26.554 | 26.5439 | 26.5326 | 26.5058 | 26.4807 | 26.4574 | 27.0164 | 27.0161 | 27.0157 | 27.0137 | 27.0113 | 27.0085 | 27.0069 | 27.0048 | 27.0027 | 27.0007 | 26.9967 | 26.9874 | 26.9787 | 26.9706
THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | -1.3869 | -1.3918 | -1.4058 | -1.4291 | -1.4593 | -1.4889 | -1.5181 | -1.5467 | -1.5778 | -1.6086 | -1.6697 | -2.5507 | -2.6065 | -2.6616 | -1.3508 | -1.3611 | -1.3909 | -1.4275 | -1.4635 | -1.4991 | -1.5342 | -1.5687 | -1.6061 | -1.6433 | -1.717 | -2.4156 | -2.482 | -2.5477 | -1.5451 | -1.5555 | -1.5852 | -1.6217 | -1.6576 | -1.6929 | -1.7275 | -1.7615 | -1.7985 | -1.8352 | -1.9079 | -2.7894 | -2.8549 | -2.9196
| ROUSAY | CT |  |  |  | -1.3869 | -1.3908 | -1.4009 | -1.4132 | -1.4309 | -1.4509 | -1.4706 | -1.49 | -1.511 | -1.5319 | -1.5732 | -2.4405 | -2.4825 | -2.524 | -1.3506 | -1.3589 | -1.3805 | -1.4053 | -1.4296 | -1.4535 | -1.477 | -1.5003 | -1.5257 | -1.5508 | -1.6006 | -2.2843 | -2.3344 | -2.3837 | -1.545 | -1.5533 | -1.5748 | -1.5995 | -1.6238 | -1.6477 | -1.6711 | -1.6941 | -1.7191 | -1.7439 | -1.7931 | -2.6601 | -2.7094 | -2.7581
| ROUSAY | LW |  |  |  | -1.3869 | -1.3918 | -1.4058 | -1.4291 | -1.4593 | -1.4889 | -1.5181 | -1.5467 | -1.5778 | -1.6086 | -1.6697 | -2.5507 | -2.6065 | -2.6616 | -1.3508 | -1.3611 | -1.3909 | -1.4275 | -1.4635 | -1.4991 | -1.5342 | -1.5687 | -1.6061 | -1.6433 | -1.717 | -2.4156 | -2.482 | -2.5477 | -1.5451 | -1.5555 | -1.5852 | -1.6217 | -1.6576 | -1.6929 | -1.7275 | -1.7615 | -1.7985 | -1.8352 | -1.9079 | -2.7894 | -2.8549 | -2.9196
| ROUSAY | ST |  |  |  | -1.3855 | -1.3872 | -1.3913 | -1.3976 | -1.4051 | -1.4079 | -1.4109 | -1.4142 | -1.4179 | -1.4221 | -1.432 | -1.869 | -1.8928 | -1.9165 | -1.3477 | -1.3513 | -1.36 | -1.3734 | -1.3896 | -1.3955 | -1.4013 | -1.4069 | -1.4131 | -1.4192 | -1.431 | -1.7775 | -1.8059 | -1.8341 | -1.542 | -1.5457 | -1.5543 | -1.5678 | -1.5839 | -1.5898 | -1.5955 | -1.6012 | -1.6074 | -1.6134 | -1.6252 | -2.062 | -2.09 | -2.1178
| ROUSAY | FS |  |  |  | -1.3847 | -1.3849 | -1.3852 | -1.387 | -1.3892 | -1.3901 | -1.391 | -1.3922 | -1.3933 | -1.3945 | -1.3967 | -1.4019 | -1.4067 | -1.4117 | -1.346 | -1.3465 | -1.3471 | -1.351 | -1.3556 | -1.3576 | -1.3595 | -1.362 | -1.3644 | -1.3668 | -1.3715 | -1.3826 | -1.393 | -1.4027 | -1.5403 | -1.5408 | -1.5415 | -1.5453 | -1.5499 | -1.5519 | -1.5538 | -1.5563 | -1.5588 | -1.5612 | -1.5659 | -1.5769 | -1.5873 | -1.597
CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | NO | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 27.2368 | 27.1988 | 27.0918 | 26.9608 | 26.8868 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 23.562 | 22.4989 | 21.4552 | 27.499 | 27.4893 | 27.4619 | 27.4285 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 23.9368 | 22.8733 | 21.8294
| RUTHRIESTON | CT |  |  |  | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 27.2407 | 27.2154 | 27.1516 | 27.0788 | 27.0072 | 26.9367 | 26.892 | 26.8819 | 26.871 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 23.7167 | 27.5 | 27.4935 | 27.4772 | 27.4586 | 27.4403 | 27.4223 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187
| RUTHRIESTON | LW |  |  |  | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 27.2368 | 27.1988 | 27.0918 | 26.9608 | 26.8868 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 23.562 | 22.4989 | 21.4552 | 27.499 | 27.4893 | 27.4619 | 27.4285 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 23.9368 | 22.8733 | 21.8294
| RUTHRIESTON | ST |  |  |  | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 27.2464 | 27.2294 | 27.1904 | 27.13 | 27.058 | 26.999 | 26.9411 | 26.902 | 26.8855 | 26.8766 | 26.8698 | 26.8698 | 26.8698 | 26.8698 | 27.5014 | 27.4971 | 27.4871 | 27.4717 | 27.4533 | 27.4383 | 27.4235 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187 | 27.4187
| RUTHRIESTON | FS |  |  |  | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 30.761 | 27.2545 | 27.2521 | 27.2491 | 27.2336 | 27.2153 | 27.1969 | 27.1787 | 27.1555 | 27.1326 | 27.1102 | 27.0667 | 26.9627 | 26.8907 | 26.8754 | 27.5035 | 27.5029 | 27.5021 | 27.4982 | 27.4935 | 27.4888 | 27.4841 | 27.4782 | 27.4724 | 27.4666 | 27.4556 | 27.429 | 27.4187 | 27.4187
FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | NO | YES | 3.8207 | 3.8187 | 3.8159 | 3.8132 | 3.8106 | 3.8081 | 3.8056 | 3.8032 | 3.8006 | 3.8004 | 3.8004 | 3.8004 | 3.8004 | 2.4924 | 3.6916 | 3.6864 | 3.6792 | 3.6725 | 3.6659 | 3.6596 | 3.6534 | 3.6473 | 3.6407 | 3.6342 | 3.6213 | 3.5653 | 2.4555 | 2.2404 | 3.5679 | 3.5631 | 3.5565 | 3.5502 | 3.5442 | 3.5384 | 3.5326 | 3.527 | 3.521 | 3.5149 | 3.5031 | 3.4515 | 2.4309 | 2.2164
| SALEN | CT |  |  |  | 3.8208 | 3.8191 | 3.8169 | 3.8151 | 3.8132 | 3.8112 | 3.8092 | 3.8073 | 3.8054 | 3.8035 | 3.8004 | 3.8004 | 3.8004 | 3.8004 | 3.6918 | 3.6874 | 3.6819 | 3.6773 | 3.6725 | 3.6675 | 3.6623 | 3.6576 | 3.6527 | 3.648 | 3.639 | 3.5967 | 3.5585 | 2.4674 | 3.5681 | 3.564 | 3.5589 | 3.5547 | 3.5503 | 3.5457 | 3.5409 | 3.5365 | 3.532 | 3.5277 | 3.5194 | 3.4804 | 3.4442 | 2.4427
| SALEN | LW |  |  |  | 3.8207 | 3.8187 | 3.8159 | 3.8132 | 3.8106 | 3.8081 | 3.8056 | 3.8032 | 3.8006 | 3.8004 | 3.8004 | 3.8004 | 3.8004 | 2.4924 | 3.6916 | 3.6864 | 3.6792 | 3.6725 | 3.6659 | 3.6596 | 3.6534 | 3.6473 | 3.6407 | 3.6342 | 3.6213 | 3.5653 | 2.4555 | 2.2404 | 3.5679 | 3.5631 | 3.5565 | 3.5502 | 3.5442 | 3.5384 | 3.5326 | 3.527 | 3.521 | 3.5149 | 3.5031 | 3.4515 | 2.4309 | 2.2164
| SALEN | ST |  |  |  | 3.8216 | 3.8206 | 3.8195 | 3.8185 | 3.8173 | 3.815 | 3.8127 | 3.8106 | 3.8083 | 3.8062 | 3.802 | 3.8004 | 3.8004 | 3.8004 | 3.6938 | 3.6911 | 3.6885 | 3.686 | 3.6828 | 3.6771 | 3.6714 | 3.6659 | 3.6602 | 3.6548 | 3.6443 | 3.619 | 3.594 | 3.5691 | 3.5699 | 3.5675 | 3.565 | 3.5627 | 3.5598 | 3.5546 | 3.5492 | 3.5442 | 3.539 | 3.5339 | 3.5243 | 3.5009 | 3.4779 | 3.455
| SALEN | FS |  |  |  | 3.8223 | 3.8218 | 3.8215 | 3.8211 | 3.8207 | 3.82 | 3.8192 | 3.8183 | 3.8174 | 3.8165 | 3.8148 | 3.811 | 3.8073 | 3.804 | 3.6956 | 3.6942 | 3.6934 | 3.6925 | 3.6915 | 3.6896 | 3.6878 | 3.6854 | 3.6831 | 3.6809 | 3.6766 | 3.6668 | 3.6577 | 3.6492 | 3.5715 | 3.5703 | 3.5695 | 3.5687 | 3.5678 | 3.566 | 3.5643 | 3.5622 | 3.5601 | 3.558 | 3.5541 | 3.545 | 3.5366 | 3.5288
TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | YES | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 0.89682 | -0.04268 | -0.17763 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.5684 | 1.5684 | 1.5684 | 0.98865 | 0.9884 | 0.98767 | 0.98679 | 0.98592 | 0.98508 | 0.98425 | 0.98344 | 0.98252 | 0.98121 | 0.97864 | -0.079766 | -0.24542 | -0.4081
| SALEN 2 | CT |  |  |  | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 0.89682 | 0.89682 | -0.067264 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.5684 | 1.5684 | 1.5684 | 0.98865 | 0.98843 | 0.98787 | 0.98724 | 0.98662 | 0.98601 | 0.98542 | 0.98483 | 0.9842 | 0.98358 | 0.98234 | -0.017826 | -0.14748 | -0.27506
| SALEN 2 | LW |  |  |  | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 0.89682 | -0.04268 | -0.17763 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.5684 | 1.5684 | 1.5684 | 0.98865 | 0.9884 | 0.98767 | 0.98679 | 0.98592 | 0.98508 | 0.98425 | 0.98344 | 0.98257 | 0.9817 | 0.97998 | -0.079766 | -0.24542 | -0.4081
| SALEN 2 | ST |  |  |  | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.0383 | 1.0383 | 1.0383 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.6488 | 1.6488 | 1.6488 | 0.98872 | 0.98863 | 0.98841 | 0.98807 | 0.98767 | 0.98637 | 0.9851 | 0.98386 | 0.98252 | 0.98121 | 0.97864 | 0.831 | 0.82484 | 0.81869
| SALEN 2 | FS |  |  |  | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.1798 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 1.7293 | 0.98877 | 0.98875 | 0.98874 | 0.98864 | 0.98853 | 0.9881 | 0.98768 | 0.98713 | 0.9866 | 0.98608 | 0.98507 | 0.98266 | 0.98041 | 0.9783
THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | -0.013109 | -0.078092 | -0.14217 | 0.25442 | 0.24754 | 0.23291 | 0.23008 | 0.23008 | 0.23008 | -0.0067236 | -0.045332 | -0.087321 | -0.12897 | -0.21149 | -0.28701 | -0.36331 | -0.43854 | 0.28924 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | -0.038063 | -0.078632 | -0.1608 | -0.23634 | -0.31266 | -0.38792
| SANDAY | CT |  |  |  | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | -0.013109 | -0.078092 | -0.14217 | 0.25442 | 0.24754 | 0.23291 | 0.23008 | 0.23008 | 0.23008 | -0.0067236 | -0.045332 | -0.087321 | -0.12897 | -0.21149 | -0.28701 | -0.36331 | -0.43854 | 0.28924 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | -0.038063 | -0.078632 | -0.1608 | -0.23634 | -0.31266 | -0.38792
| SANDAY | LW |  |  |  | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | -0.0081339 | -0.081623 | 0.25631 | 0.25188 | 0.23973 | 0.23175 | 0.23008 | 0.23008 | 0.23008 | 0.23008 | -0.012198 | -0.044166 | -0.10753 | -0.19389 | -0.28117 | -0.36745 | 0.29016 | 0.288 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | -0.057751 | -0.14319 | -0.2305 | -0.31681
| SANDAY | ST |  |  |  | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.25837 | 0.2581 | 0.25746 | 0.25647 | 0.25528 | 0.25146 | 0.24775 | 0.24411 | 0.24053 | 0.23759 | 0.23272 | 0.23008 | 0.23008 | 0.23008 | 0.29115 | 0.29102 | 0.29071 | 0.29023 | 0.28966 | 0.2878 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611 | 0.28611
| SANDAY | FS |  |  |  | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.47116 | 0.2585 | 0.25845 | 0.2584 | 0.25811 | 0.25777 | 0.25651 | 0.25527 | 0.25368 | 0.25209 | 0.25054 | 0.2475 | 0.24066 | 0.23561 | 0.23246 | 0.29122 | 0.2912 | 0.29117 | 0.29103 | 0.29086 | 0.29025 | 0.28965 | 0.28888 | 0.28811 | 0.28735 | 0.28611 | 0.28611 | 0.28611 | 0.28611
DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6657 | 7.3121 | 6.9551 | 6.6037 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.3419 | 7.2746 | 7.2078 | 7.0754 | 6.6629 | 6.2466 | 5.8367 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.1387 | 6.7365 | 6.3306 | 5.9311
| SANDBANK | CT |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6915 | 7.4132 | 7.1393 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.1055 | 6.7808 | 6.4614 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.168 | 6.8515 | 6.5401
| SANDBANK | LW |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6657 | 7.3121 | 6.9551 | 6.6037 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.3419 | 7.2746 | 7.2078 | 7.0754 | 6.6629 | 6.2466 | 5.8367 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.1387 | 6.7365 | 6.3306 | 5.9311
| SANDBANK | ST |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6541 | 7.5124 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.228 | 7.0619 | 6.8966 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.1255 | 6.9643
| SANDBANK | FS |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449
SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| SANDWICK | CT |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| SANDWICK | LW |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| SANDWICK | ST |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| SANDWICK | FS |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 3.1451 | 3.1413 | 3.1303 | 3.1167 | 3.1033 | 3.0902 | 3.0773 | 3.0647 | 3.051 | 3.0376 | 3.0108 | 2.9898 | 2.9898 | 2.9898 | 2.0821 | 2.0535 | 1.9711 | 1.8696 | 1.7693 | 1.6939 | 1.6859 | 1.678 | 1.6695 | 1.6611 | 1.6445 | -0.20551 | -0.55036 | -0.89293 | 2.0721 | 2.0615 | 2.0309 | 1.9932 | 1.956 | 1.9199 | 1.8842 | 1.8561 | 1.8342 | 1.8336 | -0.026629 | -0.34345 | -0.67921 | -1.0094
| SCALLOWAY | CT |  |  |  | 3.1453 | 3.1425 | 3.1352 | 3.1268 | 3.1184 | 3.1103 | 3.1023 | 3.0945 | 3.086 | 3.0777 | 3.0611 | 3.0413 | 3.0213 | 3.0016 | 2.0838 | 2.0627 | 2.008 | 1.9449 | 1.8825 | 1.8221 | 1.7623 | 1.7035 | 1.6913 | 1.6861 | 1.6758 | 1.6634 | 1.651 | 1.6387 | 2.0727 | 2.0649 | 2.0446 | 2.0212 | 1.998 | 1.9756 | 1.9534 | 1.9316 | 1.9081 | 1.885 | 1.8504 | 1.8336 | 1.8336 | -0.13125
| SCALLOWAY | LW |  |  |  | 3.1451 | 3.1413 | 3.1303 | 3.1167 | 3.1033 | 3.0902 | 3.0773 | 3.0647 | 3.051 | 3.0376 | 3.0108 | 2.9898 | 2.9898 | 2.9898 | 2.0821 | 2.0535 | 1.9711 | 1.8696 | 1.7693 | 1.6939 | 1.6859 | 1.678 | 1.6695 | 1.6611 | 1.6445 | -0.20551 | -0.55036 | -0.89293 | 2.0721 | 2.0615 | 2.0309 | 1.9932 | 1.956 | 1.9199 | 1.8842 | 1.8561 | 1.8342 | 1.8336 | -0.026629 | -0.34345 | -0.67921 | -1.0094
| SCALLOWAY | ST |  |  |  | 3.1462 | 3.1448 | 3.1415 | 3.1363 | 3.13 | 3.1274 | 3.1248 | 3.1223 | 3.1195 | 3.1169 | 3.1118 | 3.0993 | 3.087 | 3.0747 | 2.0906 | 2.08 | 2.0552 | 2.0163 | 1.9695 | 1.95 | 1.9305 | 1.9114 | 1.891 | 1.8714 | 1.8331 | 1.74 | 1.6919 | 1.6842 | 2.0752 | 2.0713 | 2.0621 | 2.0477 | 2.0303 | 2.0231 | 2.0158 | 2.0087 | 2.0012 | 1.9939 | 1.9797 | 1.9451 | 1.9109 | 1.8768
| SCALLOWAY | FS |  |  |  | 3.1469 | 3.1467 | 3.1465 | 3.145 | 3.1432 | 3.1423 | 3.1415 | 3.1404 | 3.1393 | 3.1383 | 3.1363 | 3.1316 | 3.1272 | 3.123 | 2.0955 | 2.094 | 2.0921 | 2.081 | 2.0677 | 2.0613 | 2.0549 | 2.0468 | 2.0388 | 2.0311 | 2.0162 | 1.981 | 1.948 | 1.917 | 2.0771 | 2.0765 | 2.0758 | 2.0717 | 2.0668 | 2.0644 | 2.062 | 2.059 | 2.056 | 2.0532 | 2.0477 | 2.0346 | 2.0223 | 2.0108
TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.038039 | 0.037991 | 0.037853 | 0.037684 | 0.037518 | 0.037356 | 0.037142 | 0.036961 | 0.036765 | 0.036572 | 0.036196 | 0.03532 | 0.03532 | 0.03532 | 0.044035 | 0.044011 | 0.043944 | 0.043905 | 0.043875 | 0.043845 | 0.043805 | 0.043741 | 0.043673 | 0.043606 | 0.043475 | 0.042961 | 0.042956 | 0.042956
| SCAMMADALE | CT |  |  |  | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.038039 | 0.037999 | 0.037895 | 0.037777 | 0.037661 | 0.037548 | 0.037437 | 0.037329 | 0.037211 | 0.037121 | 0.037 | 0.035621 | 0.03532 | 0.03532 | 0.044035 | 0.044015 | 0.043965 | 0.043922 | 0.043901 | 0.04388 | 0.04386 | 0.04384 | 0.043818 | 0.043797 | 0.043755 | 0.043275 | 0.042956 | 0.042956
| SCAMMADALE | LW |  |  |  | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.038039 | 0.037991 | 0.037853 | 0.037684 | 0.037518 | 0.037356 | 0.037198 | 0.037094 | 0.037006 | 0.036918 | 0.036745 | 0.03532 | 0.03532 | 0.03532 | 0.044035 | 0.044011 | 0.043944 | 0.043905 | 0.043875 | 0.043845 | 0.043816 | 0.043788 | 0.043757 | 0.043726 | 0.043666 | 0.042961 | 0.042956 | 0.042956
| SCAMMADALE | ST |  |  |  | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.038053 | 0.038036 | 0.037994 | 0.037929 | 0.037851 | 0.037491 | 0.037142 | 0.036961 | 0.036765 | 0.036572 | 0.036196 | 0.03532 | 0.03532 | 0.03532 | 0.044042 | 0.044033 | 0.044013 | 0.043981 | 0.043944 | 0.04387 | 0.043805 | 0.043741 | 0.043673 | 0.043606 | 0.043475 | 0.04316 | 0.042956 | 0.042956
| SCAMMADALE | FS |  |  |  | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.06783 | 0.038062 | 0.038059 | 0.038056 | 0.038038 | 0.038017 | 0.037898 | 0.037783 | 0.037637 | 0.037491 | 0.037349 | 0.03711 | 0.036762 | 0.036436 | 0.036132 | 0.044046 | 0.044044 | 0.044043 | 0.044034 | 0.044024 | 0.043966 | 0.043923 | 0.043896 | 0.04387 | 0.043844 | 0.043793 | 0.043672 | 0.043559 | 0.043453
ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 13.6927 | 12.9949 | 12.3622 | 16.0464 | 15.9994 | 15.8976 | 15.8323 | 15.7935 | 15.7888 | 15.7888 | 15.7888 | 13.5977 | 13.3325 | 12.7867 | 11.7401 | 10.9024 | 10.143 | 16.0689 | 16.0569 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.7705 | 13.4925 | 13.2139 | 12.6404 | 11.5652 | 10.724 | 9.9613
| SCONE | CT |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 14.23 | 13.7809 | 16.0484 | 16.0119 | 15.9311 | 15.8749 | 15.8308 | 15.8001 | 15.7888 | 15.7888 | 15.7888 | 15.7888 | 13.5635 | 12.9231 | 12.3799 | 11.8459 | 16.0694 | 16.0601 | 16.0382 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.4565 | 12.7837 | 12.213 | 11.6715
| SCONE | LW |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 13.6927 | 12.9949 | 12.3622 | 16.0464 | 15.9994 | 15.8976 | 15.8323 | 15.7935 | 15.7888 | 15.7888 | 15.7888 | 13.5977 | 13.3325 | 12.7867 | 11.7401 | 10.9024 | 10.143 | 16.0689 | 16.0569 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.7705 | 13.4925 | 13.2139 | 12.6404 | 11.5652 | 10.724 | 9.9613
| SCONE | ST |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 16.0608 | 16.0424 | 16.0044 | 15.9469 | 15.8965 | 15.8731 | 15.8498 | 15.8259 | 15.8048 | 15.7954 | 15.7888 | 15.7888 | 13.6455 | 13.3245 | 16.0726 | 16.0679 | 16.0582 | 16.0432 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.5427 | 13.2054
| SCONE | FS |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 16.0693 | 16.0643 | 16.0584 | 16.0386 | 16.0156 | 15.996 | 15.9765 | 15.9527 | 15.9329 | 15.9129 | 15.8866 | 15.8301 | 15.8004 | 15.7891 | 16.0748 | 16.0735 | 16.072 | 16.0669 | 16.0611 | 16.0561 | 16.0511 | 16.045 | 16.0388 | 16.0324 | 16.0297 | 16.0297 | 16.0297 | 16.0297
THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | -0.8259 | -0.84651 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | -0.0045221 | -0.70043 | -0.73303 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | -0.79058 | -0.82057
| SHAPINSAY | CT |  |  |  | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | -0.82426 | -0.84618 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | -0.69783 | -0.73252 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | -0.78819 | -0.8201
| SHAPINSAY | LW |  |  |  | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | -0.8259 | -0.84651 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | -0.0045221 | -0.70043 | -0.73303 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | -0.79058 | -0.82057
| SHAPINSAY | ST |  |  |  | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | -0.3866 | -0.39549 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | -0.33098 | -0.34504 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | -0.33986 | -0.35279
| SHAPINSAY | FS |  |  |  | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.18946 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568 | 0.28568
BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | -0.020841 | -0.098123 | 0.29289 | 0.29247 | 0.29127 | 0.28981 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | -0.043955 | -0.12889 | 0.30701 | 0.30691 | 0.30661 | 0.30625 | 0.3059 | 0.30555 | 0.30521 | 0.30488 | 0.30444 | 0.30389 | 0.30281 | 0.2976 | -0.078846 | -0.17005
| SHIELDAIG | CT |  |  |  | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | -0.04805 | 0.29289 | 0.29254 | 0.29164 | 0.29062 | 0.28961 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | -0.0021624 | -0.073859 | 0.30701 | 0.30693 | 0.3067 | 0.30645 | 0.3062 | 0.30596 | 0.30572 | 0.30549 | 0.30524 | 0.30499 | 0.3045 | 0.29955 | -0.033969 | -0.11096
| SHIELDAIG | LW |  |  |  | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | -0.020841 | -0.098123 | 0.29289 | 0.29247 | 0.29127 | 0.28981 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | -0.043955 | -0.12889 | 0.30701 | 0.30691 | 0.30661 | 0.30625 | 0.3059 | 0.30555 | 0.30521 | 0.30488 | 0.30452 | 0.30417 | 0.30346 | 0.2976 | -0.078846 | -0.17005
| SHIELDAIG | ST |  |  |  | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.29302 | 0.29286 | 0.2925 | 0.29193 | 0.29126 | 0.28905 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.30704 | 0.307 | 0.30691 | 0.30678 | 0.30661 | 0.30606 | 0.30553 | 0.30501 | 0.30444 | 0.30389 | 0.30281 | 0.3002 | 0.29761 | -0.026461
| SHIELDAIG | FS |  |  |  | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.39522 | 0.29309 | 0.29307 | 0.29304 | 0.29288 | 0.29269 | 0.29198 | 0.29126 | 0.29035 | 0.28945 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.2887 | 0.30706 | 0.30706 | 0.30705 | 0.30701 | 0.30696 | 0.30679 | 0.30661 | 0.30639 | 0.30616 | 0.30595 | 0.30552 | 0.30452 | 0.30359 | 0.30271
SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | YES | 3.5722 | 3.5721 | 3.572 | 3.5718 | 3.5716 | 3.5714 | 3.5708 | 3.5702 | 3.5696 | 3.569 | 3.5678 | 3.5634 | 3.2644 | 3.1965 | 3.4819 | 3.4818 | 3.4815 | 3.4811 | 3.4807 | 3.4803 | 3.4791 | 3.478 | 3.4767 | 3.4755 | 3.4731 | 3.2535 | 3.1675 | 3.0833 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.2642 | 3.1794 | 3.0963
| SHIN | CT |  |  |  | 3.5722 | 3.5722 | 3.572 | 3.5719 | 3.5718 | 3.5716 | 3.5715 | 3.5714 | 3.5712 | 3.5711 | 3.5708 | 3.5657 | 3.5605 | 3.2537 | 3.4819 | 3.4819 | 3.4816 | 3.4814 | 3.4811 | 3.4808 | 3.4805 | 3.4803 | 3.48 | 3.4797 | 3.4791 | 3.282 | 3.2174 | 3.1539 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.2923 | 3.2286 | 3.166
| SHIN | LW |  |  |  | 3.5722 | 3.5721 | 3.572 | 3.5718 | 3.5716 | 3.5714 | 3.5712 | 3.571 | 3.5708 | 3.5706 | 3.5702 | 3.5634 | 3.2644 | 3.1965 | 3.4819 | 3.4818 | 3.4815 | 3.4811 | 3.4807 | 3.4803 | 3.48 | 3.4796 | 3.4791 | 3.4787 | 3.4779 | 3.2535 | 3.1675 | 3.0833 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.2642 | 3.1794 | 3.0963
| SHIN | ST |  |  |  | 3.5722 | 3.5722 | 3.5721 | 3.5721 | 3.572 | 3.5714 | 3.5708 | 3.5702 | 3.5696 | 3.569 | 3.5678 | 3.5649 | 3.5619 | 3.2893 | 3.482 | 3.4819 | 3.4818 | 3.4817 | 3.4815 | 3.4803 | 3.4791 | 3.478 | 3.4767 | 3.4755 | 3.4731 | 3.2716 | 3.2351 | 3.1989 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.282 | 3.2461 | 3.2104
| SHIN | FS |  |  |  | 3.5722 | 3.5722 | 3.5722 | 3.5722 | 3.5722 | 3.572 | 3.5718 | 3.5715 | 3.5713 | 3.571 | 3.5706 | 3.5695 | 3.5684 | 3.5674 | 3.482 | 3.482 | 3.482 | 3.4819 | 3.4819 | 3.4815 | 3.4811 | 3.4806 | 3.4801 | 3.4796 | 3.4787 | 3.4765 | 3.4744 | 3.4723 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905 | 3.4905
FORT WILLIAM | SHONA BEAG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803
| SHONA BEAG | CT |  |  |  | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803
| SHONA BEAG | LW |  |  |  | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803
| SHONA BEAG | ST |  |  |  | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803
| SHONA BEAG | FS |  |  |  | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.021256 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.011928 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803 | 0.013803
KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 38.4827 | 38.4527 | 38.3665 | 38.2603 | 38.1551 | 38.051 | 37.9477 | 37.8461 | 37.7363 | 37.6281 | 37.4368 | 37.0578 | 28.0269 | 26.6452 | 34.3226 | 34.2276 | 33.955 | 33.6192 | 33.5167 | 33.4569 | 33.3975 | 33.3391 | 33.2976 | 27.1424 | 25.7971 | 23.8591 | 22.1984 | 20.5684 | 33.7154 | 33.6875 | 33.6376 | 33.576 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.3847 | 26.016 | 23.9702 | 22.3016 | 20.671
| SKENE | CT |  |  |  | 38.4861 | 38.4666 | 38.4162 | 38.3581 | 38.3001 | 38.2426 | 38.1852 | 38.1287 | 38.0678 | 38.008 | 37.8879 | 37.3619 | 37.1894 | 37.0578 | 34.3333 | 34.2717 | 34.1123 | 33.9283 | 33.7452 | 33.567 | 33.534 | 33.5015 | 33.4665 | 33.4321 | 33.3631 | 27.3598 | 26.2871 | 25.2409 | 33.7188 | 33.6994 | 33.6664 | 33.6327 | 33.5991 | 33.5657 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.5408 | 26.4503 | 25.3857
| SKENE | LW |  |  |  | 38.4827 | 38.4527 | 38.3665 | 38.2603 | 38.1551 | 38.051 | 37.9477 | 37.8461 | 37.7363 | 37.6281 | 37.4368 | 37.0578 | 28.0269 | 26.6452 | 34.3226 | 34.2276 | 33.955 | 33.6192 | 33.5167 | 33.4569 | 33.3975 | 33.3391 | 33.2976 | 27.1424 | 25.7971 | 23.8591 | 22.1984 | 20.5684 | 33.7154 | 33.6875 | 33.6376 | 33.576 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.3847 | 26.016 | 23.9702 | 22.3016 | 20.671
| SKENE | ST |  |  |  | 38.4911 | 38.479 | 38.4508 | 38.4067 | 38.3538 | 38.3293 | 38.3047 | 38.2806 | 38.2546 | 38.2294 | 38.179 | 37.8798 | 37.7602 | 37.6431 | 34.349 | 34.3108 | 34.2215 | 34.0823 | 33.9147 | 33.8372 | 33.7595 | 33.6833 | 33.6011 | 33.5594 | 33.5304 | 33.3415 | 33.2727 | 33.2101 | 33.7237 | 33.7117 | 33.6864 | 33.6609 | 33.6302 | 33.616 | 33.6017 | 33.5878 | 33.5727 | 33.5581 | 33.5453 | 33.3507 | 33.3507 | 33.3507
| SKENE | FS |  |  |  | 38.4967 | 38.495 | 38.4928 | 38.4808 | 38.4666 | 38.4586 | 38.4506 | 38.4405 | 38.4306 | 38.421 | 38.4019 | 38.3562 | 38.3128 | 38.2718 | 34.3667 | 34.3614 | 34.3544 | 34.3166 | 34.2715 | 34.2462 | 34.2208 | 34.1892 | 34.1578 | 34.1274 | 34.067 | 33.9223 | 33.7851 | 33.6554 | 33.7293 | 33.7277 | 33.7254 | 33.7135 | 33.6993 | 33.6914 | 33.6863 | 33.6805 | 33.6747 | 33.6691 | 33.6581 | 33.6316 | 33.6064 | 33.5827
BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 7.7413 | 7.7325 | 7.7197 | 7.713 | 7.7065 | 7.7 | 7.692 | 7.6836 | 7.6746 | 7.6653 | 7.6462 | 7.6025 | 7.5788 | 6.2179 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 6.1405
| SKULAMUS | CT |  |  |  | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 7.7413 | 7.7336 | 7.7223 | 7.7171 | 7.7118 | 7.7057 | 7.6967 | 7.6875 | 7.6789 | 7.6703 | 7.6577 | 7.6091 | 7.5911 | 7.5734 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296
| SKULAMUS | LW |  |  |  | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 7.7414 | 7.7325 | 7.7197 | 7.713 | 7.7065 | 7.7 | 7.692 | 7.6836 | 7.6746 | 7.6653 | 7.652 | 7.6025 | 7.5788 | 6.2179 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 6.1405
| SKULAMUS | ST |  |  |  | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 7.7421 | 7.7371 | 7.7309 | 7.7283 | 7.7253 | 7.7151 | 7.7031 | 7.6911 | 7.6789 | 7.6668 | 7.6462 | 7.6138 | 7.6034 | 7.5932 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296
| SKULAMUS | FS |  |  |  | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 8.0516 | 7.7425 | 7.7398 | 7.7369 | 7.7358 | 7.7345 | 7.7308 | 7.7269 | 7.7221 | 7.7173 | 7.7125 | 7.704 | 7.6865 | 7.6709 | 7.6563 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296 | 7.6296
WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 31.9434 | 31.8996 | 31.7877 | 31.6521 | 31.5174 | 31.3887 | 31.2805 | 31.2134 | 31.1755 | 31.1376 | 31.0582 | 30.9325 | 30.8521 | 30.7763 | 32.278 | 32.2668 | 32.2382 | 32.2036 | 32.1692 | 32.135 | 32.1009 | 32.0669 | 32.0302 | 31.9936 | 31.9166 | 31.8536 | 31.8536 | 31.8536
| SPRINGHILL | CT |  |  |  | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 31.9519 | 31.927 | 31.8726 | 31.8113 | 31.7485 | 31.6845 | 31.6211 | 31.5565 | 31.4861 | 31.4148 | 31.295 | 31.1413 | 31.0358 | 30.953 | 32.2802 | 32.2738 | 32.2599 | 32.2443 | 32.2282 | 32.2119 | 32.1957 | 32.1792 | 32.1612 | 32.143 | 32.1055 | 31.9971 | 31.895 | 31.8536
| SPRINGHILL | LW |  |  |  | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 31.9434 | 31.8996 | 31.7877 | 31.6521 | 31.5174 | 31.3887 | 31.2805 | 31.2134 | 31.1755 | 31.1376 | 31.0582 | 30.9325 | 30.8521 | 30.7763 | 32.278 | 32.2668 | 32.2382 | 32.2036 | 32.1692 | 32.135 | 32.1009 | 32.0669 | 32.0302 | 31.9936 | 31.9166 | 31.8536 | 31.8536 | 31.8536
| SPRINGHILL | ST |  |  |  | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 31.9687 | 31.9508 | 31.9151 | 31.8623 | 31.7986 | 31.7507 | 31.7034 | 31.6555 | 31.6032 | 31.5503 | 31.4418 | 31.2281 | 31.1641 | 31.1037 | 32.2845 | 32.2799 | 32.2708 | 32.2573 | 32.241 | 32.2288 | 32.2167 | 32.2045 | 32.1911 | 32.1776 | 32.1499 | 32.0812 | 32.0192 | 31.9607
| SPRINGHILL | FS |  |  |  | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 31.9876 | 31.9815 | 31.9756 | 31.9577 | 31.9377 | 31.9208 | 31.9038 | 31.8828 | 31.8616 | 31.8406 | 31.7983 | 31.6924 | 31.5948 | 31.5062 | 32.2893 | 32.2877 | 32.2862 | 32.2817 | 32.2765 | 32.2722 | 32.2679 | 32.2625 | 32.2571 | 32.2517 | 32.2409 | 32.2139 | 32.189 | 32.1663
BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8143 | 2.0858 | 1.8406 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7986 | 5.3124 | 2.5702 | 2.2667 | 5.5504 | 5.536 | 5.4916 | 5.4361 | 5.3803 | 5.3244 | 5.2685 | 5.2134 | 5.1539 | 5.0956 | 4.978 | 4.1994 | 0.38961 | 0.1034
| ST CYRUS | CT |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.9734 | 2.3113 | 2.1355 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.513 | 2.8546 | 2.6329 | 5.5504 | 5.536 | 5.4982 | 5.454 | 5.4096 | 5.3651 | 5.3205 | 5.2766 | 5.2291 | 5.1826 | 5.0888 | 4.3886 | 0.65783 | 0.44881
| ST CYRUS | LW |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8143 | 2.0858 | 1.8406 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7986 | 5.3124 | 2.5702 | 2.2667 | 5.5513 | 5.5361 | 5.4916 | 5.4361 | 5.3803 | 5.3244 | 5.2685 | 5.2134 | 5.1539 | 5.0956 | 4.978 | 4.1994 | 0.38961 | 0.1034
| ST CYRUS | ST |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.2567 | 4.6274 | 4.5211 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7104 | 4.6598 | 4.5257 | 5.5566 | 5.5523 | 5.5423 | 5.5263 | 5.5067 | 5.4806 | 5.4544 | 5.4287 | 5.4008 | 5.3738 | 5.3196 | 4.9443 | 3.0569 | 2.9304
| ST CYRUS | FS |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.5585 | 5.5578 | 5.5569 | 5.5523 | 5.5467 | 5.5382 | 5.5297 | 5.5189 | 5.5082 | 5.4978 | 5.4771 | 5.4273 | 5.3798 | 5.335
ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 09165377 | NO | NO | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9302 | 34.9274 | 34.9203 | 34.9142 | 34.9121 | 34.9101 | 34.908 | 34.906 | 34.9038 | 34.9017 | 34.3297 | 29.8891 | 29.8891 | 29.8891
| ST FERGUS GAS TERM | CT |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9302 | 34.9274 | 34.9203 | 34.9142 | 34.9121 | 34.9101 | 34.908 | 34.906 | 34.9038 | 34.9017 | 34.3297 | 29.8891 | 29.8891 | 29.8891
| ST FERGUS GAS TERM | LW |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9308 | 34.9287 | 34.9227 | 34.9153 | 34.9132 | 34.9113 | 34.9095 | 34.9076 | 34.9057 | 34.9038 | 34.3322 | 29.8891 | 29.8891 | 29.8891
| ST FERGUS GAS TERM | ST |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.8979 | 38.6873 | 38.6873 | 38.6873 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.7054 | 29.5212 | 29.5212 | 29.5212 | 34.9315 | 34.9309 | 34.9294 | 34.9271 | 34.9244 | 34.9209 | 34.9175 | 34.9147 | 34.9138 | 34.9129 | 34.6273 | 34.4455 | 34.4413 | 34.4372
| ST FERGUS GAS TERM | FS |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34.9318 | 34.9316 | 34.9315 | 34.9307 | 34.9298 | 34.9286 | 34.9275 | 34.926 | 34.9245 | 34.9231 | 34.9203 | 34.9146 | 34.913 | 34.9115
ST FILLANS | ST FILLANS P S | MINIMUM HEADROOM | NN 69422464 | YES | YES | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | CT |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | LW |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | ST |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| ST FILLANS P S | FS |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 28.2508 | 28.2495 | 28.2459 | 28.2416 | 28.2374 | 28.2332 | 28.2276 | 28.2216 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.6807 | 27.6792 | 27.6753 | 27.6705 | 27.6658 | 27.6612 | 27.655 | 27.6483 | 27.6411 | 27.6341 | 27.6203 | 27.5827 | 27.5827 | 27.5827
| ST MACHAR | CT |  |  |  | 28.2511 | 28.2503 | 28.2484 | 28.2464 | 28.2443 | 28.2422 | 28.2402 | 28.2383 | 28.2362 | 28.2341 | 28.23 | 28.2173 | 28.2173 | 28.2173 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.681 | 27.6801 | 27.6781 | 27.6758 | 27.6735 | 27.6712 | 27.669 | 27.6668 | 27.6645 | 27.6622 | 27.6576 | 27.6359 | 27.6137 | 27.5925
| ST MACHAR | LW |  |  |  | 28.2508 | 28.2495 | 28.2459 | 28.2416 | 28.2374 | 28.2332 | 28.2292 | 28.2252 | 28.2208 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.6807 | 27.6792 | 27.6753 | 27.6705 | 27.6658 | 27.6612 | 27.6567 | 27.6523 | 27.6475 | 27.6427 | 27.6326 | 27.5827 | 27.5827 | 27.5827
| ST MACHAR | ST |  |  |  | 28.2512 | 28.2502 | 28.2478 | 28.2443 | 28.24 | 28.2337 | 28.2276 | 28.2216 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.6811 | 27.68 | 27.6774 | 27.6735 | 27.6688 | 27.6618 | 27.655 | 27.6483 | 27.6411 | 27.6341 | 27.6203 | 27.5842 | 27.5827 | 27.5827
| ST MACHAR | FS |  |  |  | 28.2519 | 28.2518 | 28.2516 | 28.2509 | 28.25 | 28.2483 | 28.2466 | 28.2444 | 28.2423 | 28.2402 | 28.2361 | 28.2264 | 28.2173 | 28.2173 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.5357 | 27.682 | 27.6818 | 27.6816 | 27.6808 | 27.6798 | 27.6779 | 27.676 | 27.6736 | 27.6712 | 27.6689 | 27.6644 | 27.6537 | 27.643 | 27.6326
THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 6.2837 | 6.2807 | 6.273 | 6.2631 | 6.2533 | 6.2437 | 6.2342 | 6.2249 | 6.2147 | 6.2047 | 6.1848 | 1.9278 | 1.6152 | 1.3069 | 5.3484 | 5.3484 | 3.9262 | 3.8037 | 3.682 | 3.5622 | 3.4448 | 3.3296 | 3.2036 | 3.079 | 2.832 | 0.8802 | 0.5035 | 0.13188 | 5.2015 | 5.2015 | 5.2015 | 3.9632 | 3.8825 | 3.803 | 3.7252 | 3.6487 | 3.5652 | 3.4742 | 3.2326 | 0.69094 | 0.32402 | -0.037961
| ST MARYS | CT |  |  |  | 6.2837 | 6.2807 | 6.273 | 6.2642 | 6.2555 | 6.2469 | 6.2385 | 6.2303 | 6.2213 | 6.2123 | 6.1947 | 2.0904 | 1.8387 | 1.5904 | 5.3484 | 5.3484 | 3.9262 | 3.8165 | 3.7085 | 3.6023 | 3.4982 | 3.396 | 3.2843 | 3.1739 | 2.9549 | 1.0762 | 0.77285 | 0.47353 | 5.2015 | 5.2015 | 5.2015 | 3.9716 | 3.9 | 3.8296 | 3.7606 | 3.6928 | 3.6187 | 3.5455 | 3.3528 | 0.88184 | 0.58637 | 0.29482
| ST MARYS | LW |  |  |  | 6.2841 | 6.2812 | 6.2731 | 6.2631 | 6.2533 | 6.2437 | 6.2342 | 6.2249 | 6.2147 | 6.2047 | 6.1848 | 1.9278 | 1.6152 | 1.3069 | 5.3484 | 5.3484 | 3.9276 | 3.8037 | 3.682 | 3.5622 | 3.4448 | 3.3296 | 3.2036 | 3.079 | 2.832 | 0.8802 | 0.5035 | 0.13188 | 5.2015 | 5.2015 | 5.2015 | 3.9632 | 3.8825 | 3.803 | 3.7252 | 3.6487 | 3.5652 | 3.4742 | 3.2326 | 0.69094 | 0.32402 | -0.037961
| ST MARYS | ST |  |  |  | 6.2849 | 6.2839 | 6.2815 | 6.2778 | 6.2734 | 6.2707 | 6.268 | 6.2655 | 6.2627 | 6.2599 | 6.2545 | 3.2351 | 3.2351 | 3.2351 | 5.3484 | 5.3484 | 5.3484 | 3.9858 | 3.9307 | 3.8972 | 3.8647 | 3.833 | 3.7979 | 3.7638 | 3.6971 | 2.758 | 2.5975 | 2.4374 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 3.9826 | 3.9593 | 3.9367 | 3.8924 | 2.7161 | 2.6097 | 2.5036
| ST MARYS | FS |  |  |  | 6.2854 | 6.2852 | 6.285 | 6.284 | 6.2827 | 6.2818 | 6.2809 | 6.2798 | 6.2787 | 6.2776 | 6.2755 | 6.2704 | 6.2657 | 6.2612 | 5.3484 | 5.3484 | 5.3484 | 5.3484 | 5.3484 | 5.3484 | 5.3484 | 5.3484 | 3.9968 | 3.9833 | 3.9571 | 3.8945 | 3.8358 | 3.7801 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 5.2015 | 3.9844 | 3.9475
WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 27.5476 | 27.529 | 27.4697 | 27.4383 | 27.4144 | 27.4113 | 27.4083 | 27.4054 | 27.4021 | 27.399 | 27.3926 | 27.3704 | 27.3477 | 27.3254 | 25.1782 | 25.1544 | 25.0787 | 25.0386 | 24.9995 | 24.962 | 24.9251 | 24.8889 | 24.8497 | 24.8109 | 24.7329 | 24.547 | 24.3775 | 24.3411 | 25.4054 | 25.3897 | 25.3395 | 25.3129 | 25.2869 | 25.2621 | 25.2376 | 25.2136 | 25.1876 | 25.1619 | 25.1102 | 24.9304 | 24.8642 | 24.8642
| ST NICHOLAS | CT |  |  |  | 27.5491 | 27.5353 | 27.491 | 27.4755 | 27.4598 | 27.4435 | 27.4244 | 27.4137 | 27.4118 | 27.4099 | 27.4067 | 27.3967 | 27.3864 | 27.3765 | 25.1801 | 25.1625 | 25.1059 | 25.086 | 25.0661 | 25.0452 | 25.0193 | 24.9904 | 24.9672 | 24.9448 | 24.9057 | 24.7826 | 24.6664 | 24.5925 | 25.4067 | 25.3951 | 25.3575 | 25.3443 | 25.3311 | 25.3172 | 25.3001 | 25.2809 | 25.2655 | 25.2507 | 25.2247 | 25.1431 | 25.06 | 24.9797
| ST NICHOLAS | LW |  |  |  | 27.5476 | 27.529 | 27.4697 | 27.4383 | 27.4144 | 27.4113 | 27.4083 | 27.4054 | 27.4021 | 27.399 | 27.3926 | 27.3704 | 27.3477 | 27.3254 | 25.1782 | 25.1544 | 25.0787 | 25.0386 | 24.9995 | 24.962 | 24.9251 | 24.8889 | 24.8497 | 24.8109 | 24.7329 | 24.547 | 24.3775 | 24.3411 | 25.4054 | 25.3897 | 25.3395 | 25.3129 | 25.2869 | 25.2621 | 25.2376 | 25.2136 | 25.1876 | 25.1619 | 25.1102 | 24.9304 | 24.8642 | 24.8642
| ST NICHOLAS | ST |  |  |  | 27.5533 | 27.544 | 27.5157 | 27.5038 | 27.4892 | 27.4653 | 27.4391 | 27.4157 | 27.4121 | 27.4096 | 27.4048 | 27.3923 | 27.3799 | 27.3678 | 25.1855 | 25.1736 | 25.1375 | 25.1222 | 25.1036 | 25.0731 | 25.0396 | 25.0046 | 24.9719 | 24.9402 | 24.882 | 24.729 | 24.6179 | 24.5277 | 25.4103 | 25.4024 | 25.3785 | 25.3683 | 25.356 | 25.3358 | 25.3136 | 25.2903 | 25.2687 | 25.2477 | 25.2091 | 25.1076 | 25.0073 | 24.9094
| ST NICHOLAS | FS |  |  |  | 27.5577 | 27.5534 | 27.5413 | 27.5371 | 27.5324 | 27.5242 | 27.5161 | 27.5066 | 27.4971 | 27.4879 | 27.47 | 27.4308 | 27.4128 | 27.4088 | 25.1911 | 25.1856 | 25.1701 | 25.1648 | 25.1587 | 25.1483 | 25.138 | 25.1258 | 25.1137 | 25.1019 | 25.0791 | 25.0289 | 24.9795 | 24.9313 | 25.414 | 25.4104 | 25.4001 | 25.3966 | 25.3926 | 25.3856 | 25.3788 | 25.3707 | 25.3627 | 25.3548 | 25.3397 | 25.3065 | 25.2737 | 25.2417
ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0.41857 | 0.41771 | 0.41523 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.39027 | 0.38937 | 0.38677 | 0.38358 | 0.38046 | 0.37741 | 0.37443 | 0.37151 | 0.36836 | 0.36522 | 0.35902 | 0.33454 | 0.31617 | 0.31617 | 0.41638 | 0.41629 | 0.41603 | 0.41572 | 0.41541 | 0.41511 | 0.41481 | 0.41452 | 0.41421 | 0.4139 | 0.41328 | 0.41086 | 0.40841 | 0.406
| STOCKINISH | CT |  |  |  | 0.41857 | 0.41785 | 0.416 | 0.41388 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.39027 | 0.38952 | 0.38758 | 0.38535 | 0.38317 | 0.38105 | 0.37896 | 0.37692 | 0.37472 | 0.37253 | 0.3682 | 0.34551 | 0.32263 | 0.31617 | 0.41638 | 0.41631 | 0.41611 | 0.41589 | 0.41568 | 0.41547 | 0.41526 | 0.41506 | 0.41484 | 0.41462 | 0.41419 | 0.41194 | 0.40968 | 0.40744
| STOCKINISH | LW |  |  |  | 0.41857 | 0.41771 | 0.41523 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.39027 | 0.38937 | 0.38677 | 0.38358 | 0.38046 | 0.37741 | 0.37443 | 0.37151 | 0.36836 | 0.36522 | 0.35902 | 0.33454 | 0.31617 | 0.31617 | 0.41638 | 0.41629 | 0.41603 | 0.41572 | 0.41541 | 0.41511 | 0.41481 | 0.41452 | 0.41421 | 0.4139 | 0.41328 | 0.41086 | 0.40841 | 0.406
| STOCKINISH | ST |  |  |  | 0.41883 | 0.41853 | 0.41782 | 0.41672 | 0.41541 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.39055 | 0.39023 | 0.38949 | 0.38834 | 0.38696 | 0.38466 | 0.3824 | 0.38021 | 0.37783 | 0.3755 | 0.37096 | 0.36001 | 0.34922 | 0.33847 | 0.41641 | 0.41638 | 0.4163 | 0.41619 | 0.41605 | 0.41582 | 0.4156 | 0.41538 | 0.41515 | 0.41492 | 0.41447 | 0.41338 | 0.41231 | 0.41125
| STOCKINISH | FS |  |  |  | 0.41897 | 0.41893 | 0.41888 | 0.41857 | 0.41821 | 0.41749 | 0.41678 | 0.41586 | 0.41496 | 0.41408 | 0.41385 | 0.41385 | 0.41385 | 0.41385 | 0.39069 | 0.39065 | 0.3906 | 0.39028 | 0.38989 | 0.38914 | 0.38839 | 0.38743 | 0.38649 | 0.38556 | 0.38377 | 0.37952 | 0.37557 | 0.37193 | 0.41642 | 0.41642 | 0.41641 | 0.41638 | 0.41634 | 0.41627 | 0.41619 | 0.4161 | 0.41601 | 0.41591 | 0.41574 | 0.41531 | 0.41492 | 0.41456
PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | -0.20743 | -0.33943 | -0.50964 | -0.68 | -0.84427 | -1.0025 | -1.1545 | -1.3006 | -1.3906 | -1.4355 | -1.5238 | -1.7459 | -1.9962 | -2.2652 | -0.17235 | -0.27819 | -0.41433 | -0.55063 | -0.68207 | -0.80864 | -0.93034 | -1.0472 | -1.1193 | -1.1555 | -1.2267 | -1.4055 | -1.6068 | -1.8231 | -0.21821 | -0.35133 | -0.52243 | -0.6937 | -0.85885 | -1.0179 | -1.1708 | -1.3176 | -1.4081 | -1.4534 | -1.5423 | -1.7661 | -2.0181 | -2.2889
| STONEFIELD | CT |  |  |  | -0.20743 | -0.33943 | -0.50964 | -0.68 | -0.84427 | -1.0025 | -1.1545 | -1.3006 | -1.3906 | -1.4355 | -1.5238 | -1.7459 | -1.9962 | -2.2652 | -0.17235 | -0.27819 | -0.41433 | -0.55063 | -0.68207 | -0.80864 | -0.93034 | -1.0472 | -1.1193 | -1.1555 | -1.2267 | -1.4055 | -1.6068 | -1.8231 | -0.21821 | -0.35133 | -0.52243 | -0.6937 | -0.85885 | -1.0179 | -1.1708 | -1.3176 | -1.4081 | -1.4534 | -1.5423 | -1.7661 | -2.0181 | -2.2889
| STONEFIELD | LW |  |  |  | -0.018615 | -0.040451 | -0.066457 | -0.095815 | -0.12806 | -0.1629 | -0.20005 | -0.2392 | -0.28711 | -0.33643 | -0.43773 | -0.71065 | -1.0434 | -1.4375 | -0.020511 | -0.038375 | -0.059477 | -0.083321 | -0.10948 | -0.13771 | -0.16779 | -0.19948 | -0.23821 | -0.27807 | -0.35993 | -0.58141 | -0.85092 | -1.1697 | -0.027089 | -0.049455 | -0.075672 | -0.10526 | -0.13777 | -0.17291 | -0.21038 | -0.24988 | -0.29822 | -0.34798 | -0.4502 | -0.72534 | -1.0609 | -1.4586
| STONEFIELD | ST |  |  |  | 0.015937 | 0.0090474 | -0.0086387 | -0.017337 | -0.027285 | -0.039604 | -0.051576 | -0.063208 | -0.074998 | -0.091865 | -0.12424 | -0.21302 | -0.29865 | -0.39904 | 0.0081027 | -0.0033375 | -0.011667 | -0.019918 | -0.02803 | -0.038144 | -0.047973 | -0.057524 | -0.067219 | -0.080985 | -0.10742 | -0.17976 | -0.24955 | -0.33118 | 0.00604 | -0.0054631 | -0.015844 | -0.026068 | -0.036086 | -0.048473 | -0.060511 | -0.072206 | -0.084056 | -0.10104 | -0.13363 | -0.22306 | -0.30929 | -0.41045
| STONEFIELD | FS |  |  |  | 0.0090474 | -0.0086387 | -0.017508 | -0.031969 | -0.046803 | -0.061558 | -0.076112 | -0.090538 | -0.10476 | -0.11878 | -0.14621 | -0.22749 | -0.31429 | -0.39874 | -0.0031895 | -0.011295 | -0.019405 | -0.031489 | -0.043434 | -0.055352 | -0.067109 | -0.078784 | -0.090294 | -0.10164 | -0.12383 | -0.18951 | -0.25956 | -0.32772 | -0.0053416 | -0.015539 | -0.025739 | -0.040903 | -0.055885 | -0.070775 | -0.085463 | -0.10001 | -0.11436 | -0.12851 | -0.15617 | -0.2382 | -0.3258 | -0.41106
FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 30.9803 | 30.9704 | 30.9418 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 21.4058 | 17.8222 | 16.6061 | 29.8792 | 29.8271 | 29.6778 | 29.4934 | 29.31 | 29.1278 | 28.9464 | 28.7679 | 23.7592 | 23.3142 | 22.4219 | 19.8186 | 16.5499 | 15.0844 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 23.5337 | 23.0808 | 22.6357 | 21.7431 | 18.7995 | 14.989 | 13.523
| STONEHAVEN | CT |  |  |  | 30.9813 | 30.9746 | 30.9572 | 30.937 | 30.9168 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 22.8515 | 20.1986 | 19.4007 | 29.8843 | 29.8491 | 29.7581 | 29.6527 | 29.5472 | 29.4418 | 29.3362 | 29.2323 | 29.1202 | 29.0107 | 28.7897 | 22.1691 | 19.4139 | 18.4522 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 23.5849 | 21.1509 | 17.8539 | 16.892
| STONEHAVEN | LW |  |  |  | 30.9803 | 30.9704 | 30.9418 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 21.4058 | 17.8222 | 16.6061 | 29.8792 | 29.8271 | 29.6778 | 29.4934 | 29.31 | 29.1278 | 28.9464 | 28.7679 | 23.7592 | 23.3142 | 22.4219 | 19.8186 | 16.5499 | 15.0844 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 23.5337 | 23.0808 | 22.6357 | 21.7431 | 18.7995 | 14.989 | 13.523
| STONEHAVEN | ST |  |  |  | 30.9831 | 30.9789 | 30.9693 | 30.9542 | 30.936 | 30.9245 | 30.9131 | 30.9127 | 30.9127 | 30.9127 | 30.9127 | 23.4912 | 22.4717 | 22.4717 | 29.8933 | 29.8717 | 29.8212 | 29.7424 | 29.6474 | 29.5876 | 29.5276 | 29.4687 | 29.4052 | 29.3438 | 29.2206 | 28.5593 | 22.4485 | 21.7775 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 23.1706 | 21.3296 | 20.6584
| STONEHAVEN | FS |  |  |  | 30.985 | 30.9844 | 30.9836 | 30.9796 | 30.9747 | 30.971 | 30.9672 | 30.9625 | 30.9578 | 30.9533 | 30.9443 | 30.9227 | 30.9127 | 30.9127 | 29.9034 | 29.9003 | 29.8962 | 29.8751 | 29.8498 | 29.8302 | 29.8104 | 29.7858 | 29.7614 | 29.7378 | 29.6907 | 29.578 | 29.4711 | 29.3701 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677 | 30.2677
STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 67734109 | YES | NO | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.8105 | 8.8105 | 8.8104 | 8.8103 | 8.8102 | 8.8101 | 8.81 | 8.8099 | 8.8098 | 8.8096 | 8.8094 | 8.8089 | 8.8084 | 8.8079 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537
| STONEYHILL | CT |  |  |  | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.8105 | 8.8105 | 8.8104 | 8.8103 | 8.8103 | 8.8102 | 8.8101 | 8.81 | 8.81 | 8.8099 | 8.8097 | 8.8094 | 8.809 | 8.8087 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537
| STONEYHILL | LW |  |  |  | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.8105 | 8.8105 | 8.8104 | 8.8103 | 8.8102 | 8.8101 | 8.81 | 8.8099 | 8.8098 | 8.8096 | 8.8094 | 8.8089 | 8.8084 | 8.8079 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537
| STONEYHILL | ST |  |  |  | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.8105 | 8.8105 | 8.8105 | 8.8104 | 8.8104 | 8.8103 | 8.8103 | 8.8102 | 8.8102 | 8.8101 | 8.81 | 8.8098 | 8.8096 | 8.8094 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537
| STONEYHILL | FS |  |  |  | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.0989 | 8.8105 | 8.8105 | 8.8105 | 8.8105 | 8.8105 | 8.8105 | 8.8105 | 8.8104 | 8.8104 | 8.8104 | 8.8104 | 8.8103 | 8.8102 | 8.8101 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537 | 8.9537
PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.45 | 25.4258 | 25.3931 | 25.3559 | 25.3189 | 25.2819 | 25.2418 | 25.2061 | 25.1723 | 25.1568 | 25.1249 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
| STONEYWOOD T1&T2 | CT |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4502 | 25.4288 | 25.3991 | 25.3669 | 25.3341 | 25.2995 | 25.2608 | 25.2237 | 25.1866 | 25.1636 | 25.1249 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
| STONEYWOOD T1&T2 | LW |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.45 | 25.4258 | 25.3931 | 25.3559 | 25.3189 | 25.2819 | 25.2418 | 25.2061 | 25.1723 | 25.1568 | 25.1278 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
| STONEYWOOD T1&T2 | ST |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4558 | 25.4423 | 25.4265 | 25.4084 | 25.389 | 25.3635 | 25.3352 | 25.3082 | 25.2803 | 25.2622 | 25.231 | 25.1717 | 25.1221 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
| STONEYWOOD T1&T2 | FS |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4603 | 25.4525 | 25.4445 | 25.4355 | 25.4267 | 25.416 | 25.4048 | 25.3938 | 25.3831 | 25.3765 | 25.3635 | 25.3399 | 25.3224 | 25.3057 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | YES | NO | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2927 | 15.2643 | 15.2261 | 15.1825 | 15.1391 | 15.0958 | 15.0488 | 15.007 | 14.9673 | 14.9516 | 14.9213 | 14.8253 | 14.8181 | 14.8181 | 16.0309 | 16.0197 | 16.0046 | 15.9875 | 15.9704 | 15.9534 | 15.9349 | 15.9184 | 15.9028 | 15.8957 | 15.881 | 15.8464 | 15.8135 | 15.7811
| STONEYWOOD T3 | CT |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2929 | 15.2679 | 15.2331 | 15.1953 | 15.1569 | 15.1164 | 15.071 | 15.0276 | 14.9841 | 14.958 | 14.9213 | 14.8371 | 14.8181 | 14.8181 | 16.031 | 16.0211 | 16.0074 | 15.9925 | 15.9774 | 15.9615 | 15.9436 | 15.9266 | 15.9094 | 15.8988 | 15.881 | 15.8524 | 15.8293 | 15.807
| STONEYWOOD T3 | LW |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2927 | 15.2643 | 15.2261 | 15.1825 | 15.1391 | 15.0958 | 15.0488 | 15.007 | 14.9673 | 14.9516 | 14.924 | 14.8253 | 14.8181 | 14.8181 | 16.0309 | 16.0197 | 16.0046 | 15.9875 | 15.9704 | 15.9534 | 15.9349 | 15.9184 | 15.9028 | 15.8957 | 15.8823 | 15.8464 | 15.8135 | 15.7811
| STONEYWOOD T3 | ST |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2995 | 15.2837 | 15.2652 | 15.244 | 15.2213 | 15.1913 | 15.1582 | 15.1265 | 15.0939 | 15.0727 | 15.0361 | 14.9666 | 14.9187 | 14.8728 | 16.0335 | 16.0273 | 16.02 | 16.0117 | 16.0028 | 15.991 | 15.9779 | 15.9655 | 15.9527 | 15.9443 | 15.9299 | 15.9026 | 15.8797 | 15.8636
| STONEYWOOD T3 | FS |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.3048 | 15.2956 | 15.2863 | 15.2757 | 15.2654 | 15.2529 | 15.2398 | 15.2269 | 15.2144 | 15.2066 | 15.1914 | 15.1637 | 15.1432 | 15.1237 | 16.0356 | 16.032 | 16.0284 | 16.0242 | 16.0201 | 16.0152 | 16.01 | 16.005 | 16.0001 | 15.997 | 15.991 | 15.9801 | 15.972 | 15.9644
CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.52789 | 0.52641 | 0.52266 | 0.51807 | 0.51348 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | -0.080352 | -1.0041 | -1.1168 | -1.2277 | 0.30486 | 0.30486 | 0.30486 | -0.030188 | -0.079378 | -0.12867 | -0.17948 | -0.22945 | -0.28344 | -0.33552 | -0.43503 | -1.2192 | -1.3475 | -1.4738 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | -0.0088249 | -0.06533 | -0.11887 | -0.17042 | -0.22611 | -0.27984 | -0.38212 | -1.3294 | -1.4617 | -1.592
| STRACHUR | CT |  |  |  | 0.52793 | 0.52674 | 0.52401 | 0.52088 | 0.51771 | 0.5145 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | -0.8479 | -0.94169 | -1.0338 | 0.30486 | 0.30486 | 0.30486 | -0.00017662 | -0.034067 | -0.068481 | -0.10096 | -0.13254 | -0.17016 | -0.20729 | -0.27629 | -1.0414 | -1.1481 | -1.253 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | -0.033562 | -0.06977 | -0.10925 | -0.14755 | -0.21874 | -1.1459 | -1.2561 | -1.3642
| STRACHUR | LW |  |  |  | 0.52789 | 0.52641 | 0.52266 | 0.51807 | 0.51348 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | 0.51202 | -0.080352 | -1.0041 | -1.1168 | -1.2277 | 0.30486 | 0.30486 | 0.30486 | -0.030188 | -0.079378 | -0.12867 | -0.17948 | -0.22945 | -0.28344 | -0.33552 | -0.43503 | -1.2192 | -1.3475 | -1.4738 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | -0.0088249 | -0.06533 | -0.11887 | -0.17042 | -0.22611 | -0.27984 | -0.38212 | -1.3294 | -1.4617 | -1.592
| STRACHUR | ST |  |  |  | 0.53012 | 0.52775 | 0.52658 | 0.52482 | 0.52272 | 0.52139 | 0.52018 | 0.519 | 0.51771 | 0.51648 | 0.51434 | -0.21972 | -0.2602 | -0.30561 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | -0.007669 | -0.020243 | -0.034089 | -0.047243 | -0.070137 | -0.44903 | -0.5031 | -0.55756 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | -0.4651 | -0.52168 | -0.57786
| STRACHUR | FS |  |  |  | 0.53279 | 0.53111 | 0.52923 | 0.52768 | 0.52701 | 0.52653 | 0.52609 | 0.52559 | 0.52508 | 0.5246 | 0.52375 | 0.52186 | 0.52019 | 0.51863 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | 0.30486 | -0.0075667 | -0.02427 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323 | 0.32323
TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | NO | 0.3002 | -0.063782 | -0.20526 | -0.35214 | -0.49385 | -0.63038 | -0.76174 | -0.88789 | -0.9656 | -1.0058 | -1.085 | -1.3714 | -1.6058 | -1.8544 | 0.3867 | -0.0076147 | -0.12839 | -0.24815 | -0.36375 | -0.47519 | -0.58247 | -0.68555 | -0.75016 | -0.78482 | -0.8531 | -1.1002 | -1.3052 | -1.5213 | 0.35994 | -0.06129 | -0.20197 | -0.34135 | -0.48403 | -0.62211 | -0.75499 | -0.88262 | -0.96165 | -1.003 | -1.0852 | -1.3806 | -1.623 | -1.8796
| STRATHDON | CT |  |  |  | 0.3002 | -0.063782 | -0.20526 | -0.35214 | -0.49385 | -0.63038 | -0.76174 | -0.88789 | -0.9656 | -1.0058 | -1.085 | -1.3714 | -1.6058 | -1.8544 | 0.3867 | -0.0076147 | -0.12839 | -0.24815 | -0.36375 | -0.47519 | -0.58247 | -0.68555 | -0.75016 | -0.78482 | -0.8531 | -1.1002 | -1.3052 | -1.5213 | 0.35994 | -0.06129 | -0.20197 | -0.34135 | -0.48403 | -0.62211 | -0.75499 | -0.88262 | -0.96165 | -1.003 | -1.0852 | -1.3806 | -1.623 | -1.8796
| STRATHDON | LW |  |  |  | 0.44816 | 0.43102 | 0.41122 | 0.38892 | 0.36435 | 0.33773 | 0.30929 | -0.0015451 | -0.04723 | -0.093991 | -0.1897 | -0.54022 | -0.865 | -1.2331 | 0.48007 | 0.46905 | 0.45599 | 0.44122 | 0.42502 | 0.40755 | 0.38893 | 0.36932 | -0.016205 | -0.056248 | -0.13811 | -0.4407 | -0.72237 | -1.0392 | 0.51294 | 0.49522 | 0.47474 | 0.45169 | 0.42628 | 0.39875 | 0.36935 | -0.019873 | -0.064713 | -0.11057 | -0.20435 | -0.55653 | -0.89292 | -1.2727
| STRATHDON | ST |  |  |  | 0.47083 | 0.46492 | 0.45703 | 0.44935 | 0.44187 | 0.43278 | 0.42394 | 0.41536 | 0.40683 | 0.39438 | 0.37049 | -0.042725 | -0.13613 | -0.24044 | 0.49443 | 0.49062 | 0.48548 | 0.48036 | 0.47532 | 0.469 | 0.46286 | 0.45689 | 0.4509 | 0.44246 | 0.42623 | -0.019722 | -0.10321 | -0.19559 | 0.53638 | 0.53027 | 0.52211 | 0.51417 | 0.50644 | 0.49704 | 0.4879 | 0.47903 | 0.47021 | 0.45733 | 0.43263 | -0.064986 | -0.1588 | -0.26302
| STRATHDON | FS |  |  |  | 0.46492 | 0.45703 | 0.44914 | 0.43747 | 0.42595 | 0.41458 | 0.40337 | 0.39232 | 0.38141 | 0.37066 | 0.34963 | 0.28704 | -0.060767 | -0.1395 | 0.49073 | 0.48574 | 0.48075 | 0.47331 | 0.46595 | 0.45859 | 0.45133 | 0.44411 | 0.43699 | 0.42998 | 0.41625 | 0.37568 | -0.024217 | -0.090979 | 0.53027 | 0.52211 | 0.51396 | 0.50189 | 0.48998 | 0.47822 | 0.46663 | 0.4552 | 0.44392 | 0.43281 | 0.41106 | 0.34634 | -0.07571 | -0.15249
STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | NO | 6.7891 | 6.7877 | 6.7839 | 6.7793 | 6.7746 | 6.7699 | 6.7652 | 6.7606 | 6.7556 | 6.1233 | 5.486 | 4.1701 | 0.91508 | 0.57556 | 5.2322 | 5.2122 | 5.1604 | 5.0969 | 5.0315 | 4.9666 | 4.902 | 4.8386 | 4.7701 | 4.1616 | 3.4855 | 1.9689 | -0.73941 | -1.1413 | 4.9511 | 4.9401 | 4.9118 | 4.8771 | 4.8414 | 4.784 | 4.722 | 4.661 | 4.5952 | 3.8413 | 3.0225 | 1.2184 | -2.1027 | -2.4888
| STRICHEN | CT |  |  |  | 6.7891 | 6.7877 | 6.7839 | 6.7796 | 6.7753 | 6.7711 | 6.7668 | 6.7626 | 6.7581 | 6.1262 | 5.4899 | 4.1812 | 1.128 | 0.87122 | 5.2322 | 5.2122 | 5.1604 | 5.1007 | 5.0414 | 4.9827 | 4.9242 | 4.8668 | 4.8047 | 4.2026 | 3.5393 | 2.1215 | -0.48739 | -0.79133 | 4.9511 | 4.9401 | 4.9118 | 4.8792 | 4.8469 | 4.7994 | 4.7433 | 4.6881 | 4.6285 | 3.8807 | 3.0741 | 1.3649 | -1.8607 | -2.1526
| STRICHEN | LW |  |  |  | 6.7893 | 6.788 | 6.7841 | 6.7793 | 6.7746 | 6.7699 | 6.7652 | 6.7606 | 6.7556 | 6.1233 | 5.486 | 4.1701 | 0.91508 | 0.57556 | 5.2348 | 5.2161 | 5.1627 | 5.0969 | 5.0315 | 4.9666 | 4.902 | 4.8386 | 4.7701 | 4.1616 | 3.4855 | 1.9689 | -0.73941 | -1.1413 | 4.9525 | 4.9423 | 4.9131 | 4.8771 | 4.8414 | 4.784 | 4.722 | 4.661 | 4.5952 | 3.8413 | 3.0225 | 1.2184 | -2.1027 | -2.4888
| STRICHEN | ST |  |  |  | 6.7898 | 6.7894 | 6.7885 | 6.787 | 6.7852 | 6.7826 | 6.78 | 6.7774 | 6.7746 | 6.4582 | 6.1391 | 5.483 | 4.1377 | 4.1251 | 5.2411 | 5.2356 | 5.2227 | 5.2026 | 5.1784 | 5.142 | 5.1058 | 5.0704 | 5.0322 | 4.7244 | 4.3802 | 3.6469 | 2.3223 | 2.1494 | 4.956 | 4.9529 | 4.9459 | 4.9349 | 4.9217 | 4.9018 | 4.882 | 4.8627 | 4.8418 | 4.4666 | 4.0513 | 3.1732 | 1.5411 | 1.3751
| STRICHEN | FS |  |  |  | 6.79 | 6.7899 | 6.7898 | 6.7893 | 6.7887 | 6.7879 | 6.787 | 6.7859 | 6.7848 | 6.7837 | 6.7816 | 6.7766 | 6.7718 | 6.7674 | 5.2436 | 5.2426 | 5.2412 | 5.2346 | 5.2266 | 5.2144 | 5.2023 | 5.1869 | 5.1717 | 5.1569 | 5.1279 | 5.0587 | 4.9935 | 4.9322 | 4.9573 | 4.9568 | 4.956 | 4.9524 | 4.948 | 4.9414 | 4.9347 | 4.9263 | 4.918 | 4.91 | 4.8941 | 4.8563 | 4.8098 | 4.7509
THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 10.232 | 10.2093 | 10.1504 | 10.0821 | 10.0147 | 9.9477 | 9.883 | 9.8196 | 9.7479 | 9.678 | 9.5394 | 8.0893 | 7.7389 | 7.3909 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
| STROMNESS | CT |  |  |  | 10.232 | 10.2093 | 10.1504 | 10.0821 | 10.0147 | 9.9477 | 9.883 | 9.8196 | 9.7479 | 9.678 | 9.5394 | 8.0893 | 7.7389 | 7.3909 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
| STROMNESS | LW |  |  |  | 10.2426 | 10.2368 | 10.2206 | 10.1998 | 10.1789 | 10.1575 | 10.1379 | 10.1187 | 10.0944 | 10.072 | 10.0273 | 8.4539 | 7.9795 | 7.5094 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
| STROMNESS | ST |  |  |  | 10.2443 | 10.2421 | 10.2371 | 10.2291 | 10.2194 | 10.1785 | 10.1393 | 10.101 | 10.0574 | 10.0155 | 9.9334 | 9.1809 | 8.9834 | 8.7859 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.2392 | 13.2392 | 13.2392 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.5387 | 11.5387 | 11.5387
| STROMNESS | FS |  |  |  | 10.2453 | 10.2448 | 10.2442 | 10.2416 | 10.2386 | 10.225 | 10.2118 | 10.195 | 10.1777 | 10.161 | 10.1285 | 10.05 | 9.9762 | 9.9051 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937
THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | -0.65409 | -0.67519 | -0.69652 | 0.13458 | 0.13429 | 0.13349 | 0.13248 | 0.13149 | 0.1305 | 0.12956 | 0.12865 | 0.12758 | 0.12655 | 0.12488 | -0.59032 | -0.61443 | -0.63837 | 0.1517 | 0.15156 | 0.15117 | 0.15068 | 0.1502 | 0.14972 | 0.14926 | 0.1491 | 0.1491 | 0.1491 | 0.1491 | -0.74352 | -0.76569 | -0.78861
| STRONSAY | CT |  |  |  | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | -0.64924 | -0.66847 | -0.68878 | 0.13458 | 0.13434 | 0.13373 | 0.13302 | 0.13232 | 0.13161 | 0.13095 | 0.1303 | 0.12953 | 0.12879 | 0.12734 | -0.58389 | -0.60688 | -0.62968 | 0.1517 | 0.15158 | 0.15129 | 0.15094 | 0.1506 | 0.15026 | 0.14993 | 0.14962 | 0.14924 | 0.1491 | 0.1491 | -0.7376 | -0.75875 | -0.77996
| STRONSAY | LW |  |  |  | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | -0.65409 | -0.67519 | -0.69652 | 0.13458 | 0.13429 | 0.13349 | 0.13248 | 0.13149 | 0.1305 | 0.12956 | 0.12865 | 0.12758 | 0.12655 | 0.12488 | -0.59032 | -0.61443 | -0.63837 | 0.1517 | 0.15156 | 0.15117 | 0.15068 | 0.1502 | 0.14972 | 0.14926 | 0.1491 | 0.1491 | 0.1491 | 0.1491 | -0.74352 | -0.76569 | -0.78861
| STRONSAY | ST |  |  |  | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | -0.22913 | -0.23784 | -0.24742 | 0.13466 | 0.13455 | 0.1343 | 0.1339 | 0.13343 | 0.13224 | 0.1311 | 0.12998 | 0.12872 | 0.1275 | 0.12533 | -0.24471 | -0.25545 | -0.26621 | 0.15174 | 0.15168 | 0.15156 | 0.15137 | 0.15114 | 0.15056 | 0.15001 | 0.14946 | 0.1491 | 0.1491 | 0.1491 | -0.31472 | -0.3246 | -0.33449
| STRONSAY | FS |  |  |  | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.13471 | 0.13469 | 0.13467 | 0.13455 | 0.13441 | 0.13402 | 0.13364 | 0.13316 | 0.13267 | 0.13219 | 0.13127 | 0.12904 | 0.12695 | 0.12521 | 0.15176 | 0.15175 | 0.15174 | 0.15168 | 0.15162 | 0.15143 | 0.15124 | 0.15101 | 0.15077 | 0.15054 | 0.15009 | 0.1491 | 0.1491 | 0.1491
FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 0.42596 | 0.41887 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | -0.012785 | -0.063718 | -0.11373 | 0.34973 | 0.34385 | 0.32973 | 0.3147 | 0.29986 | 0.29236 | 0.29033 | 0.28809 | 0.28561 | 0.28348 | -0.014545 | -0.067051 | -0.11923 | -0.17047 | 0.39312 | 0.38533 | 0.36661 | 0.34667 | 0.32699 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | -0.0084829 | -0.059296 | -0.10919
| STRONTIAN | CT |  |  |  | 0.42596 | 0.41887 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | -0.012785 | -0.063718 | -0.11373 | 0.34973 | 0.34385 | 0.32973 | 0.3147 | 0.29986 | 0.29236 | 0.29033 | 0.28809 | 0.28561 | 0.28348 | -0.014545 | -0.067051 | -0.11923 | -0.17047 | 0.39312 | 0.38533 | 0.36661 | 0.34667 | 0.32699 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | 0.31074 | -0.0084829 | -0.059296 | -0.10919
| STRONTIAN | LW |  |  |  | 0.42922 | 0.42737 | 0.42403 | 0.42152 | 0.41904 | 0.41662 | 0.41423 | 0.40917 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.35242 | 0.35089 | 0.34812 | 0.34604 | 0.34399 | 0.34199 | 0.34 | 0.33581 | 0.33064 | 0.32838 | 0.32406 | 0.29056 | 0.28329 | -0.044511 | 0.3967 | 0.39466 | 0.39099 | 0.38823 | 0.38551 | 0.38285 | 0.38022 | 0.37466 | 0.36781 | 0.36481 | 0.35908 | 0.31074 | 0.31074 | 0.31074
| STRONTIAN | ST |  |  |  | 0.4298 | 0.42885 | 0.42747 | 0.42659 | 0.42548 | 0.41979 | 0.41406 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.40844 | 0.35291 | 0.35212 | 0.35098 | 0.35025 | 0.34933 | 0.34461 | 0.33987 | 0.33401 | 0.32742 | 0.32253 | 0.31289 | 0.293 | 0.28989 | 0.2868 | 0.39734 | 0.39629 | 0.39478 | 0.39381 | 0.39259 | 0.38633 | 0.38004 | 0.37227 | 0.36353 | 0.35705 | 0.34427 | 0.31357 | 0.31074 | 0.31074
| STRONTIAN | FS |  |  |  | 0.43025 | 0.42976 | 0.42925 | 0.42895 | 0.42861 | 0.42674 | 0.42489 | 0.42195 | 0.4188 | 0.41647 | 0.41184 | 0.40844 | 0.40844 | 0.40844 | 0.35328 | 0.35288 | 0.35245 | 0.35221 | 0.35192 | 0.35037 | 0.34884 | 0.3464 | 0.34379 | 0.34186 | 0.33802 | 0.32917 | 0.32108 | 0.31343 | 0.39783 | 0.3973 | 0.39673 | 0.39641 | 0.39603 | 0.39397 | 0.39194 | 0.38871 | 0.38525 | 0.38269 | 0.37759 | 0.36586 | 0.35513 | 0.34499
SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 1.9265 | 1.9257 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.233 | 1.2306 | 1.2272 | 1.2241 | 1.221 | 1.218 | 1.215 | 1.2121 | 1.209 | 1.2059 | 1.1997 | 1.1926 | 1.1882 | 1.1839 | 0.79867 | 0.79601 | 0.78835 | 0.77892 | 0.76965 | 0.76582 | 0.76284 | 0.75992 | 0.75676 | 0.75363 | 0.74743 | 0.7403 | 0.73684 | -0.046957
| SUMBURGH | CT |  |  |  | 1.9265 | 1.9258 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.233 | 1.2311 | 1.2281 | 1.2259 | 1.2238 | 1.2218 | 1.2197 | 1.2177 | 1.2156 | 1.2134 | 1.2092 | 1.2036 | 1.198 | 1.1925 | 0.7987 | 0.79653 | 0.7909 | 0.78444 | 0.77807 | 0.77185 | 0.76753 | 0.76553 | 0.76336 | 0.76122 | 0.75697 | 0.75142 | 0.74581 | 0.74029
| SUMBURGH | LW |  |  |  | 1.9265 | 1.9257 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.233 | 1.2306 | 1.2272 | 1.2241 | 1.221 | 1.218 | 1.215 | 1.2121 | 1.209 | 1.2059 | 1.1997 | 1.1926 | 1.1882 | 1.1839 | 0.79867 | 0.79601 | 0.78835 | 0.77892 | 0.76965 | 0.76582 | 0.76284 | 0.75992 | 0.75676 | 0.75363 | 0.74743 | 0.7403 | 0.73684 | -0.046957
| SUMBURGH | ST |  |  |  | 1.9267 | 1.9264 | 1.9258 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.2337 | 1.2329 | 1.2309 | 1.2287 | 1.2274 | 1.2264 | 1.2255 | 1.2247 | 1.2237 | 1.2228 | 1.221 | 1.2165 | 1.2122 | 1.2078 | 0.79948 | 0.79853 | 0.79633 | 0.79288 | 0.78874 | 0.78597 | 0.78324 | 0.78057 | 0.77771 | 0.7749 | 0.76943 | 0.76435 | 0.75996 | 0.7556
| SUMBURGH | FS |  |  |  | 1.9268 | 1.9268 | 1.9268 | 1.9264 | 1.9261 | 1.9258 | 1.9255 | 1.9252 | 1.9248 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.9247 | 1.2341 | 1.2339 | 1.2338 | 1.2329 | 1.2319 | 1.2311 | 1.2303 | 1.2293 | 1.2289 | 1.2285 | 1.2278 | 1.2261 | 1.2245 | 1.223 | 0.79991 | 0.79978 | 0.79961 | 0.79861 | 0.79742 | 0.79651 | 0.79561 | 0.79444 | 0.79331 | 0.7922 | 0.79004 | 0.78495 | 0.78019 | 0.77571
ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 17.727 | 17.6344 | 17.5154 | 17.4001 | 17.2885 | 17.1803 | 17.0771 | 16.9779 | 16.9303 | 16.905 | 16.8557 | 16.7285 | 16.6108 | 16.5047 | 16.2825 | 16.1919 | 16.0742 | 15.9569 | 15.885 | 15.8123 | 15.7458 | 15.6816 | 15.6464 | 15.6229 | 15.5776 | 15.4861 | 15.4048 | 13.6642 | 16.4695 | 16.3658 | 16.2322 | 16.1071 | 16.0017 | 15.8994 | 15.8018 | 15.7081 | 15.663 | 15.639 | 15.5921 | 15.4711 | 15.359 | 13.6458
| TAIN | CT |  |  |  | 17.727 | 17.6344 | 17.5154 | 17.4001 | 17.2885 | 17.1803 | 17.0771 | 16.9779 | 16.9303 | 16.905 | 16.8557 | 16.7285 | 16.6108 | 16.5047 | 16.2825 | 16.1919 | 16.0742 | 15.9569 | 15.885 | 15.8123 | 15.7458 | 15.6816 | 15.6464 | 15.6229 | 15.5776 | 15.4861 | 15.4048 | 13.6642 | 16.4695 | 16.3658 | 16.2322 | 16.1071 | 16.0017 | 15.8994 | 15.8018 | 15.7081 | 15.663 | 15.639 | 15.5921 | 15.4711 | 15.359 | 13.6458
| TAIN | LW |  |  |  | 17.858 | 17.8411 | 17.8209 | 17.7966 | 17.77 | 17.7408 | 17.7112 | 17.6802 | 17.6521 | 17.6233 | 17.5645 | 17.3993 | 17.2558 | 17.1041 | 16.3864 | 16.3529 | 16.3064 | 16.2344 | 16.1583 | 16.0969 | 16.066 | 16.0347 | 16.0082 | 15.9815 | 15.9279 | 15.8008 | 15.7173 | 15.6288 | 16.6123 | 16.5906 | 16.5635 | 16.5283 | 16.4902 | 16.4479 | 16.4071 | 16.3704 | 16.3437 | 16.3164 | 16.2606 | 16.1034 | 15.9471 | 15.7839
| TAIN | ST |  |  |  | 17.8786 | 17.8725 | 17.8648 | 17.8561 | 17.8472 | 17.8354 | 17.8245 | 17.814 | 17.8039 | 17.7905 | 17.7647 | 17.7066 | 17.6534 | 17.6038 | 16.4081 | 16.394 | 16.3795 | 16.3505 | 16.3171 | 16.265 | 16.222 | 16.1797 | 16.1407 | 16.1197 | 16.0884 | 16.0193 | 15.9522 | 15.9201 | 16.6356 | 16.6275 | 16.6177 | 16.6045 | 16.5905 | 16.5706 | 16.5531 | 16.5359 | 16.5199 | 16.4999 | 16.462 | 16.3949 | 16.3441 | 16.2958
| TAIN | FS |  |  |  | 17.8736 | 17.8663 | 17.8592 | 17.8481 | 17.8371 | 17.8256 | 17.8146 | 17.8035 | 17.7927 | 17.7821 | 17.7615 | 17.7016 | 17.6482 | 17.5985 | 16.4076 | 16.3977 | 16.3909 | 16.3736 | 16.3551 | 16.3301 | 16.3086 | 16.2845 | 16.2636 | 16.2431 | 16.2034 | 16.1044 | 16.0524 | 16.0121 | 16.6308 | 16.6221 | 16.6142 | 16.6007 | 16.5871 | 16.572 | 16.5578 | 16.5432 | 16.5294 | 16.5159 | 16.4895 | 16.4157 | 16.3497 | 16.2936
ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 3.2515 | 3.2515 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0069 | 1.9796 | 1.95 | 1.9186 | 1.8514 | 1.7113 | 1.5699 | 1.4307 | 3.0416 | 3.0343 | 2.1052 | 2.0662 | 2.0279 | 1.9903 | 1.9534 | 1.9171 | 1.8779 | 1.8389 | 1.7617 | 1.6085 | 1.4538 | 1.3016 | 3.0038 | 2.9999 | 1.8956 | 1.8636 | 1.8287 | 1.7941 | 1.7602 | 1.7269 | 1.6908 | 1.6549 | 1.5839 | 1.4273 | 1.2656 | 1.1064
| TARBERT | CT |  |  |  | 3.2515 | 3.2515 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0154 | 1.9924 | 1.9696 | 1.9228 | 1.8094 | 1.691 | 1.5747 | 3.0416 | 3.0345 | 2.1108 | 2.0805 | 2.0507 | 2.0215 | 1.9928 | 1.9647 | 1.9342 | 1.9039 | 1.8439 | 1.7158 | 1.5863 | 1.4591 | 3.0038 | 2.9999 | 1.9002 | 1.8753 | 1.8497 | 1.8229 | 1.7965 | 1.7706 | 1.7426 | 1.7147 | 1.6595 | 1.5395 | 1.4041 | 1.2711
| TARBERT | LW |  |  |  | 3.2515 | 3.2515 | 2.0181 | 2.0181 | 2.0181 | 2.0181 | 2.0069 | 1.9796 | 1.95 | 1.9186 | 1.8514 | 1.7113 | 1.5699 | 1.4307 | 3.042 | 3.0343 | 2.1052 | 2.0662 | 2.0279 | 1.9903 | 1.9534 | 1.9171 | 1.8779 | 1.8389 | 1.7617 | 1.6085 | 1.4538 | 1.3016 | 3.0041 | 2.9999 | 1.8956 | 1.8636 | 1.8287 | 1.7941 | 1.7602 | 1.7269 | 1.6908 | 1.6549 | 1.5839 | 1.4273 | 1.2656 | 1.1064
| TARBERT | ST |  |  |  | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.0455 | 3.045 | 3.0439 | 3.0421 | 3.0399 | 3.0315 | 3.0232 | 3.0152 | 3.0065 | 2.9979 | 2.9916 | 2.9816 | 2.9716 | 2.9645 | 3.006 | 3.0057 | 3.0051 | 3.0041 | 3.0029 | 2.9983 | 2.9942 | 2.9926 | 2.9909 | 2.9891 | 2.9885 | 2.9885 | 2.9885 | 2.9885
| TARBERT | FS |  |  |  | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.2515 | 3.0458 | 3.0457 | 3.0456 | 3.0451 | 3.0445 | 3.0414 | 3.0383 | 3.0343 | 3.0304 | 3.0266 | 3.0191 | 3.0016 | 2.9925 | 2.9887 | 3.0061 | 3.0061 | 3.006 | 3.0058 | 3.0054 | 3.0037 | 3.002 | 2.9998 | 2.9977 | 2.9956 | 2.9934 | 2.9899 | 2.9885 | 2.9885
PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | -0.0089012 | -0.020222 | -0.031353 | 0.007234 | 0.0071092 | 0.0068905 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | -0.00075484 | -0.0017659 | -0.0037667 | -0.017034 | -0.03039 | -0.043522 | 0.0084274 | 0.008401 | 0.0083249 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | -0.00022718 | -0.0012385 | -0.00324 | -0.016511 | -0.029872 | -0.043008
| TARBERT JURA | CT |  |  |  | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | -0.0032303 | -0.011364 | -0.019392 | 0.0072341 | 0.0071219 | 0.0069579 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | -0.0008202 | -0.010344 | -0.019939 | -0.02941 | 0.0084274 | 0.0084054 | 0.0083483 | 0.0082832 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | -0.00029256 | -0.0098191 | -0.019418 | -0.028892
| TARBERT JURA | LW |  |  |  | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | -0.0089012 | -0.020222 | -0.031353 | 0.007234 | 0.0071092 | 0.0068905 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | -0.00075484 | -0.0017659 | -0.0037667 | -0.017034 | -0.03039 | -0.043522 | 0.0084274 | 0.008401 | 0.0083249 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | -0.00022718 | -0.0012385 | -0.00324 | -0.016511 | -0.029872 | -0.043008
| TARBERT JURA | ST |  |  |  | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | -0.0024762 | -0.0074596 | -0.012414 | 0.0072763 | 0.0072228 | 0.0071132 | 0.0070107 | 0.0068884 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | -0.0010336 | -0.0034999 | -0.0094541 | -0.015333 | -0.021178 | 0.0084399 | 0.0084253 | 0.0084024 | 0.0083667 | 0.0083241 | 0.0082451 | 0.0082451 | 0.0082451 | 0.0082451 | -0.00050601 | -0.0029732 | -0.0089293 | -0.01481 | -0.020657
| TARBERT JURA | FS |  |  |  | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.013019 | 0.0073012 | 0.0072943 | 0.0072855 | 0.0072308 | 0.0071658 | 0.0070441 | 0.00694 | 0.0068058 | 0.0067794 | 0.0067794 | 0.0067794 | 0.0067794 | -0.0014917 | -0.0034849 | 0.008452 | 0.0084487 | 0.0084444 | 0.0084268 | 0.0084149 | 0.0083783 | 0.0083421 | 0.0082954 | 0.0082495 | 0.0082451 | 0.0082451 | 0.0082451 | -0.00096431 | -0.0029581
PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2722 | 3.1745 | 3.0664 | 2.9513 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.3608 | 3.2256 | 3.0922 | 3.3293 | 3.3219 | 3.311 | 3.2978 | 3.2875 | 3.2772 | 3.267 | 3.2568 | 3.2468 | 3.2373 | 3.2188 | 3.1439 | 3.0685 | 2.9941
| TARBERT LOCH FYNE | CT |  |  |  | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2216 | 3.1383 | 3.043 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4255 | 3.3112 | 3.1985 | 3.3295 | 3.3233 | 3.3148 | 3.3051 | 3.2977 | 3.2898 | 3.2813 | 3.2728 | 3.2646 | 3.2574 | 3.2437 | 3.18 | 3.1162 | 3.0534
| TARBERT LOCH FYNE | LW |  |  |  | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2722 | 3.1745 | 3.0664 | 2.9513 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.3608 | 3.2256 | 3.0922 | 3.3293 | 3.3219 | 3.311 | 3.2978 | 3.2875 | 3.2772 | 3.267 | 3.2568 | 3.2468 | 3.2373 | 3.2188 | 3.1439 | 3.0685 | 2.9941
| TARBERT LOCH FYNE | ST |  |  |  | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2451 | 3.2048 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4025 | 3.3317 | 3.3278 | 3.3237 | 3.318 | 3.3131 | 3.3055 | 3.2975 | 3.2895 | 3.2815 | 3.2743 | 3.2607 | 3.2289 | 3.198 | 3.1671
| TARBERT LOCH FYNE | FS |  |  |  | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.2803 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.3335 | 3.3315 | 3.3302 | 3.328 | 3.3263 | 3.3236 | 3.3209 | 3.3176 | 3.3145 | 3.3116 | 3.306 | 3.2935 | 3.2821 | 3.2716
TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | YES | YES | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7621 | 1.6337 | 2.2331 | 2.233 | 2.2326 | 2.2321 | 2.2316 | 2.2312 | 2.2305 | 2.2295 | 2.2285 | 2.2274 | 2.2253 | 2.2177 | 1.6949 | 1.5815
| TAYNUILT | CT |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7626 | 2.2331 | 2.233 | 2.2327 | 2.2324 | 2.2321 | 2.2317 | 2.2314 | 2.2311 | 2.2308 | 2.2304 | 2.2297 | 2.2222 | 1.7761 | 1.6954
| TAYNUILT | LW |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7621 | 1.6337 | 2.2331 | 2.233 | 2.2326 | 2.2321 | 2.2316 | 2.2312 | 2.2307 | 2.2303 | 2.2298 | 2.2293 | 2.2283 | 2.2177 | 1.6949 | 1.5815
| TAYNUILT | ST |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2332 | 2.2331 | 2.233 | 2.2328 | 2.2326 | 2.2316 | 2.2305 | 2.2295 | 2.2285 | 2.2274 | 2.2253 | 2.2203 | 1.785 | 1.7318
| TAYNUILT | FS |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2332 | 2.2332 | 2.2332 | 2.2331 | 2.2331 | 2.2327 | 2.2324 | 2.232 | 2.2316 | 2.2313 | 2.2305 | 2.2287 | 2.227 | 2.2255
BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 28.3499 | 28.2829 | 28.197 | 26.9975 | 26.7936 | 26.5921 | 26.3978 | 26.2081 | 26.0437 | 25.9021 | 25.6153 | 24.6787 | 23.6502 | 22.6457 | 27.8926 | 27.8196 | 27.7289 | 27.68 | 26.8883 | 26.6835 | 26.4858 | 26.2922 | 26.1141 | 25.9421 | 25.488 | 24.3268 | 23.1664 | 22.0363 | 32.4038 | 32.3242 | 32.2126 | 32.1064 | 32.0032 | 31.9028 | 31.8062 | 31.7129 | 31.6504 | 31.6082 | 31.5236 | 31.329 | 31.222 | 26.3115
| THIMBLEROW | CT |  |  |  | 28.3499 | 28.2829 | 28.197 | 26.9975 | 26.7936 | 26.5921 | 26.3978 | 26.2081 | 26.0437 | 25.9021 | 25.6153 | 24.9629 | 24.3198 | 23.6917 | 27.8926 | 27.8196 | 27.7289 | 27.68 | 26.8883 | 26.6835 | 26.4858 | 26.2922 | 26.1141 | 25.9542 | 25.6299 | 24.8933 | 24.169 | 23.4651 | 32.4038 | 32.3242 | 32.2126 | 32.1064 | 32.0032 | 31.9028 | 31.8062 | 31.7129 | 31.6504 | 31.6082 | 31.5236 | 31.329 | 31.222 | 31.1223
| THIMBLEROW | LW |  |  |  | 28.4462 | 28.435 | 28.4222 | 28.4076 | 28.3917 | 26.8624 | 26.6787 | 26.4959 | 26.2979 | 26.101 | 25.7017 | 24.6787 | 23.6502 | 22.6457 | 27.9713 | 27.9404 | 27.8728 | 27.8562 | 27.8465 | 26.81 | 26.6001 | 26.3918 | 26.166 | 25.9421 | 25.488 | 24.3268 | 23.1664 | 22.0363 | 32.5072 | 32.4861 | 32.4466 | 32.3995 | 32.3511 | 32.3012 | 32.2508 | 32.1998 | 32.1445 | 32.0889 | 31.9755 | 31.8289 | 31.6827 | 26.3115
| THIMBLEROW | ST |  |  |  | 28.461 | 28.4571 | 28.452 | 28.447 | 28.4421 | 28.4362 | 28.4304 | 28.4249 | 28.4197 | 26.9739 | 26.777 | 26.29 | 25.8272 | 25.3742 | 27.9913 | 27.9802 | 27.9578 | 27.9257 | 27.8879 | 27.8736 | 27.8701 | 27.8667 | 27.8636 | 26.9245 | 26.6968 | 26.1353 | 25.6006 | 25.0788 | 32.5263 | 32.5189 | 32.5058 | 32.4887 | 32.4694 | 32.4464 | 32.4241 | 32.4023 | 32.3796 | 32.3547 | 32.3054 | 32.181 | 32.0645 | 32.0014
| THIMBLEROW | FS |  |  |  | 28.4571 | 28.452 | 28.4468 | 28.4392 | 28.4317 | 28.4243 | 28.417 | 28.4099 | 28.4028 | 28.3958 | 28.3821 | 28.3413 | 26.9139 | 26.7327 | 27.9927 | 27.987 | 27.9809 | 27.9659 | 27.9494 | 27.931 | 27.913 | 27.8918 | 27.8708 | 27.8562 | 27.8406 | 27.8158 | 26.9077 | 26.7115 | 32.5241 | 32.518 | 32.5116 | 32.4998 | 32.4874 | 32.4743 | 32.4615 | 32.4474 | 32.4334 | 32.4198 | 32.3927 | 32.319 | 32.2461 | 32.1771
TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | -0.0090003 | 0.025289 | 0.025116 | 0.024688 | 0.024367 | 0.024053 | 0.023746 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | -0.0043384 | -0.01896 | -0.033308 | 0.029322 | 0.029269 | 0.029178 | 0.029066 | 0.028957 | 0.02885 | 0.028745 | 0.028643 | 0.028638 | 0.028638 | 0.028638 | -0.0025062 | -0.017133 | -0.031485
| TIRORAN BRIDGE | CT |  |  |  | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.025289 | 0.025145 | 0.024771 | 0.024545 | 0.024325 | 0.02411 | 0.0239 | 0.023694 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | -0.0077117 | -0.018332 | 0.029322 | 0.029274 | 0.029206 | 0.029127 | 0.029051 | 0.028976 | 0.028903 | 0.028832 | 0.028754 | 0.028678 | 0.028638 | 0.028638 | -0.0058807 | -0.016504
| TIRORAN BRIDGE | LW |  |  |  | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | -0.0090003 | 0.025289 | 0.025116 | 0.024688 | 0.024367 | 0.024053 | 0.023746 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | -0.0043384 | -0.01896 | -0.033308 | 0.029322 | 0.029269 | 0.029178 | 0.029066 | 0.028957 | 0.02885 | 0.028745 | 0.028643 | 0.028638 | 0.028638 | 0.028638 | -0.0025062 | -0.017133 | -0.031485
| TIRORAN BRIDGE | ST |  |  |  | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.02534 | 0.025276 | 0.025125 | 0.024892 | 0.024686 | 0.02434 | 0.024001 | 0.02367 | 0.023547 | 0.023547 | 0.023547 | 0.023547 | -0.00098677 | -0.0072207 | 0.029347 | 0.029316 | 0.029271 | 0.029228 | 0.029177 | 0.029056 | 0.028939 | 0.028823 | 0.028699 | 0.028638 | 0.028638 | 0.028638 | 0.028638 | -0.0053895
| TIRORAN BRIDGE | FS |  |  |  | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.04522 | 0.02537 | 0.025362 | 0.025351 | 0.025285 | 0.025207 | 0.024988 | 0.024773 | 0.024624 | 0.024481 | 0.024341 | 0.024068 | 0.023547 | 0.023547 | 0.023547 | 0.029361 | 0.029357 | 0.029352 | 0.02932 | 0.029286 | 0.029245 | 0.029206 | 0.029155 | 0.029105 | 0.029057 | 0.028962 | 0.028739 | 0.028638 | 0.028638
BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.49483 | 0.49446 | 0.4934 | 0.49209 | 0.49079 | 0.46988 | 0.46837 | 0.44889 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244
| TOMATIN | CT |  |  |  | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.49483 | 0.49452 | 0.49373 | 0.49282 | 0.49191 | 0.47342 | 0.47255 | 0.45384 | 0.4454 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244
| TOMATIN | LW |  |  |  | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.49483 | 0.49446 | 0.4934 | 0.49209 | 0.49079 | 0.46988 | 0.46837 | 0.44889 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244
| TOMATIN | ST |  |  |  | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.49493 | 0.4948 | 0.49448 | 0.49399 | 0.4934 | 0.47836 | 0.47514 | 0.45994 | 0.44995 | 0.44476 | 0.44422 | 0.44422 | 0.44422 | 0.44422 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244
| TOMATIN | FS |  |  |  | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.6983 | 0.495 | 0.49498 | 0.49495 | 0.49482 | 0.49466 | 0.48876 | 0.48753 | 0.48017 | 0.47344 | 0.46692 | 0.46278 | 0.45349 | 0.45059 | 0.44829 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244 | 0.41244
LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | -0.00027527 | 0.0018883 | 0.0018787 | 0.001851 | 0.0018172 | 0.0017841 | 0.0017562 | 0.0017323 | 0.0017089 | 0.0017007 | 0.0016941 | 0.0016848 | -0.0001414 | -0.0011736 | -0.0021741 | 0.0021303 | 0.0021256 | 0.0021122 | 0.0020957 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | -0.00080225 | -0.001803
| TORBOLL | CT |  |  |  | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0018883 | 0.0018803 | 0.0018596 | 0.0018359 | 0.0018127 | 0.00179 | 0.0017685 | 0.0017521 | 0.0017344 | 0.0017168 | 0.0017003 | 0.0016848 | -0.00038677 | -0.0011117 | 0.0021303 | 0.0021264 | 0.0021163 | 0.0021048 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | -3.2616e-05 | -0.00074036
| TORBOLL | LW |  |  |  | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | -0.00027527 | 0.0018883 | 0.0018787 | 0.001851 | 0.0018172 | 0.0017841 | 0.0017562 | 0.0017323 | 0.0017089 | 0.0017007 | 0.0016947 | 0.0016848 | -0.0001414 | -0.0011736 | -0.0021741 | 0.0021303 | 0.0021256 | 0.0021122 | 0.0020957 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | -0.00080225 | -0.001803
| TORBOLL | ST |  |  |  | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0018912 | 0.0018876 | 0.0018792 | 0.0018663 | 0.0018508 | 0.0018043 | 0.0017616 | 0.0017279 | 0.0017027 | 0.0016941 | 0.0016848 | 0.0016848 | -7.2513e-05 | -0.00051039 | 0.0021317 | 0.0021299 | 0.0021259 | 0.0021196 | 0.0021121 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | -0.00015303
| TORBOLL | FS |  |  |  | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0033318 | 0.0018928 | 0.0018924 | 0.0018918 | 0.0018881 | 0.0018838 | 0.001869 | 0.0018541 | 0.0018345 | 0.0018157 | 0.0017969 | 0.0017629 | 0.0017045 | 0.0016902 | 0.0016848 | 0.0021325 | 0.0021322 | 0.002132 | 0.0021302 | 0.0021281 | 0.0021209 | 0.0021137 | 0.0021041 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951 | 0.0020951
KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 30.4383 | 30.3168 | 30.0964 | 29.9141 | 29.7907 | 29.6703 | 29.5526 | 29.4531 | 29.4116 | 29.391 | 29.3504 | 28.8673 | 23.1549 | 22.0237 | 27.5768 | 27.4989 | 27.3686 | 27.2878 | 27.2444 | 27.2025 | 23.5308 | 23.1291 | 22.6944 | 22.2654 | 21.4062 | 19.8412 | 18.2198 | 16.9613 | 28.2518 | 28.1824 | 28.0935 | 28.0101 | 27.9297 | 27.8522 | 27.7778 | 23.627 | 23.2456 | 22.8689 | 22.0446 | 20.3759 | 18.6345 | 17.363
| TORRYBURN | CT |  |  |  | 30.4383 | 30.3168 | 30.0964 | 29.9141 | 29.7907 | 29.6703 | 29.5526 | 29.4531 | 29.4116 | 29.391 | 29.3504 | 28.8673 | 28.338 | 28.2297 | 27.5768 | 27.4989 | 27.3686 | 27.2878 | 27.2444 | 27.2025 | 27.1622 | 27.1236 | 23.7264 | 23.5153 | 23.0907 | 21.9125 | 20.6927 | 19.8335 | 28.2518 | 28.1824 | 28.0935 | 28.0101 | 27.9297 | 27.8522 | 27.7778 | 27.7063 | 27.6657 | 23.7253 | 23.346 | 22.1509 | 20.9013 | 20.0453
| TORRYBURN | LW |  |  |  | 30.5257 | 30.4236 | 30.2024 | 30.1097 | 30.0547 | 30.0364 | 30.0168 | 29.9961 | 29.9729 | 29.949 | 29.8998 | 29.3828 | 23.1549 | 22.0237 | 27.6476 | 27.5961 | 27.466 | 27.4573 | 27.4476 | 27.4372 | 23.5308 | 23.1291 | 22.6944 | 22.2654 | 21.4062 | 19.8412 | 18.2198 | 16.9613 | 28.3515 | 28.3399 | 28.3266 | 28.3116 | 28.295 | 28.2771 | 28.2579 | 23.627 | 23.2456 | 22.8689 | 22.0446 | 20.3759 | 18.6345 | 17.363
| TORRYBURN | ST |  |  |  | 30.7467 | 30.5253 | 30.4339 | 30.2945 | 30.2078 | 30.1744 | 30.1517 | 30.1305 | 30.1084 | 30.0843 | 30.0604 | 29.8252 | 29.572 | 29.5291 | 27.7562 | 27.6508 | 27.6062 | 27.5391 | 27.478 | 27.4744 | 27.471 | 27.4676 | 27.4644 | 27.4598 | 27.4509 | 23.5817 | 22.8452 | 22.2897 | 28.3667 | 28.3628 | 28.3574 | 28.3523 | 28.3472 | 28.3411 | 28.3351 | 28.3294 | 28.3239 | 28.3159 | 28.3006 | 28.0704 | 23.2208 | 22.7283
| TORRYBURN | FS |  |  |  | 30.7597 | 30.7491 | 30.6791 | 30.6352 | 30.5846 | 30.5484 | 30.5122 | 30.469 | 30.4263 | 30.3849 | 30.3026 | 30.1334 | 30.043 | 29.9607 | 27.7611 | 27.7546 | 27.72 | 27.6971 | 27.6709 | 27.6516 | 27.6323 | 27.6097 | 27.5875 | 27.5658 | 27.5228 | 27.4174 | 27.3918 | 27.367 | 28.3628 | 28.3574 | 28.3521 | 28.3443 | 28.3365 | 28.3288 | 28.3213 | 28.3138 | 28.3065 | 28.2993 | 28.2851 | 28.2429 | 28.1988 | 28.1562
LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | -0.0098263 | -0.078211 | 0.094115 | 0.093769 | 0.092758 | 0.091502 | 0.090259 | 0.089038 | 0.086293 | 0.084668 | 0.083997 | 0.083911 | 0.083911 | -0.0287 | -0.1106 | -0.19089 | 0.10613 | 0.10596 | 0.10547 | 0.10486 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | -0.010817 | -0.092121 | -0.17243
| TRESSADY | CT |  |  |  | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | -0.04452 | 0.094115 | 0.093828 | 0.093072 | 0.092198 | 0.091332 | 0.09048 | 0.089638 | 0.088809 | 0.087977 | 0.087303 | 0.085971 | -0.010439 | -0.081471 | -0.15133 | 0.10613 | 0.10599 | 0.10562 | 0.1052 | 0.10478 | 0.10436 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | -0.062983 | -0.13287
| TRESSADY | LW |  |  |  | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | -0.0098263 | -0.078211 | 0.094115 | 0.093769 | 0.092758 | 0.091502 | 0.090259 | 0.089038 | 0.087917 | 0.087022 | 0.086055 | 0.085095 | 0.084546 | -0.0287 | -0.1106 | -0.19089 | 0.10613 | 0.10596 | 0.10547 | 0.10486 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | -0.010817 | -0.092121 | -0.17243
| TRESSADY | ST |  |  |  | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.094215 | 0.094088 | 0.093788 | 0.093318 | 0.09275 | 0.089183 | 0.086293 | 0.084668 | 0.083997 | 0.083911 | 0.083911 | -0.010557 | -0.045327 | -0.079895 | 0.10618 | 0.10612 | 0.10597 | 0.10574 | 0.10547 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | -0.027013 | -0.061407
| TRESSADY | FS |  |  |  | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.17183 | 0.094274 | 0.094258 | 0.094237 | 0.094108 | 0.093953 | 0.092776 | 0.09163 | 0.090145 | 0.088689 | 0.087482 | 0.085368 | 0.083911 | 0.083911 | 0.083911 | 0.10621 | 0.1062 | 0.10619 | 0.10613 | 0.10605 | 0.10548 | 0.10492 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435 | 0.10435
SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 9.1877 | 9.1322 | 9.061 | 8.9964 | 8.9342 | 8.8743 | 8.8167 | 8.7614 | 8.7314 | 8.7165 | 8.6872 | 8.6189 | 7.6377 | 7.4442 | 8.6602 | 8.6109 | 8.5468 | 8.4902 | 8.455 | 8.4212 | 8.3886 | 8.3573 | 8.3397 | 8.3305 | 8.3145 | 8.28 | 7.6327 | 7.4543 | 8.7554 | 8.6945 | 8.6163 | 8.5453 | 8.4768 | 8.4109 | 8.3476 | 8.2867 | 8.2535 | 8.2369 | 7.7684 | 7.5744 | 7.3778 | 7.1789
| TUMBLIN | CT |  |  |  | 9.1877 | 9.1322 | 9.061 | 8.9964 | 8.9342 | 8.8743 | 8.8167 | 8.7614 | 8.7314 | 8.7165 | 8.6872 | 8.6189 | 7.6377 | 7.4442 | 8.6602 | 8.6109 | 8.5468 | 8.4902 | 8.455 | 8.4212 | 8.3886 | 8.3573 | 8.3397 | 8.3305 | 8.3145 | 8.28 | 7.6327 | 7.4543 | 8.7554 | 8.6945 | 8.6163 | 8.5453 | 8.4768 | 8.4109 | 8.3476 | 8.2867 | 8.2535 | 8.2369 | 7.7684 | 7.5744 | 7.3778 | 7.1789
| TUMBLIN | LW |  |  |  | 9.2674 | 9.2582 | 9.2475 | 9.2355 | 9.2222 | 9.2079 | 9.1926 | 9.1764 | 9.159 | 9.1411 | 9.1043 | 9.0063 | 8.8966 | 7.7094 | 8.7301 | 8.7212 | 8.7096 | 8.6961 | 8.6816 | 8.6664 | 8.6503 | 8.6335 | 8.6155 | 8.5972 | 8.5599 | 8.4758 | 8.4203 | 7.5929 | 8.8427 | 8.8324 | 8.8203 | 8.8066 | 8.7916 | 8.7754 | 8.7581 | 8.7399 | 8.7204 | 8.7004 | 8.6591 | 8.537 | 7.6775 | 7.4073
| TUMBLIN | ST |  |  |  | 9.2797 | 9.2765 | 9.2722 | 9.2681 | 9.264 | 9.2591 | 9.2544 | 9.2497 | 9.2455 | 9.2393 | 9.2275 | 9.1958 | 9.1675 | 9.1375 | 8.7411 | 8.738 | 8.7336 | 8.7288 | 8.7239 | 8.7123 | 8.7008 | 8.6896 | 8.6782 | 8.6654 | 8.6405 | 8.5775 | 8.5573 | 8.5421 | 8.8561 | 8.8526 | 8.8478 | 8.843 | 8.8384 | 8.8317 | 8.8251 | 8.8187 | 8.8127 | 8.8046 | 8.789 | 8.7478 | 8.7105 | 8.6714
| TUMBLIN | FS |  |  |  | 9.2765 | 9.2722 | 9.268 | 9.2617 | 9.2555 | 9.2493 | 9.2433 | 9.2373 | 9.2314 | 9.2256 | 9.2143 | 9.1806 | 9.1457 | 9.1121 | 8.7384 | 8.7346 | 8.7308 | 8.725 | 8.7191 | 8.7113 | 8.7036 | 8.6953 | 8.6871 | 8.679 | 8.6634 | 8.6203 | 8.5772 | 8.5359 | 8.8526 | 8.848 | 8.8433 | 8.8363 | 8.8295 | 8.8223 | 8.8153 | 8.8082 | 8.8012 | 8.7943 | 8.7808 | 8.7414 | 8.701 | 8.662
TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | -0.29551 | -0.58296 | -0.98936 | -1.4023 | -1.8006 | -2.1842 | -2.5531 | -2.9074 | -3.0615 | -3.1406 | -3.2963 | -3.6938 | -4.0281 | -4.3589 | -0.19875 | -0.45962 | -0.79686 | -1.1256 | -1.4428 | -1.7482 | -2.042 | -2.3251 | -2.4505 | -2.5157 | -2.6439 | -2.9751 | -3.2555 | -3.533 | -0.40286 | -0.71793 | -1.1293 | -1.5459 | -1.948 | -2.3352 | -2.7075 | -3.065 | -3.2203 | -3.2999 | -3.4562 | -3.8546 | -4.189 | -4.5245
| TUMMEL BRIDGE | CT |  |  |  | -0.29551 | -0.58296 | -0.98936 | -1.4023 | -1.8006 | -2.1842 | -2.5531 | -2.9074 | -3.0615 | -3.1406 | -3.2963 | -3.6938 | -4.0281 | -4.3589 | -0.19875 | -0.45962 | -0.79686 | -1.1256 | -1.4428 | -1.7482 | -2.042 | -2.3251 | -2.4505 | -2.5157 | -2.6439 | -2.9751 | -3.2555 | -3.533 | -0.40286 | -0.71793 | -1.1293 | -1.5459 | -1.948 | -2.3352 | -2.7075 | -3.065 | -3.2203 | -3.2999 | -3.4562 | -3.8546 | -4.189 | -4.5245
| TUMMEL BRIDGE | LW |  |  |  | 0.49216 | 0.4413 | 0.38256 | -0.047694 | -0.11633 | -0.19068 | -0.2701 | -0.35396 | -0.4351 | -0.52525 | -0.71002 | -1.2177 | -1.6743 | -2.1579 | 0.39975 | 0.36764 | 0.32772 | -0.0047722 | -0.071088 | -0.14202 | -0.217 | -0.2975 | -0.36902 | -0.44238 | -0.59264 | -1.0091 | -1.3852 | -1.7885 | 0.29856 | -0.0041412 | -0.067117 | -0.13829 | -0.21635 | -0.3006 | -0.39032 | -0.49264 | -0.58095 | -0.67158 | -0.85724 | -1.372 | -1.8359 | -2.3268
| TUMMEL BRIDGE | ST |  |  |  | 0.55942 | 0.54187 | 0.51847 | 0.49568 | 0.4735 | 0.44652 | 0.42031 | 0.39485 | 0.36987 | -0.031687 | -0.097534 | -0.23627 | -0.39824 | -0.53939 | 0.44053 | 0.42941 | 0.41396 | 0.39808 | 0.38214 | 0.36203 | 0.34246 | 0.32344 | 0.30441 | -0.012979 | -0.08028 | -0.22491 | -0.35551 | -0.47073 | 0.35602 | 0.34098 | 0.32087 | 0.30119 | 0.28199 | -0.0033893 | -0.032422 | -0.060626 | -0.088495 | -0.12816 | -0.20444 | -0.38817 | -0.5533 | -0.69786
| TUMMEL BRIDGE | FS |  |  |  | 0.54187 | 0.51847 | 0.49508 | 0.46044 | 0.42626 | 0.39254 | -0.0073289 | -0.038213 | -0.068666 | -0.098688 | -0.15744 | -0.33227 | -0.47417 | -0.62664 | 0.4303 | 0.4162 | 0.40208 | 0.38071 | 0.35948 | 0.33798 | 0.31676 | 0.29546 | -0.013796 | -0.041423 | -0.095471 | -0.25714 | -0.39422 | -0.51821 | 0.34107 | 0.32109 | 0.30111 | 0.27148 | -0.019173 | -0.054581 | -0.089507 | -0.12415 | -0.15832 | -0.19199 | -0.25788 | -0.45296 | -0.61474 | -0.76976
MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 24.6249 | 24.6169 | 24.5964 | 24.5726 | 24.5486 | 24.5247 | 24.5008 | 24.4772 | 24.4517 | 24.4275 | 23.7116 | 14.2536 | 11.3103 | 11.3103 | 21.0396 | 21.0123 | 20.9415 | 20.8592 | 20.7767 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.3454 | 12.1929 | 8.8183 | 8.2023 | 21.0229 | 21.0049 | 20.9583 | 20.9042 | 20.8613 | 20.8267 | 20.7919 | 20.7578 | 20.7209 | 20.6848 | 19.9459 | 13.7086 | 9.6402 | 8.9961
| TURRIFF | CT |  |  |  | 24.6249 | 24.6169 | 24.5964 | 24.5726 | 24.5486 | 24.5247 | 24.5008 | 24.4772 | 24.4517 | 24.4275 | 23.7116 | 14.2536 | 11.3103 | 11.3103 | 21.0396 | 21.0123 | 20.9415 | 20.8592 | 20.7767 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.3454 | 12.1929 | 8.8183 | 8.2023 | 21.0229 | 21.0049 | 20.9583 | 20.9042 | 20.8613 | 20.8267 | 20.7919 | 20.7578 | 20.7209 | 20.6848 | 19.9459 | 13.7086 | 9.6402 | 8.9961
| TURRIFF | LW |  |  |  | 24.6275 | 24.6235 | 24.612 | 24.5974 | 24.5826 | 24.5676 | 24.5522 | 24.5371 | 24.5209 | 24.5052 | 23.8045 | 14.2536 | 11.3103 | 11.3103 | 21.0488 | 21.0349 | 20.9951 | 20.945 | 20.8939 | 20.842 | 20.7891 | 20.737 | 20.7096 | 20.7096 | 20.3454 | 12.6389 | 9.1334 | 8.3896 | 21.029 | 21.0198 | 20.9936 | 20.9607 | 20.927 | 20.8929 | 20.8665 | 20.8446 | 20.8211 | 20.7984 | 20.0857 | 18.4664 | 9.9696 | 9.192
| TURRIFF | ST |  |  |  | 24.6788 | 24.6275 | 24.6245 | 24.6198 | 24.6139 | 24.6031 | 24.5922 | 24.5815 | 24.57 | 24.5588 | 24.2021 | 23.4031 | 13.8657 | 13.8657 | 21.2258 | 21.0489 | 21.0384 | 21.022 | 21.0018 | 20.9646 | 20.927 | 20.8901 | 20.8502 | 20.8119 | 20.528 | 20.1219 | 12.7727 | 12.4639 | 21.1454 | 21.029 | 21.0221 | 21.0113 | 20.998 | 20.9735 | 20.9488 | 20.9245 | 20.8983 | 20.8761 | 20.5104 | 19.6897 | 18.1532 | 18.1117
| TURRIFF | FS |  |  |  | 24.6794 | 24.6791 | 24.6787 | 24.6772 | 24.6753 | 24.6716 | 24.6678 | 24.6631 | 24.6585 | 24.654 | 24.6449 | 24.6232 | 24.6025 | 24.583 | 21.2277 | 21.2268 | 21.2254 | 21.2201 | 21.2137 | 21.2008 | 21.1878 | 21.1716 | 21.1555 | 21.1399 | 21.1088 | 21.0339 | 20.9626 | 20.8952 | 21.1467 | 21.1461 | 21.1452 | 21.1417 | 21.1375 | 21.129 | 21.1204 | 21.1098 | 21.0992 | 21.0889 | 21.0684 | 21.0191 | 20.9722 | 20.9279
RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 3.2293 | 3.2292 | 3.2289 | 3.2286 | 3.2283 | 3.2279 | 3.2275 | 3.2272 | 3.2268 | 3.2264 | 3.226 | 3.226 | 3.226 | 3.226 | 2.9153 | 2.9152 | 2.9151 | 2.9149 | 2.9146 | 2.9144 | 2.9142 | 2.914 | 2.9137 | 2.9135 | 2.913 | 2.9117 | 2.9104 | 2.9091 | 3.0469 | 3.0466 | 3.0459 | 3.0449 | 3.0439 | 3.0429 | 3.0419 | 3.0409 | 3.0398 | 3.0387 | 3.0365 | 3.0309 | 3.0252 | 3.0194
| TYNDRUM | CT |  |  |  | 3.2293 | 3.2292 | 3.229 | 3.2288 | 3.2285 | 3.2283 | 3.228 | 3.2278 | 3.2275 | 3.2272 | 3.2266 | 3.226 | 3.226 | 3.226 | 2.9153 | 2.9152 | 2.9151 | 2.915 | 2.9148 | 2.9146 | 2.9145 | 2.9143 | 2.9142 | 2.914 | 2.9136 | 2.9127 | 2.9117 | 2.9108 | 3.0469 | 3.0467 | 3.0461 | 3.0454 | 3.0447 | 3.044 | 3.0433 | 3.0426 | 3.0418 | 3.041 | 3.0394 | 3.0352 | 3.031 | 3.0268
| TYNDRUM | LW |  |  |  | 3.2293 | 3.2292 | 3.2289 | 3.2286 | 3.2283 | 3.2279 | 3.2275 | 3.2272 | 3.2268 | 3.2264 | 3.226 | 3.226 | 3.226 | 3.226 | 2.9153 | 2.9152 | 2.9151 | 2.9149 | 2.9146 | 2.9144 | 2.9142 | 2.914 | 2.9137 | 2.9135 | 2.913 | 2.9117 | 2.9104 | 2.9091 | 3.0469 | 3.0466 | 3.0459 | 3.0449 | 3.0439 | 3.0429 | 3.0419 | 3.0409 | 3.0398 | 3.0387 | 3.0365 | 3.0309 | 3.0252 | 3.0194
| TYNDRUM | ST |  |  |  | 3.2293 | 3.2293 | 3.2292 | 3.2291 | 3.2289 | 3.2288 | 3.2286 | 3.2284 | 3.2282 | 3.228 | 3.2277 | 3.2267 | 3.226 | 3.226 | 2.9153 | 2.9153 | 2.9152 | 2.9152 | 2.9151 | 2.9149 | 2.9148 | 2.9147 | 2.9146 | 2.9145 | 2.9143 | 2.9136 | 2.9131 | 2.9125 | 3.047 | 3.0469 | 3.0466 | 3.0463 | 3.0458 | 3.0453 | 3.0448 | 3.0444 | 3.0439 | 3.0433 | 3.0423 | 3.0395 | 3.0369 | 3.0342
| TYNDRUM | FS |  |  |  | 3.2293 | 3.2293 | 3.2293 | 3.2293 | 3.2293 | 3.2292 | 3.2291 | 3.2291 | 3.229 | 3.2289 | 3.2288 | 3.2284 | 3.228 | 3.2277 | 2.9153 | 2.9153 | 2.9153 | 2.9153 | 2.9153 | 2.9152 | 2.9152 | 2.9151 | 2.9151 | 2.9151 | 2.915 | 2.9147 | 2.9145 | 2.9143 | 3.047 | 3.047 | 3.047 | 3.0469 | 3.0467 | 3.0466 | 3.0464 | 3.0462 | 3.046 | 3.0458 | 3.0454 | 3.0443 | 3.0433 | 3.0422
DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 3.2834 | 3.1927 | 3.0762 | 2.9657 | 2.4587 | 2.3624 | 2.2687 | 2.1522 | 2.0873 | 2.0448 | 1.9564 | 1.7401 | 1.5359 | 1.3323 | 3.2226 | 3.1676 | 3.0965 | 3.0287 | 2.9633 | 2.4434 | 2.3353 | 2.2309 | 2.169 | 2.1257 | 2.0403 | 1.8413 | 1.6514 | 1.4539 | 3.137 | 3.0474 | 2.9324 | 2.4164 | 2.275 | 2.1383 | 2.0063 | 1.8791 | 1.8058 | 1.7561 | 1.6581 | 1.4291 | 1.212 | 0.99572
| UIG | CT |  |  |  | 3.2834 | 3.1927 | 3.0762 | 2.9657 | 2.4587 | 2.3624 | 2.2687 | 2.1522 | 2.0873 | 2.0448 | 1.9564 | 1.7401 | 1.5359 | 1.3323 | 3.2226 | 3.1676 | 3.0965 | 3.0287 | 2.9633 | 2.4434 | 2.3353 | 2.2309 | 2.169 | 2.1257 | 2.0403 | 1.8413 | 1.6514 | 1.4539 | 3.137 | 3.0474 | 2.9324 | 2.4164 | 2.275 | 2.1383 | 2.0063 | 1.8791 | 1.8058 | 1.7561 | 1.6581 | 1.4291 | 1.212 | 0.99572
| UIG | LW |  |  |  | 3.4138 | 3.3987 | 3.3813 | 3.3616 | 3.3399 | 3.3165 | 3.2914 | 3.2649 | 3.241 | 3.2164 | 3.1658 | 2.3446 | 2.0757 | 1.8043 | 3.312 | 3.2983 | 3.279 | 3.2651 | 3.25 | 3.2339 | 3.2168 | 3.199 | 3.1825 | 3.1656 | 3.1311 | 2.2592 | 1.9979 | 1.7354 | 3.2658 | 3.2509 | 3.2336 | 3.2142 | 3.1928 | 3.1696 | 3.1449 | 3.1188 | 3.0952 | 2.4402 | 2.309 | 2.0205 | 1.7295 | 1.4337
| UIG | ST |  |  |  | 3.4338 | 3.4286 | 3.4216 | 3.4149 | 3.4083 | 3.4003 | 3.3925 | 3.3849 | 3.3777 | 3.3671 | 3.3468 | 3.3012 | 3.261 | 3.2245 | 3.3271 | 3.3223 | 3.315 | 3.3063 | 3.2971 | 3.2899 | 3.2845 | 3.2793 | 3.2742 | 3.2672 | 3.2536 | 3.2229 | 3.1954 | 3.1702 | 3.2855 | 3.2804 | 3.2735 | 3.2668 | 3.2603 | 3.2524 | 3.2447 | 3.2372 | 3.2301 | 3.2196 | 3.1996 | 3.1546 | 3.1149 | 2.4436
| UIG | FS |  |  |  | 3.4286 | 3.4216 | 3.4147 | 3.4044 | 3.3942 | 3.3842 | 3.3743 | 3.3646 | 3.355 | 3.3455 | 3.327 | 3.2718 | 3.2236 | 3.1791 | 3.3239 | 3.3188 | 3.3137 | 3.3054 | 3.2969 | 3.2886 | 3.2805 | 3.2721 | 3.2642 | 3.2583 | 3.2466 | 3.2121 | 3.182 | 3.1541 | 3.2804 | 3.2735 | 3.2666 | 3.2565 | 3.2465 | 3.2366 | 3.2268 | 3.2172 | 3.2077 | 3.1983 | 3.18 | 3.1255 | 3.0779 | 3.034
GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | YES | YES | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.2625 | 1.2549 | 1.233 | 1.2061 | 1.1796 | 1.1536 | 1.128 | 1.1028 | 1.0756 | 1.0608 | 1.0608 | 1.0608 | -0.16842 | -0.3922 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | -0.16202 | -0.38535
| ULLAPOOL | CT |  |  |  | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.2629 | 1.2572 | 1.2423 | 1.2254 | 1.2087 | 1.1922 | 1.176 | 1.16 | 1.1428 | 1.1257 | 1.0918 | 1.0608 | 1.0608 | 1.0608 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218
| ULLAPOOL | LW |  |  |  | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.2625 | 1.2549 | 1.233 | 1.2061 | 1.1796 | 1.1536 | 1.128 | 1.1028 | 1.0756 | 1.0608 | 1.0608 | 1.0608 | -0.16842 | -0.3922 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | -0.16202 | -0.38535
| ULLAPOOL | ST |  |  |  | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.2648 | 1.262 | 1.2555 | 1.2454 | 1.2333 | 1.2237 | 1.2143 | 1.2051 | 1.1951 | 1.1853 | 1.1662 | 1.1197 | 1.072 | 1.0608 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218
| ULLAPOOL | FS |  |  |  | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.5383 | 1.2661 | 1.2657 | 1.2652 | 1.2623 | 1.2588 | 1.2556 | 1.2525 | 1.2484 | 1.2444 | 1.2404 | 1.2328 | 1.2148 | 1.1973 | 1.1804 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218 | 1.218
SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 1.1621 | 1.162 | 1.1617 | 1.1614 | 1.161 | 1.1607 | 1.1603 | 1.1596 | 1.1589 | 1.1582 | 1.1569 | 1.1511 | 1.1434 | 1.1358 | 0.71228 | 0.71174 | 0.71019 | 0.70826 | 0.70632 | 0.70453 | 0.70227 | 0.69848 | 0.69442 | 0.69053 | 0.69053 | 0.69053 | 0.69053 | 0.69053 | 0.90942 | 0.90938 | 0.90927 | 0.90914 | 0.909 | 0.90888 | 0.90872 | 0.90845 | 0.90817 | 0.90789 | 0.90735 | 0.90508 | 0.90202 | 0.899
| UNST | CT |  |  |  | 1.1621 | 1.162 | 1.1618 | 1.1616 | 1.1613 | 1.1611 | 1.1609 | 1.1606 | 1.1604 | 1.1602 | 1.1598 | 1.1522 | 1.1445 | 1.137 | 0.71228 | 0.71183 | 0.71066 | 0.70929 | 0.70791 | 0.70665 | 0.70537 | 0.70412 | 0.7028 | 0.70155 | 0.69907 | 0.69053 | 0.69053 | 0.69053 | 0.90942 | 0.90939 | 0.90931 | 0.90921 | 0.90911 | 0.90903 | 0.90894 | 0.90885 | 0.90875 | 0.90867 | 0.90849 | 0.90548 | 0.90245 | 0.89946
| UNST | LW |  |  |  | 1.1621 | 1.162 | 1.1617 | 1.1614 | 1.161 | 1.1607 | 1.1604 | 1.1601 | 1.1598 | 1.1594 | 1.1588 | 1.1511 | 1.1434 | 1.1358 | 0.71228 | 0.71174 | 0.71019 | 0.70826 | 0.70632 | 0.70453 | 0.70273 | 0.70096 | 0.69909 | 0.69731 | 0.69377 | 0.69053 | 0.69053 | 0.69053 | 0.90942 | 0.90938 | 0.90927 | 0.90914 | 0.909 | 0.90888 | 0.90875 | 0.90863 | 0.90849 | 0.90837 | 0.90812 | 0.90508 | 0.90202 | 0.899
| UNST | ST |  |  |  | 1.1621 | 1.1621 | 1.162 | 1.1619 | 1.1617 | 1.161 | 1.1603 | 1.1596 | 1.1589 | 1.1582 | 1.1569 | 1.1535 | 1.1503 | 1.147 | 0.71244 | 0.71223 | 0.71175 | 0.71099 | 0.71006 | 0.70614 | 0.70227 | 0.69848 | 0.69442 | 0.69053 | 0.69053 | 0.69053 | 0.69053 | 0.69053 | 0.90943 | 0.90942 | 0.90938 | 0.90933 | 0.90927 | 0.90899 | 0.90872 | 0.90845 | 0.90817 | 0.90789 | 0.90735 | 0.90604 | 0.90474 | 0.90344
| UNST | FS |  |  |  | 1.1621 | 1.1621 | 1.1621 | 1.1621 | 1.162 | 1.1618 | 1.1616 | 1.1613 | 1.161 | 1.1607 | 1.1602 | 1.1589 | 1.1577 | 1.1566 | 0.71254 | 0.7125 | 0.71245 | 0.71223 | 0.71196 | 0.71066 | 0.70937 | 0.70771 | 0.7061 | 0.70452 | 0.70147 | 0.69423 | 0.69053 | 0.69053 | 0.90944 | 0.90944 | 0.90943 | 0.90942 | 0.9094 | 0.90931 | 0.90922 | 0.9091 | 0.90899 | 0.90888 | 0.90866 | 0.90815 | 0.90768 | 0.90723
SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 12.0456 | 12.0261 | 11.9753 | 11.917 | 11.8595 | 11.8033 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 10.138 | 9.7787 | 12.3425 | 12.3411 | 12.3375 | 12.3334 | 12.3294 | 12.3254 | 12.3214 | 12.3174 | 12.3131 | 12.3088 | 12.3003 | 12.2811 | 12.2604 | 10.2836
| VOE | CT |  |  |  | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 12.0456 | 12.0261 | 11.9753 | 11.917 | 11.8595 | 11.8033 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 10.2817 | 10.007 | 12.3425 | 12.3411 | 12.3375 | 12.3334 | 12.3294 | 12.3254 | 12.3214 | 12.3174 | 12.3131 | 12.3088 | 12.3003 | 12.2844 | 12.2686 | 12.253
| VOE | LW |  |  |  | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 12.0493 | 12.0332 | 11.9868 | 11.9295 | 11.8731 | 11.818 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 10.138 | 9.7787 | 12.3427 | 12.3416 | 12.3383 | 12.3343 | 12.3303 | 12.3265 | 12.3224 | 12.3185 | 12.3142 | 12.3099 | 12.3017 | 12.2811 | 12.2604 | 10.2836
| VOE | ST |  |  |  | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 12.0541 | 12.0485 | 12.0351 | 12.0142 | 11.9891 | 11.9656 | 11.9408 | 11.9166 | 11.8904 | 11.8645 | 11.8149 | 11.7909 | 11.7909 | 11.7909 | 12.3431 | 12.3427 | 12.3417 | 12.3403 | 12.3385 | 12.3368 | 12.3351 | 12.3334 | 12.3316 | 12.3297 | 12.3262 | 12.3182 | 12.3103 | 12.3024
| VOE | FS |  |  |  | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 13.0211 | 12.0567 | 12.056 | 12.055 | 12.0489 | 12.0417 | 12.0336 | 12.0249 | 12.014 | 12.0032 | 11.9925 | 11.9721 | 11.9259 | 11.8832 | 11.8432 | 12.3432 | 12.3432 | 12.3431 | 12.3427 | 12.3422 | 12.3416 | 12.341 | 12.3402 | 12.3395 | 12.3387 | 12.3373 | 12.334 | 12.331 | 12.3282
GLENAGNES | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1067 | 25.0961 | 25.0649 | 25.026 | 24.988 | 24.9494 | 24.9102 | 24.8719 | 24.8292 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
| WALTON | CT |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1076 | 25.1004 | 25.0813 | 25.0591 | 25.0371 | 25.0151 | 24.994 | 24.9733 | 24.9502 | 24.9241 | 24.8703 | 24.821 | 24.821 | 24.821
| WALTON | LW |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1067 | 25.0961 | 25.0649 | 25.026 | 24.988 | 24.9494 | 24.9102 | 24.8719 | 24.8292 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
| WALTON | ST |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2614 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1825 | 25.1056 | 25.0961 | 25.081 | 25.0629 | 25.0076 | 24.9538 | 24.9011 | 24.8437 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
| WALTON | FS |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2633 | 24.2628 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1843 | 25.1838 | 25.1103 | 25.1063 | 25.1016 | 25.0869 | 25.0723 | 25.0534 | 25.0345 | 25.0155 | 24.9782 | 24.8879 | 24.821 | 24.821
INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | NO | 36.5373 | 36.4999 | 36.45 | 36.4009 | 36.3527 | 36.3053 | 36.2586 | 36.1808 | 36.13 | 36.0794 | 35.9809 | 35.7116 | 35.4352 | 35.1933 | 30.2054 | 30.1617 | 30.1033 | 30.0458 | 29.9895 | 29.9341 | 29.8794 | 29.7885 | 29.7291 | 29.6699 | 29.5548 | 29.2398 | 28.9189 | 28.6906 | 32.7751 | 32.7348 | 32.6809 | 32.6279 | 32.5759 | 32.5248 | 32.4743 | 32.3904 | 32.3356 | 32.281 | 32.1747 | 31.8841 | 31.5857 | 31.292
| WATERLOO PLACE | CT |  |  |  | 36.5378 | 36.5064 | 36.4682 | 36.435 | 36.4014 | 36.3657 | 36.3267 | 36.2651 | 36.2272 | 36.191 | 36.1184 | 35.939 | 35.7572 | 35.577 | 30.2059 | 30.1692 | 30.1246 | 30.0858 | 30.0465 | 30.0046 | 29.959 | 29.887 | 29.8427 | 29.8004 | 29.7155 | 29.5057 | 29.293 | 29.0824 | 32.7756 | 32.7418 | 32.7005 | 32.6647 | 32.6285 | 32.5899 | 32.5478 | 32.4814 | 32.4405 | 32.4014 | 32.323 | 32.1294 | 31.9332 | 31.7388
| WATERLOO PLACE | LW |  |  |  | 36.5373 | 36.4999 | 36.45 | 36.4009 | 36.3527 | 36.3053 | 36.2586 | 36.1808 | 36.13 | 36.0794 | 35.9809 | 35.7116 | 35.4352 | 35.1933 | 30.2054 | 30.1617 | 30.1033 | 30.0458 | 29.9895 | 29.9341 | 29.8794 | 29.7885 | 29.7291 | 29.6699 | 29.5548 | 29.2398 | 28.9189 | 28.6906 | 32.7751 | 32.7348 | 32.6809 | 32.6279 | 32.5759 | 32.5248 | 32.4743 | 32.3904 | 32.3356 | 32.281 | 32.1747 | 31.8841 | 31.5857 | 31.292
| WATERLOO PLACE | ST |  |  |  | 36.5451 | 36.5259 | 36.5083 | 36.4907 | 36.4689 | 36.4425 | 36.414 | 36.3705 | 36.3426 | 36.316 | 36.2631 | 36.1379 | 36.0145 | 35.8913 | 30.2145 | 30.1921 | 30.1715 | 30.1509 | 30.1254 | 30.0945 | 30.0612 | 30.0103 | 29.9776 | 29.9465 | 29.8847 | 29.7383 | 29.594 | 29.4499 | 32.7835 | 32.7629 | 32.7438 | 32.7248 | 32.7013 | 32.6728 | 32.6421 | 32.5951 | 32.565 | 32.5362 | 32.4792 | 32.3441 | 32.2109 | 32.078
| WATERLOO PLACE | FS |  |  |  | 36.5508 | 36.5412 | 36.5365 | 36.5311 | 36.5245 | 36.5157 | 36.5073 | 36.4898 | 36.479 | 36.4682 | 36.4471 | 36.3995 | 36.3551 | 36.3127 | 30.2212 | 30.21 | 30.2045 | 30.1981 | 30.1904 | 30.1801 | 30.1703 | 30.1498 | 30.1371 | 30.1246 | 30.0999 | 30.0442 | 29.9923 | 29.9427 | 32.7897 | 32.7794 | 32.7743 | 32.7684 | 32.7613 | 32.7518 | 32.7427 | 32.7238 | 32.7121 | 32.7006 | 32.6778 | 32.6264 | 32.5784 | 32.5327
LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | NO | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0481 | 26.0132 | 25.927 | 25.8289 | 25.7403 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 21.0499 | 26.0175 | 25.9751 | 25.8701 | 25.7507 | 25.6428 | 25.5308 | 25.4254 | 25.3313 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
| WEST KIRKTON | CT |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0481 | 26.0132 | 25.9283 | 25.84 | 25.7594 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 26.0175 | 25.9751 | 25.8717 | 25.7642 | 25.6661 | 25.565 | 25.4701 | 25.3805 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
| WEST KIRKTON | LW |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0512 | 26.0162 | 25.927 | 25.8289 | 25.7403 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 21.0499 | 26.0213 | 25.9787 | 25.8701 | 25.7507 | 25.6428 | 25.5308 | 25.4254 | 25.3313 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
| WEST KIRKTON | ST |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0595 | 26.0451 | 26.014 | 25.9784 | 25.9427 | 25.8904 | 25.8416 | 25.7958 | 25.7464 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 26.0315 | 26.0139 | 25.9761 | 25.9327 | 25.8892 | 25.8255 | 25.7661 | 25.7104 | 25.6502 | 25.5851 | 25.4592 | 25.3222 | 25.3222 | 25.3222
| WEST KIRKTON | FS |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0633 | 26.0573 | 26.0467 | 26.0317 | 26.0177 | 25.9991 | 25.9823 | 25.9635 | 25.9441 | 25.924 | 25.8847 | 25.7926 | 25.7139 | 25.7078 | 26.0361 | 26.0287 | 26.0158 | 25.9976 | 25.9806 | 25.9579 | 25.9374 | 25.9146 | 25.8909 | 25.8665 | 25.8187 | 25.7065 | 25.6106 | 25.5246
KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | -0.1517 | -0.24676 | -0.36929 | -0.48535 | -0.59729 | -0.70509 | -0.80876 | -0.9083 | -0.95334 | -0.97632 | -1.0215 | -1.1441 | -1.2536 | -1.3631 | -0.12471 | -0.20089 | -0.2995 | -0.39307 | -0.48333 | -0.57026 | -0.65388 | -0.73419 | -0.77107 | -0.79033 | -0.82821 | -0.9346 | -1.0295 | -1.1243 | -0.15765 | -0.25326 | -0.37666 | -0.49361 | -0.60641 | -0.71504 | -0.81951 | -0.91983 | -0.96543 | -0.98886 | -1.0349 | -1.1591 | -1.27 | -1.3813
| WESTER DRUMMOND | CT |  |  |  | -0.1517 | -0.24676 | -0.36929 | -0.48535 | -0.59729 | -0.70509 | -0.80876 | -0.9083 | -0.95334 | -0.97632 | -1.0215 | -1.1441 | -1.2536 | -1.3631 | -0.12471 | -0.20089 | -0.2995 | -0.39307 | -0.48333 | -0.57026 | -0.65388 | -0.73419 | -0.77107 | -0.79033 | -0.82821 | -0.9346 | -1.0295 | -1.1243 | -0.15765 | -0.25326 | -0.37666 | -0.49361 | -0.60641 | -0.71504 | -0.81951 | -0.91983 | -0.96543 | -0.98886 | -1.0349 | -1.1591 | -1.27 | -1.3813
| WESTER DRUMMOND | LW |  |  |  | -0.016476 | -0.034962 | -0.061508 | -0.092248 | -0.12489 | -0.15921 | -0.19501 | -0.23209 | -0.26685 | -0.30228 | -0.37431 | -0.54196 | -0.70172 | -0.86307 | -0.017353 | -0.033228 | -0.057332 | -0.085649 | -0.11541 | -0.14643 | -0.17858 | -0.21166 | -0.2432 | -0.27525 | -0.3402 | -0.48488 | -0.62345 | -0.76309 | -0.02245 | -0.041275 | -0.069066 | -0.10156 | -0.13591 | -0.1719 | -0.20935 | -0.24803 | -0.28454 | -0.32172 | -0.39733 | -0.56975 | -0.73454 | -0.90082
| WESTER DRUMMOND | ST |  |  |  | 0.0090503 | -0.0013498 | -0.010892 | -0.021757 | -0.033193 | -0.044313 | -0.055142 | -0.065677 | -0.076066 | -0.089848 | -0.11636 | -0.17638 | -0.23053 | -0.28012 | 0.0036717 | -0.005249 | -0.013811 | -0.023887 | -0.0347 | -0.044593 | -0.054233 | -0.063617 | -0.072966 | -0.084994 | -0.10816 | -0.16093 | -0.209 | -0.25343 | -0.00066472 | -0.0072009 | -0.017118 | -0.028553 | -0.040772 | -0.052358 | -0.063645 | -0.074628 | -0.085504 | -0.099754 | -0.12718 | -0.18943 | -0.2458 | -0.29763
| WESTER DRUMMOND | FS |  |  |  | -0.0013498 | -0.0076534 | -0.014762 | -0.026306 | -0.037971 | -0.049287 | -0.060444 | -0.071727 | -0.082842 | -0.093798 | -0.11522 | -0.17762 | -0.23195 | -0.28206 | -0.0035156 | -0.0094607 | -0.015447 | -0.025229 | -0.035123 | -0.044504 | -0.053751 | -0.063186 | -0.072476 | -0.081633 | -0.099532 | -0.15129 | -0.19646 | -0.23814 | -0.0056067 | -0.013012 | -0.020456 | -0.03232 | -0.04425 | -0.055671 | -0.06693 | -0.078323 | -0.089552 | -0.10066 | -0.12238 | -0.18552 | -0.24053 | -0.29127
CARRADALE | WESTPARK FERGUS | MINIMUM HEADROOM | NR 66116 20950 | YES | YES | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821
| WESTPARK FERGUS | CT |  |  |  | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821
| WESTPARK FERGUS | LW |  |  |  | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821
| WESTPARK FERGUS | ST |  |  |  | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821
| WESTPARK FERGUS | FS |  |  |  | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0993 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0674 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821 | 4.0821
THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | -2.1365 | -2.1393 | -2.1472 | -2.1569 | -2.1665 | -2.1759 | -2.1851 | -2.1941 | -2.2041 | -2.2138 | -2.2332 | -4.0032 | -4.0447 | -4.0862 | -2.7875 | -2.7929 | -2.8083 | -2.8273 | -2.8459 | -2.8643 | -2.8822 | -2.8998 | -2.9191 | -2.9381 | -2.9758 | -4.4138 | -4.4653 | -4.517 | -3.1273 | -3.131 | -3.1415 | -3.1544 | -3.1671 | -3.1796 | -3.1918 | -3.2038 | -3.2169 | -3.2299 | -3.2556 | -4.9963 | -5.0314 | -5.0667
| WESTRAY | CT |  |  |  | -2.1365 | -2.1388 | -2.1447 | -2.1515 | -2.1582 | -2.1648 | -2.1712 | -2.1775 | -2.1844 | -2.1913 | -2.2048 | -3.9527 | -3.988 | -4.0231 | -2.7875 | -2.792 | -2.8035 | -2.8167 | -2.8298 | -2.8426 | -2.8551 | -2.8674 | -2.8809 | -2.8942 | -2.9206 | -4.3509 | -4.3949 | -4.4385 | -3.1273 | -3.1304 | -3.1382 | -3.1472 | -3.1561 | -3.1649 | -3.1734 | -3.1817 | -3.1909 | -3.2 | -3.218 | -4.9535 | -4.9834 | -5.0132
| WESTRAY | LW |  |  |  | -2.1365 | -2.1393 | -2.1472 | -2.1569 | -2.1665 | -2.1759 | -2.1851 | -2.1941 | -2.2041 | -2.2138 | -2.2332 | -4.0032 | -4.0447 | -4.0862 | -2.7875 | -2.7929 | -2.8083 | -2.8273 | -2.8459 | -2.8643 | -2.8822 | -2.8998 | -2.9191 | -2.9381 | -2.9758 | -4.4138 | -4.4653 | -4.517 | -3.1273 | -3.131 | -3.1415 | -3.1544 | -3.1671 | -3.1796 | -3.1918 | -3.2038 | -3.2169 | -3.2299 | -3.2556 | -4.9963 | -5.0314 | -5.0667
| WESTRAY | ST |  |  |  | -2.1357 | -2.1367 | -2.139 | -2.1427 | -2.147 | -2.1494 | -2.1517 | -2.154 | -2.1565 | -2.159 | -2.1637 | -3.0065 | -3.0243 | -3.042 | -2.7859 | -2.7879 | -2.7924 | -2.7995 | -2.808 | -2.8127 | -2.8172 | -2.8216 | -2.8265 | -2.8313 | -2.8406 | -3.5565 | -3.5786 | -3.6006 | -3.1262 | -3.1276 | -3.1307 | -3.1355 | -3.1413 | -3.1445 | -3.1476 | -3.1506 | -3.1539 | -3.1571 | -3.1635 | -4.0317 | -4.0468 | -4.0618
| WESTRAY | FS |  |  |  | -2.1352 | -2.1354 | -2.1355 | -2.1366 | -2.1378 | -2.1386 | -2.1394 | -2.1404 | -2.1414 | -2.1424 | -2.1443 | -2.1489 | -2.1533 | -2.1574 | -2.785 | -2.7853 | -2.7856 | -2.7877 | -2.7901 | -2.7917 | -2.7932 | -2.7951 | -2.7971 | -2.799 | -2.8028 | -2.8118 | -2.8202 | -2.8282 | -3.1256 | -3.1258 | -3.1261 | -3.1274 | -3.1291 | -3.1302 | -3.1312 | -3.1325 | -3.1339 | -3.1352 | -3.1377 | -3.1438 | -3.1496 | -3.155
TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | NO | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.6087 | 7.0726 | 6.5409 | 9.0924 | 9.0709 | 9.0083 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.2045 | 7.0442 | 6.7238 | 6.0736 | 5.419 | 4.7783 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.3257 | 7.0051 | 6.3547 | 5.6999 | 5.059
| WHITEHOUSE | CT |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.7103 | 7.3583 | 9.0924 | 9.0737 | 9.0253 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.1451 | 6.683 | 6.2183 | 5.7634 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 6.9643 | 6.4994 | 6.0444
| WHITEHOUSE | LW |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.6087 | 7.0726 | 6.5409 | 9.0926 | 9.0709 | 9.0083 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.2045 | 7.0442 | 6.7238 | 6.0736 | 5.419 | 4.7783 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.3257 | 7.0051 | 6.3547 | 5.6999 | 5.059
| WHITEHOUSE | ST |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 9.0995 | 9.0923 | 9.0755 | 9.0492 | 9.0174 | 8.9878 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.1426 | 6.8557 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.1371
| WHITEHOUSE | FS |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 9.1027 | 9.1016 | 9.1 | 9.0917 | 9.0817 | 9.0721 | 9.0624 | 9.0502 | 9.0381 | 9.0263 | 9.0031 | 8.9792 | 8.9792 | 8.9792 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593
PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 19.7746 | 19.6748 | 19.5467 | 19.4209 | 19.2995 | 19.1826 | 19.0703 | 18.9624 | 14.0334 | 13.3168 | 11.8329 | 9.343 | 7.5719 | 6.0047 | 17.5457 | 17.3698 | 17.1942 | 17.1239 | 17.0561 | 16.9908 | 13.1166 | 12.372 | 11.5643 | 10.747 | 9.0545 | 6.2441 | 4.2835 | 2.563 | 17.8069 | 17.6576 | 17.4589 | 17.2565 | 17.0572 | 16.9022 | 13.3298 | 12.5698 | 11.7445 | 10.9094 | 9.18 | 6.2916 | 4.2547 | 2.4642
| WHITESTRIPES | CT |  |  |  | 19.7746 | 19.6748 | 19.5467 | 19.4209 | 19.2995 | 19.1826 | 19.0703 | 18.9624 | 14.4351 | 13.8962 | 12.78 | 11.3581 | 10.2395 | 9.1567 | 17.5457 | 17.3698 | 17.1942 | 17.1239 | 17.0561 | 16.9908 | 13.5946 | 12.9853 | 12.3628 | 11.7504 | 10.4805 | 8.894 | 7.6666 | 6.4861 | 17.8069 | 17.6576 | 17.4589 | 17.2565 | 17.0572 | 16.9022 | 13.6246 | 12.9961 | 12.3655 | 11.7385 | 10.4391 | 8.7978 | 7.516 | 6.2786
| WHITESTRIPES | LW |  |  |  | 19.918 | 19.9014 | 19.8822 | 19.8606 | 19.8367 | 19.8109 | 19.7834 | 19.7543 | 14.0334 | 13.3168 | 11.8329 | 9.343 | 7.5719 | 6.0047 | 17.6582 | 17.5258 | 17.3816 | 17.3696 | 17.3563 | 17.3418 | 13.1166 | 12.372 | 11.5643 | 10.747 | 9.0545 | 6.2441 | 4.2835 | 2.563 | 17.9533 | 17.8784 | 17.7678 | 17.6369 | 17.5537 | 17.528 | 13.3298 | 12.5698 | 11.7445 | 10.9094 | 9.18 | 6.2916 | 4.2547 | 2.4642
| WHITESTRIPES | ST |  |  |  | 19.94 | 19.9342 | 19.9266 | 19.9191 | 19.9119 | 19.9031 | 19.8945 | 19.8862 | 19.8779 | 19.8659 | 19.8428 | 19.7794 | 19.7191 | 14.0546 | 17.8008 | 17.6536 | 17.549 | 17.4121 | 17.3982 | 17.3933 | 17.3885 | 17.3839 | 17.3793 | 17.3725 | 17.3596 | 13.0957 | 12.3428 | 11.6173 | 18.0366 | 17.9615 | 17.9057 | 17.85 | 17.7882 | 17.7463 | 17.7035 | 17.659 | 17.6104 | 17.5827 | 17.5597 | 13.3078 | 12.5323 | 11.7822
| WHITESTRIPES | FS |  |  |  | 19.9342 | 19.9266 | 19.9189 | 19.9076 | 19.8965 | 19.8854 | 19.8746 | 19.8639 | 19.8533 | 19.8429 | 19.8225 | 19.7618 | 19.6973 | 19.6346 | 17.8202 | 17.7966 | 17.6814 | 17.6242 | 17.5598 | 17.5119 | 17.4629 | 17.409 | 17.3655 | 17.3597 | 17.3483 | 17.3144 | 17.2783 | 17.2433 | 18.0424 | 18.026 | 17.9652 | 17.9301 | 17.8917 | 17.8614 | 17.8361 | 17.8102 | 17.7837 | 17.7567 | 17.7013 | 17.5497 | 17.4194 | 17.3523
CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0426 | 9.0416 | 9.0388 | 9.0354 | 9.032 | 9.0287 | 9.0249 | 9.0181 | 9.0109 | 9.0037 | 8.9898 | 8.9283 | 8.8589 | 8.8329 | 9.0561 | 9.0557 | 9.0544 | 9.0528 | 9.0512 | 9.0497 | 9.048 | 9.0449 | 9.0416 | 9.0383 | 9.0319 | 9.0211 | 9.0211 | 9.0211
| WHITING BAY | CT |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0426 | 9.0418 | 9.0397 | 9.0373 | 9.0349 | 9.0326 | 9.0303 | 9.0281 | 9.0257 | 9.0233 | 9.0186 | 8.9371 | 8.8614 | 8.835 | 9.0561 | 9.0557 | 9.0548 | 9.0537 | 9.0526 | 9.0515 | 9.0505 | 9.0495 | 9.0484 | 9.0473 | 9.0451 | 9.0211 | 9.0211 | 9.0211
| WHITING BAY | LW |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0426 | 9.0416 | 9.0388 | 9.0354 | 9.032 | 9.0287 | 9.0254 | 9.0223 | 9.0189 | 9.0155 | 9.0088 | 8.9283 | 8.8589 | 8.8329 | 9.0561 | 9.0557 | 9.0544 | 9.0528 | 9.0512 | 9.0497 | 9.0483 | 9.0468 | 9.0452 | 9.0437 | 9.0406 | 9.0211 | 9.0211 | 9.0211
| WHITING BAY | ST |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0429 | 9.0425 | 9.0417 | 9.0404 | 9.0388 | 9.0318 | 9.0249 | 9.0181 | 9.0109 | 9.0037 | 8.9898 | 8.9561 | 8.9227 | 8.8895 | 9.0563 | 9.0561 | 9.0557 | 9.0551 | 9.0544 | 9.0511 | 9.048 | 9.0449 | 9.0416 | 9.0383 | 9.0319 | 9.0211 | 9.0211 | 9.0211
| WHITING BAY | FS |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0431 | 9.043 | 9.043 | 9.0426 | 9.0422 | 9.0398 | 9.0375 | 9.0346 | 9.0317 | 9.0288 | 9.0233 | 9.0101 | 8.9979 | 8.9864 | 9.0563 | 9.0563 | 9.0563 | 9.0561 | 9.0559 | 9.0548 | 9.0538 | 9.0524 | 9.0511 | 9.0498 | 9.0473 | 9.0412 | 9.0356 | 9.0304
MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 22.4566 | 22.455 | 22.4519 | 22.4485 | 22.4452 | 22.442 | 22.4384 | 22.4347 | 22.4313 | 22.428 | 22.4216 | 22.4038 | 22.384 | 22.3648 | 20.9147 | 20.9029 | 20.8801 | 20.854 | 20.8298 | 20.8061 | 20.7792 | 20.7514 | 20.7261 | 20.7013 | 20.6531 | 20.5206 | 20.372 | 20.2288 | 20.8876 | 20.883 | 20.874 | 20.8637 | 20.8542 | 20.8449 | 20.8343 | 20.8234 | 20.8134 | 20.8036 | 20.7847 | 20.7326 | 20.6741 | 20.6177
| WICK | CT |  |  |  | 22.4566 | 22.4553 | 22.4529 | 22.4504 | 22.4481 | 22.4458 | 22.443 | 22.4402 | 22.4376 | 22.4351 | 22.4303 | 22.4182 | 22.404 | 22.3899 | 20.9148 | 20.9049 | 20.8873 | 20.8688 | 20.8516 | 20.8342 | 20.8134 | 20.7919 | 20.7728 | 20.7544 | 20.7187 | 20.6279 | 20.5217 | 20.4167 | 20.8877 | 20.8838 | 20.8769 | 20.8696 | 20.8628 | 20.856 | 20.8478 | 20.8393 | 20.8318 | 20.8245 | 20.8105 | 20.7748 | 20.733 | 20.6917
| WICK | LW |  |  |  | 22.4566 | 22.455 | 22.4519 | 22.4485 | 22.4452 | 22.442 | 22.4384 | 22.4347 | 22.4313 | 22.428 | 22.4216 | 22.4038 | 22.384 | 22.3648 | 20.9147 | 20.9029 | 20.8801 | 20.854 | 20.8298 | 20.8061 | 20.7792 | 20.7514 | 20.7261 | 20.7013 | 20.6531 | 20.5206 | 20.372 | 20.2288 | 20.8876 | 20.883 | 20.874 | 20.8637 | 20.8542 | 20.8449 | 20.8343 | 20.8234 | 20.8134 | 20.8036 | 20.7847 | 20.7326 | 20.6741 | 20.6177
| WICK | ST |  |  |  | 22.457 | 22.4563 | 22.4553 | 22.4539 | 22.4524 | 22.4508 | 22.4489 | 22.447 | 22.4452 | 22.4436 | 22.4404 | 22.4326 | 22.4237 | 22.415 | 20.9182 | 20.9126 | 20.9048 | 20.8945 | 20.8833 | 20.8715 | 20.8574 | 20.8429 | 20.83 | 20.8176 | 20.7938 | 20.7358 | 20.6693 | 20.6041 | 20.889 | 20.8868 | 20.8837 | 20.8797 | 20.8753 | 20.8706 | 20.8651 | 20.8594 | 20.8543 | 20.8494 | 20.84 | 20.8172 | 20.7911 | 20.7654
| WICK | FS |  |  |  | 22.4574 | 22.4571 | 22.4568 | 22.4564 | 22.4559 | 22.4554 | 22.4548 | 22.4539 | 22.4533 | 22.4526 | 22.4513 | 22.4483 | 22.4451 | 22.4418 | 20.9207 | 20.9184 | 20.9167 | 20.9133 | 20.9099 | 20.9059 | 20.901 | 20.895 | 20.8899 | 20.8848 | 20.8752 | 20.8531 | 20.8292 | 20.804 | 20.89 | 20.8891 | 20.8884 | 20.8871 | 20.8857 | 20.8842 | 20.8822 | 20.8799 | 20.8779 | 20.8759 | 20.8721 | 20.8634 | 20.854 | 20.8441
WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 21.3896 | 21.3882 | 21.3848 | 21.3807 | 21.3767 | 21.3727 | 21.3687 | 21.3647 | 21.3605 | 21.3563 | 21.346 | 21.2921 | 21.2352 | 21.1793 | 30.9154 | 30.9079 | 30.8898 | 30.8681 | 30.8465 | 30.8251 | 30.8038 | 30.7828 | 30.7601 | 30.7381 | 30.6831 | 30.5244 | 30.5244 | 30.5244 | 20.8476 | 20.8432 | 20.8326 | 20.8197 | 20.807 | 20.7944 | 20.7819 | 20.7695 | 20.7562 | 20.7432 | 20.7108 | 20.542 | 20.3269 | 19.9977
| WOODHILL | CT |  |  |  | 21.3899 | 21.3889 | 21.3868 | 21.3845 | 21.3821 | 21.3796 | 21.3773 | 21.3749 | 21.3724 | 21.37 | 21.3649 | 21.3227 | 21.2791 | 21.238 | 30.9167 | 30.9115 | 30.9004 | 30.8882 | 30.8753 | 30.8622 | 30.8497 | 30.8372 | 30.8237 | 30.8107 | 30.7839 | 30.559 | 30.5244 | 30.5244 | 20.8484 | 20.8453 | 20.8388 | 20.8316 | 20.824 | 20.8163 | 20.8089 | 20.8016 | 20.7936 | 20.7859 | 20.7702 | 20.6378 | 20.5012 | 20.344
| WOODHILL | LW |  |  |  | 21.3896 | 21.3882 | 21.3848 | 21.3807 | 21.3767 | 21.3727 | 21.3687 | 21.3647 | 21.3605 | 21.3563 | 21.346 | 21.2921 | 21.2352 | 21.1793 | 30.9154 | 30.9079 | 30.8898 | 30.8681 | 30.8465 | 30.8251 | 30.8038 | 30.7828 | 30.7601 | 30.7381 | 30.6831 | 30.5244 | 30.5244 | 30.5244 | 20.8476 | 20.8432 | 20.8326 | 20.8197 | 20.807 | 20.7944 | 20.7819 | 20.7695 | 20.7562 | 20.7432 | 20.7108 | 20.542 | 20.3269 | 19.9977
| WOODHILL | ST |  |  |  | 21.4053 | 21.3905 | 21.3894 | 21.3878 | 21.3858 | 21.3816 | 21.3775 | 21.3735 | 21.3691 | 21.3649 | 21.3564 | 21.328 | 21.2996 | 21.2733 | 30.9988 | 30.92 | 30.914 | 30.9055 | 30.895 | 30.8726 | 30.8509 | 30.8295 | 30.8063 | 30.7837 | 30.7388 | 30.5871 | 30.5244 | 30.5244 | 20.8967 | 20.8503 | 20.8468 | 20.8418 | 20.8356 | 20.8224 | 20.8096 | 20.797 | 20.7834 | 20.77 | 20.7436 | 20.6543 | 20.5655 | 20.4832
| WOODHILL | FS |  |  |  | 21.4065 | 21.4062 | 21.3975 | 21.3969 | 21.3964 | 21.395 | 21.3937 | 21.392 | 21.3903 | 21.3887 | 21.3855 | 21.3777 | 21.3686 | 21.3587 | 31.0053 | 31.0038 | 30.9572 | 30.9542 | 30.9512 | 30.9441 | 30.9369 | 30.9279 | 30.9189 | 30.9103 | 30.8936 | 30.8521 | 30.8037 | 30.7506 | 20.9005 | 20.8997 | 20.8722 | 20.8705 | 20.8687 | 20.8645 | 20.8603 | 20.855 | 20.8497 | 20.8446 | 20.8348 | 20.8103 | 20.7818 | 20.7506
| TX lookup |  |  |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
[6 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43

## Local Authority Reference
Local Authority | Grid Supply Point | Primary Substation
Aberdeen City | CLAYHILLS | BALNAGASK
Aberdeen City | CLAYHILLS | CLAYHILLS
Aberdeen City | CLAYHILLS | COMMERCE STREET
Aberdeen City | CLAYHILLS | CRAIGINCHES
Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
Aberdeen City | CRAIGIEBUCKLER | CULTER
Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeen City | DYCE | DYCE NORTH
Aberdeen City | KINTORE | PARK
Aberdeen City | KINTORE | SKENE
Aberdeen City | KINTORE | TORRYBURN
Aberdeen City | PERSLEY | BRIDGE OF DON
Aberdeen City | PERSLEY | HAUDAGAIN
Aberdeen City | PERSLEY | NORTHFIELD
Aberdeen City | PERSLEY | ST MACHAR
Aberdeen City | PERSLEY | STONEYWOOD T1&T2
Aberdeen City | PERSLEY | STONEYWOOD T3
Aberdeen City | PERSLEY | WHITESTRIPES
Aberdeen City | REDMOSS | KINCORTH
Aberdeen City | REDMOSS | REDMOSS
Aberdeen City | WILLOWDALE | DENBURN
Aberdeen City | WILLOWDALE | GREYFRIARS
Aberdeen City | WILLOWDALE | HAYTON
Aberdeen City | WILLOWDALE | ST NICHOLAS
Aberdeen City | WOODHILL | QUEENS LANE NORTH
Aberdeen City | WOODHILL | SPRINGHILL
Aberdeen City | WOODHILL | WOODHILL
Aberdeenshire | BOAT OF GARTEN | AVIEMORE
Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
Aberdeenshire | BRIDGE OF DUN | INCHBARE
Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
Aberdeenshire | BRIDGE OF DUN | ST CYRUS
Aberdeenshire | COUPAR ANGUS | DALRULZION
Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
Aberdeenshire | CRAIGIEBUCKLER | CULTER
Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeenshire | DYCE | BALMEDIE
Aberdeenshire | DYCE | DYCE NORTH
Aberdeenshire | DYCE | ELLON 11 kV
Aberdeenshire | DYCE | KINGSEAT
Aberdeenshire | FIDDES | EDZELL
Aberdeenshire | FIDDES | INVERBERVIE
Aberdeenshire | FIDDES | LAURENCEKIRK
Aberdeenshire | FIDDES | STONEHAVEN
Aberdeenshire | FRASERBURGH | FRASERBURGH
Aberdeenshire | KEITH | CULLEN
Aberdeenshire | KEITH | DUFFTOWN
Aberdeenshire | KEITH | HUNTLY
Aberdeenshire | KEITH | INSCH
Aberdeenshire | KEITH | KEITH
Aberdeenshire | KEITH | LIMEHILLOCKS
Aberdeenshire | KEITH | MARNOCH
Aberdeenshire | KINTORE | BANCHORY
Aberdeenshire | KINTORE | FYVIE
Aberdeenshire | KINTORE | INVERURIE
Aberdeenshire | KINTORE | KEMNAY
Aberdeenshire | KINTORE | METHLICK
Aberdeenshire | KINTORE | MIDMAR
Aberdeenshire | KINTORE | OLDMELDRUM
Aberdeenshire | KINTORE | PARK
Aberdeenshire | KINTORE | SKENE
Aberdeenshire | KINTORE | TORRYBURN
Aberdeenshire | LUNANHEAD | MARYTON
Aberdeenshire | MACDUFF | MACDUFF
Aberdeenshire | MACDUFF | PORTSOY
Aberdeenshire | MACDUFF | TURRIFF
Aberdeenshire | PERSLEY | BRIDGE OF DON
Aberdeenshire | PERSLEY | WHITESTRIPES
Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE 11kV
Aberdeenshire | PETERHEAD GRANGE | PHEAD NORTH ST
Aberdeenshire | PETERHEAD SHELL | BODDAM
Aberdeenshire | REDMOSS | KINCORTH
Aberdeenshire | REDMOSS | NEWTONHILL
Aberdeenshire | REDMOSS | REDMOSS
Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
Aberdeenshire | STRICHEN | HATTON
Aberdeenshire | STRICHEN | MAUD
Aberdeenshire | STRICHEN | MINTLAW
Aberdeenshire | STRICHEN | NEW PITSLIGO
Aberdeenshire | STRICHEN | STONEYHILL
Aberdeenshire | STRICHEN | STRICHEN
Aberdeenshire | TARLAND | ABOYNE
Aberdeenshire | TARLAND | BALLATER
Aberdeenshire | TARLAND | MOSSAT
Aberdeenshire | TARLAND | STRATHDON
Aberdeenshire | TARLAND | WHITEHOUSE
Aberdeenshire | TUMMEL BRIDGE | BONSKEID
Aberdeenshire | WOODHILL | SPRINGHILL
Angus | ABERNETHY | BALBEGGIE
Angus | ARBROATH | CARNOUSTIE
Angus | ARBROATH | CHARLES AVENUE
Angus | ARBROATH | ELLIOT DEPOT
Angus | ARBROATH | HUME STREET
Angus | ARBROATH | REDFORD
Angus | BRIDGE OF DUN | BRECHIN
Angus | BRIDGE OF DUN | BRIDGE OF DUN 11kV
Angus | BRIDGE OF DUN | INCHBARE
Angus | BRIDGE OF DUN | LOGIE PERT
Angus | BRIDGE OF DUN | MILL RD MONTROSE
Angus | BRIDGE OF DUN | MONTROSE NORTH
Angus | BRIDGE OF DUN | ST CYRUS
Angus | CHARLESTON | GOURDIE
Angus | COUPAR ANGUS | ALYTH
Angus | COUPAR ANGUS | COUPAR ANGUS
Angus | COUPAR ANGUS | DALRULZION
Angus | COUPAR ANGUS | LEOCH
Angus | FIDDES | EDZELL
Angus | FIDDES | LAURENCEKIRK
Angus | KINTORE | BANCHORY
Angus | LUNANHEAD | FRIOCKHEIM
Angus | LUNANHEAD | INVERARITY
Angus | LUNANHEAD | LOCHSIDE
Angus | LUNANHEAD | LUNANHEAD
Angus | LUNANHEAD | MARYTON
Angus | LYNDHURST | MACALPINE ROAD
Angus | LYNDHURST | WEST KIRKTON
Angus | MILTON OF CRAIGIE | ASHLUDIE
Angus | MILTON OF CRAIGIE | BALDOVIE
Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
Angus | MILTON OF CRAIGIE | EDZELL STREET
Angus | MILTON OF CRAIGIE | LONGHAUGH
Angus | TARLAND | BALLATER
Argyll and Bute | CARRADALE | BALLURE
Argyll and Bute | CARRADALE | CAMPBELTOWN
Argyll and Bute | CARRADALE | CLAONAIG
Argyll and Bute | CARRADALE | DIPPEN
Argyll and Bute | CARRADALE | WESTPARK FERGUS
Argyll and Bute | CLACHAN | BUTTERBRIDGE
Argyll and Bute | CLACHAN | DOUGLAS PIER
Argyll and Bute | CLACHAN | INVERARAY
Argyll and Bute | CLACHAN | LOCHGOILHEAD
Argyll and Bute | CLACHAN | STRACHUR
Argyll and Bute | DUNOON | BRUCHAG
Argyll and Bute | DUNOON | COLINTRAIVE
Argyll and Bute | DUNOON | DUNOON
Argyll and Bute | DUNOON | GLENDARUEL
Argyll and Bute | DUNOON | INNELLAN
Argyll and Bute | DUNOON | KAMES
Argyll and Bute | DUNOON | NEWTON
Argyll and Bute | DUNOON | OTTER FERRY
Argyll and Bute | DUNOON | ROTHESAY
Argyll and Bute | DUNOON | SANDBANK
Argyll and Bute | FORT WILLIAM | SALEN
Argyll and Bute | KILLIN | CASHLIE
Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
Argyll and Bute | PORT ANN | BOWMORE
Argyll and Bute | PORT ANN | CRINAN
Argyll and Bute | PORT ANN | CROMALT
Argyll and Bute | PORT ANN | INVERNEIL
Argyll and Bute | PORT ANN | LOCHGILPHEAD
Argyll and Bute | PORT ANN | LUSSAGIVEN
Argyll and Bute | PORT ANN | PORT ASKAIG
Argyll and Bute | PORT ANN | PORT ELLEN
Argyll and Bute | PORT ANN | STONEFIELD
Argyll and Bute | PORT ANN | TARBERT JURA
Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
Argyll and Bute | RANNOCH | BLACKMOUNT
Argyll and Bute | RANNOCH | GLENETIVE
Argyll and Bute | RANNOCH | TYNDRUM
Argyll and Bute | STRATHLEVEN | DRYMEN
Argyll and Bute | TAYNUILT | BARCALDINE
Argyll and Bute | TAYNUILT | CONNEL
Argyll and Bute | TAYNUILT | DALMALLY
Argyll and Bute | TAYNUILT | DERVAIG
Argyll and Bute | TAYNUILT | EREDINE
Argyll and Bute | TAYNUILT | KENMORE
Argyll and Bute | TAYNUILT | KERRERA
Argyll and Bute | TAYNUILT | KILCHRENAN
Argyll and Bute | TAYNUILT | KILMELFORD PS
Argyll and Bute | TAYNUILT | KILNINVER
Argyll and Bute | TAYNUILT | KINLOCH
Argyll and Bute | TAYNUILT | LOCHDONHEAD
Argyll and Bute | TAYNUILT | OBAN
Argyll and Bute | TAYNUILT | SCAMMADALE
Argyll and Bute | TAYNUILT | TAYNUILT
Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
Clackmannanshire | ABERNETHY | GLENDEVON
Clackmannanshire | ABERNETHY | MILNATHORT
Clackmannanshire | BRACO | GLENEAGLES
Dundee City | CHARLESTON | CHARLESTON
Dundee City | CHARLESTON | GOURDIE
Dundee City | CHARLESTON | MENZIESHILL
Dundee City | CHARLESTON | NINEWELLS
Dundee City | COUPAR ANGUS | LEOCH
Dundee City | DUDHOPE | CONSTABLE STREET
Dundee City | DUDHOPE | ROSEBANK STREET
Dundee City | GLENAGNES | OVERGATE
Dundee City | GLENAGNES | WALTON
Dundee City | LYNDHURST | LOCHEE
Dundee City | LYNDHURST | LYNDHURST
Dundee City | LYNDHURST | MACALPINE ROAD
Dundee City | LYNDHURST | WEST KIRKTON
Dundee City | MILTON OF CRAIGIE | ASHLUDIE
Dundee City | MILTON OF CRAIGIE | BALDOVIE
Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
Dundee City | MILTON OF CRAIGIE | EDZELL STREET
Dundee City | MILTON OF CRAIGIE | LONGHAUGH
Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
East Dunbartonshire | BRACO | KIPPEN
East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
East Dunbartonshire | STRATHLEVEN | KILLEARN
Eilean Siar | ARDMORE | AIRD
Eilean Siar | ARDMORE | CLACHAN
Eilean Siar | ARDMORE | DRIMORE
Eilean Siar | ARDMORE | LOCH CARNAN
Eilean Siar | ARDMORE | POLLACHAR
Eilean Siar | ARDMORE | STOCKINISH
Eilean Siar | ARDMORE | TARBERT
Eilean Siar | STORNOWAY | ARNISH
Eilean Siar | STORNOWAY | BARVAS
Eilean Siar | STORNOWAY | BATTERY POINT
Eilean Siar | STORNOWAY | CALLANISH
Eilean Siar | STORNOWAY | COLL
Eilean Siar | STORNOWAY | GISLA
Eilean Siar | STORNOWAY | HARRIS GRID
Eilean Siar | STORNOWAY | LAXAY
Eilean Siar | STORNOWAY | MAARUIG
Fife | ABERNETHY | ABERNETHY
Fife | ABERNETHY | BRIDGE OF EARN
Fife | ABERNETHY | GLENDEVON
Fife | ABERNETHY | MILNATHORT
Highland | ALNESS | BALALDIE
Highland | ALNESS | CONTULLICH
Highland | ALNESS | CROSSHILLS
Highland | ALNESS | GLASTULLICH
Highland | ALNESS | INVERGORDON
Highland | ALNESS | NIGG
Highland | ALNESS | PEDDIESTON
Highland | ALNESS | TAIN
Highland | BEAULY | AIGAS
Highland | BEAULY | BLACKSTAND
Highland | BEAULY | CONON BRIDGE
Highland | BEAULY | DINGWALL
Highland | BEAULY | KILTARLITY
Highland | BEAULY | MARYBANK
Highland | BEAULY | MUIR OF ORD
Highland | BEAULY | MUIREND
Highland | BOAT OF GARTEN | AVIEMORE
Highland | BOAT OF GARTEN | BALLINDALLOCH
Highland | BOAT OF GARTEN | BOAT OF GARTEN 11 kV
Highland | BOAT OF GARTEN | DALWHINNIE
Highland | BOAT OF GARTEN | GRANTOWN
Highland | BOAT OF GARTEN | KINGUSSIE
Highland | BOAT OF GARTEN | TOMATIN
Highland | BROADFORD | ACHINTEE
Highland | BROADFORD | BROADFORD
Highland | BROADFORD | KISHORNHILL
Highland | BROADFORD | KYLE
Highland | BROADFORD | LOWER OLLACH
Highland | BROADFORD | NOSTIE BRIDGE
Highland | BROADFORD | SHIELDAIG
Highland | BROADFORD | SKULAMUS
Highland | BRORA | BRORA
Highland | BRORA | DORNOCH
Highland | BRORA | GOLSPIE
Highland | BRORA | HELMSDALE
Highland | CASSLEY | OVERSCAIG
Highland | CASSLEY | RHICONICH
Highland | CEANNACROC | DRUMNADROCHIT
Highland | DOUNREAY | BETTYHILL
Highland | DOUNREAY | COLDBACKIE
Highland | DOUNREAY | DOUNREAY
Highland | DOUNREAY | FORSS
Highland | DUNOON | DUNOON
Highland | DUNVEGAN | DRYNOCH
Highland | DUNVEGAN | DUNVEGAN GRID
Highland | DUNVEGAN | PORTREE
Highland | DUNVEGAN | UIG
Highland | FORT AUGUSTUS | ABERCHALDER
Highland | FORT AUGUSTUS | BUNOICH
Highland | FORT AUGUSTUS | GLEN LAOGH
Highland | FORT AUGUSTUS | GLENDOE PRIMARY
Highland | FORT AUGUSTUS | INVERGARRY
Highland | FORT WILLIAM | ANNAT
Highland | FORT WILLIAM | ARISAIG
Highland | FORT WILLIAM | CORRAN
Highland | FORT WILLIAM | GLENUIG
Highland | FORT WILLIAM | INVERLOCHY
Highland | FORT WILLIAM | KINGAIRLOCH
Highland | FORT WILLIAM | KINLOCHMOIDART
Highland | FORT WILLIAM | LIDDESDALE
Highland | FORT WILLIAM | LOCHALINE
Highland | FORT WILLIAM | MALLAIG
Highland | FORT WILLIAM | PINEGROVE
Highland | FORT WILLIAM | POOR HOUSE
Highland | FORT WILLIAM | RAHOY
Highland | FORT WILLIAM | SHONA BEAG
Highland | FORT WILLIAM | STRONTIAN
Highland | GRUDIE BRIDGE | ACHILTIBUIE
Highland | GRUDIE BRIDGE | AULTBEA
Highland | GRUDIE BRIDGE | CONON FALLS
Highland | GRUDIE BRIDGE | DRUMRUNIE
Highland | GRUDIE BRIDGE | GARBAT FOREST
Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
Highland | GRUDIE BRIDGE | INVERBROOM
Highland | GRUDIE BRIDGE | KERRY FALLS
Highland | GRUDIE BRIDGE | KINLOCHEWE
Highland | GRUDIE BRIDGE | LETTEREWE
Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
Highland | GRUDIE BRIDGE | LOCHINVER
Highland | GRUDIE BRIDGE | ULLAPOOL
Highland | INVERNESS | CULLODEN
Highland | INVERNESS | DALNEIGH
Highland | INVERNESS | ERROGIE
Highland | INVERNESS | FOYERS
Highland | INVERNESS | HILTON
Highland | INVERNESS | INVERARNIE
Highland | INVERNESS | INVERNESS 11 kV
Highland | INVERNESS | RAIGMORE
Highland | INVERNESS | WATERLOO PLACE
Highland | KEITH | ABERLOUR
Highland | KILLIN | WESTER DRUMMOND
Highland | KINLOCHLEVEN | GLENCOE
Highland | KINLOCHLEVEN | KINLOCHLEVEN
Highland | LAIRG | LAIRG GRID
Highland | LAIRG | TORBOLL
Highland | LAIRG | TRESSADY
Highland | MYBSTER | LATHERON
Highland | MYBSTER | MELVICH
Highland | MYBSTER | WICK
Highland | NAIRN | ARDERSIER
Highland | NAIRN | DALCROSS
Highland | NAIRN | FORRES
Highland | NAIRN | LETHEN
Highland | NAIRN | NAIRN CENTRAL
Highland | QUOICH | QUOICH PRIMARY
Highland | RANNOCH | BLACKMOUNT
Highland | RANNOCH | BRIDGE OF GAUR
Highland | RANNOCH | GLENETIVE
Highland | SHIN | GLEDFIELD
Highland | SHIN | SHIN
Highland | ST FILLANS | COMRIE
Highland | TAYNUILT | BARCALDINE
Highland | TAYNUILT | SALEN 2
Highland | THURSO | HALKIRK
Highland | THURSO | HASTIGROW
Highland | THURSO | MOUNT PLEASANT
Highland | THURSO | ORMLIE
Highland | TUMMEL BRIDGE | BONSKEID
Highland | TUMMEL BRIDGE | CALVINE
Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
Moray | BOAT OF GARTEN | AVIEMORE
Moray | BOAT OF GARTEN | BALLINDALLOCH
Moray | BOAT OF GARTEN | GRANTOWN
Moray | ELGIN | ASHGROVE
Moray | ELGIN | BILBOHALL
Moray | ELGIN | BURGHEAD
Moray | ELGIN | CUMMING STREET
Moray | ELGIN | ELGIN
Moray | ELGIN | FOCHABERS
Moray | ELGIN | KINLOSS
Moray | ELGIN | LHANBRYDE
Moray | ELGIN | LOSSIEMOUTH
Moray | KEITH | ABERLOUR
Moray | KEITH | BUCKIE
Moray | KEITH | CULLEN
Moray | KEITH | DUFFTOWN
Moray | KEITH | HUNTLY
Moray | KEITH | KEITH
Moray | KEITH | LIMEHILLOCKS
Moray | KEITH | MARNOCH
Moray | KEITH | ROTHES
Moray | MACDUFF | PORTSOY
Moray | NAIRN | FORRES
Moray | NAIRN | LETHEN
Moray | NAIRN | NAIRN CENTRAL
Moray | TARLAND | BALLATER
Moray | TARLAND | MOSSAT
Moray | TARLAND | STRATHDON
North Ayrshire | CARRADALE | BALLIEKINE
North Ayrshire | CARRADALE | BRODICK
North Ayrshire | CARRADALE | MACHRIE
North Ayrshire | CARRADALE | WHITING BAY
North Ayrshire | DUNOON | BRUCHAG
North Lanarkshire | BRACO | KIPPEN
Orkney Islands | THURSO | BURGARHILL
Orkney Islands | THURSO | EDAY
Orkney Islands | THURSO | FLOTTA
Orkney Islands | THURSO | KIRKWALL
Orkney Islands | THURSO | LYNESS
Orkney Islands | THURSO | NORTH HOY
Orkney Islands | THURSO | ROUSAY
Orkney Islands | THURSO | SANDAY
Orkney Islands | THURSO | SHAPINSAY
Orkney Islands | THURSO | ST MARYS
Orkney Islands | THURSO | STROMNESS
Orkney Islands | THURSO | STRONSAY
Orkney Islands | THURSO | WESTRAY
Perth and Kinross | ABERNETHY | ABERNETHY
Perth and Kinross | ABERNETHY | BALBEGGIE
Perth and Kinross | ABERNETHY | BRIDGE OF EARN
Perth and Kinross | ABERNETHY | ERROL
Perth and Kinross | ABERNETHY | GLENDEVON
Perth and Kinross | ABERNETHY | HARBOUR
Perth and Kinross | ABERNETHY | MILNATHORT
Perth and Kinross | ABERNETHY | SCONE
Perth and Kinross | BOAT OF GARTEN | AVIEMORE
Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
Perth and Kinross | BRACO | CALLANDER
Perth and Kinross | BRACO | CRIEFF
Perth and Kinross | BRACO | DUNBLANE
Perth and Kinross | BRACO | FORTEVIOT
Perth and Kinross | BRACO | GLENEAGLES
Perth and Kinross | BURGHMUIR | BURGHMUIR
Perth and Kinross | BURGHMUIR | GOODLYBURN
Perth and Kinross | BURGHMUIR | INVERALMOND
Perth and Kinross | BURGHMUIR | REDGORTON
Perth and Kinross | BURGHMUIR | THIMBLEROW
Perth and Kinross | CHARLESTON | GOURDIE
Perth and Kinross | CHARLESTON | NINEWELLS
Perth and Kinross | COUPAR ANGUS | ALYTH
Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
Perth and Kinross | COUPAR ANGUS | CAPUTH
Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
Perth and Kinross | COUPAR ANGUS | DALRULZION
Perth and Kinross | COUPAR ANGUS | LEOCH
Perth and Kinross | FORT WILLIAM | INVERLOCHY
Perth and Kinross | KILLIN | CASHLIE
Perth and Kinross | KILLIN | CHAORACH
Perth and Kinross | KILLIN | COSHIEVILLE
Perth and Kinross | KILLIN | KILLIN TOWN
Perth and Kinross | KILLIN | LOCHEARNHEAD
Perth and Kinross | LUNANHEAD | MARYTON
Perth and Kinross | RANNOCH | BLACKMOUNT
Perth and Kinross | RANNOCH | BRIDGE OF GAUR
Perth and Kinross | RANNOCH | GLENETIVE
Perth and Kinross | RANNOCH | TYNDRUM
Perth and Kinross | ST FILLANS | DALCHONZIE
Perth and Kinross | ST FILLANS | ST FILLANS P S
Perth and Kinross | TARLAND | BALLATER
Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
Perth and Kinross | TUMMEL BRIDGE | BONSKEID
Perth and Kinross | TUMMEL BRIDGE | CALVINE
Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
Shetland Islands | SHETLAND | FIRTH
Shetland Islands | SHETLAND | GUTCHER
Shetland Islands | SHETLAND | MID YELL
Shetland Islands | SHETLAND | SANDWICK
Shetland Islands | SHETLAND | SCALLOWAY
Shetland Islands | SHETLAND | SUMBURGH
Shetland Islands | SHETLAND | TUMBLIN
Shetland Islands | SHETLAND | UNST
Shetland Islands | SHETLAND | VOE
Shetland Islands | WOODHILL | BRAE
Stirling | BRACO | CALLANDER
Stirling | BRACO | DUNBLANE
Stirling | BRACO | GLENEAGLES
Stirling | BRACO | KIPPEN
Stirling | KILLIN | CASHLIE
Stirling | KILLIN | CHAORACH
Stirling | KILLIN | COSHIEVILLE
Stirling | KILLIN | KILLIN TOWN
Stirling | KILLIN | LOCHEARNHEAD
Stirling | KILLIN | LUBNAIG
Stirling | RANNOCH | TYNDRUM
Stirling | ST FILLANS | DALCHONZIE
Stirling | ST FILLANS | ST FILLANS P S
Stirling | STRATHLEVEN | ABERFOYLE
Stirling | STRATHLEVEN | DRYMEN
Stirling | STRATHLEVEN | KEPCULLOCH
Stirling | STRATHLEVEN | KILLEARN
Stirling | TAYNUILT | DALMALLY
West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
West Dunbartonshire | STRATHLEVEN | DRYMEN
West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
| GSPs in November 2022 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2024 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2028 | Under active review
| Killin | 2024 | Under active review | 2030 | Under active review
| Rannoch | 2024 | Under active review | 2025 | Under active review
| St Fillans | 2024 | Under active review | 2028 | Under active review
| Tummel Bridge | 2024 | Under active review | 2025 | Under active review
| Redmoss | NA |  | NA
| Woodhill | NA |  | NA
| Ardkinglas | 2024 | Under active review | 2030 | Under active review
| Ardmore | NA | Under active review | 2026 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2030 | Under active review
| Lyndhurst | 2032 | Under active review | 2030 | Under active review
| Peterhead Grange | 2033 | Under active review | 2026 | Under active review
| Dunbeath | NA |  | 2028 | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2026 | Under active review | 2026 | Under active review
| Brora | NA |  | 2030 | Under active review
| Dunvegan | NA |  | 2026 | Under active review
| Fasnakyle | 2024 | Under active review | 2027 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2030 | Under active review
| Shin | NA |  | 2027 | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2027 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2024 | Under active review | N/A
| Kinlochleven | 2024 | Under active review | N/A
| Glenfarclas | 2024 | Under active review | N/A
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2028 | Under active review
| Craigiebuckler | NA |  | NA
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | NA
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2030 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2029 | Under active review | 2029 | Under active review
| Quoich | NA |  | NA
| Boat of Garten | 2024 | Under active review | 2028 | Under active review
| Inverness | N/A |  | 2024 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2024 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2028 | Under active review
| Carradale 1 | 2024 | Under active review | 2034 | Under active review
| Carradale 2 | 2024 | Under active review | 2034 | Under active review
| Clachan | 2024 | Under active review | 2030 | Under active review
| Dunoon | 2024 | Under active review | 2028 | Under active review
| Fort William | 2024 | Under active review | 2024 | Under active review
| Port Ann | 2027 | Under active review | 2034 | Under active review
| Taynuilt | 2024 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | NA
| Mybster 2 | NA |  | NA
| Thurso | NA |  | NA
| Sloy | 2024 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2023-03-01 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 For storage, both the demand and generation EISDs may be relevant.
3 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.