## Contents
SHEPD Network Scenario Headroom Report 2024 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations up to 2050. SHEPD have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
May 2024
Version 1.1

## Key Information
SHEPD Network Scenario Headroom Report 2024 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD.
`
May 2024
Version 1.1

## Primary Headroom Dem
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[8 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.19013 | 0.17908 | 0.1668 | 0.1542 | 0.14429 | 0.12889 | 0.10888 | 0.10041 | 0.10012 | 0.10317 | 0.098139 | 0.078031 | 0.052786 | 0.022946 | 0.19342 | 0.18123 | 0.16828 | 0.1554 | 0.14598 | 0.1309 | 0.11065 | 0.10334 | 0.10476 | 0.10874 | 0.10479 | 0.085241 | 0.056495 | 0.022669 | 0.19134 | 0.17855 | 0.16417 | 0.14973 | 0.13858 | 0.12168 | 0.099608 | 0.091813 | 0.090118 | 0.095254 | 0.090132 | 0.068296 | 0.03794 | 0.0023032
|  | ABERCHALDER | CT |  |  |  | 0 | 0.19013 | 0.1857 | 0.1813 | 0.16898 | 0.16112 | 0.15217 | 0.13739 | 0.12776 | 0.12968 | 0.13241 | 0.12751 | 0.10986 | 0.10069 | 0.088278 | 0.19342 | 0.19002 | 0.18688 | 0.17421 | 0.16763 | 0.16007 | 0.14618 | 0.13744 | 0.1405 | 0.14364 | 0.13927 | 0.12351 | 0.11425 | 0.10044 | 0.19134 | 0.18701 | 0.18263 | 0.16851 | 0.16034 | 0.15101 | 0.13534 | 0.12619 | 0.12663 | 0.13103 | 0.12573 | 0.1071 | 0.097172 | 0.083466
|  | ABERCHALDER | LW |  |  |  | 0 | 0.19049 | 0.17908 | 0.1668 | 0.1542 | 0.14429 | 0.12889 | 0.10888 | 0.10041 | 0.10012 | 0.10317 | 0.098139 | 0.078031 | 0.052786 | 0.022946 | 0.19357 | 0.18123 | 0.16828 | 0.1554 | 0.14598 | 0.1309 | 0.11065 | 0.10334 | 0.10476 | 0.10874 | 0.10479 | 0.085241 | 0.056495 | 0.022669 | 0.19171 | 0.17855 | 0.16417 | 0.14973 | 0.13858 | 0.12168 | 0.099608 | 0.091813 | 0.090118 | 0.095254 | 0.090132 | 0.068296 | 0.03794 | 0.0023032
|  | ABERCHALDER | ST |  |  |  | 0 | 0.1915 | 0.18939 | 0.18162 | 0.1751 | 0.16997 | 0.16519 | 0.15973 | 0.15415 | 0.14745 | 0.14037 | 0.13361 | 0.10822 | 0.077581 | 0.052362 | 0.1945 | 0.19318 | 0.18533 | 0.17916 | 0.17481 | 0.17107 | 0.16687 | 0.16221 | 0.15634 | 0.15013 | 0.14445 | 0.11909 | 0.084361 | 0.053703 | 0.19267 | 0.19051 | 0.18139 | 0.17395 | 0.16835 | 0.16336 | 0.15793 | 0.15234 | 0.14565 | 0.13868 | 0.13225 | 0.10365 | 0.067564 | 0.037032
|  | ABERCHALDER | FS |  |  |  | 0 | 0.19252 | 0.19105 | 0.18801 | 0.18471 | 0.1813 | 0.1776 | 0.17279 | 0.16785 | 0.16136 | 0.15478 | 0.15031 | 0.13327 | 0.12609 | 0.11746 | 0.19491 | 0.1939 | 0.19077 | 0.18739 | 0.18391 | 0.18016 | 0.17509 | 0.1705 | 0.16418 | 0.15777 | 0.15409 | 0.14225 | 0.13879 | 0.12908 | 0.1936 | 0.1923 | 0.18889 | 0.18522 | 0.18145 | 0.17743 | 0.17212 | 0.1668 | 0.1598 | 0.1527 | 0.14836 | 0.13014 | 0.12572 | 0.11716
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0.315 | 3.5403 | 3.3307 | 3.0383 | 2.7229 | 2.3853 | 1.969 | 1.53 | 1.1456 | 0.70594 | 0.3579 | 0.15288 | -0.46299 | -0.65803 | -0.91286 | 4.5306 | 4.3737 | 4.1954 | 4.0046 | 3.804 | 3.5486 | 3.2843 | 3.0482 | 2.7691 | 2.5694 | 2.4525 | 2.0922 | 1.9818 | 1.7423 | 4.4619 | 4.2615 | 3.9973 | 3.7114 | 3.4043 | 3.0164 | 2.6162 | 2.2689 | 1.8708 | 1.5646 | 1.3844 | 0.81852 | 0.63286 | 0.39812
|  | ABERFELDY | CT |  |  |  | 0.315 | 3.5631 | 3.3715 | 3.0882 | 2.7601 | 2.3979 | 1.9739 | 1.53 | 1.1475 | 0.79359 | 0.50366 | 0.30515 | -0.33051 | -0.59343 | -0.84146 | 4.5508 | 4.4115 | 4.2397 | 4.0346 | 3.8103 | 3.5588 | 3.2908 | 3.0547 | 2.8321 | 2.6568 | 2.5305 | 2.1594 | 1.9818 | 1.7423 | 4.4821 | 4.299 | 4.0424 | 3.7427 | 3.4079 | 3.0231 | 2.6162 | 2.2724 | 1.9539 | 1.6937 | 1.5167 | 0.94547 | 0.7003 | 0.47408
|  | ABERFELDY | LW |  |  |  | 0.315 | 3.5403 | 3.3307 | 3.0383 | 2.7229 | 2.3853 | 1.969 | 1.5376 | 1.1456 | 0.70594 | 0.3579 | 0.15288 | -0.46299 | -0.65803 | -0.91286 | 4.5306 | 4.3737 | 4.1954 | 4.0046 | 3.804 | 3.5486 | 3.2843 | 3.0482 | 2.7691 | 2.5694 | 2.4525 | 2.0922 | 1.9834 | 1.824 | 4.4619 | 4.2615 | 3.9973 | 3.7114 | 3.4043 | 3.0164 | 2.6205 | 2.2689 | 1.8708 | 1.5646 | 1.3844 | 0.81852 | 0.63286 | 0.39812
|  | ABERFELDY | ST |  |  |  | 0.315 | 3.5854 | 3.4526 | 3.2853 | 3.1034 | 2.9221 | 2.6959 | 2.5142 | 2.2951 | 2.047 | 1.8463 | 1.7214 | 0.99063 | 0.66091 | 0.38445 | 4.5749 | 4.4727 | 4.3549 | 4.2181 | 4.0834 | 3.9201 | 3.792 | 3.637 | 3.4618 | 3.3311 | 3.2438 | 2.7287 | 2.4758 | 2.2333 | 4.5197 | 4.3876 | 4.2358 | 4.0648 | 3.8964 | 3.691 | 3.5299 | 3.3359 | 3.1171 | 2.9447 | 2.8296 | 2.1741 | 1.8622 | 1.5983
|  | ABERFELDY | FS |  |  |  | 0.315 | 3.6215 | 3.5449 | 3.443 | 3.3269 | 3.1955 | 3.0232 | 2.8834 | 2.7188 | 2.5145 | 2.3455 | 2.1882 | 1.3508 | 0.69666 | 0.28121 | 4.6143 | 4.5363 | 4.4494 | 4.3574 | 4.252 | 4.1174 | 4.0125 | 3.8999 | 3.7564 | 3.6434 | 3.5345 | 2.9476 | 2.4503 | 1.9943 | 4.5601 | 4.4786 | 4.3735 | 4.2657 | 4.1428 | 3.9867 | 3.8638 | 3.7206 | 3.5412 | 3.3942 | 3.2547 | 2.4991 | 1.9019 | 1.5137
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.375 | 3.2166 | 3.1371 | 3.0335 | 2.8996 | 2.7579 | 2.5959 | 2.4241 | 2.31 | 2.2134 | 2.0928 | 2.0099 | 1.6479 | 1.4286 | 1.1817 | 3.7029 | 3.6531 | 3.6033 | 3.5332 | 3.4617 | 3.3778 | 3.293 | 3.214 | 3.1468 | 3.0577 | 3.008 | 2.8052 | 2.714 | 2.5701 | 3.6781 | 3.604 | 3.5173 | 3.4017 | 3.2807 | 3.1407 | 2.9961 | 2.8879 | 2.7961 | 2.6742 | 2.601 | 2.2896 | 2.121 | 1.9176
|  | ABERFOYLE | CT |  |  |  | 0.375 | 3.2166 | 3.1371 | 3.0335 | 2.8996 | 2.7579 | 2.5959 | 2.4241 | 2.31 | 2.2134 | 2.1146 | 2.062 | 1.7436 | 1.5425 | 1.3243 | 3.7029 | 3.6531 | 3.6033 | 3.5332 | 3.4617 | 3.3778 | 3.293 | 3.214 | 3.1468 | 3.0738 | 3.0382 | 2.8326 | 2.7222 | 2.5701 | 3.6781 | 3.604 | 3.5173 | 3.4017 | 3.2807 | 3.1407 | 2.9961 | 2.8879 | 2.7961 | 2.6996 | 2.6517 | 2.3686 | 2.2128 | 2.0383
|  | ABERFOYLE | LW |  |  |  | 0.375 | 3.2276 | 3.1574 | 3.066 | 2.9434 | 2.8235 | 2.6545 | 2.4908 | 2.3714 | 2.2239 | 2.0928 | 2.0099 | 1.6479 | 1.4286 | 1.1817 | 3.7083 | 3.6648 | 3.6233 | 3.5587 | 3.5036 | 3.4103 | 3.328 | 3.2505 | 3.1482 | 3.0577 | 3.008 | 2.8052 | 2.714 | 2.5919 | 3.6873 | 3.6218 | 3.5465 | 3.4394 | 3.3404 | 3.1904 | 3.0513 | 2.9406 | 2.7992 | 2.6742 | 2.601 | 2.2896 | 2.121 | 1.9176
|  | ABERFOYLE | ST |  |  |  | 0.375 | 3.2426 | 3.1956 | 3.1334 | 3.0689 | 3.0049 | 2.9252 | 2.8505 | 2.7678 | 2.6683 | 2.5894 | 2.484 | 2.0562 | 1.8643 | 1.7573 | 3.7199 | 3.695 | 3.6625 | 3.6295 | 3.5988 | 3.5538 | 3.5134 | 3.462 | 3.3972 | 3.3529 | 3.2839 | 2.9967 | 2.8719 | 2.7674 | 3.7027 | 3.6617 | 3.609 | 3.5549 | 3.5031 | 3.4337 | 3.3703 | 3.2954 | 3.2032 | 3.1364 | 3.0391 | 2.6533 | 2.4994 | 2.4226
|  | ABERFOYLE | FS |  |  |  | 0.375 | 3.2641 | 3.2368 | 3.2081 | 3.1784 | 3.1401 | 3.1095 | 3.0662 | 3.0021 | 2.9388 | 2.8651 | 2.7866 | 2.3748 | 1.9955 | 1.7963 | 3.726 | 3.7119 | 3.6931 | 3.6744 | 3.6484 | 3.631 | 3.6004 | 3.5596 | 3.5211 | 3.4726 | 3.42 | 3.1433 | 2.8792 | 2.6407 | 3.7185 | 3.6955 | 3.6699 | 3.644 | 3.6091 | 3.5842 | 3.5442 | 3.4864 | 3.431 | 3.3635 | 3.2911 | 2.9194 | 2.5896 | 2.4287
| KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 0.918 | 0.98313 | 0.90999 | 0.83385 | 0.77187 | 0.66795 | 0.48332 | 0.26638 | 0.11 | -0.047508 | -0.46916 | -0.60777 | -1.0024 | -1.1981 | -1.4003 | 1.4632 | 1.4029 | 1.3328 | 1.2382 | 1.1565 | 1.0416 | 0.89811 | 0.79333 | 0.68043 | 0.28 | 0.17668 | -0.097824 | -0.30199 | -0.44649 | 1.1692 | 1.0977 | 1.0233 | 0.89727 | 0.77405 | 0.60983 | 0.41092 | 0.26306 | 0.10715 | -0.32422 | -0.46409 | -0.84233 | -1.0172 | -1.2154
|  | ABERLOUR | CT |  |  |  | 0.918 | 0.98759 | 0.93604 | 0.87876 | 0.7998 | 0.66795 | 0.49324 | 0.27693 | 0.11719 | 0.01044 | -0.36926 | -0.47148 | -0.83128 | -1.0459 | -1.2254 | 1.4651 | 1.4301 | 1.378 | 1.261 | 1.1811 | 1.0872 | 0.95638 | 0.84783 | 0.77796 | 0.40993 | 0.33608 | 0.13848 | 0.070104 | 0.0061488 | 1.1726 | 1.1269 | 1.0692 | 0.90578 | 0.78024 | 0.63473 | 0.44358 | 0.29205 | 0.19222 | -0.19514 | -0.29479 | -0.5921 | -0.72913 | -0.85741
|  | ABERLOUR | LW |  |  |  | 0.918 | 0.98313 | 0.90999 | 0.83385 | 0.77187 | 0.66913 | 0.48332 | 0.26638 | 0.11 | -0.047508 | -0.46916 | -0.60777 | -1.0024 | -1.1981 | -1.4003 | 1.4632 | 1.4029 | 1.3328 | 1.2382 | 1.1565 | 1.0416 | 0.89811 | 0.79333 | 0.68043 | 0.28 | 0.17668 | -0.097824 | -0.22961 | -0.35112 | 1.1692 | 1.0977 | 1.0233 | 0.89727 | 0.77405 | 0.60983 | 0.41092 | 0.26306 | 0.10715 | -0.32422 | -0.46409 | -0.84233 | -1.0172 | -1.1692
|  | ABERLOUR | ST |  |  |  | 0.918 | 0.99772 | 0.96233 | 0.90803 | 0.87362 | 0.84332 | 0.8126 | 0.77163 | 0.68066 | 0.56443 | 0.17708 | 0.042441 | -0.66971 | -1.0312 | -1.2629 | 1.4731 | 1.4507 | 1.408 | 1.3787 | 1.3294 | 1.2765 | 1.2135 | 1.1469 | 1.0554 | 0.67267 | 0.56504 | -0.032425 | -0.30199 | -0.44649 | 1.1825 | 1.1526 | 1.1015 | 1.0672 | 1.0152 | 0.93977 | 0.85178 | 0.76229 | 0.64197 | 0.23914 | 0.098172 | -0.66502 | -1.0171 | -1.2154
|  | ABERLOUR | FS |  |  |  | 0.918 | 1.0053 | 0.97931 | 0.94549 | 0.92035 | 0.90039 | 0.87422 | 0.84162 | 0.80823 | 0.76951 | 0.58732 | 0.52938 | -0.096989 | -0.69146 | -1.0586 | 1.4772 | 1.4614 | 1.4379 | 1.4176 | 1.4001 | 1.3775 | 1.3375 | 1.2887 | 1.2286 | 1.0158 | 0.93821 | 0.44364 | 0.018083 | -0.23795 | 1.1886 | 1.1672 | 1.1376 | 1.1138 | 1.0936 | 1.0677 | 1.0352 | 0.98368 | 0.90277 | 0.67242 | 0.57115 | -0.064116 | -0.6431 | -0.99839
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0.109 | 1.3051 | 1.2431 | 1.1647 | 1.0591 | 0.95431 | 0.83272 | 0.7036 | 0.63825 | 0.55829 | 0.48848 | 0.45696 | 0.28934 | 0.17872 | 0.067118 | 1.7947 | 1.7594 | 1.7174 | 1.6681 | 1.6171 | 1.5424 | 1.4717 | 1.4216 | 1.3557 | 1.2986 | 1.2777 | 1.1634 | 1.1029 | 0.99095 | 1.5966 | 1.5522 | 1.4893 | 1.4101 | 1.3327 | 1.239 | 1.1258 | 1.0497 | 0.95381 | 0.87112 | 0.83947 | 0.67121 | 0.578 | 0.47007
|  | ABERNETHY | CT |  |  |  | 0.109 | 1.3051 | 1.2431 | 1.1647 | 1.0591 | 0.95431 | 0.83272 | 0.7036 | 0.63825 | 0.58632 | 0.53658 | 0.49625 | 0.36952 | 0.28547 | 0.19721 | 1.7947 | 1.7612 | 1.7253 | 1.6682 | 1.618 | 1.5567 | 1.4909 | 1.44 | 1.3977 | 1.3524 | 1.3115 | 1.2102 | 1.1347 | 1.0173 | 1.5966 | 1.5522 | 1.4932 | 1.4101 | 1.3327 | 1.244 | 1.1433 | 1.0699 | 1.0106 | 0.94915 | 0.89575 | 0.77582 | 0.70968 | 0.63192
|  | ABERNETHY | LW |  |  |  | 0.109 | 1.3164 | 1.2518 | 1.169 | 1.0727 | 0.96901 | 0.83774 | 0.70895 | 0.63937 | 0.55829 | 0.48848 | 0.45696 | 0.28934 | 0.17872 | 0.067118 | 1.7998 | 1.7594 | 1.7174 | 1.6681 | 1.6171 | 1.5424 | 1.4717 | 1.4216 | 1.3557 | 1.2986 | 1.2777 | 1.1634 | 1.1029 | 1.0271 | 1.6044 | 1.5546 | 1.4893 | 1.4154 | 1.3377 | 1.239 | 1.1258 | 1.0497 | 0.95381 | 0.87112 | 0.83947 | 0.67121 | 0.578 | 0.47007
|  | ABERNETHY | ST |  |  |  | 0.109 | 1.3244 | 1.2825 | 1.2252 | 1.1618 | 1.1072 | 1.043 | 0.98388 | 0.92399 | 0.85655 | 0.80536 | 0.742 | 0.47733 | 0.35246 | 0.2812 | 1.8051 | 1.785 | 1.7555 | 1.7217 | 1.6956 | 1.6621 | 1.6325 | 1.5978 | 1.5522 | 1.5214 | 1.4796 | 1.2642 | 1.1438 | 1.0275 | 1.6109 | 1.5812 | 1.5358 | 1.488 | 1.445 | 1.397 | 1.3509 | 1.3055 | 1.254 | 1.2096 | 1.1528 | 0.87371 | 0.75632 | 0.69242
|  | ABERNETHY | FS |  |  |  | 0.109 | 1.3532 | 1.3267 | 1.3061 | 1.2865 | 1.2622 | 1.2451 | 1.218 | 1.1771 | 1.1247 | 1.0717 | 1.0343 | 0.77304 | 0.52229 | 0.41846 | 1.8162 | 1.8022 | 1.7881 | 1.7745 | 1.757 | 1.7452 | 1.722 | 1.6968 | 1.6595 | 1.6216 | 1.5988 | 1.4024 | 1.1928 | 0.99095 | 1.6312 | 1.6124 | 1.5965 | 1.5806 | 1.562 | 1.5465 | 1.525 | 1.4929 | 1.453 | 1.4125 | 1.381 | 1.1346 | 0.91614 | 0.83001
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 1.709 | 5.8498 | 5.6025 | 5.2342 | 4.7972 | 4.2911 | 3.7223 | 3.1041 | 2.738 | 2.3893 | 2.1769 | 2.1729 | 1.5504 | 1.1173 | 0.70323 | 8.1443 | 8.016 | 7.8378 | 7.6285 | 7.3813 | 7.1085 | 6.7937 | 6.5494 | 6.3031 | 6.1449 | 6.1961 | 5.8114 | 5.5429 | 5.0786 | 7.2453 | 7.0377 | 6.7415 | 6.3893 | 5.9931 | 5.554 | 5.045 | 4.7139 | 4.3977 | 4.1936 | 4.0866 | 3.4932 | 3.1768 | 2.9314
|  | ABOYNE | CT |  |  |  | 1.709 | 5.8498 | 5.6025 | 5.2342 | 4.7972 | 4.2911 | 3.7223 | 3.1041 | 2.738 | 2.3893 | 2.1769 | 2.2166 | 1.6361 | 1.2544 | 0.862 | 8.1443 | 8.016 | 7.8378 | 7.6285 | 7.3813 | 7.1085 | 6.7937 | 6.5494 | 6.3031 | 6.1449 | 6.2098 | 5.8114 | 5.5429 | 5.168 | 7.2453 | 7.0377 | 6.7415 | 6.3893 | 5.9931 | 5.554 | 5.045 | 4.7139 | 4.3977 | 4.1936 | 4.1889 | 3.6908 | 3.4209 | 3.1695
|  | ABOYNE | LW |  |  |  | 1.709 | 5.8928 | 5.667 | 5.313 | 4.8947 | 4.4287 | 3.8683 | 3.285 | 2.8998 | 2.4472 | 2.3692 | 2.1729 | 1.5504 | 1.1173 | 0.70323 | 8.1639 | 8.0447 | 7.8815 | 7.6868 | 7.4706 | 7.1931 | 6.8917 | 6.6438 | 6.3223 | 6.3285 | 6.1961 | 5.8441 | 5.6643 | 5.4743 | 7.2787 | 7.0913 | 6.8186 | 6.502 | 6.1468 | 5.7025 | 5.2139 | 4.865 | 4.4292 | 4.3036 | 4.0866 | 3.4932 | 3.1768 | 2.9314
|  | ABOYNE | ST |  |  |  | 1.709 | 5.9237 | 5.7381 | 5.4972 | 5.2442 | 4.9785 | 4.6908 | 4.4011 | 4.1007 | 3.727 | 3.4759 | 3.1956 | 2.3177 | 1.8722 | 1.6437 | 8.1851 | 8.0972 | 7.9821 | 7.8597 | 7.7264 | 7.5764 | 7.4142 | 7.2281 | 6.976 | 6.8257 | 6.6495 | 5.9188 | 5.5886 | 5.4445 | 7.3118 | 7.171 | 6.9776 | 6.7746 | 6.5547 | 6.3136 | 6.0582 | 5.7869 | 5.4285 | 5.1579 | 4.8612 | 3.7273 | 3.2504 | 3.0473
|  | ABOYNE | FS |  |  |  | 1.709 | 6.0485 | 5.9339 | 5.861 | 5.7716 | 5.6716 | 5.5708 | 5.4496 | 5.2366 | 4.9623 | 4.7434 | 4.5494 | 3.399 | 2.4433 | 1.8558 | 8.2322 | 8.1728 | 8.1273 | 8.0695 | 8.002 | 7.9328 | 7.837 | 7.7086 | 7.5225 | 7.3839 | 7.2623 | 6.4597 | 5.7994 | 5.0786 | 7.4005 | 7.3133 | 7.2458 | 7.1674 | 7.0774 | 6.9816 | 6.8621 | 6.6813 | 6.4323 | 6.2299 | 6.0305 | 4.8398 | 3.8309 | 3.222
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | YES | 0.057 | 0.048038 | 0.035233 | 0.0024618 | -0.033836 | -0.070111 | -0.11401 | -0.16732 | -0.18585 | -0.22608 | -0.25186 | -0.2843 | -0.37699 | -0.42362 | -0.49656 | 0.13145 | 0.11873 | 0.09459 | 0.067152 | 0.041594 | 0.0085432 | -0.037557 | -0.054911 | -0.085501 | -0.10517 | -0.12868 | -0.19846 | -0.2378 | -0.29896 | 0.11132 | 0.094509 | 0.060564 | 0.018421 | -0.023414 | -0.075244 | -0.14224 | -0.16727 | -0.20804 | -0.23469 | -0.26551 | -0.35883 | -0.41187 | -0.48912
|  | ACHILTIBUIE | CT |  |  |  | 0.057 | 0.052439 | 0.037694 | 0.010788 | -0.028321 | -0.065509 | -0.10335 | -0.15269 | -0.17036 | -0.19848 | -0.22846 | -0.24239 | -0.32534 | -0.35694 | -0.40328 | 0.13275 | 0.12453 | 0.10835 | 0.079608 | 0.053313 | 0.029638 | -0.010422 | -0.02935 | -0.049753 | -0.071987 | -0.084955 | -0.14922 | -0.17517 | -0.21816 | 0.11132 | 0.098336 | 0.070772 | 0.026326 | -0.0187 | -0.060619 | -0.12283 | -0.14844 | -0.17492 | -0.20272 | -0.21805 | -0.2998 | -0.33349 | -0.38119
|  | ACHILTIBUIE | LW |  |  |  | 0.057 | 0.055416 | 0.035233 | 0.0024618 | -0.033836 | -0.070111 | -0.11401 | -0.16732 | -0.18585 | -0.22608 | -0.25186 | -0.2843 | -0.37699 | -0.42362 | -0.49656 | 0.13444 | 0.11873 | 0.09459 | 0.067152 | 0.041594 | 0.0085432 | -0.037557 | -0.054911 | -0.085501 | -0.10517 | -0.12868 | -0.19846 | -0.2378 | -0.29896 | 0.11406 | 0.094509 | 0.060564 | 0.018421 | -0.023414 | -0.075244 | -0.14224 | -0.16727 | -0.20804 | -0.23469 | -0.26551 | -0.35883 | -0.41187 | -0.48912
|  | ACHILTIBUIE | ST |  |  |  | 0.057 | 0.048038 | 0.046469 | 0.027044 | 0.0084778 | -0.011605 | -0.030194 | -0.050476 | -0.068106 | -0.090086 | -0.11287 | -0.13154 | -0.25344 | -0.31401 | -0.34677 | 0.13145 | 0.13003 | 0.11758 | 0.10619 | 0.091862 | 0.080162 | 0.065889 | 0.053712 | 0.034323 | 0.01341 | 0.00093706 | -0.10923 | -0.16862 | -0.21237 | 0.12071 | 0.10672 | 0.090372 | 0.072555 | 0.0491 | 0.028864 | 0.0052529 | -0.014686 | -0.043374 | -0.073239 | -0.092833 | -0.23361 | -0.30183 | -0.34217
|  | ACHILTIBUIE | FS |  |  |  | 0.057 | 0.057384 | 0.059576 | 0.05423 | 0.04694 | 0.039898 | 0.030815 | 0.022019 | 0.0069152 | -0.011487 | -0.027695 | -0.044202 | -0.14 | -0.2437 | -0.28866 | 0.13635 | 0.13702 | 0.13354 | 0.12698 | 0.12089 | 0.11158 | 0.10315 | 0.090817 | 0.073274 | 0.060225 | 0.045107 | -0.033897 | -0.10928 | -0.16099 | 0.12844 | 0.1191 | 0.11541 | 0.10638 | 0.098523 | 0.085251 | 0.074324 | 0.056969 | 0.032838 | 0.015426 | -0.006345 | -0.11582 | -0.21877 | -0.2653
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0 | 0.48033 | 0.45837 | 0.44721 | 0.43648 | 0.42352 | 0.4047 | 0.37766 | 0.37034 | 0.35938 | 0.34823 | 0.34408 | 0.31254 | 0.28416 | 0.24922 | 0.4855 | 0.46361 | 0.45561 | 0.44651 | 0.43701 | 0.42154 | 0.39719 | 0.39167 | 0.38226 | 0.37238 | 0.36935 | 0.33986 | 0.31026 | 0.27368 | 0.46784 | 0.44467 | 0.42824 | 0.41725 | 0.40481 | 0.38545 | 0.35573 | 0.3488 | 0.33726 | 0.32498 | 0.32185 | 0.28802 | 0.25593 | 0.21641
|  | AIGAS | CT |  |  |  | 0 | 0.48033 | 0.46498 | 0.46059 | 0.44973 | 0.43734 | 0.42457 | 0.40323 | 0.39637 | 0.39065 | 0.38271 | 0.37553 | 0.35915 | 0.34725 | 0.33055 | 0.48603 | 0.47322 | 0.47394 | 0.46558 | 0.45813 | 0.45117 | 0.43359 | 0.4277 | 0.4224 | 0.41437 | 0.40687 | 0.39156 | 0.38176 | 0.36657 | 0.46808 | 0.45383 | 0.44569 | 0.43532 | 0.424 | 0.41331 | 0.39025 | 0.38302 | 0.37704 | 0.36753 | 0.35886 | 0.34216 | 0.33052 | 0.31365
|  | AIGAS | LW |  |  |  | 0 | 0.4806 | 0.45837 | 0.44721 | 0.43648 | 0.42352 | 0.4047 | 0.37766 | 0.37034 | 0.35938 | 0.34823 | 0.34408 | 0.31254 | 0.28416 | 0.24922 | 0.4855 | 0.46361 | 0.45561 | 0.44651 | 0.43701 | 0.42154 | 0.39719 | 0.39167 | 0.38226 | 0.37238 | 0.36935 | 0.33986 | 0.31026 | 0.27368 | 0.46784 | 0.44467 | 0.42824 | 0.41725 | 0.40481 | 0.38545 | 0.35573 | 0.3488 | 0.33726 | 0.32498 | 0.32185 | 0.28802 | 0.25593 | 0.21641
|  | AIGAS | ST |  |  |  | 0 | 0.48503 | 0.47852 | 0.46536 | 0.45222 | 0.45278 | 0.4511 | 0.44266 | 0.43717 | 0.43136 | 0.4218 | 0.4167 | 0.36757 | 0.33375 | 0.30795 | 0.48993 | 0.48558 | 0.47387 | 0.46257 | 0.46381 | 0.46493 | 0.45799 | 0.45428 | 0.45032 | 0.44228 | 0.43938 | 0.39226 | 0.3559 | 0.3259 | 0.47245 | 0.46706 | 0.45388 | 0.44108 | 0.43558 | 0.43635 | 0.42685 | 0.42173 | 0.41636 | 0.40576 | 0.40164 | 0.34783 | 0.30922 | 0.27882
|  | AIGAS | FS |  |  |  | 0 | 0.48744 | 0.4826 | 0.47633 | 0.46895 | 0.46119 | 0.46292 | 0.46452 | 0.45667 | 0.4507 | 0.44545 | 0.43907 | 0.41124 | 0.38709 | 0.37438 | 0.49058 | 0.48704 | 0.48079 | 0.47343 | 0.4657 | 0.46996 | 0.47049 | 0.46378 | 0.45855 | 0.45438 | 0.44941 | 0.42972 | 0.41395 | 0.40348 | 0.47387 | 0.46969 | 0.46303 | 0.45523 | 0.44703 | 0.44557 | 0.44724 | 0.43857 | 0.43232 | 0.42735 | 0.42045 | 0.39364 | 0.37136 | 0.35994
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0.895 | 4.0143 | 3.9417 | 3.8498 | 3.6997 | 3.5331 | 3.3891 | 3.2115 | 3.0546 | 2.8871 | 2.7591 | 2.6128 | 2.1951 | 2.0067 | 1.7899 | 4.982 | 4.9326 | 4.8748 | 4.7626 | 4.655 | 4.5645 | 4.4637 | 4.3771 | 4.2695 | 4.181 | 4.0883 | 3.8319 | 3.7249 | 3.6224 | 4.3332 | 4.2757 | 4.2116 | 4.0943 | 3.9731 | 3.8733 | 3.7265 | 3.5867 | 3.4295 | 3.2996 | 3.1682 | 2.7737 | 2.5889 | 2.4143
|  | AIRD | CT |  |  |  | 0.895 | 4.0245 | 3.9589 | 3.8731 | 3.7106 | 3.5331 | 3.4026 | 3.2115 | 3.0546 | 2.9207 | 2.8245 | 2.7111 | 2.2835 | 2.0576 | 1.9016 | 4.9992 | 4.9644 | 4.9186 | 4.7887 | 4.6667 | 4.5953 | 4.4899 | 4.4068 | 4.337 | 4.28 | 4.2212 | 4.0341 | 3.9181 | 3.7646 | 4.3502 | 4.3056 | 4.2474 | 4.102 | 3.9731 | 3.8828 | 3.7265 | 3.5937 | 3.4809 | 3.3899 | 3.3011 | 2.9405 | 2.7356 | 2.6145
|  | AIRD | LW |  |  |  | 0.895 | 4.0143 | 3.9417 | 3.8498 | 3.6997 | 3.5474 | 3.3891 | 3.2322 | 3.0713 | 2.8871 | 2.7591 | 2.6128 | 2.1951 | 2.0067 | 1.7899 | 4.982 | 4.9326 | 4.8748 | 4.7626 | 4.655 | 4.5645 | 4.4637 | 4.3771 | 4.2695 | 4.181 | 4.0883 | 3.8319 | 3.7249 | 3.6224 | 4.3332 | 4.2757 | 4.2116 | 4.0943 | 3.9805 | 3.8733 | 3.7288 | 3.5867 | 3.4295 | 3.2996 | 3.1682 | 2.7737 | 2.5889 | 2.4143
|  | AIRD | ST |  |  |  | 0.895 | 4.0497 | 4.0233 | 3.9809 | 3.8914 | 3.8109 | 3.7546 | 3.704 | 3.6452 | 3.5921 | 3.518 | 3.4449 | 2.9326 | 2.5945 | 2.3387 | 5.0112 | 4.9967 | 4.9678 | 4.8911 | 4.8107 | 4.7718 | 4.7311 | 4.6874 | 4.6363 | 4.5751 | 4.5091 | 4.0907 | 3.88 | 3.7618 | 4.3654 | 4.3482 | 4.3155 | 4.2378 | 4.1584 | 4.114 | 4.0674 | 4.0162 | 3.9534 | 3.8802 | 3.8008 | 3.3006 | 3.0549 | 2.8231
|  | AIRD | FS |  |  |  | 0.895 | 4.0753 | 4.0508 | 4.022 | 3.9605 | 3.8887 | 3.8549 | 3.8079 | 3.7583 | 3.6884 | 3.6137 | 3.5603 | 3.1221 | 2.7268 | 2.4042 | 5.0369 | 5.0236 | 5.008 | 4.9522 | 4.8894 | 4.8595 | 4.8257 | 4.7925 | 4.7467 | 4.6955 | 4.651 | 4.3519 | 4.0682 | 3.8453 | 4.3912 | 4.376 | 4.3577 | 4.3018 | 4.2385 | 4.206 | 4.1686 | 4.1305 | 4.0781 | 4.0199 | 3.966 | 3.6034 | 3.2294 | 2.8721
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.30966 | 0.30621 | 0.3028 | 0.29857 | 0.29325 | 0.28793 | 0.28028 | 0.27257 | 0.27374 | 0.27858 | 0.27404 | 0.27061 | 0.26887 | 0.26558 | 0.30321 | 0.30006 | 0.29719 | 0.29403 | 0.28983 | 0.2857 | 0.27948 | 0.27294 | 0.27946 | 0.27989 | 0.27471 | 0.27814 | 0.27744 | 0.27537 | 0.30611 | 0.3026 | 0.29925 | 0.29552 | 0.29065 | 0.28561 | 0.27835 | 0.27112 | 0.27041 | 0.276 | 0.27202 | 0.26835 | 0.26681 | 0.26369
|  | AIRIGH-NA-BRODAIG | CT |  |  |  | 0 | 0.30969 | 0.30621 | 0.3028 | 0.29857 | 0.29325 | 0.28793 | 0.28037 | 0.28053 | 0.27589 | 0.28092 | 0.27746 | 0.27261 | 0.27072 | 0.26811 | 0.30321 | 0.30006 | 0.29719 | 0.29403 | 0.28983 | 0.2857 | 0.27948 | 0.28475 | 0.28122 | 0.28542 | 0.28273 | 0.27961 | 0.27867 | 0.27699 | 0.30611 | 0.3026 | 0.29925 | 0.29552 | 0.29065 | 0.28561 | 0.27835 | 0.27778 | 0.27276 | 0.27833 | 0.27491 | 0.27031 | 0.26862 | 0.26618
|  | AIRIGH-NA-BRODAIG | LW |  |  |  | 0 | 0.30966 | 0.30633 | 0.30351 | 0.29916 | 0.29504 | 0.28818 | 0.28028 | 0.27257 | 0.27374 | 0.27858 | 0.27453 | 0.27061 | 0.26887 | 0.26558 | 0.30328 | 0.30035 | 0.29782 | 0.2944 | 0.2914 | 0.28595 | 0.2796 | 0.27294 | 0.27946 | 0.28357 | 0.28047 | 0.27814 | 0.27744 | 0.27537 | 0.30627 | 0.30301 | 0.3 | 0.29601 | 0.29238 | 0.28587 | 0.27837 | 0.27112 | 0.27041 | 0.276 | 0.27202 | 0.26835 | 0.26681 | 0.26369
|  | AIRIGH-NA-BRODAIG | ST |  |  |  | 0 | 0.31076 | 0.30948 | 0.30759 | 0.30532 | 0.30265 | 0.29944 | 0.29575 | 0.29155 | 0.28612 | 0.28036 | 0.27404 | 0.27511 | 0.27541 | 0.27472 | 0.3042 | 0.30302 | 0.30153 | 0.29969 | 0.29766 | 0.29525 | 0.2924 | 0.28904 | 0.2846 | 0.27989 | 0.27471 | 0.28066 | 0.28133 | 0.28088 | 0.30721 | 0.30578 | 0.30397 | 0.3018 | 0.29942 | 0.29661 | 0.29313 | 0.28917 | 0.28407 | 0.27867 | 0.27276 | 0.27256 | 0.27301 | 0.2724
|  | AIRIGH-NA-BRODAIG | FS |  |  |  | 0 | 0.31108 | 0.31007 | 0.30894 | 0.30753 | 0.30601 | 0.30421 | 0.30209 | 0.29942 | 0.29596 | 0.29222 | 0.28806 | 0.28448 | 0.27597 | 0.27269 | 0.30451 | 0.30359 | 0.30257 | 0.30132 | 0.29997 | 0.29838 | 0.29652 | 0.29415 | 0.2911 | 0.28796 | 0.28451 | 0.28711 | 0.28162 | 0.27929 | 0.30764 | 0.30664 | 0.3055 | 0.30411 | 0.30263 | 0.30089 | 0.29887 | 0.29621 | 0.29284 | 0.28938 | 0.2856 | 0.28159 | 0.27356 | 0.27048
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 3.16 | -0.6628 | -0.89879 | -1.2581 | -1.6486 | -2.088 | -2.616 | -3.07 | -3.4948 | -3.8522 | -4.1992 | -4.4743 | -5.2217 | -5.5833 | -5.9063 | 0.26927 | 0.11525 | -0.083897 | -0.28927 | -0.51015 | -0.78614 | -1.0276 | -1.2563 | -1.4556 | -1.6577 | -1.8244 | -2.2428 | -2.4816 | -2.8179 | -0.13007 | -0.3403 | -0.65334 | -0.98864 | -1.3624 | -1.8231 | -2.2307 | -2.6136 | -2.9412 | -3.2649 | -3.528 | -4.2272 | -4.4865 | -4.7795
|  | ALYTH | CT |  |  |  | 3.16 | -0.46157 | -0.69418 | -1.0079 | -1.3904 | -1.8614 | -2.4452 | -2.9723 | -3.4258 | -3.7618 | -4.041 | -4.274 | -5.164 | -5.5833 | -5.9063 | 0.44161 | 0.29012 | 0.12594 | -0.084293 | -0.3398 | -0.65577 | -0.95158 | -1.2147 | -1.4017 | -1.553 | -1.7006 | -2.2162 | -2.4816 | -2.8179 | 0.052261 | -0.15356 | -0.42148 | -0.75646 | -1.1642 | -1.6665 | -2.1353 | -2.5471 | -2.851 | -3.0983 | -3.3199 | -4.1274 | -4.4865 | -4.7795
|  | ALYTH | LW |  |  |  | 3.16 | -0.6628 | -0.89879 | -1.2581 | -1.6486 | -2.088 | -2.616 | -3.07 | -3.4948 | -3.8522 | -4.1992 | -4.4743 | -5.2217 | -5.5018 | -5.7953 | 0.26927 | 0.11525 | -0.083897 | -0.28927 | -0.51015 | -0.78614 | -1.0276 | -1.2563 | -1.4556 | -1.6577 | -1.8244 | -2.2428 | -2.3951 | -2.5947 | -0.13007 | -0.3403 | -0.65334 | -0.98864 | -1.3624 | -1.8231 | -2.2307 | -2.6136 | -2.9412 | -3.2649 | -3.528 | -4.2272 | -4.4818 | -4.7731
|  | ALYTH | ST |  |  |  | 3.16 | -0.41636 | -0.60347 | -0.79127 | -0.97462 | -1.2195 | -1.5062 | -1.7424 | -1.9406 | -2.0859 | -2.2506 | -2.3969 | -3.18 | -3.6799 | -4.1903 | 0.46935 | 0.35055 | 0.23503 | 0.12446 | -0.03246 | -0.21577 | -0.37821 | -0.51466 | -0.61414 | -0.73175 | -0.84303 | -1.4448 | -1.8112 | -2.2104 | 0.095944 | -0.063028 | -0.22367 | -0.37849 | -0.58729 | -0.82748 | -1.0359 | -1.2141 | -1.3489 | -1.505 | -1.65 | -2.4232 | -2.8834 | -3.3289
|  | ALYTH | FS |  |  |  | 3.16 | -0.16019 | -0.29978 | -0.43362 | -0.58552 | -0.75943 | -0.95346 | -1.1135 | -1.2954 | -1.4664 | -1.6625 | -1.8491 | -2.8502 | -3.623 | -4.1813 | 0.67379 | 0.58061 | 0.49363 | 0.39085 | 0.27413 | 0.14124 | 0.026934 | -0.0933 | -0.20922 | -0.34621 | -0.4817 | -1.2168 | -1.8492 | -2.4769 | 0.32653 | 0.20813 | 0.094659 | -0.035701 | -0.18169 | -0.34725 | -0.48519 | -0.64408 | -0.79723 | -0.97355 | -1.1419 | -2.0734 | -2.7964 | -3.2885
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 0.096 | 5.8757 | 5.7772 | 5.6218 | 5.4296 | 5.2374 | 5.0219 | 4.7622 | 4.6821 | 4.6146 | 4.548 | 4.4505 | 4.1886 | 4.0227 | 3.8434 | 6.3069 | 6.2715 | 6.2311 | 6.1682 | 6.118 | 6.0612 | 5.9732 | 5.9301 | 5.8778 | 5.816 | 5.758 | 5.6107 | 5.5393 | 5.4386 | 6.2078 | 6.1581 | 6.089 | 5.9897 | 5.846 | 5.6838 | 5.4876 | 5.4255 | 5.3553 | 5.2409 | 5.136 | 4.886 | 4.7337 | 4.5579
|  | ANNAT | CT |  |  |  | 0.096 | 5.8757 | 5.7772 | 5.6218 | 5.4296 | 5.2374 | 5.0219 | 4.7622 | 4.6821 | 4.6146 | 4.5518 | 4.5049 | 4.3143 | 4.1777 | 4.0291 | 6.3069 | 6.2743 | 6.2335 | 6.1682 | 6.118 | 6.0612 | 5.9732 | 5.9301 | 5.8918 | 5.8543 | 5.8201 | 5.7183 | 5.6379 | 5.4785 | 6.2078 | 6.1581 | 6.089 | 5.9897 | 5.846 | 5.6838 | 5.4876 | 5.4255 | 5.3553 | 5.277 | 5.2134 | 5.0244 | 4.9049 | 4.7668
|  | ANNAT | LW |  |  |  | 0.096 | 5.8939 | 5.8004 | 5.6543 | 5.4815 | 5.3157 | 5.1032 | 4.8613 | 4.77 | 4.6516 | 4.548 | 4.4505 | 4.1886 | 4.0227 | 3.8434 | 6.3091 | 6.2715 | 6.2311 | 6.1815 | 6.1398 | 6.0739 | 5.9926 | 5.946 | 5.8778 | 5.816 | 5.758 | 5.6107 | 5.5393 | 5.4486 | 6.2134 | 6.1612 | 6.0964 | 6.0184 | 5.9055 | 5.7433 | 5.5587 | 5.4874 | 5.3593 | 5.2409 | 5.136 | 4.886 | 4.7337 | 4.5579
|  | ANNAT | ST |  |  |  | 0.096 | 5.9055 | 5.8402 | 5.7483 | 5.6622 | 5.5751 | 5.4784 | 5.3883 | 5.2969 | 5.199 | 5.0939 | 5.0034 | 4.5532 | 4.3978 | 4.3146 | 6.3171 | 6.3023 | 6.2742 | 6.2489 | 6.2225 | 6.1909 | 6.1594 | 6.1211 | 6.0747 | 6.0232 | 5.9762 | 5.6788 | 5.5676 | 5.513 | 6.224 | 6.1982 | 6.1538 | 6.1125 | 6.0693 | 6.0194 | 5.9469 | 5.8719 | 5.7883 | 5.6991 | 5.6201 | 5.1995 | 5.0346 | 4.9474
|  | ANNAT | FS |  |  |  | 0.096 | 5.9524 | 5.912 | 5.8813 | 5.8546 | 5.8207 | 5.7908 | 5.7512 | 5.6766 | 5.608 | 5.5313 | 5.4503 | 5.0335 | 4.5622 | 4.3764 | 6.3244 | 6.3147 | 6.3009 | 6.2884 | 6.2719 | 6.2558 | 6.2339 | 6.2066 | 6.1779 | 6.1453 | 6.1113 | 5.9103 | 5.7008 | 5.4386 | 6.239 | 6.2224 | 6.203 | 6.1851 | 6.1622 | 6.1399 | 6.1108 | 6.0704 | 6.0287 | 5.9822 | 5.9331 | 5.6231 | 5.2352 | 5.0577
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.10589 | 0.10502 | 0.10423 | 0.10341 | 0.10227 | 0.10115 | 0.099415 | 0.097446 | 0.095437 | 0.093557 | 0.09191 | 0.089144 | 0.088593 | 0.088103 | 0.1025 | 0.1017 | 0.101 | 0.10028 | 0.099261 | 0.098278 | 0.096695 | 0.094789 | 0.092819 | 0.090985 | 0.089376 | 0.087064 | 0.086685 | 0.086559 | 0.020966 | 0.02014 | 0.019423 | 0.018673 | 0.017623 | 0.016606 | 0.014985 | 0.013063 | 0.01108 | 0.0092324 | 0.0076119 | 0.00529 | 0.0048793 | 0.0047269
|  | ARDCHYLE | CT |  |  |  | 0 | 0.10589 | 0.10502 | 0.10423 | 0.10341 | 0.10227 | 0.10115 | 0.099415 | 0.097446 | 0.095986 | 0.09425 | 0.092552 | 0.089144 | 0.088593 | 0.088103 | 0.1025 | 0.1017 | 0.101 | 0.10028 | 0.099261 | 0.098278 | 0.096695 | 0.094789 | 0.09338 | 0.091683 | 0.090012 | 0.087064 | 0.086877 | 0.086712 | 0.020966 | 0.02014 | 0.019423 | 0.018673 | 0.017623 | 0.016606 | 0.014985 | 0.013063 | 0.011641 | 0.0099336 | 0.0082547 | 0.00529 | 0.0051514 | 0.0050404
|  | ARDCHYLE | LW |  |  |  | 0 | 0.10591 | 0.1051 | 0.10439 | 0.10344 | 0.10264 | 0.10116 | 0.099462 | 0.097685 | 0.095437 | 0.093557 | 0.09191 | 0.089592 | 0.089033 | 0.088542 | 0.10251 | 0.10175 | 0.10114 | 0.10031 | 0.099625 | 0.098284 | 0.096729 | 0.095013 | 0.092819 | 0.090985 | 0.089376 | 0.087504 | 0.087316 | 0.087147 | 0.020978 | 0.020201 | 0.01957 | 0.018704 | 0.017991 | 0.016615 | 0.015023 | 0.01329 | 0.01108 | 0.0092324 | 0.0076119 | 0.0057314 | 0.0055927 | 0.0054851
|  | ARDCHYLE | ST |  |  |  | 0 | 0.10615 | 0.10581 | 0.10537 | 0.10483 | 0.10424 | 0.10355 | 0.10274 | 0.10179 | 0.10053 | 0.0992 | 0.097733 | 0.09032 | 0.088897 | 0.088486 | 0.10275 | 0.10247 | 0.1021 | 0.10163 | 0.10112 | 0.10051 | 0.099776 | 0.098892 | 0.097699 | 0.096429 | 0.095027 | 0.088054 | 0.087048 | 0.086901 | 0.021219 | 0.020922 | 0.02053 | 0.02004 | 0.019504 | 0.018863 | 0.018109 | 0.017207 | 0.015995 | 0.014707 | 0.013287 | 0.0062376 | 0.0052385 | 0.0051028
|  | ARDCHYLE | FS |  |  |  | 0 | 0.10625 | 0.10599 | 0.10571 | 0.10536 | 0.105 | 0.10457 | 0.10406 | 0.10338 | 0.10251 | 0.10161 | 0.10062 | 0.094188 | 0.089115 | 0.088597 | 0.1028 | 0.10257 | 0.10231 | 0.10197 | 0.10162 | 0.1012 | 0.10071 | 0.10008 | 0.09926 | 0.098412 | 0.097471 | 0.091297 | 0.086685 | 0.086559 | 0.021282 | 0.021043 | 0.020772 | 0.020431 | 0.020072 | 0.019646 | 0.019141 | 0.018498 | 0.017664 | 0.016799 | 0.015843 | 0.0095865 | 0.0048793 | 0.0047269
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.176 | 4.0313 | 3.9559 | 3.8453 | 3.7051 | 3.5627 | 3.4025 | 3.2138 | 3.1171 | 3.0614 | 2.9702 | 2.8896 | 2.6511 | 2.5053 | 2.3552 | 5.0377 | 4.9932 | 4.9307 | 4.8667 | 4.7997 | 4.7201 | 4.6176 | 4.5458 | 4.4898 | 4.421 | 4.3593 | 4.21 | 4.1359 | 3.97 | 4.5341 | 4.4752 | 4.3939 | 4.296 | 4.1994 | 4.0923 | 3.9498 | 3.8551 | 3.76 | 3.6635 | 3.5761 | 3.3574 | 3.2638 | 3.1711
|  | ARDERSIER | CT |  |  |  | 0.176 | 4.0313 | 3.9559 | 3.8463 | 3.7051 | 3.5627 | 3.4025 | 3.2138 | 3.1171 | 3.0736 | 3.0081 | 2.9548 | 2.7498 | 2.6259 | 2.5 | 5.0377 | 4.9958 | 4.9441 | 4.8694 | 4.8026 | 4.7234 | 4.6246 | 4.55 | 4.522 | 4.4657 | 4.4146 | 4.2484 | 4.1478 | 4.0001 | 4.5341 | 4.4791 | 4.4027 | 4.296 | 4.1994 | 4.0936 | 3.9513 | 3.8723 | 3.8289 | 3.7679 | 3.7168 | 3.5431 | 3.4389 | 3.3275
|  | ARDERSIER | LW |  |  |  | 0.176 | 4.0377 | 3.9631 | 3.8453 | 3.7203 | 3.5849 | 3.4315 | 3.2463 | 3.1452 | 3.0614 | 2.9702 | 2.8896 | 2.6511 | 2.5053 | 2.3552 | 5.0394 | 4.9932 | 4.9307 | 4.8667 | 4.7997 | 4.7201 | 4.6176 | 4.5458 | 4.4898 | 4.421 | 4.3593 | 4.21 | 4.1359 | 4.0443 | 4.5359 | 4.4752 | 4.3939 | 4.3036 | 4.2095 | 4.0923 | 3.9498 | 3.8551 | 3.76 | 3.6635 | 3.5761 | 3.3574 | 3.2638 | 3.1711
|  | ARDERSIER | ST |  |  |  | 0.176 | 4.0595 | 4.0036 | 3.933 | 3.8627 | 3.7816 | 3.7102 | 3.6264 | 3.5642 | 3.4773 | 3.3928 | 3.3008 | 2.9348 | 2.7769 | 2.6954 | 5.055 | 5.0267 | 4.9895 | 4.9542 | 4.9103 | 4.8734 | 4.8251 | 4.79 | 4.7325 | 4.6784 | 4.6158 | 4.3316 | 4.1838 | 4.0469 | 4.554 | 4.5195 | 4.4688 | 4.4178 | 4.3598 | 4.3028 | 4.2365 | 4.1784 | 4.0989 | 4.0176 | 3.9282 | 3.5037 | 3.3339 | 3.2625
|  | ARDERSIER | FS |  |  |  | 0.176 | 4.1024 | 4.0659 | 4.0432 | 4.009 | 3.9843 | 3.9478 | 3.9205 | 3.8583 | 3.8046 | 3.7368 | 3.6732 | 3.3281 | 2.9547 | 2.8183 | 5.072 | 5.0515 | 5.0351 | 5.0096 | 4.9929 | 4.965 | 4.9422 | 4.9012 | 4.8664 | 4.8192 | 4.7773 | 4.5258 | 4.2189 | 3.97 | 4.5763 | 4.5531 | 4.5329 | 4.5061 | 4.4828 | 4.4518 | 4.4215 | 4.3728 | 4.3237 | 4.2664 | 4.2103 | 3.882 | 3.5537 | 3.3931
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0.023 | 0.06549 | 0.055324 | 0.044361 | 0.033355 | 0.025209 | 0.012285 | -0.0047478 | -0.010908 | -0.010676 | -0.003636 | -0.0067585 | -0.019855 | -0.043088 | -0.06953 | 0.062335 | 0.05058 | 0.038242 | 0.026139 | 0.017576 | 0.0037192 | -0.014974 | -0.020793 | -0.017971 | -0.012373 | -0.014854 | -0.030356 | -0.058352 | -0.090039 | 0.067596 | 0.055684 | 0.042629 | 0.029747 | 0.020334 | 0.0055909 | -0.014041 | -0.019978 | -0.021316 | -0.014034 | -0.017227 | -0.032974 | -0.061475 | -0.093689
|  | ARDOCHY | CT |  |  |  | 0.023 | 0.06549 | 0.062435 | 0.059251 | 0.048476 | 0.042384 | 0.03549 | 0.023368 | 0.016292 | 0.018516 | 0.023885 | 0.020722 | 0.009388 | 0.0026194 | -0.0069965 | 0.062347 | 0.059674 | 0.057221 | 0.045434 | 0.039842 | 0.033325 | 0.020987 | 0.013976 | 0.01766 | 0.021793 | 0.018616 | 0.0070857 | -0.00068275 | -0.011952 | 0.067596 | 0.064647 | 0.061431 | 0.048798 | 0.042283 | 0.03475 | 0.021349 | 0.014329 | 0.014682 | 0.020425 | 0.016717 | 0.0039715 | -0.0041269 | -0.015636
|  | ARDOCHY | LW |  |  |  | 0.023 | 0.065575 | 0.055324 | 0.044361 | 0.033355 | 0.025209 | 0.012285 | -0.0047478 | -0.010908 | -0.010676 | -0.003636 | -0.0067585 | -0.019855 | -0.043088 | -0.06953 | 0.062335 | 0.05058 | 0.038242 | 0.026139 | 0.017576 | 0.0037192 | -0.014974 | -0.020793 | -0.017971 | -0.012373 | -0.014854 | -0.030356 | -0.058352 | -0.090039 | 0.067628 | 0.055684 | 0.042629 | 0.029747 | 0.020334 | 0.0055909 | -0.014041 | -0.019978 | -0.021316 | -0.014034 | -0.017227 | -0.032974 | -0.061475 | -0.093689
|  | ARDOCHY | ST |  |  |  | 0.023 | 0.066456 | 0.065223 | 0.058749 | 0.053589 | 0.049896 | 0.046669 | 0.043065 | 0.039051 | 0.034107 | 0.028937 | 0.024195 | 0.006317 | -0.020505 | -0.043777 | 0.063189 | 0.062256 | 0.054961 | 0.049391 | 0.045703 | 0.042694 | 0.039314 | 0.035449 | 0.030669 | 0.025668 | 0.021302 | 0.00072358 | -0.031617 | -0.060614 | 0.068472 | 0.067341 | 0.059638 | 0.053648 | 0.049548 | 0.046133 | 0.042358 | 0.038188 | 0.033124 | 0.027844 | 0.02321 | -0.0011679 | -0.034086 | -0.063061
|  | ARDOCHY | FS |  |  |  | 0.023 | 0.06688 | 0.065951 | 0.063402 | 0.060629 | 0.057783 | 0.054715 | 0.050606 | 0.046747 | 0.041486 | 0.036159 | 0.033035 | 0.023627 | 0.024601 | 0.019848 | 0.063377 | 0.062627 | 0.059759 | 0.056671 | 0.053513 | 0.050137 | 0.045519 | 0.041528 | 0.03594 | 0.030288 | 0.027453 | 0.021498 | 0.022831 | 0.017276 | 0.068845 | 0.067989 | 0.06513 | 0.062056 | 0.058863 | 0.055442 | 0.05079 | 0.046557 | 0.040742 | 0.034866 | 0.031816 | 0.020172 | 0.021612 | 0.016159
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 0.04 | 2.2197 | 2.1926 | 2.1513 | 2.1078 | 2.0543 | 2.01 | 1.9379 | 1.9081 | 1.8614 | 1.8214 | 1.8081 | 1.7251 | 1.6787 | 1.6115 | 2.0669 | 2.0444 | 2.0167 | 1.9885 | 1.9604 | 1.9271 | 1.8771 | 1.8551 | 1.8188 | 1.7874 | 1.7769 | 1.7108 | 1.6733 | 1.6167 | 2.1683 | 2.1401 | 2.1009 | 2.0603 | 2.0182 | 1.9696 | 1.9 | 1.871 | 1.8238 | 1.7833 | 1.7707 | 1.6873 | 1.6407 | 1.571
|  | ARISAIG | CT |  |  |  | 0.04 | 2.2197 | 2.1954 | 2.1557 | 2.1086 | 2.0543 | 2.0102 | 1.9395 | 1.9118 | 1.8862 | 1.8583 | 1.8339 | 1.7899 | 1.7607 | 1.7171 | 2.0669 | 2.0512 | 2.0299 | 2.0006 | 1.969 | 1.9466 | 1.9024 | 1.8798 | 1.8578 | 1.8333 | 1.8105 | 1.7669 | 1.7401 | 1.6942 | 2.1683 | 2.1455 | 2.1107 | 2.0677 | 2.0186 | 1.9808 | 1.9151 | 1.8872 | 1.8604 | 1.831 | 1.8045 | 1.7594 | 1.7334 | 1.6923
|  | ARISAIG | LW |  |  |  | 0.04 | 2.222 | 2.1926 | 2.1513 | 2.1078 | 2.062 | 2.01 | 1.9379 | 1.9081 | 1.8614 | 1.8214 | 1.8081 | 1.7251 | 1.6787 | 1.6115 | 2.0678 | 2.0444 | 2.0167 | 1.9885 | 1.9604 | 1.9271 | 1.8771 | 1.8551 | 1.8188 | 1.7874 | 1.7769 | 1.7108 | 1.6733 | 1.6167 | 2.17 | 2.1401 | 2.1009 | 2.0603 | 2.0182 | 1.9696 | 1.9 | 1.871 | 1.8238 | 1.7833 | 1.7707 | 1.6873 | 1.6407 | 1.571
|  | ARISAIG | ST |  |  |  | 0.04 | 2.2215 | 2.2149 | 2.1951 | 2.1757 | 2.1556 | 2.1375 | 2.1122 | 2.0848 | 2.0652 | 2.0332 | 2.0099 | 1.8752 | 1.8201 | 1.7915 | 2.067 | 2.0648 | 2.0504 | 2.0369 | 2.0236 | 2.0122 | 1.9949 | 1.9755 | 1.9623 | 1.939 | 1.923 | 1.8083 | 1.7486 | 1.7014 | 2.1692 | 2.1643 | 2.1454 | 2.1271 | 2.1085 | 2.0924 | 2.0686 | 2.0421 | 2.0239 | 1.9927 | 1.9713 | 1.8358 | 1.7783 | 1.7469
|  | ARISAIG | FS |  |  |  | 0.04 | 2.2298 | 2.224 | 2.2152 | 2.2068 | 2.1985 | 2.1871 | 2.1767 | 2.1556 | 2.1296 | 2.1157 | 2.0923 | 1.9713 | 1.8754 | 1.8344 | 2.0709 | 2.0679 | 2.0606 | 2.0535 | 2.0465 | 2.0369 | 2.0275 | 2.012 | 1.9921 | 1.9818 | 1.965 | 1.8738 | 1.7966 | 1.7358 | 2.1764 | 2.1715 | 2.1627 | 2.1545 | 2.1461 | 2.1347 | 2.1243 | 2.1041 | 2.0786 | 2.0656 | 2.0433 | 1.928 | 1.8412 | 1.8041
| STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | YES | 0.368 | 11.632 | 11.632 | 11.6207 | 11.613 | 11.6079 | 11.5906 | 11.5857 | 11.5291 | 11.5091 | 11.4921 | 11.465 | 11.3377 | 10.9677 | 10.3767 | 11.6317 | 11.6314 | 11.6207 | 11.613 | 11.6079 | 11.5906 | 11.5857 | 11.5291 | 11.5091 | 11.4921 | 11.4622 | 11.2976 | 10.7945 | 10.0557 | 11.6316 | 11.6312 | 11.6174 | 11.6077 | 11.6011 | 11.5791 | 11.5727 | 11.5016 | 11.476 | 11.4542 | 11.4196 | 11.2566 | 10.7919 | 10.0532
|  | ARNISH | CT |  |  |  | 0.368 | 11.632 | 11.632 | 11.6305 | 11.6279 | 11.6153 | 11.6019 | 11.5985 | 11.5728 | 11.5469 | 11.5246 | 11.5001 | 11.3698 | 11.1713 | 10.9367 | 11.6317 | 11.6314 | 11.6291 | 11.6256 | 11.6091 | 11.592 | 11.5874 | 11.5548 | 11.5219 | 11.4934 | 11.4622 | 11.2976 | 11.1072 | 10.811 | 11.6316 | 11.6312 | 11.6289 | 11.6253 | 11.6078 | 11.5907 | 11.5862 | 11.5535 | 11.5201 | 11.4915 | 11.4601 | 11.2944 | 11.046 | 10.7539
|  | ARNISH | LW |  |  |  | 0.368 | 11.632 | 11.632 | 11.632 | 11.632 | 11.632 | 11.632 | 11.632 | 11.6039 | 11.5748 | 11.5508 | 11.5238 | 11.3818 | 10.9677 | 10.3767 | 11.6317 | 11.6314 | 11.6306 | 11.6304 | 11.6302 | 11.6297 | 11.6292 | 11.5937 | 11.5566 | 11.5254 | 11.491 | 11.312 | 10.7945 | 10.0557 | 11.6317 | 11.6313 | 11.6296 | 11.6293 | 11.629 | 11.6285 | 11.6278 | 11.5927 | 11.5554 | 11.5236 | 11.489 | 11.3091 | 10.7919 | 10.0532
|  | ARNISH | ST |  |  |  | 0.368 | 11.632 | 11.632 | 11.6207 | 11.613 | 11.6079 | 11.5906 | 11.5857 | 11.5291 | 11.5091 | 11.4921 | 11.465 | 11.3377 | 11.0315 | 10.6925 | 11.632 | 11.632 | 11.6207 | 11.613 | 11.6079 | 11.5906 | 11.5857 | 11.5291 | 11.5091 | 11.4921 | 11.465 | 11.3377 | 11.0315 | 10.6925 | 11.6318 | 11.6317 | 11.6174 | 11.6077 | 11.6011 | 11.5791 | 11.5727 | 11.5016 | 11.476 | 11.4542 | 11.4196 | 11.2566 | 10.8721 | 10.4487
|  | ARNISH | FS |  |  |  | 0.368 | 11.632 | 11.632 | 11.6297 | 11.6274 | 11.6247 | 11.622 | 11.6196 | 11.5992 | 11.5853 | 11.5714 | 11.5575 | 11.5407 | 11.5257 | 11.4963 | 11.6319 | 11.6318 | 11.6288 | 11.6258 | 11.6223 | 11.6188 | 11.6157 | 11.5899 | 11.5723 | 11.5545 | 11.5368 | 11.5128 | 11.4898 | 11.4419 | 11.6319 | 11.6318 | 11.6288 | 11.6257 | 11.6222 | 11.6186 | 11.6156 | 11.5897 | 11.572 | 11.5538 | 11.5361 | 11.51 | 11.4873 | 11.4398
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 3.424 | -0.43897 | 9.7075 | 8.1576 | 6.3483 | 4.7722 | 3.0639 | 1.3644 | -0.56208 | -2.2818 | -3.729 | -4.9154 | -8.7552 | -11.3762 | -12.4197 | 1.1942 | 11.0718 | 9.7403 | 8.2701 | 7.1838 | 6.0439 | 4.9002 | 3.5921 | 2.2728 | 1.3546 | 0.62802 | -1.8286 | -3.5238 | -4.2791 | -0.10809 | 10.4367 | 9.2567 | 7.633 | 6.2278 | 4.7175 | 3.1884 | 1.4698 | -0.15452 | -1.4341 | -2.4743 | -5.9012 | -8.2207 | -9.1456
|  | ASHGROVE | CT |  |  |  | 3.424 | -0.20829 | 10.1742 | 8.7304 | 6.804 | 5.0488 | 3.1754 | 1.4176 | -0.45028 | -1.9882 | -3.4663 | -4.594 | -8.7552 | -11.3762 | -12.4197 | 1.4434 | 11.5919 | 10.4029 | 8.8088 | 7.5767 | 6.2863 | 5.1247 | 3.8308 | 2.612 | 1.5668 | 0.79764 | -1.7673 | -3.5238 | -4.2791 | 0.13279 | 10.9324 | 9.8642 | 8.0834 | 6.5139 | 4.8419 | 3.2628 | 1.5982 | 0.13323 | -1.1927 | -2.1912 | -5.85 | -8.2207 | -9.1456
|  | ASHGROVE | LW |  |  |  | 3.424 | -0.43897 | 9.7075 | 8.1576 | 6.3483 | 4.7722 | 3.0639 | 1.3644 | -0.56208 | -2.2818 | -3.729 | -4.9154 | -8.7488 | -10.8245 | -11.8122 | 1.1942 | 11.0718 | 9.7403 | 8.2701 | 7.1838 | 6.0439 | 4.9002 | 3.5921 | 2.2728 | 1.3546 | 0.62802 | -1.8286 | -3.3792 | -3.9052 | -0.10809 | 10.4367 | 9.2567 | 7.633 | 6.2278 | 4.7175 | 3.1884 | 1.4698 | -0.15452 | -1.4341 | -2.4743 | -5.9012 | -7.8429 | -8.729
|  | ASHGROVE | ST |  |  |  | 3.424 | -0.10602 | 10.389 | 9.2888 | 7.8473 | 6.6462 | 5.3983 | 4.3786 | 3.201 | 1.8532 | 0.74745 | -0.1546 | -3.8601 | -6.6711 | -8.2696 | 1.4851 | 11.6906 | 10.5848 | 9.1359 | 8.0431 | 6.8973 | 5.9578 | 4.8615 | 3.5875 | 2.6038 | 1.8423 | -0.90137 | -2.8638 | -3.6709 | 0.16543 | 11.0263 | 10.0095 | 8.6773 | 7.6417 | 6.5527 | 5.67 | 4.6157 | 3.4037 | 2.417 | 1.5728 | -1.7571 | -4.4286 | -5.9314
|  | ASHGROVE | FS |  |  |  | 3.424 | 0.22185 | 10.9485 | 10.1417 | 9.0844 | 8.0893 | 6.9014 | 6.1786 | 5.2458 | 4.143 | 3.2564 | 2.3543 | -2.2899 | -6.0812 | -8.106 | 1.7818 | 12.2079 | 11.4166 | 10.3406 | 9.4057 | 8.2672 | 7.5883 | 6.7821 | 5.7828 | 5.026 | 4.2559 | 0.35177 | -2.5374 | -3.8028 | 0.43862 | 11.5055 | 10.7683 | 9.7783 | 8.8927 | 7.8171 | 7.1815 | 6.4304 | 5.5035 | 4.7818 | 4.0366 | -0.23177 | -3.6689 | -5.475
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 0.952 | 2.7753 | 2.5202 | 18.1789 | 17.6193 | 17.0064 | 16.3063 | 15.4461 | 15.0281 | 14.3081 | 13.5949 | 12.9534 | 11.213 | 10.2621 | 9.4832 | 5.9889 | 5.9075 | 20.45 | 20.205 | 19.8919 | 19.5339 | 19.0691 | 18.9015 | 18.5191 | 18.1115 | 17.7423 | 16.7531 | 16.0053 | 15.0886 | 4.6512 | 4.4027 | 19.3731 | 18.8827 | 18.3552 | 17.7472 | 16.9669 | 16.6019 | 15.9132 | 15.2495 | 14.652 | 13.0616 | 12.2759 | 11.576
|  | ASHLUDIE | CT |  |  |  | 0.952 | 2.7753 | 2.5202 | 18.1789 | 17.6193 | 17.0064 | 16.3063 | 15.4461 | 15.0281 | 14.4495 | 13.9009 | 13.4254 | 11.3753 | 10.2621 | 9.4832 | 5.9889 | 5.9182 | 20.4569 | 20.205 | 19.8919 | 19.5339 | 19.0691 | 18.9015 | 18.5761 | 18.2463 | 17.9469 | 16.7531 | 16.0053 | 15.0886 | 4.6512 | 4.4027 | 19.3731 | 18.8827 | 18.3552 | 17.7472 | 16.9669 | 16.6019 | 16.0694 | 15.5595 | 15.1155 | 13.2568 | 12.2759 | 11.576
|  | ASHLUDIE | LW |  |  |  | 0.952 | 2.8005 | 2.5315 | 18.2011 | 17.6522 | 17.128 | 16.395 | 15.5683 | 15.1093 | 14.3081 | 13.5949 | 12.9534 | 11.213 | 10.6222 | 9.9131 | 5.9899 | 5.9075 | 20.45 | 20.2464 | 19.9997 | 19.6009 | 19.1417 | 18.9779 | 18.5191 | 18.1115 | 17.7423 | 16.8477 | 16.5971 | 16.2145 | 4.6762 | 4.4085 | 19.3902 | 18.9036 | 18.4625 | 17.8003 | 17.0473 | 16.6591 | 15.9132 | 15.2495 | 14.652 | 13.0616 | 12.5344 | 11.88
|  | ASHLUDIE | ST |  |  |  | 0.952 | 2.9 | 2.7646 | 18.7348 | 18.5644 | 18.4205 | 18.2262 | 18.008 | 17.8131 | 17.523 | 17.218 | 17.2386 | 15.4527 | 14.27 | 13.1341 | 6.0141 | 5.9842 | 20.5501 | 20.5033 | 20.4611 | 20.4017 | 20.2876 | 20.1423 | 19.9186 | 19.6808 | 19.7035 | 18.3741 | 17.507 | 16.4948 | 4.7699 | 4.6432 | 19.8746 | 19.7105 | 19.5762 | 19.3861 | 19.1693 | 18.9794 | 18.6823 | 18.3691 | 18.4359 | 16.7154 | 15.6939 | 14.7688
|  | ASHLUDIE | FS |  |  |  | 0.952 | 2.9247 | 2.8235 | 18.8205 | 18.6954 | 18.5576 | 18.4444 | 18.2851 | 18.0362 | 17.7913 | 17.508 | 17.2094 | 15.7914 | 13.9868 | 12.5792 | 6.0159 | 5.9941 | 20.5694 | 20.5368 | 20.4985 | 20.4644 | 20.4136 | 20.2576 | 20.0823 | 19.8751 | 19.6547 | 18.6134 | 17.0042 | 15.181 | 4.7893 | 4.6958 | 19.9525 | 19.833 | 19.7002 | 19.5945 | 19.4375 | 19.2054 | 18.9821 | 18.7131 | 18.4286 | 17.1973 | 15.5817 | 14.3212
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | YES | 0.195 | -1.0352 | -1.0844 | -1.1606 | -1.2607 | -1.3584 | -1.467 | -1.5884 | -1.6437 | -1.7236 | -1.8182 | -1.9026 | -2.0778 | -2.1753 | -2.3202 | -0.33162 | -0.37269 | -0.41694 | -0.47756 | -0.53469 | -0.61027 | -0.69239 | -0.75966 | -0.83694 | -0.90906 | -0.97463 | -1.0985 | -1.1598 | -1.2615 | -0.63667 | -0.69647 | -0.76704 | -0.86758 | -0.96454 | -1.0774 | -1.198 | -1.2845 | -1.3759 | -1.4657 | -1.5461 | -1.7004 | -1.7943 | -1.9253
|  | AULTBEA | CT |  |  |  | 0.195 | -1.0352 | -1.0844 | -1.1606 | -1.2607 | -1.3584 | -1.467 | -1.5884 | -1.6437 | -1.6963 | -1.7654 | -1.8261 | -1.9657 | -2.0451 | -2.1542 | -0.33162 | -0.37139 | -0.41207 | -0.47612 | -0.53469 | -0.60302 | -0.67868 | -0.74712 | -0.7933 | -0.84955 | -0.90158 | -1.0259 | -1.0958 | -1.2091 | -0.63667 | -0.69647 | -0.76704 | -0.86758 | -0.96454 | -1.0774 | -1.198 | -1.2845 | -1.3388 | -1.4055 | -1.4646 | -1.5954 | -1.6681 | -1.7635
|  | AULTBEA | LW |  |  |  | 0.195 | -1.0277 | -1.0794 | -1.1552 | -1.2444 | -1.332 | -1.4462 | -1.5681 | -1.6306 | -1.7236 | -1.8182 | -1.9026 | -2.0778 | -2.1753 | -2.3202 | -0.32781 | -0.37269 | -0.41694 | -0.47756 | -0.52653 | -0.61027 | -0.69239 | -0.75966 | -0.83694 | -0.90906 | -0.97463 | -1.0985 | -1.1598 | -1.2615 | -0.62924 | -0.69215 | -0.76396 | -0.85978 | -0.94157 | -1.069 | -1.1919 | -1.2802 | -1.3759 | -1.4657 | -1.5461 | -1.7004 | -1.7943 | -1.9253
|  | AULTBEA | ST |  |  |  | 0.195 | -1.0198 | -1.0498 | -1.0968 | -1.143 | -1.1918 | -1.238 | -1.2919 | -1.339 | -1.3983 | -1.4522 | -1.5157 | -1.7936 | -1.9189 | -1.9791 | -0.32136 | -0.33782 | -0.36858 | -0.39739 | -0.43123 | -0.45679 | -0.49621 | -0.52945 | -0.58057 | -0.61648 | -0.67021 | -0.91581 | -1.0304 | -1.1191 | -0.62017 | -0.6483 | -0.69696 | -0.74278 | -0.79591 | -0.83672 | -0.89625 | -0.9437 | -1.0143 | -1.0626 | -1.1351 | -1.4276 | -1.5433 | -1.6007
|  | AULTBEA | FS |  |  |  | 0.195 | -0.99865 | -1.0174 | -1.0332 | -1.0494 | -1.0684 | -1.0894 | -1.1082 | -1.1481 | -1.1892 | -1.2347 | -1.28 | -1.5211 | -1.7686 | -1.8974 | -0.3122 | -0.32345 | -0.3385 | -0.35322 | -0.37306 | -0.39595 | -0.41203 | -0.44541 | -0.47795 | -0.51844 | -0.559 | -0.77325 | -0.98645 | -1.1621 | -0.60126 | -0.61907 | -0.63935 | -0.6584 | -0.68423 | -0.71376 | -0.73162 | -0.77806 | -0.82097 | -0.87507 | -0.92962 | -1.1946 | -1.4266 | -1.5237
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 6.233 | -0.886 | -1.2813 | -1.6826 | -2.1948 | -2.7428 | -3.3282 | -4.0477 | -4.6055 | -4.9916 | -5.4889 | -5.8898 | -6.9286 | -7.3182 | -7.8599 | 3.5407 | 3.279 | 3.0654 | 2.7681 | 2.5074 | 2.2393 | 1.8474 | 1.4709 | 1.1961 | 0.85671 | 0.5197 | -0.78761 | -1.5707 | -1.8397 | 1.385 | 1.0284 | 0.66314 | 0.19848 | -0.29646 | -0.82075 | -1.4853 | -2.0022 | -2.393 | -2.9155 | -3.3324 | -4.3901 | -4.7621 | -5.3219
|  | AVIEMORE | CT |  |  |  | 6.233 | -0.886 | -1.2661 | -1.6818 | -2.1948 | -2.7428 | -3.3282 | -4.0477 | -4.6055 | -4.9916 | -5.4056 | -5.7106 | -6.5748 | -6.8603 | -7.2357 | 3.5443 | 3.3087 | 3.075 | 2.7681 | 2.5074 | 2.2393 | 1.8474 | 1.4709 | 1.1961 | 0.90781 | 0.66223 | 0.093621 | 0.032493 | -0.23071 | 1.385 | 1.0437 | 0.67155 | 0.19848 | -0.29646 | -0.82075 | -1.4853 | -2.0022 | -2.3663 | -2.7756 | -3.0954 | -3.9753 | -4.2338 | -4.601
|  | AVIEMORE | LW |  |  |  | 6.233 | -0.88293 | -1.2813 | -1.6826 | -2.1213 | -2.5788 | -3.1825 | -3.862 | -4.4071 | -4.9614 | -5.4889 | -5.8898 | -6.9286 | -7.3182 | -7.8599 | 3.5407 | 3.279 | 3.0654 | 2.864 | 2.6656 | 2.3508 | 1.9787 | 1.6439 | 1.2369 | 0.85671 | 0.5197 | -0.33062 | -0.5417 | -0.78798 | 1.3929 | 1.0284 | 0.66314 | 0.26234 | -0.15105 | -0.70528 | -1.3415 | -1.8437 | -2.393 | -2.9155 | -3.3324 | -4.3901 | -4.7621 | -5.3219
|  | AVIEMORE | ST |  |  |  | 6.233 | -0.80362 | -1.0524 | -1.3087 | -1.5402 | -1.8039 | -2.0849 | -2.3819 | -2.7303 | -3.107 | -3.5218 | -3.9295 | -5.7391 | -6.3406 | -6.5002 | 3.5962 | 3.471 | 3.3052 | 3.1663 | 3.0051 | 2.8181 | 2.6002 | 2.3398 | 2.0161 | 1.6619 | 1.2804 | -0.78761 | -1.5707 | -1.8397 | 1.4623 | 1.2475 | 1.015 | 0.80695 | 0.57131 | 0.32337 | 0.052618 | -0.26416 | -0.61774 | -1.0181 | -1.4225 | -3.299 | -4.2535 | -4.5677
|  | AVIEMORE | FS |  |  |  | 6.233 | -0.68992 | -0.87166 | -0.98453 | -1.0946 | -1.2311 | -1.374 | -1.539 | -1.7812 | -2.0624 | -2.3224 | -2.5885 | -4.0661 | -5.4502 | -6.1185 | 3.6262 | 3.5301 | 3.429 | 3.3413 | 3.2357 | 3.1153 | 2.9715 | 2.814 | 2.6139 | 2.4177 | 2.2136 | 0.88233 | -0.33293 | -1.0481 | 1.5512 | 1.4008 | 1.3007 | 1.2037 | 1.0829 | 0.95744 | 0.79558 | 0.57348 | 0.30594 | 0.066269 | -0.19128 | -1.6657 | -3.0311 | -3.691
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 0.202 | -2.1034 | -2.2424 | -2.4144 | -2.6099 | -2.8439 | -3.1092 | -3.4551 | -3.6184 | -3.7559 | -3.8892 | -4.0383 | -4.5144 | -4.7453 | -4.9983 | -0.88364 | -0.97472 | -1.0804 | -1.2136 | -1.3585 | -1.5028 | -1.704 | -1.832 | -1.9469 | -2.0796 | -2.2259 | -2.5665 | -2.7258 | -3.08 | -1.5999 | -1.7371 | -1.9084 | -2.1143 | -2.3554 | -2.6064 | -2.9251 | -3.0799 | -3.2192 | -3.4013 | -3.5974 | -4.062 | -4.2513 | -4.4973
|  | BALALDIE | CT |  |  |  | 0.202 | -2.1034 | -2.2424 | -2.4144 | -2.6099 | -2.8439 | -3.1092 | -3.4551 | -3.6184 | -3.7559 | -3.8892 | -4.0006 | -4.3458 | -4.5221 | -4.7155 | -0.88364 | -0.97472 | -1.0804 | -1.2136 | -1.3585 | -1.5028 | -1.704 | -1.832 | -1.9469 | -2.0686 | -2.179 | -2.473 | -2.6119 | -2.8315 | -1.5999 | -1.7371 | -1.9084 | -2.1143 | -2.3554 | -2.6064 | -2.9251 | -3.0799 | -3.2192 | -3.3768 | -3.5167 | -3.8714 | -4.0102 | -4.1848
|  | BALALDIE | LW |  |  |  | 0.202 | -2.0863 | -2.2168 | -2.3753 | -2.5784 | -2.7477 | -2.9963 | -3.298 | -3.4605 | -3.6745 | -3.8633 | -4.0383 | -4.5144 | -4.7453 | -4.9983 | -0.87388 | -0.96134 | -1.0552 | -1.1768 | -1.2775 | -1.4351 | -1.6247 | -1.7445 | -1.9215 | -2.0796 | -2.2259 | -2.5665 | -2.6845 | -2.8527 | -1.5835 | -1.7126 | -1.8675 | -2.0638 | -2.24 | -2.4944 | -2.7884 | -2.9452 | -3.1872 | -3.4013 | -3.5974 | -4.062 | -4.2513 | -4.4973
|  | BALALDIE | ST |  |  |  | 0.202 | -2.0584 | -2.1397 | -2.2343 | -2.348 | -2.4518 | -2.5729 | -2.6778 | -2.8106 | -2.9615 | -3.1381 | -3.3058 | -4.1576 | -4.4967 | -4.6277 | -0.85458 | -0.90122 | -0.96066 | -1.032 | -1.0992 | -1.1794 | -1.2554 | -1.3533 | -1.4706 | -1.6016 | -1.7174 | -2.4207 | -2.7258 | -2.9281 | -1.5555 | -1.6316 | -1.7264 | -1.8375 | -1.9427 | -2.0647 | -2.1827 | -2.3181 | -2.4824 | -2.6633 | -2.8212 | -3.7037 | -4.0277 | -4.147
|  | BALALDIE | FS |  |  |  | 0.202 | -2.0151 | -2.0666 | -2.1133 | -2.1494 | -2.2019 | -2.2442 | -2.3072 | -2.3814 | -2.4958 | -2.6029 | -2.7241 | -3.3737 | -4.1131 | -4.5138 | -0.83411 | -0.86551 | -0.9 | -0.93061 | -0.97183 | -1.0091 | -1.0622 | -1.1211 | -1.2082 | -1.2922 | -1.3863 | -1.9473 | -2.5706 | -3.08 | -1.5147 | -1.5631 | -1.6093 | -1.6493 | -1.7031 | -1.7506 | -1.8169 | -1.898 | -2.0162 | -2.1302 | -2.2572 | -2.9738 | -3.6825 | -4.0449
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.779 | 1.1396 | 3.9068 | 3.6543 | 3.2632 | 2.865 | 2.3817 | 1.9225 | 1.5719 | 1.2992 | 0.99872 | 0.59118 | -0.25252 | -0.63229 | -0.9604 | 2.8366 | 5.4345 | 5.3056 | 5.1055 | 4.9114 | 4.6714 | 4.4415 | 4.253 | 4.0872 | 3.9022 | 3.6009 | 3.0692 | 2.881 | 2.5893 | 1.5917 | 4.4821 | 4.2626 | 3.9288 | 3.5914 | 3.1791 | 2.7735 | 2.4542 | 2.1963 | 1.918 | 1.5339 | 0.75189 | 0.41148 | 0.10478
|  | BALBEGGIE | CT |  |  |  | 0.779 | 1.14 | 3.9157 | 3.6671 | 3.2731 | 2.865 | 2.3817 | 1.9225 | 1.5719 | 1.3167 | 1.0607 | 0.70685 | -0.17053 | -0.58261 | -0.8901 | 2.8427 | 5.4552 | 5.3333 | 5.1252 | 4.9207 | 4.6898 | 4.4489 | 4.2532 | 4.1205 | 3.9731 | 3.6976 | 3.1259 | 2.881 | 2.5893 | 1.5936 | 4.496 | 4.2827 | 3.9427 | 3.5914 | 3.1839 | 2.7735 | 2.4542 | 2.2348 | 2.0002 | 1.6661 | 0.8682 | 0.51574 | 0.24386
|  | BALBEGGIE | LW |  |  |  | 0.779 | 1.1396 | 3.9068 | 3.6543 | 3.2632 | 2.8692 | 2.3874 | 1.9564 | 1.6025 | 1.2992 | 0.99872 | 0.59118 | -0.25252 | -0.63229 | -0.9604 | 2.8366 | 5.4345 | 5.3056 | 5.1055 | 4.9114 | 4.6714 | 4.4415 | 4.253 | 4.0872 | 3.9022 | 3.6009 | 3.0692 | 2.882 | 2.6958 | 1.5917 | 4.4821 | 4.2626 | 3.9288 | 3.5937 | 3.1791 | 2.79 | 2.4704 | 2.1963 | 1.918 | 1.5339 | 0.75189 | 0.41148 | 0.10478
|  | BALBEGGIE | ST |  |  |  | 0.779 | 1.1796 | 4.01 | 3.8544 | 3.6455 | 3.4386 | 3.2035 | 3.0258 | 2.8461 | 2.6839 | 2.5004 | 2.1607 | 1.1375 | 0.62845 | 0.26548 | 2.8643 | 5.5143 | 5.4254 | 5.3114 | 5.1966 | 5.0693 | 4.9668 | 4.8573 | 4.7605 | 4.6445 | 4.3776 | 3.5984 | 3.2453 | 2.9296 | 1.6311 | 4.5892 | 4.4526 | 4.2794 | 4.105 | 3.9137 | 3.7577 | 3.597 | 3.4505 | 3.2808 | 2.9598 | 1.9822 | 1.5161 | 1.1931
|  | BALBEGGIE | FS |  |  |  | 0.779 | 1.2411 | 4.1013 | 4.0268 | 3.9062 | 3.7822 | 3.6542 | 3.5458 | 3.3919 | 3.2244 | 3.0741 | 2.8327 | 1.8819 | 1.0427 | 0.52437 | 2.8955 | 5.5581 | 5.5119 | 5.439 | 5.3607 | 5.2826 | 5.2077 | 5.1142 | 5.0077 | 4.9167 | 4.739 | 4.0379 | 3.3636 | 2.7998 | 1.6845 | 4.6673 | 4.6033 | 4.5049 | 4.4003 | 4.2967 | 4.2 | 4.0664 | 3.9171 | 3.7866 | 3.566 | 2.6864 | 1.9091 | 1.452
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 1.986 | 10.7923 | 9.9843 | 9.0569 | 7.9857 | 6.6349 | 5.1875 | 3.4947 | 1.6917 | 0.20469 | -1.1261 | -2.3852 | -4.9484 | -6.1297 | -7.0325 | 12.1975 | 11.3886 | 10.6965 | 9.9281 | 8.8926 | 7.7756 | 6.4667 | 5.2482 | 4.1076 | 3.262 | 2.3967 | 0.70056 | -0.21639 | -1.4847 | 13.0483 | 12.2814 | 11.421 | 10.4246 | 9.1663 | 7.8211 | 6.2406 | 4.5559 | 3.18 | 1.9377 | 0.76097 | -1.6063 | -2.5823 | -3.3985
|  | BALDOVIE | CT |  |  |  | 1.986 | 11.0063 | 10.3117 | 9.4559 | 8.3326 | 6.8609 | 5.3713 | 3.7601 | 2.0152 | 0.74326 | -0.61026 | -1.7971 | -4.7672 | -6.1297 | -7.0325 | 12.4408 | 11.7628 | 11.1207 | 10.2446 | 9.0912 | 7.8701 | 6.6839 | 5.4992 | 4.4481 | 3.4686 | 2.5672 | 0.70056 | -0.21639 | -1.2712 | 13.2481 | 12.5891 | 11.7946 | 10.7469 | 9.3725 | 7.994 | 6.4941 | 4.8649 | 3.6989 | 2.4372 | 1.3287 | -1.3805 | -2.5823 | -3.3985
|  | BALDOVIE | LW |  |  |  | 1.986 | 10.7923 | 9.9843 | 9.0569 | 7.9857 | 6.6349 | 5.1875 | 3.4947 | 1.6917 | 0.20469 | -1.1261 | -2.3852 | -4.9484 | -5.6357 | -6.4136 | 12.1975 | 11.3886 | 10.6965 | 9.9281 | 8.8926 | 7.7756 | 6.4667 | 5.2482 | 4.1076 | 3.262 | 2.3967 | 0.92033 | 0.60946 | 0.26406 | 13.0483 | 12.2814 | 11.421 | 10.4246 | 9.1663 | 7.8211 | 6.2406 | 4.5559 | 3.18 | 1.9377 | 0.76097 | -1.6063 | -2.223 | -2.9487
|  | BALDOVIE | ST |  |  |  | 1.986 | 11.074 | 10.4853 | 9.9636 | 9.2741 | 8.2859 | 7.2987 | 6.34 | 5.3314 | 4.2091 | 3.2343 | 2.3207 | 0.33626 | -0.93403 | -2.1878 | 12.4694 | 11.8478 | 11.2609 | 10.4943 | 9.4109 | 8.1975 | 7.0852 | 5.9935 | 4.8553 | 3.8564 | 2.941 | 1.6351 | 1.2818 | 0.43281 | 13.314 | 12.7593 | 12.2651 | 11.5586 | 10.5364 | 9.4666 | 8.4701 | 7.4437 | 6.3676 | 5.4389 | 4.5822 | 3.1479 | 1.9999 | 0.89243
|  | BALDOVIE | FS |  |  |  | 1.986 | 11.3354 | 10.8675 | 10.4289 | 9.8738 | 9.0084 | 7.9553 | 7.273 | 6.4891 | 5.6025 | 4.8776 | 4.0279 | 0.59034 | -1.7217 | -3.4958 | 12.7431 | 12.2404 | 11.8086 | 11.227 | 10.3153 | 9.0828 | 8.3185 | 7.5707 | 6.7233 | 6.0098 | 5.1867 | 2.3739 | 0.8843 | -1.4847 | 13.5576 | 13.1161 | 12.7034 | 12.1817 | 11.3649 | 10.2887 | 9.6101 | 8.9208 | 8.1384 | 7.4784 | 6.6778 | 3.4724 | 1.3425 | -0.24863
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 0.472 | 5.219 | 5.054 | 4.8218 | 4.481 | 4.1178 | 3.7297 | 3.273 | 3.0294 | 2.8301 | 2.6645 | 2.519 | 2.0408 | 1.653 | 1.2352 | 8.4837 | 8.4061 | 8.3358 | 8.2446 | 8.068 | 7.8362 | 7.5398 | 7.3303 | 7.1518 | 6.9637 | 6.7934 | 6.381 | 6.172 | 5.8525 | 6.9469 | 6.799 | 6.571 | 6.2655 | 5.9477 | 5.5794 | 5.1613 | 4.9352 | 4.7525 | 4.577 | 4.3584 | 3.7646 | 3.4156 | 2.9491
|  | BALLATER | CT |  |  |  | 0.472 | 5.219 | 5.054 | 4.8235 | 4.481 | 4.1178 | 3.7297 | 3.273 | 3.0334 | 2.8844 | 2.7551 | 2.6548 | 2.2211 | 1.9253 | 1.5942 | 8.4838 | 8.4379 | 8.3985 | 8.2992 | 8.1059 | 7.9245 | 7.6514 | 7.4379 | 7.3241 | 7.166 | 7.0203 | 6.5919 | 6.4146 | 6.1336 | 6.9469 | 6.799 | 6.5935 | 6.2799 | 5.9557 | 5.6111 | 5.1955 | 4.9772 | 4.8422 | 4.7197 | 4.6134 | 4.0562 | 3.8002 | 3.4677
|  | BALLATER | LW |  |  |  | 0.472 | 5.2439 | 5.0753 | 4.8218 | 4.4874 | 4.1346 | 3.7305 | 3.2797 | 3.0294 | 2.8301 | 2.6645 | 2.519 | 2.0408 | 1.653 | 1.2352 | 8.4837 | 8.4061 | 8.3358 | 8.2446 | 8.068 | 7.8362 | 7.5398 | 7.3303 | 7.1518 | 6.9637 | 6.7934 | 6.381 | 6.172 | 5.8525 | 6.9743 | 6.8077 | 6.571 | 6.2655 | 5.9477 | 5.5794 | 5.1613 | 4.9352 | 4.7525 | 4.577 | 4.3584 | 3.7646 | 3.4156 | 2.9491
|  | BALLATER | ST |  |  |  | 0.472 | 5.2591 | 5.1468 | 4.9797 | 4.7905 | 4.6057 | 4.406 | 4.2127 | 4.018 | 3.8368 | 3.6499 | 3.4587 | 2.6684 | 2.271 | 2.0374 | 8.4968 | 8.4749 | 8.4258 | 8.3719 | 8.3213 | 8.2626 | 8.1658 | 8.0314 | 7.9181 | 7.7764 | 7.6283 | 6.8969 | 6.5469 | 6.2724 | 6.993 | 6.8848 | 6.7289 | 6.5587 | 6.3945 | 6.2176 | 6.0447 | 5.8697 | 5.706 | 5.5337 | 5.3578 | 4.5977 | 4.1723 | 3.9181
|  | BALLATER | FS |  |  |  | 0.472 | 5.3213 | 5.2577 | 5.2261 | 5.1611 | 5.0857 | 5.0154 | 4.9339 | 4.7818 | 4.6218 | 4.485 | 4.3373 | 3.5828 | 2.7803 | 2.4054 | 8.5003 | 8.4847 | 8.4618 | 8.4272 | 8.386 | 8.3452 | 8.2926 | 8.2367 | 8.1677 | 8.1088 | 8.0209 | 7.4107 | 6.7894 | 6.3852 | 7.0631 | 6.9948 | 6.9532 | 6.8928 | 6.8241 | 6.7604 | 6.6833 | 6.5468 | 6.4001 | 6.2751 | 6.1413 | 5.4509 | 4.6566 | 4.2873
| CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.012 | 0.41503 | 0.40309 | 0.39426 | 0.3838 | 0.36803 | 0.33545 | 0.3042 | 0.28372 | 0.26935 | 0.26318 | 0.24353 | 0.20455 | 0.19085 | 0.16687 | 0.64546 | 0.65229 | 0.64426 | 0.63463 | 0.62498 | 0.61269 | 0.60225 | 0.59413 | 0.58853 | 0.58757 | 0.57568 | 0.54468 | 0.53826 | 0.51542 | 0.42659 | 0.43652 | 0.4262 | 0.40595 | 0.38411 | 0.35836 | 0.33335 | 0.32173 | 0.31403 | 0.31195 | 0.30721 | 0.28866 | 0.27639 | 0.26101
|  | BALLIEKINE | CT |  |  |  | 0.012 | 0.41503 | 0.40309 | 0.39426 | 0.3838 | 0.36803 | 0.33545 | 0.3042 | 0.28372 | 0.26935 | 0.26318 | 0.25155 | 0.21758 | 0.20466 | 0.18391 | 0.65816 | 0.65229 | 0.64426 | 0.63463 | 0.62498 | 0.61269 | 0.60225 | 0.59413 | 0.58853 | 0.58757 | 0.58323 | 0.54854 | 0.53826 | 0.51542 | 0.4405 | 0.43652 | 0.4262 | 0.40595 | 0.38411 | 0.35836 | 0.33335 | 0.32173 | 0.31403 | 0.31195 | 0.30721 | 0.2938 | 0.28313 | 0.26858
|  | BALLIEKINE | LW |  |  |  | 0.012 | 0.4154 | 0.4048 | 0.39807 | 0.38585 | 0.38171 | 0.3513 | 0.32298 | 0.30155 | 0.27599 | 0.26362 | 0.24353 | 0.20455 | 0.19085 | 0.16687 | 0.65887 | 0.6537 | 0.64715 | 0.63824 | 0.63136 | 0.61864 | 0.60931 | 0.60098 | 0.59096 | 0.58798 | 0.57568 | 0.54468 | 0.54094 | 0.52749 | 0.44052 | 0.43688 | 0.43198 | 0.41394 | 0.39693 | 0.37232 | 0.35051 | 0.3379 | 0.32355 | 0.3174 | 0.3084 | 0.28866 | 0.27639 | 0.26101
|  | BALLIEKINE | ST |  |  |  | 0.012 | 0.41562 | 0.41556 | 0.40998 | 0.40529 | 0.40048 | 0.39228 | 0.37972 | 0.37296 | 0.35451 | 0.35067 | 0.33243 | 0.26105 | 0.25058 | 0.25062 | 0.64546 | 0.65724 | 0.65408 | 0.6511 | 0.64822 | 0.64414 | 0.63871 | 0.6353 | 0.62808 | 0.62564 | 0.61848 | 0.58856 | 0.57296 | 0.56173 | 0.42659 | 0.44053 | 0.43879 | 0.43712 | 0.43348 | 0.42642 | 0.41768 | 0.41084 | 0.39979 | 0.39417 | 0.3831 | 0.34048 | 0.33007 | 0.3301
|  | BALLIEKINE | FS |  |  |  | 0.012 | 0.41722 | 0.4144 | 0.40963 | 0.40498 | 0.40305 | 0.39975 | 0.39334 | 0.38276 | 0.37712 | 0.36451 | 0.35057 | 0.30545 | 0.25495 | 0.25298 | 0.64845 | 0.65668 | 0.6578 | 0.65666 | 0.65622 | 0.65554 | 0.65376 | 0.64921 | 0.64638 | 0.64124 | 0.63567 | 0.61804 | 0.56466 | 0.5281 | 0.42821 | 0.43828 | 0.43889 | 0.43745 | 0.43658 | 0.43539 | 0.43329 | 0.42989 | 0.42766 | 0.4235 | 0.41886 | 0.38469 | 0.3344 | 0.33246
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 0.476 | 7.3387 | 7.2539 | 7.1193 | 6.9773 | 6.8253 | 6.6588 | 6.4346 | 6.3093 | 6.1938 | 6.0739 | 5.9664 | 5.6352 | 5.4247 | 5.2049 | 7.6512 | 7.5914 | 7.5307 | 7.4663 | 7.4086 | 7.32 | 7.207 | 7.1267 | 7.035 | 6.944 | 6.859 | 6.6156 | 6.3879 | 6.2752 | 7.2596 | 7.1752 | 7.0467 | 6.9128 | 6.777 | 6.6125 | 6.4056 | 6.2793 | 6.1674 | 6.0428 | 5.9305 | 5.6195 | 5.4115 | 5.214
|  | BALLINDALLOCH | CT |  |  |  | 0.476 | 7.3387 | 7.2539 | 7.1325 | 6.986 | 6.8253 | 6.6694 | 6.4391 | 6.3166 | 6.2222 | 6.1586 | 6.0845 | 5.8104 | 5.6657 | 5.5114 | 7.6512 | 7.611 | 7.5646 | 7.4748 | 7.412 | 7.3486 | 7.2446 | 7.1617 | 7.0989 | 7.0439 | 6.9882 | 6.855 | 6.8228 | 6.7612 | 7.2596 | 7.1817 | 7.0726 | 6.93 | 6.784 | 6.6513 | 6.4549 | 6.3282 | 6.2302 | 6.169 | 6.0842 | 5.8215 | 5.7079 | 5.5724
|  | BALLINDALLOCH | LW |  |  |  | 0.476 | 7.3513 | 7.2554 | 7.1193 | 6.9773 | 6.83 | 6.6588 | 6.4346 | 6.3093 | 6.1938 | 6.0739 | 5.9664 | 5.6352 | 5.4247 | 5.2049 | 7.652 | 7.5914 | 7.5307 | 7.4663 | 7.4086 | 7.32 | 7.207 | 7.1267 | 7.035 | 6.944 | 6.859 | 6.6264 | 6.5128 | 6.4079 | 7.2701 | 7.1752 | 7.0467 | 6.9128 | 6.777 | 6.6125 | 6.4056 | 6.2793 | 6.1674 | 6.0428 | 5.9305 | 5.6195 | 5.4321 | 5.214
|  | BALLINDALLOCH | ST |  |  |  | 0.476 | 7.3664 | 7.3115 | 7.2243 | 7.1446 | 7.0538 | 6.972 | 6.8738 | 6.7767 | 6.6943 | 6.5846 | 6.4663 | 5.9277 | 5.6615 | 5.5053 | 7.6619 | 7.645 | 7.6052 | 7.5683 | 7.5287 | 7.4888 | 7.439 | 7.3792 | 7.3068 | 7.2263 | 7.1367 | 6.6156 | 6.3879 | 6.2752 | 7.2847 | 7.2369 | 7.156 | 7.0817 | 6.9994 | 6.9253 | 6.8359 | 6.7451 | 6.6641 | 6.5652 | 6.4559 | 5.7366 | 5.4115 | 5.253
|  | BALLINDALLOCH | FS |  |  |  | 0.476 | 7.401 | 7.3662 | 7.3348 | 7.2929 | 7.2651 | 7.22 | 7.1796 | 7.1054 | 7.0183 | 6.9592 | 6.8777 | 6.4724 | 6.0008 | 5.7851 | 7.6673 | 7.6573 | 7.6382 | 7.6149 | 7.5909 | 7.5605 | 7.5244 | 7.4845 | 7.4319 | 7.3827 | 7.3315 | 7.0055 | 6.6831 | 6.4711 | 7.314 | 7.2839 | 7.254 | 7.2148 | 7.1857 | 7.1421 | 7.1008 | 7.0317 | 6.9496 | 6.8903 | 6.8143 | 6.3718 | 5.8319 | 5.5208
| CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0.046 | 1.7135 | 1.695 | 1.6701 | 1.6372 | 1.5879 | 1.523 | 1.4528 | 1.4208 | 1.3981 | 1.3854 | 1.3446 | 1.2669 | 1.2396 | 1.1979 | 1.604 | 1.5908 | 1.5737 | 1.552 | 1.5328 | 1.5078 | 1.4819 | 1.4654 | 1.4538 | 1.449 | 1.4326 | 1.3812 | 1.369 | 1.3339 | 1.6115 | 1.5943 | 1.5714 | 1.5409 | 1.5142 | 1.4835 | 1.4485 | 1.4157 | 1.3815 | 1.3536 | 1.3187 | 1.2437 | 1.2192 | 1.18
|  | BALLURE | CT |  |  |  | 0.046 | 1.7138 | 1.695 | 1.6701 | 1.6372 | 1.5879 | 1.523 | 1.4528 | 1.4208 | 1.3981 | 1.3895 | 1.3637 | 1.2899 | 1.2636 | 1.2291 | 1.6043 | 1.5908 | 1.5737 | 1.552 | 1.5328 | 1.5078 | 1.4819 | 1.4654 | 1.4538 | 1.4524 | 1.4432 | 1.3905 | 1.369 | 1.3339 | 1.6121 | 1.5943 | 1.5714 | 1.5409 | 1.5142 | 1.4835 | 1.4485 | 1.4157 | 1.3815 | 1.3694 | 1.3389 | 1.2665 | 1.2427 | 1.2108
|  | BALLURE | LW |  |  |  | 0.046 | 1.7135 | 1.6971 | 1.6764 | 1.6493 | 1.6174 | 1.5536 | 1.4895 | 1.4544 | 1.4257 | 1.3854 | 1.3446 | 1.2669 | 1.2396 | 1.1979 | 1.604 | 1.594 | 1.5795 | 1.5593 | 1.5448 | 1.519 | 1.4951 | 1.4781 | 1.4674 | 1.449 | 1.4326 | 1.3812 | 1.3691 | 1.3439 | 1.6115 | 1.5961 | 1.5772 | 1.5521 | 1.5302 | 1.4944 | 1.4569 | 1.4242 | 1.3894 | 1.3536 | 1.3187 | 1.2437 | 1.2192 | 1.18
|  | BALLURE | ST |  |  |  | 0.046 | 1.7198 | 1.7101 | 1.699 | 1.6846 | 1.6697 | 1.6513 | 1.6302 | 1.6122 | 1.5841 | 1.5576 | 1.5247 | 1.3685 | 1.3202 | 1.311 | 1.6075 | 1.5994 | 1.5935 | 1.5842 | 1.5763 | 1.5652 | 1.5527 | 1.5458 | 1.5309 | 1.5206 | 1.5047 | 1.4395 | 1.4165 | 1.4002 | 1.6176 | 1.6087 | 1.5985 | 1.5852 | 1.5715 | 1.5543 | 1.5344 | 1.5175 | 1.4907 | 1.4657 | 1.4343 | 1.2848 | 1.2392 | 1.2311
|  | BALLURE | FS |  |  |  | 0.046 | 1.7244 | 1.7178 | 1.7117 | 1.7048 | 1.6967 | 1.6886 | 1.6775 | 1.6621 | 1.6472 | 1.6283 | 1.6075 | 1.4882 | 1.3645 | 1.2884 | 1.612 | 1.6065 | 1.6037 | 1.6005 | 1.5966 | 1.5938 | 1.5879 | 1.578 | 1.5721 | 1.5611 | 1.5493 | 1.4971 | 1.4036 | 1.3377 | 1.6218 | 1.6156 | 1.6099 | 1.6034 | 1.5957 | 1.5881 | 1.5775 | 1.5629 | 1.549 | 1.5311 | 1.5114 | 1.3981 | 1.2815 | 1.2086
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 0.152 | 3.5665 | 3.4344 | 3.0643 | 2.5709 | 2.0186 | 1.3761 | 0.45876 | -0.32409 | -1.174 | -1.6996 | -1.9418 | -2.5892 | -3.1734 | -3.5738 | 4.4072 | 4.3521 | 4.2454 | 4.0869 | 3.8362 | 3.5172 | 2.8973 | 2.3339 | 1.7169 | 1.3816 | 1.2463 | 0.97086 | 0.64245 | 0.29017 | 3.9343 | 3.8401 | 3.6174 | 3.3065 | 2.9427 | 2.5108 | 1.7396 | 1.0899 | 0.35915 | -0.12395 | -0.33674 | -0.89359 | -1.3989 | -1.7519
|  | BALMEDIE | CT |  |  |  | 0.152 | 3.5665 | 3.4344 | 3.0643 | 2.5709 | 2.0186 | 1.3761 | 0.45876 | -0.31029 | -1.0743 | -1.6242 | -1.9418 | -2.5892 | -3.1734 | -3.5738 | 4.4075 | 4.3521 | 4.2454 | 4.0869 | 3.8362 | 3.5172 | 2.9105 | 2.3722 | 1.8226 | 1.4467 | 1.2463 | 0.97086 | 0.64245 | 0.29017 | 3.9343 | 3.8401 | 3.6174 | 3.3065 | 2.9427 | 2.5108 | 1.7396 | 1.0899 | 0.4335 | -0.046616 | -0.33674 | -0.88627 | -1.3989 | -1.7519
|  | BALMEDIE | LW |  |  |  | 0.152 | 3.5719 | 3.4466 | 3.0942 | 2.622 | 2.0559 | 1.4224 | 0.48134 | -0.32409 | -1.174 | -1.6996 | -1.7375 | -2.5773 | -2.9942 | -3.3876 | 4.4072 | 4.3586 | 4.2754 | 4.1545 | 3.8775 | 3.5545 | 2.8973 | 2.3339 | 1.7169 | 1.3816 | 1.4403 | 1.0152 | 0.8383 | 0.6595 | 3.9368 | 3.8513 | 3.6579 | 3.3939 | 3.0296 | 2.6117 | 1.8007 | 1.1112 | 0.35915 | -0.12395 | -0.17327 | -0.89359 | -1.2607 | -1.6091
|  | BALMEDIE | ST |  |  |  | 0.152 | 3.6138 | 3.5401 | 3.3453 | 3.1197 | 2.8511 | 2.5626 | 2.0201 | 1.5232 | 0.94673 | 0.59211 | 0.36838 | -0.41977 | -1.1151 | -1.6898 | 4.4233 | 4.4024 | 4.3427 | 4.2698 | 4.1799 | 4.0749 | 3.6025 | 3.1653 | 2.6514 | 2.3454 | 2.1903 | 1.7323 | 1.4084 | 0.99422 | 3.9679 | 3.9234 | 3.8193 | 3.6999 | 3.5556 | 3.3964 | 2.9118 | 2.4579 | 1.925 | 1.5869 | 1.388 | 0.6367 | 0.18155 | -0.2173
|  | BALMEDIE | FS |  |  |  | 0.152 | 3.6356 | 3.5725 | 3.4445 | 3.2904 | 3.1016 | 2.926 | 2.5485 | 2.1968 | 1.7481 | 1.4043 | 1.1095 | -0.13708 | -0.79669 | -1.5347 | 4.4281 | 4.4103 | 4.3685 | 4.3156 | 4.2494 | 4.1861 | 3.8725 | 3.6026 | 3.2565 | 3.0334 | 2.849 | 1.9189 | 1.4057 | 0.67883 | 3.9806 | 3.9447 | 3.8776 | 3.7996 | 3.7033 | 3.6098 | 3.2888 | 2.9935 | 2.6172 | 2.3504 | 2.1227 | 1.0662 | 0.42762 | -0.20545
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 0.001 | 9.5104 | 9.3915 | 9.1726 | 8.9059 | 8.6298 | 8.2561 | 7.8094 | 7.388 | 6.9319 | 6.4975 | 6.0989 | 4.9489 | 4.9475 | 4.6334 | 9.0789 | 9.0059 | 8.8959 | 8.7634 | 8.6292 | 8.4449 | 8.2163 | 8.0107 | 7.7822 | 7.5615 | 7.3583 | 6.5682 | 5.6536 | 3.1289 | 9.3801 | 9.3057 | 9.1265 | 8.8726 | 8.6192 | 8.2423 | 7.7792 | 7.3326 | 6.8264 | 6.3374 | 5.8866 | 4.6847 | 4.6248 | 4.1336
|  | BALNAGASK | CT |  |  |  | 0.001 | 9.5446 | 9.4384 | 9.272 | 9.0405 | 8.7947 | 8.5263 | 8.1778 | 7.748 | 7.3808 | 7.0258 | 6.7162 | 5.4874 | 5.1258 | 4.8486 | 9.0826 | 9.0119 | 8.915 | 8.7692 | 8.6292 | 8.475 | 8.2683 | 8.0425 | 7.8437 | 7.6437 | 7.4619 | 6.5682 | 5.8478 | 4.6764 | 9.3981 | 9.3425 | 9.1883 | 8.9487 | 8.6924 | 8.4239 | 8.0522 | 7.6276 | 7.2671 | 6.9005 | 6.5747 | 5.4225 | 5.1464 | 4.7984
|  | BALNAGASK | LW |  |  |  | 0.001 | 9.5104 | 9.3915 | 9.1726 | 8.9059 | 8.6298 | 8.2561 | 7.8094 | 7.388 | 6.9319 | 6.4975 | 6.0989 | 4.9489 | 4.9475 | 4.6334 | 9.0789 | 9.0059 | 8.8959 | 8.7634 | 8.6322 | 8.4449 | 8.2163 | 8.0107 | 7.7822 | 7.5615 | 7.3583 | 6.7587 | 6.6908 | 6.4035 | 9.3801 | 9.3057 | 9.1265 | 8.8726 | 8.6192 | 8.2423 | 7.7792 | 7.3326 | 6.8264 | 6.3374 | 5.8866 | 4.6847 | 4.6248 | 4.1336
|  | BALNAGASK | ST |  |  |  | 0.001 | 9.5701 | 9.5237 | 9.4764 | 9.4223 | 9.3583 | 9.2749 | 9.1931 | 9.0873 | 8.957 | 8.8123 | 8.6523 | 7.8272 | 7.396 | 6.9471 | 9.0982 | 9.0629 | 9.0168 | 8.9674 | 8.9123 | 8.8456 | 8.7767 | 8.6908 | 8.5871 | 8.4723 | 8.3449 | 7.5224 | 6.74 | 5.534 | 9.4134 | 9.387 | 9.3579 | 9.3273 | 9.2648 | 9.1586 | 9.0504 | 8.9125 | 8.7419 | 8.5518 | 8.3418 | 7.2779 | 6.8455 | 6.525
|  | BALNAGASK | FS |  |  |  | 0.001 | 9.6094 | 9.5981 | 9.5695 | 9.5208 | 9.4549 | 9.3858 | 9.2999 | 9.2058 | 9.0837 | 8.9589 | 8.8363 | 7.6884 | 6.5625 | 5.7298 | 9.1217 | 9.0926 | 9.0548 | 9.009 | 8.9511 | 8.8871 | 8.8012 | 8.705 | 8.5868 | 8.4656 | 8.3442 | 7.3518 | 5.6536 | 3.1289 | 9.4264 | 9.4148 | 9.4005 | 9.3814 | 9.3527 | 9.2849 | 9.1824 | 9.0817 | 8.942 | 8.7988 | 8.6591 | 7.5165 | 6.4509 | 5.7255
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 2.616 | 1.1291 | 0.38043 | -0.67964 | -1.8902 | -3.0192 | -4.4078 | -5.8476 | -6.7553 | -7.5957 | -8.3618 | -9.0633 | -11.5042 | -13.2732 | -15.1866 | 4.207 | 3.662 | 3.0934 | 2.4401 | 1.9115 | 1.1464 | -0.025124 | -0.48532 | -0.90087 | -1.297 | -1.6704 | -3.3408 | -4.8907 | -6.6559 | 3.0218 | 2.2813 | 1.2512 | 0.091336 | -0.96363 | -2.3257 | -3.7442 | -4.5894 | -5.4012 | -6.1431 | -6.823 | -9.2322 | -11.111 | -13.1959
|  | BANCHORY | CT |  |  |  | 2.616 | 1.1336 | 0.68861 | -0.053948 | -1.2781 | -2.3338 | -3.4991 | -4.7901 | -5.6904 | -6.4112 | -7.0573 | -7.6184 | -9.9105 | -11.3702 | -12.6088 | 4.2151 | 4.0492 | 3.8658 | 3.1352 | 2.7517 | 2.2969 | 1.4016 | 0.92989 | 0.56369 | 0.22539 | -0.070827 | -1.481 | -2.5168 | -3.7459 | 3.0347 | 2.664 | 2.0344 | 0.8618 | -0.081218 | -1.1349 | -2.352 | -3.1777 | -3.8491 | -4.4753 | -5.0294 | -7.1747 | -8.5365 | -9.7538
|  | BANCHORY | LW |  |  |  | 2.616 | 1.1291 | 0.38043 | -0.67964 | -1.8902 | -3.0192 | -4.4078 | -5.8476 | -6.7553 | -7.5957 | -8.3618 | -9.0633 | -11.5042 | -13.2732 | -15.1866 | 4.207 | 3.662 | 3.0934 | 2.4401 | 1.9115 | 1.1464 | -0.025124 | -0.48532 | -0.90087 | -1.297 | -1.6704 | -3.3408 | -4.8907 | -6.6559 | 3.0218 | 2.2813 | 1.2512 | 0.091336 | -0.96363 | -2.3257 | -3.7442 | -4.5894 | -5.4012 | -6.1431 | -6.823 | -9.2322 | -11.111 | -13.1959
|  | BANCHORY | ST |  |  |  | 2.616 | 1.2579 | 0.98379 | 0.40721 | -0.12739 | -0.61354 | -1.054 | -1.6281 | -2.1002 | -2.567 | -2.7139 | -3.0971 | -5.9914 | -8.3666 | -10.5624 | 4.2502 | 4.1662 | 3.8082 | 3.5226 | 3.291 | 3.0812 | 2.64 | 2.3017 | 1.9794 | 1.7563 | 1.4766 | -0.94685 | -2.879 | -4.5349 | 3.0678 | 2.9557 | 2.3881 | 1.8905 | 1.4393 | 1.039 | 0.50334 | 0.040536 | -0.434 | -0.56731 | -0.95164 | -4.013 | -6.4892 | -8.73
|  | BANCHORY | FS |  |  |  | 2.616 | 1.3642 | 1.1547 | 0.8741 | 0.53409 | 0.21795 | -0.11345 | -0.61374 | -1.0395 | -1.5291 | -2.0226 | -2.4488 | -4.2438 | -6.4237 | -8.2538 | 4.2715 | 4.2143 | 4.0704 | 3.9041 | 3.7299 | 3.545 | 3.1445 | 2.8992 | 2.5994 | 2.2915 | 2.0725 | 0.99685 | -0.30044 | -2.1621 | 3.0945 | 3.0246 | 2.8413 | 2.5281 | 2.2371 | 1.9162 | 1.4188 | 1.0097 | 0.5272 | 0.039629 | -0.36128 | -2.022 | -4.0405 | -5.6971
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 1.695 | -4.3351 | -4.4095 | -4.5501 | -4.7271 | -4.8949 | -5.0822 | -5.2931 | -5.4099 | -5.4587 | -5.5813 | -5.6906 | -5.9515 | -6.059 | -6.2134 | -3.7646 | -3.7891 | -3.8212 | -3.8672 | -3.9621 | -4.0704 | -4.1966 | -4.2807 | -4.3372 | -4.4348 | -4.5229 | -4.7138 | -4.7779 | -4.8838 | -4.2062 | -4.2389 | -4.281 | -4.3742 | -4.548 | -4.7326 | -4.9399 | -5.0162 | -5.0491 | -5.144 | -5.2437 | -5.4983 | -5.6154 | -5.7723
|  | BARCALDINE | CT |  |  |  | 1.695 | -4.3351 | -4.4095 | -4.5501 | -4.7271 | -4.8949 | -5.0822 | -5.2931 | -5.4099 | -5.4549 | -5.5364 | -5.6077 | -5.8074 | -5.887 | -6.0012 | -3.7642 | -3.7815 | -3.8098 | -3.8672 | -3.9621 | -4.0704 | -4.1966 | -4.2807 | -4.3147 | -4.377 | -4.4368 | -4.6145 | -4.6832 | -4.8106 | -4.2053 | -4.2315 | -4.273 | -4.3742 | -4.548 | -4.7326 | -4.9399 | -5.0162 | -5.0491 | -5.1081 | -5.1685 | -5.3511 | -5.4344 | -5.5502
|  | BARCALDINE | LW |  |  |  | 1.695 | -4.3274 | -4.4029 | -4.542 | -4.6925 | -4.8551 | -5.0294 | -5.2291 | -5.3522 | -5.4587 | -5.5813 | -5.6906 | -5.9515 | -6.059 | -6.2134 | -3.7646 | -3.7891 | -3.8212 | -3.8562 | -3.9462 | -4.0519 | -4.1759 | -4.2612 | -4.3372 | -4.4348 | -4.5229 | -4.7138 | -4.7779 | -4.8838 | -4.2062 | -4.2389 | -4.281 | -4.3307 | -4.4917 | -4.6611 | -4.8504 | -4.936 | -5.032 | -5.144 | -5.2437 | -5.4983 | -5.6154 | -5.7723
|  | BARCALDINE | ST |  |  |  | 1.695 | -4.3051 | -4.353 | -4.4276 | -4.5001 | -4.586 | -4.6639 | -4.7471 | -4.8103 | -4.9093 | -5.0043 | -5.1135 | -5.5529 | -5.7092 | -5.7721 | -3.7566 | -3.7625 | -3.7822 | -3.8004 | -3.8214 | -3.8433 | -3.8859 | -3.9272 | -3.9932 | -4.0561 | -4.1297 | -4.4702 | -4.6101 | -4.7216 | -4.1943 | -4.203 | -4.2283 | -4.2537 | -4.2835 | -4.3145 | -4.375 | -4.4355 | -4.5171 | -4.5962 | -4.6862 | -5.1098 | -5.2739 | -5.3479
|  | BARCALDINE | FS |  |  |  | 1.695 | -4.2778 | -4.3071 | -4.3412 | -4.3866 | -4.4192 | -4.4716 | -4.5047 | -4.5707 | -4.6275 | -4.7025 | -4.7741 | -5.157 | -5.5517 | -5.7037 | -3.7545 | -3.7579 | -3.7697 | -3.7846 | -3.797 | -3.8163 | -3.8308 | -3.8492 | -3.869 | -3.899 | -3.948 | -4.2313 | -4.5451 | -4.775 | -4.1911 | -4.196 | -4.2116 | -4.2317 | -4.2494 | -4.2761 | -4.2952 | -4.3207 | -4.3489 | -4.3826 | -4.4153 | -4.7114 | -5.0986 | -5.2572
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.196 | 0.45865 | 0.40969 | 0.18868 | -0.01134 | -0.22675 | -0.50138 | -0.78023 | -1.0567 | -1.3385 | -1.5546 | -1.774 | -2.4586 | -2.9623 | -3.2666 | 1.114 | 1.0434 | 0.91435 | 0.82009 | 0.7237 | 0.57038 | 0.42593 | 0.27185 | 0.094086 | -0.013016 | -0.14646 | -0.46146 | -0.66665 | -0.91845 | 0.76327 | 0.71669 | 0.62934 | 0.57251 | 0.51886 | 0.42243 | 0.18612 | -0.066072 | -0.34121 | -0.54091 | -0.75347 | -1.3575 | -1.6958 | -2.0056
|  | BARVAS | CT |  |  |  | 0.196 | 0.46804 | 0.41647 | 0.23149 | 0.015709 | -0.21824 | -0.48288 | -0.77228 | -1.0408 | -1.2629 | -1.4381 | -1.613 | -2.432 | -2.9623 | -3.2666 | 1.1185 | 1.0585 | 0.96551 | 0.85377 | 0.74169 | 0.61634 | 0.48054 | 0.32297 | 0.19775 | 0.11069 | -0.0053739 | -0.41173 | -0.66665 | -0.91845 | 0.77235 | 0.74037 | 0.67999 | 0.61178 | 0.55656 | 0.46461 | 0.22968 | -0.021225 | -0.22775 | -0.38895 | -0.56121 | -1.2708 | -1.6958 | -1.9643
|  | BARVAS | LW |  |  |  | 0.196 | 0.45865 | 0.40969 | 0.18868 | -0.01134 | -0.22675 | -0.50138 | -0.78023 | -1.0567 | -1.3385 | -1.5546 | -1.774 | -2.4586 | -2.8311 | -3.2093 | 1.114 | 1.0434 | 0.91435 | 0.82009 | 0.7237 | 0.57038 | 0.42593 | 0.27185 | 0.094086 | -0.013016 | -0.14646 | -0.46146 | -0.62536 | -0.82321 | 0.76327 | 0.71669 | 0.62934 | 0.57251 | 0.51886 | 0.42243 | 0.18612 | -0.066072 | -0.34121 | -0.54091 | -0.75347 | -1.3575 | -1.6682 | -2.0056
|  | BARVAS | ST |  |  |  | 0.196 | 0.48033 | 0.46233 | 0.3818 | 0.30089 | 0.21372 | 0.13821 | 0.049606 | -0.037916 | -0.13808 | -0.20941 | -0.31065 | -1.0265 | -1.6099 | -2.1137 | 1.1431 | 1.1096 | 1.0401 | 0.99074 | 0.93373 | 0.89136 | 0.83258 | 0.76264 | 0.67631 | 0.62263 | 0.53399 | 0.025041 | -0.28634 | -0.57716 | 0.78417 | 0.76683 | 0.71322 | 0.68355 | 0.65164 | 0.62359 | 0.58939 | 0.54841 | 0.49822 | 0.45935 | 0.40622 | -0.19777 | -0.6392 | -1.0505
|  | BARVAS | FS |  |  |  | 0.196 | 0.4921 | 0.47946 | 0.44601 | 0.41845 | 0.36974 | 0.31209 | 0.26133 | 0.16463 | 0.062457 | -0.043578 | -0.12434 | -0.77783 | -1.5161 | -2.1228 | 1.1585 | 1.1334 | 1.0892 | 1.0502 | 1.0168 | 0.97221 | 0.93522 | 0.87199 | 0.80145 | 0.72567 | 0.67905 | 0.24697 | -0.23677 | -0.69955 | 0.79529 | 0.78328 | 0.75028 | 0.73076 | 0.71068 | 0.68694 | 0.66085 | 0.62852 | 0.59037 | 0.55077 | 0.523 | 0.09778 | -0.5329 | -1.0045
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 1.6 | 0.0052901 | -0.47205 | 12.3673 | 11.1946 | 10.049 | 8.7345 | 7.1015 | 5.8442 | 4.4902 | 2.3318 | 0.42509 | -3.8205 | -6.1709 | -7.1574 | 3.8915 | 3.5779 | 16.1056 | 15.3847 | 14.6295 | 13.7449 | 12.6511 | 11.7766 | 10.7407 | 8.9917 | 7.4334 | 4.1335 | 2.3037 | 1.183 | 1.9073 | 1.6346 | 14.5583 | 13.5151 | 12.3998 | 11.11 | 9.5347 | 8.3124 | 6.9316 | 4.825 | 2.9514 | -1.4047 | -3.6917 | -4.5686
|  | BATTERY POINT | CT |  |  |  | 1.6 | 0.0052901 | -0.47205 | 12.3673 | 11.1946 | 10.049 | 8.7345 | 7.1015 | 5.8442 | 4.5461 | 2.5255 | 0.79506 | -3.7643 | -6.1709 | -7.1574 | 3.8915 | 3.5779 | 16.1056 | 15.3847 | 14.6295 | 13.7449 | 12.6511 | 11.7766 | 10.8186 | 9.0937 | 7.5978 | 4.1335 | 2.3037 | 1.4138 | 1.9242 | 1.6346 | 14.5583 | 13.5151 | 12.3998 | 11.11 | 9.5347 | 8.3124 | 7.0325 | 5.0375 | 3.3204 | -1.2871 | -3.6917 | -4.5686
|  | BATTERY POINT | LW |  |  |  | 1.6 | 0.007486 | -0.448 | 12.4236 | 11.3405 | 10.3039 | 9.0089 | 7.3927 | 6.0823 | 4.4902 | 2.3318 | 0.42509 | -3.8205 | -5.627 | -6.7694 | 3.893 | 3.5924 | 16.1608 | 15.5102 | 14.8312 | 13.9438 | 12.8057 | 11.8983 | 10.7407 | 8.9917 | 7.4334 | 4.1483 | 2.7407 | 2.1612 | 1.9073 | 1.6379 | 14.6509 | 13.6582 | 12.6419 | 11.362 | 9.778 | 8.4975 | 6.9316 | 4.825 | 2.9514 | -1.4047 | -3.3147 | -4.3436
|  | BATTERY POINT | ST |  |  |  | 1.6 | 0.15933 | -0.12393 | 13.1148 | 12.5159 | 11.9625 | 11.2941 | 10.5093 | 9.7054 | 8.7505 | 6.9813 | 5.3442 | -0.65741 | -3.2252 | -4.1438 | 3.9894 | 3.8315 | 16.5324 | 16.0941 | 15.6178 | 15.0221 | 14.3453 | 13.6237 | 12.7722 | 11.1192 | 9.6031 | 5.3512 | 3.2099 | 2.1169 | 1.9985 | 1.8693 | 14.9514 | 14.5233 | 14.0927 | 13.3989 | 12.6081 | 11.7852 | 10.8178 | 8.9511 | 7.0617 | 1.288 | -0.97404 | -2.398
|  | BATTERY POINT | FS |  |  |  | 1.6 | 0.291 | 0.086829 | 13.455 | 13.0474 | 12.6201 | 12.0967 | 11.5885 | 10.9334 | 10.2116 | 9.0846 | 7.9469 | 2.983 | -1.7805 | -4.4662 | 4.0437 | 3.9232 | 16.6831 | 16.368 | 16.0069 | 15.4819 | 15.0233 | 14.4853 | 13.8777 | 12.8777 | 11.8627 | 7.5775 | 3.5207 | 1.183 | 2.0457 | 1.9522 | 15.0842 | 14.7769 | 14.427 | 13.9518 | 13.5201 | 12.989 | 12.271 | 11.1428 | 9.9972 | 4.8902 | 0.12747 | -2.3321
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0.11 | -0.0010454 | -0.038249 | -0.090072 | -0.15974 | -0.21828 | -0.2995 | -0.38856 | -0.44899 | -0.49407 | -0.55113 | -0.60201 | -0.72176 | -0.78672 | -0.87168 | 0.26952 | 0.24352 | 0.21156 | 0.1699 | 0.14257 | 0.088133 | 0.032011 | -0.010498 | -0.045183 | -0.087863 | -0.12652 | -0.2159 | -0.26155 | -0.33117 | 0.17123 | 0.13591 | 0.08399 | 0.017107 | -0.031131 | -0.1152 | -0.20097 | -0.25954 | -0.30305 | -0.35878 | -0.40856 | -0.52553 | -0.59087 | -0.67778
|  | BETTYHILL | CT |  |  |  | 0.11 | -0.0010454 | -0.038249 | -0.08886 | -0.15937 | -0.21828 | -0.29483 | -0.3797 | -0.43873 | -0.48268 | -0.49989 | -0.53678 | -0.64555 | -0.69493 | -0.75381 | 0.26952 | 0.24823 | 0.22303 | 0.18083 | 0.14994 | 0.10859 | 0.05991 | 0.016419 | -0.016739 | -0.033598 | -0.06457 | -0.15317 | -0.19541 | -0.26282 | 0.17123 | 0.13652 | 0.09025 | 0.022806 | -0.031131 | -0.10232 | -0.18212 | -0.23984 | -0.28293 | -0.29976 | -0.33661 | -0.44199 | -0.48789 | -0.54461
|  | BETTYHILL | LW |  |  |  | 0.11 | 0.0042959 | -0.036027 | -0.090072 | -0.15974 | -0.21083 | -0.2995 | -0.38856 | -0.44899 | -0.49407 | -0.55113 | -0.60201 | -0.72176 | -0.78672 | -0.87168 | 0.27161 | 0.24352 | 0.21156 | 0.1699 | 0.14257 | 0.088133 | 0.032011 | -0.010498 | -0.045183 | -0.087863 | -0.12652 | -0.2159 | -0.26155 | -0.33117 | 0.17592 | 0.13591 | 0.08399 | 0.017107 | -0.030228 | -0.1152 | -0.20097 | -0.25954 | -0.30305 | -0.35878 | -0.40856 | -0.52553 | -0.59087 | -0.67778
|  | BETTYHILL | ST |  |  |  | 0.11 | 0.014953 | -0.011286 | -0.041565 | -0.079416 | -0.11279 | -0.15433 | -0.19976 | -0.22639 | -0.27546 | -0.31278 | -0.36337 | -0.57101 | -0.65183 | -0.70149 | 0.27911 | 0.2657 | 0.24847 | 0.22676 | 0.20883 | 0.18541 | 0.15892 | 0.1423 | 0.11016 | 0.085939 | 0.052425 | -0.1091 | -0.18637 | -0.25266 | 0.18648 | 0.16233 | 0.13362 | 0.097776 | 0.066814 | 0.027937 | -0.014815 | -0.039401 | -0.086353 | -0.1216 | -0.16987 | -0.37398 | -0.45574 | -0.50776
|  | BETTYHILL | FS |  |  |  | 0.11 | 0.02983 | 0.012209 | -0.00062081 | -0.014554 | -0.030697 | -0.044585 | -0.067478 | -0.10169 | -0.12501 | -0.16274 | -0.20018 | -0.36309 | -0.5468 | -0.61034 | 0.28494 | 0.27525 | 0.26612 | 0.2558 | 0.24383 | 0.23322 | 0.21543 | 0.19308 | 0.17624 | 0.15014 | 0.12526 | 0.0097651 | -0.12999 | -0.22821 | 0.19972 | 0.18337 | 0.17079 | 0.15712 | 0.14125 | 0.12764 | 0.10485 | 0.072119 | 0.050053 | 0.013621 | -0.021914 | -0.17526 | -0.34719 | -0.40667
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | YES | 0.023 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999
|  | BIDEN CLAN RAONAILD | CT |  |  |  | 0.023 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999
|  | BIDEN CLAN RAONAILD | LW |  |  |  | 0.023 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999
|  | BIDEN CLAN RAONAILD | ST |  |  |  | 0.023 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.084193 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999
|  | BIDEN CLAN RAONAILD | FS |  |  |  | 0.023 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.093193 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.084742 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999 | 0.088999
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 1.676 | 8.6414 | 17.6156 | 17.3759 | 17.1853 | 16.9778 | 16.7196 | 16.4273 | 16.139 | 15.8402 | 15.6076 | 15.3647 | 14.7121 | 14.3587 | 14.0671 | 7.9669 | 16.8763 | 16.7619 | 16.6798 | 16.5873 | 16.4464 | 16.2975 | 16.1394 | 15.96 | 15.8424 | 15.702 | 15.3836 | 15.2509 | 15.0902 | 8.2757 | 17.7889 | 17.676 | 17.5375 | 17.391 | 17.1933 | 16.9269 | 16.6723 | 16.4056 | 16.1972 | 15.9774 | 15.3861 | 15.0937 | 14.8248
|  | BILBOHALL | CT |  |  |  | 1.676 | 8.6414 | 17.6207 | 17.3974 | 17.2088 | 16.9922 | 16.7508 | 16.4512 | 16.1616 | 15.9245 | 15.6976 | 15.5194 | 14.7699 | 14.3587 | 14.0671 | 7.9669 | 16.8905 | 16.7917 | 16.7133 | 16.6143 | 16.4968 | 16.3559 | 16.1913 | 16.0595 | 15.9211 | 15.8311 | 15.4568 | 15.2896 | 15.1212 | 8.2757 | 17.8067 | 17.7074 | 17.5672 | 17.4193 | 17.232 | 16.963 | 16.7079 | 16.4981 | 16.2942 | 16.1373 | 15.4678 | 15.0937 | 14.8248
|  | BILBOHALL | LW |  |  |  | 1.676 | 8.6489 | 17.6156 | 17.3759 | 17.1853 | 16.9778 | 16.7196 | 16.4273 | 16.139 | 15.8402 | 15.6076 | 15.3647 | 14.7121 | 14.4166 | 14.1345 | 7.9691 | 16.8763 | 16.7619 | 16.6798 | 16.5873 | 16.4464 | 16.2975 | 16.1394 | 15.96 | 15.8424 | 15.702 | 15.3836 | 15.2509 | 15.0902 | 8.2757 | 17.7889 | 17.676 | 17.5375 | 17.391 | 17.1933 | 16.9269 | 16.6723 | 16.4056 | 16.1972 | 15.9774 | 15.3861 | 15.1108 | 14.8392
|  | BILBOHALL | ST |  |  |  | 1.676 | 8.6742 | 17.6872 | 17.5634 | 17.4859 | 17.4002 | 17.3093 | 17.2136 | 17.0983 | 16.9678 | 16.861 | 16.7161 | 15.9523 | 15.4498 | 15.0519 | 7.9887 | 16.9365 | 16.874 | 16.8331 | 16.7847 | 16.7319 | 16.6869 | 16.6174 | 16.5269 | 16.4642 | 16.3633 | 15.8668 | 15.6125 | 15.4032 | 8.2923 | 17.8461 | 17.7837 | 17.7413 | 17.6952 | 17.6367 | 17.5726 | 17.4963 | 17.4106 | 17.3385 | 17.2192 | 16.5114 | 16.0474 | 15.682
|  | BILBOHALL | FS |  |  |  | 1.676 | 8.7114 | 17.7577 | 17.688 | 17.6405 | 17.5971 | 17.543 | 17.4659 | 17.3728 | 17.2581 | 17.1436 | 17.0193 | 16.3533 | 15.7469 | 15.2997 | 8.0003 | 16.9613 | 16.9243 | 16.8923 | 16.8664 | 16.8286 | 16.7743 | 16.7311 | 16.6639 | 16.5937 | 16.5173 | 16.0983 | 15.7449 | 15.4338 | 8.3053 | 17.8729 | 17.8385 | 17.8124 | 17.7859 | 17.7536 | 17.7078 | 17.6575 | 17.5945 | 17.5306 | 17.4536 | 16.8915 | 16.3418 | 15.941
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.022142 | 0.013803 | 0.0048102 | -0.003705 | -0.009551 | -0.018797 | -0.031614 | -0.03409 | -0.037273 | -0.039949 | -0.042302 | -0.05809 | -0.080762 | -0.1058 | 0.013364 | 0.0030918 | -0.0081491 | -0.018738 | -0.026067 | -0.037449 | -0.053251 | -0.055914 | -0.059297 | -0.062153 | -0.064668 | -0.083345 | -0.11126 | -0.14237 | -0.00045981 | -0.01084 | -0.022348 | -0.033237 | -0.040891 | -0.052628 | -0.068818 | -0.07166 | -0.07522 | -0.07823 | -0.080881 | -0.10013 | -0.12846 | -0.15999
|  | BLACKMOUNT | CT |  |  |  | 0 | 0.022142 | 0.020913 | 0.019854 | 0.011388 | 0.0081799 | 0.0042267 | -0.0040796 | -0.0080918 | -0.011282 | -0.015028 | -0.018871 | -0.022968 | -0.029538 | -0.038582 | 0.013364 | 0.011992 | 0.010721 | 0.00016862 | -0.0037183 | -0.0085718 | -0.018637 | -0.023031 | -0.026567 | -0.030643 | -0.034796 | -0.0386 | -0.046184 | -0.056956 | -0.00045981 | -0.0019985 | -0.0035286 | -0.014379 | -0.018595 | -0.023798 | -0.034255 | -0.038811 | -0.042474 | -0.046654 | -0.050883 | -0.059375 | -0.067276 | -0.078273
|  | BLACKMOUNT | LW |  |  |  | 0 | 0.022216 | 0.013803 | 0.0048102 | -0.003705 | -0.009551 | -0.018797 | -0.031614 | -0.03409 | -0.037273 | -0.039949 | -0.042302 | -0.05809 | -0.080762 | -0.1058 | 0.013467 | 0.0030918 | -0.0081491 | -0.018738 | -0.026067 | -0.037449 | -0.053251 | -0.055914 | -0.059297 | -0.062153 | -0.064668 | -0.083345 | -0.11126 | -0.14237 | -0.00031649 | -0.01084 | -0.022348 | -0.033237 | -0.040891 | -0.052628 | -0.068818 | -0.07166 | -0.07522 | -0.07823 | -0.080881 | -0.10013 | -0.12846 | -0.15999
|  | BLACKMOUNT | ST |  |  |  | 0 | 0.022502 | 0.022092 | 0.016666 | 0.012712 | 0.010308 | 0.0085538 | 0.0066123 | 0.0043912 | 0.0016161 | -0.0013043 | -0.0036523 | -0.03593 | -0.055571 | -0.079264 | 0.013765 | 0.013247 | 0.0064351 | 0.0014989 | -0.0014848 | -0.0036167 | -0.0059438 | -0.0085333 | -0.011692 | -0.015001 | -0.017542 | -0.055187 | -0.07876 | -0.10786 | -1.1471e-05 | -0.00066339 | -0.0076835 | -0.012829 | -0.016022 | -0.01836 | -0.020896 | -0.023664 | -0.027008 | -0.030503 | -0.033234 | -0.071658 | -0.099827 | -0.12915
|  | BLACKMOUNT | FS |  |  |  | 0 | 0.022546 | 0.022201 | 0.020149 | 0.017977 | 0.015775 | 0.01346 | 0.010176 | 0.0075164 | 0.003694 | -0.00019818 | -0.0018253 | -0.014491 | -0.014956 | -0.019493 | 0.013885 | 0.013472 | 0.010958 | 0.0083208 | 0.0056496 | 0.0028644 | -0.001102 | -0.0042994 | -0.0088743 | -0.01352 | -0.015293 | -0.028828 | -0.027811 | -0.032917 | 0.00021538 | -0.00027664 | -0.0028514 | -0.0055492 | -0.0082812 | -0.011124 | -0.015148 | -0.01848 | -0.023194 | -0.027977 | -0.02989 | -0.044178 | -0.048732 | -0.053977
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 0.489 | 3.6106 | 3.4776 | 3.2932 | 3.1 | 2.8687 | 2.6111 | 2.3129 | 2.175 | 2.0438 | 1.9321 | 1.8027 | 1.4585 | 1.2641 | 1.0511 | 4.3307 | 4.2602 | 4.1698 | 4.0764 | 3.9644 | 3.8421 | 3.702 | 3.5985 | 3.4751 | 3.4014 | 3.3106 | 3.1029 | 3.008 | 2.8317 | 3.8581 | 3.739 | 3.5688 | 3.3877 | 3.175 | 2.9426 | 2.6753 | 2.544 | 2.4124 | 2.3182 | 2.199 | 1.8773 | 1.7001 | 1.4994
|  | BLACKSTAND | CT |  |  |  | 0.489 | 3.6106 | 3.4776 | 3.2932 | 3.1 | 2.8687 | 2.6111 | 2.3129 | 2.175 | 2.0734 | 1.9698 | 1.916 | 1.5959 | 1.4233 | 1.2433 | 4.3307 | 4.2602 | 4.1698 | 4.0764 | 3.9644 | 3.8421 | 3.7043 | 3.6014 | 3.5235 | 3.44 | 3.3958 | 3.161 | 3.0273 | 2.8317 | 3.8581 | 3.739 | 3.5688 | 3.3877 | 3.175 | 2.9426 | 2.6753 | 2.544 | 2.447 | 2.3516 | 2.3104 | 2.0192 | 1.8619 | 1.6949
|  | BLACKSTAND | LW |  |  |  | 0.489 | 3.6306 | 3.5014 | 3.3189 | 3.1297 | 2.9256 | 2.6574 | 2.3669 | 2.2171 | 2.0438 | 1.9321 | 1.8027 | 1.4585 | 1.2641 | 1.0511 | 4.3385 | 4.265 | 4.1725 | 4.0807 | 3.9849 | 3.8436 | 3.702 | 3.5985 | 3.4751 | 3.4014 | 3.3106 | 3.1029 | 3.008 | 2.883 | 3.8773 | 3.7599 | 3.5888 | 3.4122 | 3.2208 | 2.9746 | 2.7112 | 2.5698 | 2.4124 | 2.3182 | 2.199 | 1.8773 | 1.7001 | 1.4994
|  | BLACKSTAND | ST |  |  |  | 0.489 | 3.6522 | 3.5549 | 3.4441 | 3.3286 | 3.2037 | 3.0897 | 2.9424 | 2.824 | 2.6845 | 2.5743 | 2.4297 | 1.8507 | 1.6132 | 1.4899 | 4.3538 | 4.3065 | 4.2527 | 4.1956 | 4.1315 | 4.0769 | 3.999 | 3.932 | 3.8459 | 3.7856 | 3.6954 | 3.2902 | 3.0959 | 2.9225 | 3.8956 | 3.808 | 3.7036 | 3.5961 | 3.481 | 3.3769 | 3.245 | 3.1365 | 3.0091 | 2.9067 | 2.7747 | 2.2517 | 2.0296 | 1.9116
|  | BLACKSTAND | FS |  |  |  | 0.489 | 3.7088 | 3.6453 | 3.6114 | 3.5649 | 3.5262 | 3.4748 | 3.4282 | 3.3306 | 3.2289 | 3.1204 | 3.0076 | 2.4618 | 1.9221 | 1.7254 | 4.3757 | 4.3424 | 4.3211 | 4.2893 | 4.2636 | 4.2275 | 4.1957 | 4.1369 | 4.0736 | 4.0047 | 3.9334 | 3.5707 | 3.1709 | 2.8497 | 3.9488 | 3.8924 | 3.8614 | 3.8195 | 3.7848 | 3.7389 | 3.6987 | 3.61 | 3.516 | 3.4172 | 3.3159 | 2.8121 | 2.3199 | 2.1423
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 1.712 | 12.6248 | 12.3023 | 11.7527 | 11.1309 | 10.4039 | 9.5585 | 8.5887 | 7.1886 | 6.0661 | 4.8204 | 4.1109 | 2.132 | 1.1368 | 0.29761 | 14.3841 | 14.1754 | 13.9045 | 13.5646 | 13.1642 | 12.7511 | 12.2274 | 11.3552 | 10.6879 | 9.8632 | 9.4529 | 8.4008 | 7.7269 | 6.8974 | 14.1056 | 13.8249 | 13.3472 | 12.7914 | 12.1222 | 11.3887 | 10.5072 | 9.2198 | 8.2281 | 7.0711 | 6.4081 | 4.5943 | 3.8261 | 3.0703
|  | BLAIRGOWRIE | CT |  |  |  | 1.712 | 12.6482 | 12.3358 | 11.795 | 11.1641 | 10.4039 | 9.5585 | 8.5887 | 7.257 | 6.3615 | 5.2098 | 4.6148 | 2.3097 | 1.1368 | 0.29761 | 14.3909 | 14.1837 | 13.9045 | 13.5646 | 13.1642 | 12.7511 | 12.2274 | 11.3736 | 10.8737 | 10.0846 | 9.7107 | 8.4172 | 7.7269 | 6.8974 | 14.121 | 13.847 | 13.3711 | 12.8024 | 12.1222 | 11.3887 | 10.5072 | 9.2821 | 8.5254 | 7.4654 | 6.9033 | 4.8232 | 3.8261 | 3.0703
|  | BLAIRGOWRIE | LW |  |  |  | 1.712 | 12.6248 | 12.3023 | 11.7527 | 11.1309 | 10.4269 | 9.5617 | 8.6363 | 7.1886 | 6.0661 | 4.8204 | 4.1109 | 2.132 | 1.482 | 0.72528 | 14.3841 | 14.1754 | 13.9063 | 13.587 | 13.2406 | 12.792 | 12.2826 | 11.3552 | 10.6879 | 9.8632 | 9.4529 | 8.4008 | 8.105 | 7.6701 | 14.1056 | 13.8249 | 13.3472 | 12.7914 | 12.173 | 11.4012 | 10.5483 | 9.2198 | 8.2281 | 7.0711 | 6.4081 | 4.5943 | 4.0189 | 3.3196
|  | BLAIRGOWRIE | ST |  |  |  | 1.712 | 12.7553 | 12.5649 | 12.3775 | 12.2027 | 11.9775 | 11.7307 | 11.4509 | 10.8403 | 10.135 | 9.3472 | 8.9474 | 7.2927 | 6.1358 | 5.0042 | 14.4554 | 14.3393 | 14.2182 | 14.0942 | 13.9378 | 13.7718 | 13.5883 | 13.1074 | 12.5538 | 11.915 | 11.6213 | 10.4883 | 9.676 | 8.7731 | 14.2204 | 14.0663 | 13.913 | 13.7544 | 13.5506 | 13.3304 | 13.0804 | 12.5306 | 11.8862 | 11.1598 | 10.7787 | 9.2295 | 8.18 | 7.185
|  | BLAIRGOWRIE | FS |  |  |  | 1.712 | 12.8073 | 12.6602 | 12.4882 | 12.3423 | 12.1527 | 11.9358 | 11.7499 | 11.2357 | 10.6756 | 10.1407 | 9.7369 | 7.715 | 5.8188 | 4.3312 | 14.4826 | 14.3884 | 14.2764 | 14.1797 | 14.0517 | 13.9015 | 13.7653 | 13.3761 | 12.956 | 12.5496 | 12.2603 | 10.8116 | 9.257 | 7.6215 | 14.2606 | 14.1427 | 13.9997 | 13.8771 | 13.7093 | 13.5154 | 13.3462 | 12.8789 | 12.3758 | 11.8957 | 11.5294 | 9.6838 | 7.9255 | 6.583
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0 | 0.47106 | 0.46887 | 0.45169 | 0.43515 | 0.41487 | 0.39264 | 0.36606 | 0.35039 | 0.33316 | 0.31423 | 0.3034 | 0.27025 | 0.25872 | 0.24748 | 0.5743 | 0.57377 | 0.56641 | 0.56688 | 0.5583 | 0.54553 | 0.53031 | 0.51886 | 0.5017 | 0.48491 | 0.48153 | 0.45976 | 0.45076 | 0.41697 | 0.66588 | 0.66257 | 0.64526 | 0.62487 | 0.6033 | 0.58069 | 0.55256 | 0.52889 | 0.49529 | 0.466 | 0.44445 | 0.3959 | 0.37432 | 0.36741
|  | BLAIRLINNANS | CT |  |  |  | 0 | 0.47106 | 0.4691 | 0.4528 | 0.43515 | 0.41487 | 0.39264 | 0.36606 | 0.35039 | 0.33769 | 0.32469 | 0.31377 | 0.28953 | 0.2785 | 0.26774 | 0.5747 | 0.57377 | 0.56929 | 0.56688 | 0.5583 | 0.54553 | 0.53031 | 0.51886 | 0.50711 | 0.49386 | 0.48177 | 0.46594 | 0.4561 | 0.43985 | 0.66591 | 0.66257 | 0.64526 | 0.62487 | 0.6033 | 0.58069 | 0.55256 | 0.52889 | 0.51052 | 0.49162 | 0.47534 | 0.44121 | 0.43447 | 0.4286
|  | BLAIRLINNANS | LW |  |  |  | 0 | 0.47203 | 0.47176 | 0.45737 | 0.44074 | 0.42234 | 0.39899 | 0.37201 | 0.35555 | 0.33316 | 0.31423 | 0.3034 | 0.27025 | 0.25872 | 0.24748 | 0.5743 | 0.57405 | 0.57062 | 0.56717 | 0.56073 | 0.54836 | 0.53252 | 0.52157 | 0.5017 | 0.48491 | 0.48153 | 0.45976 | 0.45661 | 0.45079 | 0.66588 | 0.66391 | 0.6494 | 0.63176 | 0.61273 | 0.58574 | 0.55433 | 0.52893 | 0.49529 | 0.466 | 0.44445 | 0.3959 | 0.38879 | 0.38299
|  | BLAIRLINNANS | ST |  |  |  | 0 | 0.48169 | 0.46887 | 0.45169 | 0.45989 | 0.44911 | 0.43594 | 0.42385 | 0.41171 | 0.39601 | 0.37892 | 0.36331 | 0.28758 | 0.2609 | 0.25229 | 0.58191 | 0.57508 | 0.56641 | 0.57493 | 0.57249 | 0.56644 | 0.56294 | 0.5564 | 0.54581 | 0.53284 | 0.52416 | 0.47058 | 0.45076 | 0.43648 | 0.67736 | 0.66451 | 0.64732 | 0.65608 | 0.64422 | 0.62947 | 0.61452 | 0.59826 | 0.57676 | 0.55326 | 0.52959 | 0.4108 | 0.37432 | 0.36741
|  | BLAIRLINNANS | FS |  |  |  | 0 | 0.48524 | 0.47702 | 0.46692 | 0.47487 | 0.47261 | 0.4676 | 0.46057 | 0.45234 | 0.44225 | 0.43057 | 0.41909 | 0.35162 | 0.29222 | 0.26401 | 0.58257 | 0.57687 | 0.56993 | 0.57194 | 0.57343 | 0.5718 | 0.56674 | 0.56593 | 0.56328 | 0.55552 | 0.54789 | 0.49829 | 0.45478 | 0.41697 | 0.68115 | 0.67139 | 0.66045 | 0.66878 | 0.66467 | 0.6578 | 0.6487 | 0.63836 | 0.62516 | 0.61049 | 0.59544 | 0.50143 | 0.42006 | 0.37702
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0.547 | 6.8764 | 6.8323 | 6.7997 | 6.665 | 6.5095 | 6.3283 | 6.1144 | 6.013 | 5.9663 | 5.8654 | 5.7772 | 5.5411 | 5.4058 | 5.2382 | 7.7174 | 7.6859 | 7.6515 | 7.6098 | 7.5554 | 7.4797 | 7.3914 | 7.3446 | 7.3049 | 7.2612 | 7.223 | 7.122 | 7.0542 | 6.9626 | 7.1011 | 7.0438 | 6.9513 | 6.8323 | 6.7169 | 6.5861 | 6.4334 | 6.3708 | 6.3303 | 6.2667 | 6.2117 | 6.0446 | 5.9369 | 5.7928
|  | BOAT OF GARTEN | CT |  |  |  | 0.547 | 6.8773 | 6.8389 | 6.8098 | 6.665 | 6.5095 | 6.3283 | 6.1144 | 6.013 | 5.9699 | 5.9026 | 5.8484 | 5.6574 | 5.5447 | 5.4082 | 7.7174 | 7.6934 | 7.6649 | 7.6163 | 7.5554 | 7.4839 | 7.3988 | 7.3549 | 7.3368 | 7.3077 | 7.2841 | 7.2092 | 7.139 | 7.0176 | 7.1011 | 7.0438 | 6.9513 | 6.8323 | 6.7169 | 6.5861 | 6.4334 | 6.3708 | 6.343 | 6.3051 | 6.277 | 6.1651 | 6.0781 | 5.9865
|  | BOAT OF GARTEN | LW |  |  |  | 0.547 | 6.8764 | 6.8323 | 6.7997 | 6.6944 | 6.5623 | 6.3755 | 6.1695 | 6.0599 | 5.9663 | 5.8654 | 5.7772 | 5.5411 | 5.4058 | 5.2382 | 7.7179 | 7.6859 | 7.6515 | 7.6098 | 7.5599 | 7.4797 | 7.3914 | 7.3446 | 7.3049 | 7.2612 | 7.223 | 7.122 | 7.0542 | 6.9626 | 7.1105 | 7.0498 | 6.9573 | 6.8495 | 6.7469 | 6.6115 | 6.4611 | 6.3905 | 6.3303 | 6.2667 | 6.2117 | 6.0446 | 5.9369 | 5.7928
|  | BOAT OF GARTEN | ST |  |  |  | 0.547 | 6.888 | 6.8748 | 6.847 | 6.8297 | 6.7924 | 6.7232 | 6.6401 | 6.5772 | 6.4915 | 6.3992 | 6.3027 | 5.9425 | 5.811 | 5.7574 | 7.7252 | 7.7141 | 7.6908 | 7.6707 | 7.6479 | 7.6265 | 7.5991 | 7.5714 | 7.5341 | 7.4921 | 7.4484 | 7.2583 | 7.1746 | 7.1288 | 7.1206 | 7.084 | 7.0271 | 6.9743 | 6.9175 | 6.8633 | 6.8013 | 6.7506 | 6.6871 | 6.6195 | 6.5491 | 6.2593 | 6.1284 | 6.0592
|  | BOAT OF GARTEN | FS |  |  |  | 0.547 | 6.8924 | 6.8771 | 6.8648 | 6.8549 | 6.835 | 6.8221 | 6.7966 | 6.7656 | 6.7476 | 6.7106 | 6.6797 | 6.3368 | 5.965 | 5.8357 | 7.7305 | 7.7214 | 7.7113 | 7.7011 | 7.6877 | 7.6751 | 7.6575 | 7.6358 | 7.6138 | 7.5872 | 7.5635 | 7.4228 | 7.2849 | 7.1057 | 7.1458 | 7.1209 | 7.1038 | 7.087 | 7.0659 | 7.0467 | 7.0212 | 6.9747 | 6.9301 | 6.8785 | 6.8301 | 6.5763 | 6.3 | 6.1805
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 1.245 | 1.068 | 1.0185 | 0.9536 | 0.84729 | 0.76952 | 0.68345 | 0.45949 | -0.055434 | -0.97099 | -1.5817 | -2.1757 | -3.1579 | -3.2329 | -3.2528 | 0.90763 | 0.87488 | 0.82757 | 0.76085 | 0.69651 | 0.62529 | 0.43666 | -0.12426 | -1.1159 | -1.7304 | -2.3277 | -3.2353 | -3.2892 | -3.4542 | 1.2668 | 1.2323 | 1.1911 | 1.1231 | 1.0702 | 1.0118 | 0.83265 | 0.34104 | -0.63133 | -1.2329 | -1.8099 | -2.7697 | -2.8786 | -2.9451
|  | BODDAM | CT |  |  |  | 1.245 | 1.068 | 1.0185 | 0.9536 | 0.84729 | 0.76952 | 0.68345 | 0.45949 | -0.055434 | -0.85223 | -1.5201 | -2.1276 | -2.9507 | -2.9587 | -2.9727 | 0.90763 | 0.87488 | 0.82757 | 0.76085 | 0.69651 | 0.62529 | 0.43666 | -0.082978 | -0.91583 | -1.6322 | -2.2894 | -3.1834 | -3.2478 | -3.3393 | 1.2668 | 1.2323 | 1.1911 | 1.1231 | 1.0702 | 1.0118 | 0.83265 | 0.35303 | -0.45715 | -1.136 | -1.7493 | -2.6669 | -2.7792 | -2.8662
|  | BODDAM | LW |  |  |  | 1.245 | 1.0697 | 1.0311 | 0.99904 | 0.95496 | 0.90504 | 0.82523 | 0.60449 | -0.0018153 | -0.97099 | -1.5817 | -2.1757 | -3.1579 | -3.2329 | -3.251 | 0.91083 | 0.88466 | 0.84998 | 0.80638 | 0.75683 | 0.68904 | 0.49048 | -0.12426 | -1.1159 | -1.7304 | -2.3277 | -3.2353 | -3.2892 | -3.317 | 1.2684 | 1.2415 | 1.2213 | 1.1916 | 1.1581 | 1.104 | 0.92027 | 0.34104 | -0.63133 | -1.2329 | -1.8099 | -2.7697 | -2.8786 | -2.9451
|  | BODDAM | ST |  |  |  | 1.245 | 1.0849 | 1.071 | 1.0519 | 1.0259 | 0.99751 | 0.95839 | 0.80809 | 0.3365 | -0.45584 | -1.1333 | -1.7856 | -2.9863 | -3.1477 | -3.1605 | 0.92107 | 0.90856 | 0.89222 | 0.87115 | 0.85191 | 0.82525 | 0.69488 | 0.21593 | -0.64412 | -1.3557 | -2.0287 | -3.0967 | -3.225 | -3.3041 | 1.2787 | 1.269 | 1.2559 | 1.2372 | 1.2199 | 1.1934 | 1.0622 | 0.61189 | -0.14995 | -0.79082 | -1.4017 | -2.3972 | -2.4982 | -2.6227
|  | BODDAM | FS |  |  |  | 1.245 | 1.0887 | 1.0785 | 1.065 | 1.0496 | 1.0296 | 1.0095 | 0.91441 | 0.62395 | 0.12672 | -0.24302 | -0.66257 | -2.2242 | -2.9841 | -3.2528 | 0.9248 | 0.91454 | 0.90113 | 0.88738 | 0.87013 | 0.85544 | 0.76751 | 0.46416 | -0.072785 | -0.46835 | -0.91575 | -2.494 | -3.182 | -3.4542 | 1.2815 | 1.2741 | 1.2642 | 1.2535 | 1.2391 | 1.2273 | 1.1428 | 0.86356 | 0.3817 | 0.0303 | -0.36658 | -1.7893 | -2.4066 | -2.6677
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0.214 | -2.6123 | -2.6817 | -2.7716 | -2.8855 | -2.9981 | -3.1329 | -3.2914 | -3.4635 | -3.6416 | -3.8224 | -3.9406 | -4.3425 | -4.6231 | -4.8228 | -1.1993 | -1.2608 | -1.3384 | -1.4332 | -1.5182 | -1.6462 | -1.7691 | -1.8807 | -2.0127 | -2.1331 | -2.2067 | -2.4654 | -2.6503 | -2.7757 | -1.8401 | -1.9295 | -2.0493 | -2.2019 | -2.3436 | -2.5451 | -2.7343 | -2.9098 | -3.112 | -3.2962 | -3.4046 | -3.7914 | -3.9507 | -4.1493
|  | BONSKEID | CT |  |  |  | 0.214 | -2.6123 | -2.676 | -2.7602 | -2.8855 | -2.9981 | -3.1314 | -3.2914 | -3.4635 | -3.6087 | -3.746 | -3.8207 | -4.2226 | -4.3822 | -4.5374 | -1.1993 | -1.2504 | -1.3155 | -1.419 | -1.5083 | -1.6187 | -1.7387 | -1.8548 | -1.952 | -2.051 | -2.1072 | -2.3589 | -2.4645 | -2.6094 | -1.8401 | -1.9231 | -2.0316 | -2.192 | -2.342 | -2.5211 | -2.7106 | -2.8876 | -3.0376 | -3.1868 | -3.2655 | -3.642 | -3.7797 | -3.9241
|  | BONSKEID | LW |  |  |  | 0.214 | -2.6087 | -2.6817 | -2.7716 | -2.883 | -2.9876 | -3.1329 | -3.2861 | -3.4576 | -3.6416 | -3.8224 | -3.9406 | -4.3425 | -4.5104 | -4.7055 | -1.1958 | -1.2608 | -1.3384 | -1.4332 | -1.5182 | -1.6462 | -1.7691 | -1.8807 | -2.0127 | -2.1331 | -2.2067 | -2.4654 | -2.5772 | -2.721 | -1.8342 | -1.9295 | -2.0493 | -2.2019 | -2.3436 | -2.5451 | -2.7343 | -2.9098 | -3.112 | -3.2962 | -3.4046 | -3.7914 | -3.9507 | -4.1493
|  | BONSKEID | ST |  |  |  | 0.214 | -2.5975 | -2.6356 | -2.6914 | -2.7518 | -2.8076 | -2.8765 | -2.9363 | -3.0162 | -3.1144 | -3.2072 | -3.3005 | -4.2187 | -4.6231 | -4.8228 | -1.186 | -1.2156 | -1.2645 | -1.3165 | -1.3625 | -1.4187 | -1.4667 | -1.5302 | -1.6123 | -1.683 | -1.7592 | -2.3546 | -2.6503 | -2.7757 | -1.8156 | -1.8633 | -1.934 | -2.0123 | -2.0805 | -2.1664 | -2.2389 | -2.3333 | -2.4475 | -2.5454 | -2.648 | -3.3903 | -3.7672 | -3.9397
|  | BONSKEID | FS |  |  |  | 0.214 | -2.5858 | -2.6121 | -2.6449 | -2.679 | -2.7181 | -2.7549 | -2.7975 | -2.8547 | -2.9291 | -3.0057 | -3.0648 | -3.5503 | -4.2805 | -4.8109 | -1.1779 | -1.1992 | -1.2286 | -1.2585 | -1.2931 | -1.3252 | -1.3644 | -1.412 | -1.4766 | -1.545 | -1.5918 | -1.9504 | -2.3449 | -2.7161 | -1.8005 | -1.8338 | -1.8756 | -1.9175 | -1.9668 | -2.0095 | -2.0632 | -2.1314 | -2.2219 | -2.3145 | -2.3795 | -2.8601 | -3.4109 | -3.8932
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | YES | 0.314 | 0.93391 | 0.82914 | 0.63489 | 0.42303 | 0.19834 | -0.055331 | -0.42445 | -0.71464 | -1.0287 | -1.3103 | -1.4629 | -1.8385 | -1.993 | -2.2256 | 3.9132 | 3.8494 | 3.7424 | 3.622 | 3.501 | 3.3729 | 3.1491 | 2.8842 | 2.5231 | 2.2313 | 2.1258 | 1.8676 | 1.7897 | 1.6264 | 1.3694 | 1.272 | 1.0971 | 0.90334 | 0.70639 | 0.49767 | 0.18556 | -0.11593 | -0.48957 | -0.84332 | -0.99354 | -1.3568 | -1.495 | -1.7142
|  | BOWMORE | CT |  |  |  | 0.314 | 0.93391 | 0.82914 | 0.63489 | 0.42303 | 0.19834 | -0.055331 | -0.42445 | -0.71464 | -1.0287 | -1.301 | -1.4034 | -1.7239 | -1.8683 | -2.0775 | 3.9132 | 3.8494 | 3.7424 | 3.622 | 3.501 | 3.3729 | 3.1491 | 2.8842 | 2.5744 | 2.2623 | 2.173 | 1.9218 | 1.811 | 1.6264 | 1.3694 | 1.272 | 1.0971 | 0.90334 | 0.70639 | 0.49767 | 0.18556 | -0.11593 | -0.44802 | -0.79407 | -0.92531 | -1.2419 | -1.3718 | -1.565
|  | BOWMORE | LW |  |  |  | 0.314 | 0.94738 | 0.85423 | 0.67581 | 0.49559 | 0.29535 | 0.089465 | -0.26045 | -0.59303 | -0.99848 | -1.3103 | -1.4629 | -1.8385 | -1.993 | -2.2256 | 3.9206 | 3.8641 | 3.7672 | 3.6684 | 3.558 | 3.4391 | 3.209 | 2.917 | 2.5231 | 2.2313 | 2.1258 | 1.8676 | 1.7897 | 1.6482 | 1.3818 | 1.2953 | 1.1346 | 0.97097 | 0.78881 | 0.59832 | 0.28892 | -0.041594 | -0.48957 | -0.84332 | -0.99354 | -1.3568 | -1.495 | -1.7142
|  | BOWMORE | ST |  |  |  | 0.314 | 0.97971 | 0.91408 | 0.80623 | 0.71246 | 0.59881 | 0.50274 | 0.3232 | 0.053568 | -0.32124 | -0.63946 | -0.79562 | -1.4026 | -1.6473 | -1.8005 | 3.9396 | 3.9023 | 3.8429 | 3.791 | 3.7269 | 3.6714 | 3.5307 | 3.3071 | 2.9476 | 2.6089 | 2.5089 | 2.126 | 1.9487 | 1.8166 | 1.4125 | 1.3526 | 1.2568 | 1.1726 | 1.0692 | 0.98083 | 0.81082 | 0.58178 | 0.20071 | -0.15119 | -0.31586 | -0.93214 | -1.1588 | -1.2693
|  | BOWMORE | FS |  |  |  | 0.314 | 1.0124 | 0.97168 | 0.91473 | 0.85604 | 0.80526 | 0.74707 | 0.6506 | 0.46854 | 0.24115 | 0.035433 | -0.10974 | -0.8766 | -1.4676 | -1.7355 | 3.9553 | 3.9311 | 3.8973 | 3.8597 | 3.8299 | 3.7913 | 3.7121 | 3.5592 | 3.333 | 3.1364 | 3.022 | 2.4289 | 1.9785 | 1.6655 | 1.4408 | 1.4038 | 1.353 | 1.2987 | 1.253 | 1.198 | 1.1065 | 0.93261 | 0.69336 | 0.47283 | 0.33006 | -0.4315 | -0.99933 | -1.2501
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0.368 | -2.0996 | -2.1396 | -2.2243 | -2.333 | -2.4576 | -2.9112 | -3.3401 | -3.8252 | -4.3129 | -4.768 | -4.8985 | -5.3028 | -5.5886 | -5.7673 | -0.68602 | -0.72143 | -0.76672 | -0.82103 | -0.88587 | -1.2585 | -1.6718 | -2.102 | -2.5533 | -2.983 | -3.0479 | -3.2371 | -3.3551 | -3.4778 | -1.665 | -1.7048 | -1.7782 | -1.866 | -1.9737 | -2.3921 | -2.808 | -3.2528 | -3.7077 | -4.1404 | -4.2512 | -4.5788 | -4.7967 | -4.9381
|  | BRAE | CT |  |  |  | 0.368 | -2.0996 | -2.1375 | -2.2228 | -2.333 | -2.4576 | -2.9112 | -3.3357 | -3.7727 | -4.2068 | -4.6967 | -4.8306 | -5.2853 | -5.5886 | -5.7673 | -0.68602 | -0.7175 | -0.75899 | -0.81863 | -0.88587 | -1.2585 | -1.6084 | -1.9905 | -2.4 | -2.8905 | -2.9831 | -3.2129 | -3.3551 | -3.4778 | -1.665 | -1.6997 | -1.7709 | -1.866 | -1.9737 | -2.3921 | -2.7829 | -3.1852 | -3.5877 | -4.0434 | -4.163 | -4.5469 | -4.7967 | -4.9381
|  | BRAE | LW |  |  |  | 0.368 | -2.0971 | -2.1396 | -2.2243 | -2.3224 | -2.4262 | -2.8715 | -3.3401 | -3.8252 | -4.3129 | -4.768 | -4.8985 | -5.3028 | -5.5138 | -5.7231 | -0.68398 | -0.72143 | -0.76672 | -0.82103 | -0.87651 | -1.2563 | -1.6718 | -2.102 | -2.5533 | -2.983 | -3.0479 | -3.2371 | -3.335 | -3.4424 | -1.6633 | -1.7048 | -1.7782 | -1.863 | -1.9524 | -2.3687 | -2.808 | -3.2528 | -3.7077 | -4.1404 | -4.2512 | -4.5788 | -4.7516 | -4.9192
|  | BRAE | ST |  |  |  | 0.368 | -2.0761 | -2.0902 | -2.1146 | -2.1425 | -2.1629 | -2.5144 | -2.7984 | -3.1175 | -3.4536 | -3.8802 | -3.9543 | -4.4136 | -4.8327 | -5.1734 | -0.67274 | -0.68332 | -0.70316 | -0.72718 | -0.74203 | -1.0782 | -1.364 | -1.706 | -2.0837 | -2.5699 | -2.637 | -2.892 | -3.1053 | -3.2941 | -1.6448 | -1.657 | -1.6798 | -1.706 | -1.7238 | -2.0553 | -2.3369 | -2.6592 | -3.0021 | -3.4351 | -3.5173 | -3.9154 | -4.2026 | -4.4291
|  | BRAE | FS |  |  |  | 0.368 | -2.0811 | -2.0976 | -2.1218 | -2.1457 | -2.172 | -2.5175 | -2.7125 | -2.9304 | -3.1808 | -3.4578 | -3.5848 | -4.2464 | -4.6439 | -4.985 | -0.67379 | -0.68537 | -0.70262 | -0.71934 | -0.73992 | -1.0666 | -1.2606 | -1.4718 | -1.7294 | -2.0192 | -2.1409 | -2.7385 | -3.0282 | -3.2753 | -1.649 | -1.6635 | -1.6853 | -1.7062 | -1.7305 | -2.0515 | -2.2375 | -2.4502 | -2.697 | -2.9703 | -3.0958 | -3.741 | -4.1082 | -4.3944
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 1.643 | 3.4235 | 3.149 | 2.6752 | 2.1242 | 1.5556 | 0.88342 | -0.26894 | -1.1517 | -2.1516 | -2.7667 | -3.5593 | -6.0523 | -6.8339 | -7.4612 | 5.4469 | 5.2619 | 5.0086 | 4.7163 | 4.3903 | 4.0655 | 3.2882 | 2.7509 | 2.0725 | 1.7203 | 1.1764 | -0.53146 | -1.1397 | -1.8499 | 4.2469 | 3.9899 | 3.5589 | 3.0622 | 2.5494 | 1.9388 | 0.86693 | 0.032127 | -0.93396 | -1.4807 | -2.2443 | -4.598 | -5.1753 | -5.7651
|  | BRECHIN | CT |  |  |  | 1.643 | 3.4352 | 3.1682 | 2.7191 | 2.192 | 1.598 | 0.9872 | -0.08049 | -1.0052 | -1.8413 | -2.3835 | -3.0807 | -5.7996 | -6.8339 | -7.4612 | 5.4473 | 5.2634 | 5.0088 | 4.7163 | 4.3903 | 4.0728 | 3.3697 | 2.7889 | 2.2447 | 1.9292 | 1.4377 | -0.44038 | -1.1397 | -1.8499 | 4.2537 | 4.0011 | 3.5876 | 3.107 | 2.5674 | 2.0202 | 1.0304 | 0.15739 | -0.62523 | -1.0917 | -1.7547 | -4.2744 | -5.1753 | -5.7651
|  | BRECHIN | LW |  |  |  | 1.643 | 3.4235 | 3.149 | 2.6752 | 2.1242 | 1.5556 | 0.88342 | -0.26894 | -1.1517 | -2.1516 | -2.7667 | -3.5593 | -6.0523 | -6.6067 | -7.1922 | 5.4469 | 5.2619 | 5.0086 | 4.7195 | 4.4271 | 4.0655 | 3.2882 | 2.7509 | 2.0725 | 1.7203 | 1.1764 | -0.53146 | -0.86294 | -1.2706 | 4.2469 | 3.9899 | 3.5589 | 3.0622 | 2.5494 | 1.9388 | 0.86693 | 0.032127 | -0.93396 | -1.4807 | -2.2443 | -4.598 | -5.0995 | -5.6966
|  | BRECHIN | ST |  |  |  | 1.643 | 3.5104 | 3.3463 | 3.1797 | 3.0174 | 2.8633 | 2.7111 | 2.2155 | 1.8542 | 1.4184 | 0.90632 | 0.39461 | -1.8727 | -3.0046 | -3.9266 | 5.4978 | 5.3941 | 5.2738 | 5.1578 | 5.0376 | 4.9206 | 4.4946 | 4.2047 | 3.8541 | 3.4358 | 3.0103 | 1.0848 | 0.19182 | -0.56636 | 4.3312 | 4.1872 | 4.034 | 3.8869 | 3.7371 | 3.593 | 3.1247 | 2.777 | 2.3559 | 1.8524 | 1.3446 | -0.87564 | -1.9283 | -2.7283
|  | BRECHIN | FS |  |  |  | 1.643 | 3.5679 | 3.4513 | 3.3237 | 3.1996 | 3.0753 | 2.9463 | 2.6231 | 2.3231 | 1.9285 | 1.5205 | 1.1231 | -1.3046 | -3.4366 | -4.8568 | 5.5256 | 5.4456 | 5.3525 | 5.2624 | 5.1655 | 5.0591 | 4.7754 | 4.5487 | 4.2475 | 3.9324 | 3.6232 | 1.7112 | -0.11685 | -1.6564 | 4.3809 | 4.279 | 4.1623 | 4.0506 | 3.9316 | 3.8035 | 3.4974 | 3.221 | 2.8572 | 2.4676 | 2.0958 | -0.2037 | -2.223 | -3.5146
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | YES | 3.367 | -4.722 | -9.4853 | -15.4045 | -20.8388 | -25.1134 | -30.1825 | -36.6058 | -38.2217 | -39.963 | -41.5964 | -43.0396 | -50.6177 | -59.1026 | -68.735 | -2.1742 | -7.4666 | -13.8172 | -19.6202 | -23.8899 | -29.2516 | -36.1238 | -36.8759 | -37.5814 | -38.3283 | -38.9425 | -45.4961 | -55.6494 | -67.0274 | -4.2186 | -9.383 | -15.442 | -21.2932 | -25.8007 | -31.4112 | -38.564 | -39.9632 | -41.3886 | -42.7653 | -43.975 | -52.1016 | -62.5074 | -74.215
|  | BRIDGE OF DON | CT |  |  |  | 3.367 | -4.13 | -5.972 | -8.6912 | -14.1512 | -17.3629 | -20.7511 | -25.3508 | -27.2163 | -29.1789 | -30.9085 | -32.4862 | -38.5206 | -42.5631 | -46.3653 | -1.5755 | -3.2915 | -5.7266 | -11.623 | -14.5139 | -17.7576 | -22.3195 | -23.385 | -24.5954 | -25.6603 | -26.5924 | -30.7684 | -34.772 | -39.3692 | -3.6653 | -5.2818 | -7.4724 | -13.3068 | -16.4035 | -19.8625 | -24.744 | -26.3777 | -28.1825 | -29.7599 | -31.2012 | -37.0404 | -41.4617 | -45.8274
|  | BRIDGE OF DON | LW |  |  |  | 3.367 | -4.722 | -9.4853 | -15.4045 | -20.8388 | -25.1134 | -30.1825 | -36.6058 | -38.2217 | -39.963 | -41.5964 | -43.0396 | -50.6177 | -59.1026 | -68.735 | -2.1742 | -7.4666 | -13.8172 | -19.6202 | -23.8899 | -29.2516 | -36.1238 | -36.8759 | -37.5814 | -38.3283 | -38.9425 | -45.4961 | -55.6494 | -67.0274 | -4.2186 | -9.383 | -15.442 | -21.2932 | -25.8007 | -31.4112 | -38.564 | -39.9632 | -41.3886 | -42.7653 | -43.975 | -52.1016 | -62.5074 | -74.215
|  | BRIDGE OF DON | ST |  |  |  | 3.367 | -4 | -5.6689 | -9.5423 | -12.8863 | -15.5286 | -17.774 | -19.6877 | -20.8742 | -21.8316 | -22.8737 | -23.5653 | -33.8038 | -43.9615 | -54.1205 | -1.5288 | -3.1613 | -7.5607 | -11.4397 | -14.3883 | -16.8588 | -18.9679 | -20.1377 | -21.0964 | -22.0206 | -22.46 | -32.8486 | -44.4841 | -55.6635 | -3.6214 | -5.1418 | -9.353 | -13.0045 | -15.7799 | -18.0762 | -20.0483 | -21.2197 | -22.2544 | -23.243 | -23.8256 | -35.1676 | -47.337 | -58.6461
|  | BRIDGE OF DON | FS |  |  |  | 3.367 | -3.3211 | -4.5178 | -6.6333 | -8.8238 | -11.1412 | -13.7255 | -15.9706 | -17.3741 | -19.1138 | -20.764 | -21.4565 | -26.3447 | -29.4623 | -33.2673 | -0.86941 | -2.0419 | -4.3262 | -6.7794 | -9.3319 | -12.2199 | -14.7344 | -16.1215 | -17.8114 | -19.4263 | -20.0302 | -23.5375 | -25.3347 | -29.2202 | -3.0108 | -4.1017 | -6.2404 | -8.5132 | -10.901 | -13.5856 | -15.9854 | -17.3253 | -18.9772 | -20.5543 | -21.1581 | -25.16 | -27.8209 | -31.6083
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0.064 | -0.1007 | -0.1259 | -0.17258 | -0.21945 | -0.27001 | -0.33022 | -0.4047 | -0.45081 | -0.50603 | -0.55221 | -0.5947 | -0.73767 | -0.83081 | -0.91869 | 0.067051 | 0.041522 | 0.0057953 | -0.023763 | -0.057225 | -0.099803 | -0.15949 | -0.18354 | -0.23199 | -0.2662 | -0.30217 | -0.38482 | -0.43066 | -0.4848 | -0.022667 | -0.054392 | -0.10944 | -0.16145 | -0.21901 | -0.28782 | -0.37571 | -0.41901 | -0.48297 | -0.53163 | -0.57989 | -0.71484 | -0.79379 | -0.87678
|  | BRIDGE OF DUN | CT |  |  |  | 0.064 | -0.1007 | -0.12403 | -0.16384 | -0.21166 | -0.26413 | -0.31683 | -0.39264 | -0.43586 | -0.47612 | -0.51322 | -0.54201 | -0.68838 | -0.78383 | -0.85956 | 0.067051 | 0.047707 | 0.019353 | -0.0086487 | -0.046133 | -0.075318 | -0.12914 | -0.15556 | -0.18834 | -0.2243 | -0.25016 | -0.34396 | -0.38609 | -0.43743 | -0.022667 | -0.05168 | -0.098828 | -0.15 | -0.21204 | -0.26891 | -0.35258 | -0.39545 | -0.44011 | -0.48509 | -0.51789 | -0.66149 | -0.73677 | -0.80053
|  | BRIDGE OF DUN | LW |  |  |  | 0.064 | -0.097443 | -0.1259 | -0.17258 | -0.21945 | -0.27001 | -0.33022 | -0.4047 | -0.45081 | -0.50603 | -0.55221 | -0.5947 | -0.73767 | -0.83081 | -0.91869 | 0.06812 | 0.041522 | 0.0057953 | -0.023763 | -0.057225 | -0.099803 | -0.15949 | -0.18354 | -0.23199 | -0.2662 | -0.30217 | -0.38482 | -0.43066 | -0.4848 | -0.019145 | -0.054392 | -0.10944 | -0.16145 | -0.21901 | -0.28782 | -0.37571 | -0.41901 | -0.48297 | -0.53163 | -0.57989 | -0.71484 | -0.79379 | -0.87678
|  | BRIDGE OF DUN | ST |  |  |  | 0.064 | -0.092116 | -0.10839 | -0.13536 | -0.16274 | -0.18699 | -0.21469 | -0.23781 | -0.26512 | -0.29173 | -0.32314 | -0.35567 | -0.54342 | -0.68314 | -0.79122 | 0.07524 | 0.063938 | 0.044364 | 0.02309 | 0.0072665 | -0.015859 | -0.028075 | -0.053833 | -0.075499 | -0.10721 | -0.14071 | -0.28998 | -0.37354 | -0.44323 | -0.011001 | -0.030077 | -0.061302 | -0.094011 | -0.12139 | -0.1557 | -0.18028 | -0.21493 | -0.24567 | -0.28617 | -0.32842 | -0.52699 | -0.64723 | -0.73839
|  | BRIDGE OF DUN | FS |  |  |  | 0.064 | -0.08379 | -0.093244 | -0.1039 | -0.11608 | -0.12676 | -0.14057 | -0.15632 | -0.17494 | -0.20184 | -0.22472 | -0.24988 | -0.38604 | -0.55782 | -0.66333 | 0.076267 | 0.071006 | 0.06125 | 0.048618 | 0.039191 | 0.0234 | 0.0043335 | -0.0058416 | -0.032214 | -0.049433 | -0.073468 | -0.1934 | -0.31593 | -0.39351 | -0.0039337 | -0.014221 | -0.027572 | -0.043601 | -0.056514 | -0.075422 | -0.097319 | -0.11669 | -0.15109 | -0.17657 | -0.20858 | -0.37452 | -0.5425 | -0.62682
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.313 | 9.9909 | 9.4737 | 8.8439 | 8.1484 | 7.4376 | 6.6612 | 5.8864 | 5.0683 | 4.2823 | 3.5083 | 2.8512 | 1.1144 | 0.45213 | 0.10498 | 10.7051 | 10.3141 | 9.8982 | 9.4375 | 8.9634 | 8.4535 | 7.9332 | 7.3927 | 6.8668 | 6.3415 | 5.8728 | 4.7566 | 4.3675 | 4.0433 | 10.7127 | 10.2418 | 9.6886 | 9.07 | 8.442 | 7.7513 | 7.0485 | 6.3146 | 5.6109 | 4.9113 | 4.3076 | 2.7653 | 2.2712 | 1.9632
|  | BRIDGE OF EARN | CT |  |  |  | 0.313 | 10.1263 | 9.6898 | 9.1092 | 8.4079 | 7.6398 | 6.7989 | 6.005 | 5.2076 | 4.4948 | 3.7192 | 3.0745 | 1.1516 | 0.45213 | 0.10498 | 10.8173 | 10.4928 | 10.1153 | 9.644 | 9.1351 | 8.5785 | 8.0578 | 7.5235 | 7.045 | 6.4946 | 6.016 | 4.764 | 4.3675 | 4.0433 | 10.8388 | 10.442 | 9.9339 | 9.3074 | 8.6213 | 7.8801 | 7.1666 | 6.4498 | 5.8241 | 5.1254 | 4.536 | 2.8434 | 2.2712 | 1.9632
|  | BRIDGE OF EARN | LW |  |  |  | 0.313 | 9.9909 | 9.4737 | 8.8439 | 8.1484 | 7.4376 | 6.6612 | 5.8864 | 5.0683 | 4.2823 | 3.5083 | 2.8512 | 1.1144 | 0.60719 | 0.26484 | 10.7051 | 10.3141 | 9.8982 | 9.4375 | 8.9634 | 8.4535 | 7.9332 | 7.3927 | 6.8668 | 6.3415 | 5.8728 | 4.7566 | 4.5153 | 4.334 | 10.7127 | 10.2418 | 9.6886 | 9.07 | 8.442 | 7.7513 | 7.0485 | 6.3146 | 5.6109 | 4.9113 | 4.3076 | 2.7653 | 2.3465 | 2.0275
|  | BRIDGE OF EARN | ST |  |  |  | 0.313 | 10.1601 | 9.7762 | 9.3187 | 8.8013 | 8.2567 | 7.6784 | 7.1953 | 6.6627 | 6.1395 | 5.5332 | 4.991 | 3.3062 | 2.6566 | 2.2685 | 10.8394 | 10.559 | 10.2249 | 9.8343 | 9.4138 | 8.9612 | 8.5798 | 8.1673 | 7.762 | 7.2819 | 6.8439 | 5.595 | 5.1747 | 4.841 | 10.8719 | 10.5294 | 10.1249 | 9.6611 | 9.1708 | 8.6566 | 8.2193 | 7.7418 | 7.2713 | 6.7203 | 6.2194 | 4.6785 | 4.1241 | 3.7889
|  | BRIDGE OF EARN | FS |  |  |  | 0.313 | 10.3541 | 10.0664 | 9.7545 | 9.3778 | 8.9438 | 8.4235 | 8.0926 | 7.6866 | 7.2328 | 6.7591 | 6.3034 | 4.1785 | 3.0168 | 2.47 | 10.979 | 10.7601 | 10.5257 | 10.2306 | 9.8895 | 9.4763 | 9.2103 | 8.9016 | 8.5519 | 8.1827 | 7.8173 | 6.1448 | 5.2327 | 4.6325 | 11.0484 | 10.79 | 10.516 | 10.177 | 9.7864 | 9.3156 | 9.0203 | 8.6616 | 8.257 | 7.8324 | 7.4202 | 5.4958 | 4.4542 | 3.9796
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.046 | 0.63762 | 0.61659 | 0.60844 | 0.60238 | 0.59499 | 0.58198 | 0.56429 | 0.55178 | 0.53108 | 0.51746 | 0.49976 | 0.44999 | 0.41756 | 0.37381 | 0.59981 | 0.5751 | 0.56396 | 0.55197 | 0.53945 | 0.5196 | 0.49383 | 0.47952 | 0.4641 | 0.45377 | 0.44026 | 0.39787 | 0.36549 | 0.32215 | 0.46161 | 0.4352 | 0.41525 | 0.40019 | 0.38281 | 0.35677 | 0.3241 | 0.30517 | 0.28507 | 0.27147 | 0.25414 | 0.20173 | 0.16429 | 0.11452
|  | BRIDGE OF GAUR | CT |  |  |  | 0.046 | 0.63762 | 0.62306 | 0.63103 | 0.61715 | 0.61088 | 0.60596 | 0.59393 | 0.58083 | 0.56657 | 0.55806 | 0.545 | 0.50589 | 0.49058 | 0.46773 | 0.59981 | 0.58286 | 0.58888 | 0.56926 | 0.55854 | 0.54813 | 0.52953 | 0.5171 | 0.5063 | 0.49951 | 0.4891 | 0.45843 | 0.44658 | 0.42718 | 0.46161 | 0.44221 | 0.44137 | 0.41605 | 0.39967 | 0.38351 | 0.35784 | 0.34166 | 0.32778 | 0.31917 | 0.30632 | 0.26681 | 0.25084 | 0.22609
|  | BRIDGE OF GAUR | LW |  |  |  | 0.046 | 0.63763 | 0.61659 | 0.60844 | 0.60238 | 0.59499 | 0.58198 | 0.56429 | 0.55178 | 0.53108 | 0.51746 | 0.49976 | 0.44999 | 0.41756 | 0.37381 | 0.60017 | 0.5751 | 0.56396 | 0.55197 | 0.53945 | 0.5196 | 0.49383 | 0.47952 | 0.4641 | 0.45377 | 0.44026 | 0.39787 | 0.36549 | 0.32215 | 0.46247 | 0.4352 | 0.41525 | 0.40019 | 0.38281 | 0.35677 | 0.3241 | 0.30517 | 0.28507 | 0.27147 | 0.25414 | 0.20173 | 0.16429 | 0.11452
|  | BRIDGE OF GAUR | ST |  |  |  | 0.046 | 0.64184 | 0.63694 | 0.62589 | 0.61452 | 0.61439 | 0.61678 | 0.61322 | 0.61014 | 0.60161 | 0.59674 | 0.59062 | 0.52766 | 0.48815 | 0.46183 | 0.60478 | 0.5984 | 0.5842 | 0.56997 | 0.56963 | 0.56913 | 0.56334 | 0.55796 | 0.5473 | 0.5402 | 0.53204 | 0.4675 | 0.42709 | 0.3967 | 0.46733 | 0.45917 | 0.44262 | 0.42597 | 0.41817 | 0.41654 | 0.40787 | 0.4 | 0.3856 | 0.37559 | 0.36406 | 0.28521 | 0.24008 | 0.20789
|  | BRIDGE OF GAUR | FS |  |  |  | 0.046 | 0.64246 | 0.63846 | 0.63203 | 0.62426 | 0.62445 | 0.61731 | 0.61902 | 0.61552 | 0.61124 | 0.60351 | 0.60122 | 0.57413 | 0.54278 | 0.52311 | 0.60639 | 0.60145 | 0.59403 | 0.58521 | 0.58612 | 0.57825 | 0.57801 | 0.5728 | 0.56624 | 0.55653 | 0.55277 | 0.51909 | 0.48637 | 0.47088 | 0.47027 | 0.46425 | 0.45626 | 0.44682 | 0.44342 | 0.43337 | 0.43409 | 0.42695 | 0.41839 | 0.40593 | 0.40011 | 0.35245 | 0.30443 | 0.28469
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 0.621 | 3.6945 | 3.6308 | 3.5395 | 3.4195 | 3.2986 | 3.1615 | 3.0108 | 2.9266 | 2.8713 | 2.7827 | 2.7043 | 2.5378 | 2.44 | 2.2947 | 3.6075 | 3.567 | 3.5224 | 3.4594 | 3.399 | 3.3272 | 3.2447 | 3.1778 | 3.1011 | 3.0297 | 2.9653 | 2.8483 | 2.7922 | 2.6898 | 3.6489 | 3.6148 | 3.5716 | 3.4756 | 3.3724 | 3.2531 | 3.1257 | 3.035 | 2.9554 | 2.8617 | 2.7784 | 2.6283 | 2.5479 | 2.4155
|  | BROADFORD | CT |  |  |  | 0.621 | 3.6945 | 3.6308 | 3.5395 | 3.4195 | 3.2986 | 3.1615 | 3.0108 | 2.9266 | 2.8737 | 2.8122 | 2.7598 | 2.63 | 2.5502 | 2.4396 | 3.6075 | 3.5677 | 3.5254 | 3.4594 | 3.399 | 3.3285 | 3.2504 | 3.1813 | 3.1355 | 3.079 | 3.0267 | 2.9089 | 2.8459 | 2.7367 | 3.6489 | 3.6194 | 3.58 | 3.4756 | 3.3724 | 3.2531 | 3.1257 | 3.035 | 2.9791 | 2.9093 | 2.8473 | 2.7199 | 2.6596 | 2.5686
|  | BROADFORD | LW |  |  |  | 0.621 | 3.704 | 3.64 | 3.5541 | 3.4453 | 3.345 | 3.2015 | 3.0562 | 2.9678 | 2.8713 | 2.7827 | 2.7043 | 2.5378 | 2.44 | 2.2947 | 3.6116 | 3.567 | 3.5224 | 3.4611 | 3.4118 | 3.3272 | 3.2447 | 3.1778 | 3.1011 | 3.0297 | 2.9653 | 2.8483 | 2.7922 | 2.6898 | 3.6512 | 3.6148 | 3.5716 | 3.49 | 3.4063 | 3.2739 | 3.1471 | 3.0558 | 2.9554 | 2.8617 | 2.7784 | 2.6283 | 2.5479 | 2.4155
|  | BROADFORD | ST |  |  |  | 0.621 | 3.717 | 3.6801 | 3.6302 | 3.5821 | 3.5275 | 3.4816 | 3.42 | 3.3683 | 3.2959 | 3.2403 | 3.1649 | 2.8718 | 2.7612 | 2.714 | 3.6215 | 3.6023 | 3.5726 | 3.5449 | 3.5121 | 3.4877 | 3.4491 | 3.4164 | 3.3654 | 3.3302 | 3.2767 | 3.0362 | 2.9285 | 2.8464 | 3.66 | 3.6451 | 3.6175 | 3.591 | 3.5625 | 3.5332 | 3.476 | 3.4288 | 3.3567 | 3.3091 | 3.2347 | 2.9424 | 2.8427 | 2.7999
|  | BROADFORD | FS |  |  |  | 0.621 | 3.7356 | 3.7146 | 3.6969 | 3.6798 | 3.6568 | 3.6408 | 3.6123 | 3.5643 | 3.518 | 3.4624 | 3.4058 | 3.1236 | 2.8665 | 2.7574 | 3.6266 | 3.6159 | 3.6014 | 3.5874 | 3.5681 | 3.5552 | 3.5302 | 3.497 | 3.4649 | 3.4245 | 3.3839 | 3.1704 | 2.968 | 2.8095 | 3.6665 | 3.6574 | 3.6449 | 3.632 | 3.6165 | 3.6028 | 3.5832 | 3.5574 | 3.5296 | 3.4904 | 3.4349 | 3.1654 | 2.9353 | 2.8482
| CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.506 | 4.6925 | 4.6076 | 4.4748 | 4.2901 | 3.9898 | 3.659 | 3.2947 | 3.1125 | 2.976 | 2.8758 | 2.7544 | 2.2083 | 1.9645 | 1.6621 | 6.9488 | 6.8983 | 6.82 | 6.7087 | 6.5947 | 6.4694 | 6.3204 | 6.2111 | 6.1097 | 6.024 | 5.8599 | 5.489 | 5.3838 | 5.1836 | 5.5317 | 5.4522 | 5.3291 | 5.172 | 5.0238 | 4.8599 | 4.6468 | 4.4172 | 4.2443 | 4.1222 | 3.9107 | 3.4102 | 3.1929 | 2.9108
|  | BRODICK | CT |  |  |  | 0.506 | 4.6925 | 4.6076 | 4.4748 | 4.2901 | 3.9898 | 3.659 | 3.2947 | 3.1125 | 2.976 | 2.8758 | 2.7722 | 2.3758 | 2.1611 | 1.8198 | 6.9488 | 6.8983 | 6.82 | 6.7087 | 6.5947 | 6.4694 | 6.3204 | 6.2111 | 6.1097 | 6.024 | 5.8988 | 5.564 | 5.4242 | 5.1836 | 5.5317 | 5.4522 | 5.3291 | 5.172 | 5.0238 | 4.8599 | 4.6468 | 4.4172 | 4.2443 | 4.1222 | 3.9668 | 3.5632 | 3.3686 | 3.0937
|  | BRODICK | LW |  |  |  | 0.506 | 4.7016 | 4.6347 | 4.5412 | 4.4225 | 4.1804 | 3.8784 | 3.5661 | 3.3691 | 3.1487 | 2.9802 | 2.7544 | 2.2083 | 1.9645 | 1.6621 | 6.9507 | 6.912 | 6.8636 | 6.7977 | 6.7171 | 6.6012 | 6.4829 | 6.3567 | 6.1672 | 6.0257 | 5.8599 | 5.489 | 5.3838 | 5.2099 | 5.5402 | 5.4778 | 5.3921 | 5.2951 | 5.1901 | 5.0428 | 4.8261 | 4.5912 | 4.3102 | 4.1268 | 3.9107 | 3.4102 | 3.1929 | 2.9108
|  | BRODICK | ST |  |  |  | 0.506 | 4.7289 | 4.689 | 4.6308 | 4.5651 | 4.4878 | 4.3969 | 4.2426 | 4.1005 | 3.9335 | 3.7809 | 3.6003 | 2.7914 | 2.4101 | 2.1624 | 6.9666 | 6.9464 | 6.9203 | 6.883 | 6.834 | 6.7756 | 6.7041 | 6.6272 | 6.5275 | 6.4336 | 6.3162 | 5.737 | 5.5366 | 5.4409 | 5.5655 | 5.5288 | 5.4758 | 5.4155 | 5.3441 | 5.2682 | 5.1787 | 5.0837 | 4.9612 | 4.8417 | 4.6964 | 3.9669 | 3.6659 | 3.5046
|  | BRODICK | FS |  |  |  | 0.506 | 4.7535 | 4.7276 | 4.6956 | 4.6558 | 4.6138 | 4.5633 | 4.5133 | 4.4426 | 4.3596 | 4.271 | 4.13 | 3.3754 | 2.6914 | 2.2872 | 6.9757 | 6.9619 | 6.9473 | 6.9265 | 6.9029 | 6.8698 | 6.8371 | 6.7924 | 6.7306 | 6.6632 | 6.5888 | 6.146 | 5.6315 | 5.2371 | 5.5873 | 5.5636 | 5.5342 | 5.4971 | 5.4584 | 5.4112 | 5.3647 | 5.2988 | 5.221 | 5.1379 | 5.0463 | 4.4935 | 3.8619 | 3.5439
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 0.811 | 3.2931 | 3.2212 | 3.1131 | 2.9735 | 2.8365 | 2.6611 | 2.4523 | 2.3432 | 2.2855 | 2.1758 | 2.074 | 1.8288 | 1.6945 | 1.5287 | 4.3428 | 4.2914 | 4.229 | 4.1583 | 4.0892 | 4.0038 | 3.8913 | 3.8068 | 3.7411 | 3.66 | 3.5874 | 3.4213 | 3.3493 | 3.2212 | 3.8051 | 3.7434 | 3.656 | 3.5337 | 3.4111 | 3.2695 | 3.1063 | 3.0343 | 2.9882 | 2.9236 | 2.8358 | 2.6009 | 2.4827 | 2.3394
|  | BRORA | CT |  |  |  | 0.811 | 3.2931 | 3.2212 | 3.1131 | 2.9735 | 2.8365 | 2.6611 | 2.4523 | 2.3432 | 2.2912 | 2.2167 | 2.1407 | 1.9026 | 1.7965 | 1.6587 | 4.3428 | 4.2914 | 4.2364 | 4.1583 | 4.0904 | 4.0041 | 3.8953 | 3.8068 | 3.7728 | 3.7048 | 3.6426 | 3.4565 | 3.3633 | 3.2212 | 3.8051 | 3.7434 | 3.656 | 3.5337 | 3.4111 | 3.2695 | 3.1063 | 3.0343 | 2.9979 | 2.9525 | 2.91 | 2.6813 | 2.5837 | 2.4715
|  | BRORA | LW |  |  |  | 0.811 | 3.3047 | 3.2383 | 3.1189 | 2.9937 | 2.8574 | 2.6933 | 2.4897 | 2.3789 | 2.2855 | 2.1758 | 2.074 | 1.8288 | 1.6945 | 1.5287 | 4.3448 | 4.2951 | 4.229 | 4.1608 | 4.0892 | 4.0038 | 3.8913 | 3.808 | 3.7411 | 3.66 | 3.5874 | 3.4213 | 3.3493 | 3.2455 | 3.815 | 3.7535 | 3.657 | 3.5471 | 3.4255 | 3.2868 | 3.1262 | 3.0512 | 2.9882 | 2.9236 | 2.8358 | 2.6009 | 2.4827 | 2.3394
|  | BRORA | ST |  |  |  | 0.811 | 3.3158 | 3.2675 | 3.1999 | 3.1338 | 3.0618 | 2.9876 | 2.9057 | 2.84 | 2.7472 | 2.6569 | 2.552 | 2.1545 | 2.015 | 1.9468 | 4.3592 | 4.3292 | 4.2905 | 4.255 | 4.2108 | 4.1716 | 4.1197 | 4.083 | 4.0201 | 3.9604 | 3.8915 | 3.5874 | 3.4462 | 3.326 | 3.8257 | 3.7824 | 3.7205 | 3.6605 | 3.5965 | 3.5324 | 3.4605 | 3.4042 | 3.3329 | 3.2648 | 3.1902 | 2.8906 | 2.7415 | 2.6649
|  | BRORA | FS |  |  |  | 0.811 | 3.3491 | 3.3187 | 3.2983 | 3.2742 | 3.2542 | 3.2215 | 3.1931 | 3.1253 | 3.0733 | 2.9982 | 2.9301 | 2.5528 | 2.162 | 2.048 | 4.3728 | 4.3511 | 4.3341 | 4.3092 | 4.2945 | 4.267 | 4.2431 | 4.1995 | 4.1635 | 4.1129 | 4.0672 | 3.7959 | 3.4852 | 3.263 | 3.855 | 3.8276 | 3.8086 | 3.7858 | 3.7671 | 3.7424 | 3.7192 | 3.6696 | 3.6216 | 3.567 | 3.5155 | 3.2416 | 2.8989 | 2.7871
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 1.162 | 4.5883 | 4.515 | 4.2078 | 3.7693 | 3.2828 | 2.6311 | 1.9323 | 1.1209 | 0.24515 | -0.19963 | -0.86631 | -2.7765 | -3.5231 | -4.2643 | 7.0716 | 6.9041 | 6.6757 | 6.428 | 6.1083 | 5.8095 | 5.3666 | 4.8486 | 4.3379 | 4.1579 | 3.7232 | 2.3651 | 1.3106 | -1.6243 | 6.0649 | 5.8516 | 5.517 | 5.1363 | 4.7019 | 4.0967 | 3.4575 | 2.6918 | 1.8215 | 1.5713 | 0.9374 | -0.75194 | -1.2053 | -1.8887
|  | BROUGHTY FERRY | CT |  |  |  | 1.162 | 4.5883 | 4.515 | 4.2496 | 3.8316 | 3.3167 | 2.794 | 2.0969 | 1.3027 | 0.65088 | 0.33055 | -0.1817 | -2.4567 | -3.5231 | -4.2643 | 7.0716 | 6.9041 | 6.6757 | 6.428 | 6.1083 | 5.8095 | 5.3666 | 4.8486 | 4.4279 | 4.2977 | 3.9253 | 2.3651 | 1.3106 | -0.29504 | 6.0737 | 5.8726 | 5.5372 | 5.1748 | 4.7019 | 4.2593 | 3.6126 | 2.86 | 2.2551 | 2.1198 | 1.6343 | -0.31647 | -1.2053 | -1.8887
|  | BROUGHTY FERRY | LW |  |  |  | 1.162 | 4.59 | 4.5155 | 4.2078 | 3.7693 | 3.2828 | 2.6311 | 1.9323 | 1.1209 | 0.24515 | -0.19963 | -0.86631 | -2.7765 | -3.1799 | -3.8877 | 7.083 | 6.9242 | 6.722 | 6.4925 | 6.2377 | 5.8418 | 5.4213 | 4.9258 | 4.3379 | 4.1579 | 3.7232 | 2.6555 | 2.4818 | 1.9981 | 6.0649 | 5.8516 | 5.517 | 5.1363 | 4.7131 | 4.0967 | 3.4575 | 2.6918 | 1.8215 | 1.5713 | 0.9374 | -0.75194 | -1.1002 | -1.8078
|  | BROUGHTY FERRY | ST |  |  |  | 1.162 | 4.6119 | 4.5845 | 4.5437 | 4.5036 | 4.4519 | 4.386 | 4.3243 | 4.1617 | 3.9697 | 3.7332 | 3.4712 | 2.1609 | 1.1331 | 0.025057 | 7.1302 | 7.0574 | 6.9659 | 6.8765 | 6.7616 | 6.6175 | 6.4825 | 6.2853 | 6.0669 | 5.8012 | 5.5057 | 4.0839 | 2.9003 | 1.3002 | 6.1569 | 6.0795 | 5.9887 | 5.9072 | 5.796 | 5.648 | 5.5184 | 5.3077 | 5.0887 | 4.8047 | 4.4909 | 3.2675 | 2.4501 | 1.6869
|  | BROUGHTY FERRY | FS |  |  |  | 1.162 | 4.6176 | 4.595 | 4.5689 | 4.5407 | 4.5038 | 4.4202 | 4.2825 | 4.1116 | 3.8797 | 3.6436 | 3.4335 | 1.6193 | 0.11557 | -1.4224 | 7.1357 | 7.062 | 6.9796 | 6.8908 | 6.7816 | 6.6496 | 6.4862 | 6.3149 | 6.0722 | 5.8239 | 5.5963 | 3.7774 | 1.6379 | -1.6243 | 6.1711 | 6.0978 | 6.0144 | 5.9297 | 5.8231 | 5.6913 | 5.5388 | 5.382 | 5.1411 | 4.8952 | 4.6965 | 2.937 | 1.8167 | 0.58756
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 0.239 | 11.1028 | 10.9931 | 10.8764 | 10.7275 | 10.5385 | 10.3612 | 10.0989 | 9.8804 | 9.6398 | 9.4252 | 9.1994 | 8.6862 | 8.6031 | 8.2884 | 12.083 | 12.0153 | 11.9447 | 11.8549 | 11.742 | 11.6369 | 11.4801 | 11.3342 | 11.141 | 10.975 | 10.797 | 10.4036 | 10.3645 | 10.1339 | 11.6012 | 11.4949 | 11.3847 | 11.244 | 11.0647 | 10.8986 | 10.6494 | 10.4348 | 10.1912 | 9.9793 | 9.7555 | 9.25 | 9.175 | 8.8678
|  | BRUCHAG | CT |  |  |  | 0.239 | 11.1028 | 10.9931 | 10.8764 | 10.7275 | 10.5385 | 10.3612 | 10.0989 | 9.8804 | 9.7101 | 9.5652 | 9.4056 | 8.9535 | 8.8481 | 8.6155 | 12.083 | 12.0153 | 11.9447 | 11.8549 | 11.742 | 11.6369 | 11.4801 | 11.3342 | 11.2008 | 11.0835 | 10.9499 | 10.5558 | 10.44 | 10.1776 | 11.6012 | 11.4949 | 11.3847 | 11.244 | 11.0647 | 10.8986 | 10.6494 | 10.4348 | 10.2671 | 10.1236 | 9.9644 | 9.5162 | 9.4187 | 9.195
|  | BRUCHAG | LW |  |  |  | 0.239 | 11.1129 | 11.0131 | 10.9132 | 10.7784 | 10.6265 | 10.4176 | 10.1497 | 9.9242 | 9.6398 | 9.4252 | 9.1994 | 8.6862 | 8.6031 | 8.2884 | 12.0864 | 12.0297 | 11.9714 | 11.8925 | 11.8037 | 11.6789 | 11.5184 | 11.3604 | 11.141 | 10.975 | 10.797 | 10.4036 | 10.3645 | 10.1339 | 11.6105 | 11.5136 | 11.4198 | 11.2924 | 11.1489 | 10.9497 | 10.6928 | 10.4718 | 10.1912 | 9.9793 | 9.7555 | 9.25 | 9.175 | 8.8678
|  | BRUCHAG | ST |  |  |  | 0.239 | 11.139 | 11.0932 | 11.0631 | 11.0177 | 10.9778 | 10.9142 | 10.849 | 10.7527 | 10.6504 | 10.5218 | 10.387 | 9.875 | 9.8287 | 9.9178 | 12.0914 | 12.0751 | 12.0553 | 12.023 | 11.9932 | 11.9484 | 11.9021 | 11.8377 | 11.7679 | 11.6754 | 11.5668 | 11.0756 | 10.9412 | 10.8693 | 11.6362 | 11.593 | 11.563 | 11.5179 | 11.4782 | 11.4149 | 11.3501 | 11.2553 | 11.1546 | 11.0276 | 10.8946 | 10.3738 | 10.3173 | 10.3953
|  | BRUCHAG | FS |  |  |  | 0.239 | 11.16 | 11.1255 | 11.1062 | 11.0852 | 11.0527 | 11.0271 | 10.9804 | 10.9192 | 10.8289 | 10.7364 | 10.6603 | 10.0908 | 9.6204 | 9.4012 | 12.0994 | 12.0871 | 12.0773 | 12.0591 | 12.0333 | 12.0107 | 11.9738 | 11.9291 | 11.8654 | 11.8001 | 11.7436 | 11.2542 | 10.7907 | 10.4067 | 11.6551 | 11.6221 | 11.6021 | 11.5803 | 11.5471 | 11.5207 | 11.4734 | 11.414 | 11.3258 | 11.2353 | 11.1611 | 10.5985 | 10.1401 | 9.9256
| KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 3.398 | 6.4234 | 6.0062 | 5.1742 | 4.1636 | 3.1197 | 2.004 | 0.65905 | -0.55035 | -2.082 | -3.4914 | -4.3677 | -7.0112 | -8.7185 | -9.9103 | 7.827 | 7.5583 | 7.1548 | 6.6174 | 6.0889 | 5.5463 | 4.8212 | 4.1397 | 3.2353 | 2.3352 | 1.9447 | 0.85444 | -0.073665 | -1.0944 | 7.9801 | 7.6066 | 6.8746 | 5.983 | 5.0447 | 4.0436 | 2.8161 | 1.7478 | 0.34677 | -0.94712 | -1.7435 | -4.1278 | -5.5716 | -6.6309
|  | BUCKIE | CT |  |  |  | 3.398 | 6.4721 | 6.0384 | 5.2446 | 4.2064 | 3.1197 | 2.004 | 0.65905 | -0.51832 | -1.8543 | -3.1962 | -3.9536 | -6.9478 | -8.7185 | -9.9103 | 7.8702 | 7.5939 | 7.194 | 6.6174 | 6.0889 | 5.5463 | 4.8212 | 4.1397 | 3.3595 | 2.4841 | 2.1668 | 0.89866 | -0.073665 | -1.0944 | 8.022 | 7.6315 | 6.9329 | 6.0058 | 5.0447 | 4.0436 | 2.8161 | 1.7715 | 0.56205 | -0.66675 | -1.3508 | -4.0169 | -5.5716 | -6.6309
|  | BUCKIE | LW |  |  |  | 3.398 | 6.4234 | 6.0062 | 5.1742 | 4.1636 | 3.1356 | 2.0237 | 0.68601 | -0.55035 | -2.082 | -3.4914 | -4.3677 | -7.0112 | -8.0989 | -8.9792 | 7.827 | 7.5583 | 7.1548 | 6.675 | 6.2024 | 5.6626 | 4.9135 | 4.1739 | 3.2353 | 2.3352 | 1.9447 | 0.85444 | 0.48121 | 0.029207 | 7.9801 | 7.6066 | 6.8746 | 5.983 | 5.0825 | 4.0758 | 2.8494 | 1.7478 | 0.34677 | -0.94712 | -1.7435 | -4.1278 | -5.0974 | -5.9037
|  | BUCKIE | ST |  |  |  | 3.398 | 6.566 | 6.2699 | 5.9023 | 5.4389 | 4.9872 | 4.5524 | 4.0389 | 3.4157 | 2.6496 | 1.7775 | 1.6448 | -0.79454 | -2.7267 | -4.5049 | 7.9165 | 7.7284 | 7.4766 | 7.1496 | 6.8225 | 6.4904 | 6.059 | 5.507 | 4.8292 | 4.0196 | 3.8232 | 2.3395 | 1.6325 | 0.94303 | 8.1102 | 7.8525 | 7.5335 | 7.127 | 6.7345 | 6.3425 | 5.8685 | 5.2967 | 4.5864 | 3.7701 | 3.6649 | 1.3718 | -0.32083 | -1.8868
|  | BUCKIE | FS |  |  |  | 3.398 | 6.6683 | 6.4394 | 6.1478 | 5.7906 | 5.3856 | 5.017 | 4.6112 | 4.0558 | 3.4313 | 2.7625 | 2.2691 | -0.14382 | -2.4758 | -4.5408 | 7.972 | 7.8158 | 7.6318 | 7.3943 | 7.1165 | 6.8316 | 6.5225 | 6.1307 | 5.6559 | 5.1408 | 4.8197 | 3.2326 | 1.933 | -0.069537 | 8.1975 | 7.9986 | 7.7476 | 7.4368 | 7.0831 | 6.7525 | 6.3828 | 5.88 | 5.3153 | 4.7027 | 4.2555 | 2.0674 | -0.060842 | -1.9076
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0.138 | 1.6063 | 1.5837 | 1.5515 | 1.5133 | 1.4815 | 1.4301 | 1.3803 | 1.3488 | 1.3207 | 1.2892 | 1.2611 | 1.181 | 1.1321 | 1.0712 | 1.6801 | 1.6646 | 1.6426 | 1.6163 | 1.5981 | 1.5621 | 1.5303 | 1.5059 | 1.485 | 1.4606 | 1.4384 | 1.3799 | 1.3383 | 1.1641 | 1.6461 | 1.6283 | 1.5963 | 1.5588 | 1.5284 | 1.4781 | 1.4306 | 1.399 | 1.3713 | 1.3407 | 1.3133 | 1.2344 | 1.1836 | 1.1195
|  | BUNOICH | CT |  |  |  | 0.138 | 1.6075 | 1.5858 | 1.5593 | 1.521 | 1.4863 | 1.4431 | 1.3968 | 1.3652 | 1.3414 | 1.3264 | 1.3046 | 1.2337 | 1.2008 | 1.1614 | 1.6843 | 1.6697 | 1.6551 | 1.6285 | 1.6084 | 1.5821 | 1.5555 | 1.5276 | 1.5058 | 1.4919 | 1.4704 | 1.3955 | 1.3417 | 1.2489 | 1.653 | 1.6326 | 1.6085 | 1.5709 | 1.5386 | 1.4986 | 1.4568 | 1.4245 | 1.4 | 1.3849 | 1.3632 | 1.2942 | 1.2632 | 1.2248
|  | BUNOICH | LW |  |  |  | 0.138 | 1.6104 | 1.5837 | 1.5515 | 1.5133 | 1.4815 | 1.4301 | 1.3803 | 1.3488 | 1.3207 | 1.2892 | 1.2611 | 1.181 | 1.1321 | 1.0712 | 1.6861 | 1.6646 | 1.6426 | 1.6163 | 1.5981 | 1.5621 | 1.5303 | 1.5059 | 1.485 | 1.4606 | 1.4384 | 1.3799 | 1.3426 | 1.2922 | 1.6556 | 1.6283 | 1.5963 | 1.5588 | 1.5284 | 1.4781 | 1.4306 | 1.399 | 1.3713 | 1.3407 | 1.3133 | 1.2344 | 1.1836 | 1.1195
|  | BUNOICH | ST |  |  |  | 0.138 | 1.6063 | 1.6022 | 1.5809 | 1.5615 | 1.5435 | 1.5234 | 1.4993 | 1.4818 | 1.4545 | 1.4389 | 1.4123 | 1.288 | 1.2287 | 1.1921 | 1.6801 | 1.6817 | 1.6664 | 1.6533 | 1.642 | 1.6287 | 1.6117 | 1.5994 | 1.5778 | 1.5672 | 1.546 | 1.4237 | 1.3383 | 1.237 | 1.6461 | 1.6485 | 1.6275 | 1.6087 | 1.5918 | 1.5729 | 1.5501 | 1.5337 | 1.5074 | 1.4928 | 1.4674 | 1.3428 | 1.2804 | 1.2401
|  | BUNOICH | FS |  |  |  | 0.138 | 1.6152 | 1.6064 | 1.6033 | 1.5946 | 1.5873 | 1.579 | 1.5673 | 1.5481 | 1.5316 | 1.5095 | 1.4887 | 1.3998 | 1.299 | 1.2622 | 1.6841 | 1.6787 | 1.6761 | 1.6678 | 1.6609 | 1.6529 | 1.6405 | 1.6236 | 1.6086 | 1.5884 | 1.5698 | 1.4812 | 1.3443 | 1.1641 | 1.6553 | 1.6513 | 1.6483 | 1.6395 | 1.6322 | 1.624 | 1.6121 | 1.5936 | 1.5775 | 1.5559 | 1.535 | 1.4524 | 1.358 | 1.3236
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 0.041 | 3.1915 | 3.097 | 2.9993 | 2.8849 | 2.7437 | 2.6114 | 2.434 | 2.3249 | 2.2055 | 2.1331 | 2.0398 | 1.7768 | 1.6422 | 1.5136 | 3.3886 | 3.3343 | 3.293 | 3.2436 | 3.1734 | 3.1156 | 3.0262 | 2.9599 | 2.8829 | 2.8466 | 2.784 | 2.6525 | 2.5793 | 2.4548 | 3.1894 | 3.1021 | 3.0231 | 2.9297 | 2.8073 | 2.7044 | 2.5415 | 2.4449 | 2.3217 | 2.2572 | 2.1653 | 1.9417 | 1.8241 | 1.7058
|  | BURGARHILL | CT |  |  |  | 0.041 | 3.1915 | 3.097 | 2.9993 | 2.8849 | 2.7437 | 2.6114 | 2.434 | 2.3249 | 2.2357 | 2.182 | 2.1097 | 1.8302 | 1.6967 | 1.5787 | 3.3886 | 3.3343 | 3.293 | 3.2436 | 3.1734 | 3.1156 | 3.0262 | 2.9599 | 2.9051 | 2.8745 | 2.8254 | 2.661 | 2.5793 | 2.4749 | 3.1894 | 3.1021 | 3.0231 | 2.9297 | 2.8073 | 2.7044 | 2.5415 | 2.4449 | 2.3583 | 2.3098 | 2.235 | 1.9884 | 1.873 | 1.7624
|  | BURGARHILL | LW |  |  |  | 0.041 | 3.2079 | 3.1237 | 3.023 | 2.9027 | 2.7688 | 2.6205 | 2.4407 | 2.331 | 2.2055 | 2.1331 | 2.0398 | 1.7768 | 1.6422 | 1.5136 | 3.3937 | 3.3443 | 3.3052 | 3.2524 | 3.1929 | 3.1266 | 3.0364 | 2.9707 | 2.8829 | 2.8466 | 2.784 | 2.6525 | 2.5993 | 2.5394 | 3.2013 | 3.1225 | 3.0429 | 2.9427 | 2.8313 | 2.7097 | 2.5491 | 2.4484 | 2.3217 | 2.2572 | 2.1653 | 1.9417 | 1.8241 | 1.7058
|  | BURGARHILL | ST |  |  |  | 0.041 | 3.2179 | 3.1568 | 3.0689 | 2.9723 | 2.8859 | 2.7859 | 2.6923 | 2.6003 | 2.5184 | 2.4185 | 2.3207 | 1.9044 | 1.7135 | 1.6016 | 3.4027 | 3.3766 | 3.3402 | 3.2945 | 3.2582 | 3.2095 | 3.1658 | 3.1158 | 3.0734 | 3.0163 | 2.9608 | 2.7072 | 2.59 | 2.4965 | 3.2131 | 3.1632 | 3.0923 | 3.01 | 2.9429 | 2.8571 | 2.7771 | 2.6929 | 2.6172 | 2.5266 | 2.4365 | 2.0584 | 1.8759 | 1.7723
|  | BURGARHILL | FS |  |  |  | 0.041 | 3.2548 | 3.2191 | 3.1926 | 3.1564 | 3.1293 | 3.0922 | 3.0517 | 2.9896 | 2.9127 | 2.8533 | 2.7754 | 2.3499 | 1.955 | 1.7958 | 3.4174 | 3.3973 | 3.3837 | 3.3603 | 3.3483 | 3.3242 | 3.2965 | 3.2671 | 3.2216 | 3.1972 | 3.1516 | 2.8926 | 2.641 | 2.4548 | 3.2458 | 3.2112 | 3.1878 | 3.1531 | 3.1316 | 3.0959 | 3.0563 | 3.0043 | 2.9334 | 2.8873 | 2.8161 | 2.4262 | 2.0945 | 1.9608
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 1.645 | 5.2078 | 4.9912 | 4.6663 | 4.2603 | 3.8497 | 3.3793 | 2.8362 | 2.5995 | 2.3899 | 2.1746 | 1.9587 | 1.3731 | 1.0363 | 0.69162 | 6.1866 | 6.0657 | 5.9124 | 5.702 | 5.5064 | 5.277 | 4.994 | 4.8392 | 4.6841 | 4.5058 | 4.3501 | 3.9683 | 3.7874 | 3.2787 | 5.9397 | 5.7397 | 5.4599 | 5.1035 | 4.7532 | 4.3446 | 3.8585 | 3.6257 | 3.415 | 3.1523 | 2.9273 | 2.3549 | 2.0552 | 1.7279
|  | BURGHEAD | CT |  |  |  | 1.645 | 5.2078 | 4.9912 | 4.6663 | 4.2603 | 3.8497 | 3.3793 | 2.8362 | 2.5995 | 2.3899 | 2.2127 | 2.0806 | 1.6014 | 1.3474 | 1.0702 | 6.1866 | 6.0657 | 5.9124 | 5.702 | 5.5064 | 5.277 | 4.994 | 4.8392 | 4.6959 | 4.5595 | 4.444 | 4.0593 | 3.8255 | 3.4704 | 5.9397 | 5.7397 | 5.4599 | 5.1035 | 4.7532 | 4.3446 | 3.8585 | 3.6257 | 3.4206 | 3.2347 | 3.0871 | 2.6131 | 2.3962 | 2.148
|  | BURGHEAD | LW |  |  |  | 1.645 | 5.2387 | 5.0309 | 4.7249 | 4.3543 | 3.9674 | 3.5205 | 3.0094 | 2.7523 | 2.4319 | 2.1746 | 1.9587 | 1.3731 | 1.0363 | 0.69162 | 6.2 | 6.0757 | 5.9267 | 5.7403 | 5.5536 | 5.3275 | 5.0529 | 4.897 | 4.6841 | 4.5058 | 4.3501 | 3.9683 | 3.7874 | 3.5776 | 5.9653 | 5.7684 | 5.5017 | 5.1763 | 4.8398 | 4.4482 | 3.9827 | 3.7344 | 3.415 | 3.1523 | 2.9273 | 2.3549 | 2.0552 | 1.7279
|  | BURGHEAD | ST |  |  |  | 1.645 | 5.2693 | 5.1307 | 4.9321 | 4.7174 | 4.5165 | 4.293 | 4.0632 | 3.8622 | 3.6092 | 3.364 | 3.1522 | 2.069 | 1.6408 | 1.4375 | 6.2197 | 6.1528 | 6.0516 | 5.9392 | 5.8388 | 5.7222 | 5.5971 | 5.4845 | 5.3301 | 5.1767 | 5.0476 | 4.2463 | 3.8551 | 3.5123 | 5.9972 | 5.879 | 5.7063 | 5.5173 | 5.344 | 5.1495 | 4.9428 | 4.7683 | 4.5336 | 4.3019 | 4.1005 | 3.0235 | 2.6163 | 2.4245
|  | BURGHEAD | FS |  |  |  | 1.645 | 5.3613 | 5.2737 | 5.1962 | 5.1197 | 5.0294 | 4.9527 | 4.8578 | 4.6839 | 4.5148 | 4.3321 | 4.1505 | 3.1998 | 2.1864 | 1.7488 | 6.2557 | 6.21 | 6.1595 | 6.1097 | 6.0482 | 5.997 | 5.9265 | 5.8197 | 5.7157 | 5.5977 | 5.48 | 4.8141 | 3.9927 | 3.2787 | 6.0727 | 5.9974 | 5.9258 | 5.8559 | 5.7714 | 5.7011 | 5.6112 | 5.4542 | 5.3075 | 5.1385 | 4.9691 | 4.068 | 3.1256 | 2.7282
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 4.085 | -4.6152 | -6.1499 | -7.3204 | -8.6378 | -10.4072 | -12.4784 | -15.3331 | -18.7281 | -22.2221 | -25.787 | -29.8676 | -44.0145 | -49.099 | -49.2394 | -1.5119 | -2.7177 | -3.6018 | -4.5938 | -5.9265 | -7.4829 | -9.6702 | -12.2961 | -15.0064 | -17.7358 | -20.9095 | -31.6195 | -35.4567 | -35.5621 | -1.683 | -2.5791 | -3.4686 | -4.7328 | -6.4305 | -8.4142 | -11.162 | -14.4256 | -17.7884 | -21.2197 | -25.1232 | -38.7258 | -43.6113 | -43.7404
|  | BURGHMUIR | CT |  |  |  | 4.085 | -4.6152 | -6.1499 | -7.3204 | -8.6378 | -10.4072 | -12.4784 | -15.3331 | -18.7281 | -22.2221 | -25.3854 | -29.3556 | -44.0145 | -49.099 | -49.2394 | -1.5119 | -2.7177 | -3.6018 | -4.5938 | -5.9265 | -7.4829 | -9.6702 | -12.2961 | -15.0064 | -17.4143 | -20.5168 | -31.6195 | -35.4567 | -35.5621 | -1.683 | -2.5791 | -3.4686 | -4.7328 | -6.4305 | -8.4142 | -11.162 | -14.4256 | -17.7884 | -20.8298 | -24.6307 | -38.7258 | -43.6113 | -43.7404
|  | BURGHMUIR | LW |  |  |  | 4.085 | -4.2939 | -5.754 | -6.8917 | -8.3081 | -9.8578 | -12.2053 | -15.0777 | -18.3939 | -22.1262 | -25.787 | -29.8676 | -43.2592 | -48.2583 | -48.386 | -1.2763 | -2.4347 | -3.2933 | -4.3587 | -5.5198 | -7.2885 | -9.4941 | -12.0628 | -14.9606 | -17.7358 | -20.9095 | -31.0725 | -34.892 | -34.9876 | -1.5734 | -2.4545 | -3.2909 | -4.4252 | -5.9015 | -8.1542 | -10.9213 | -14.1067 | -17.6995 | -21.2197 | -25.1232 | -38.0044 | -42.8281 | -42.9543
|  | BURGHMUIR | ST |  |  |  | 4.085 | -2.0916 | -2.5506 | -3.2546 | -4.2554 | -5.4927 | -7.0815 | -9.1282 | -11.7773 | -14.8957 | -18.2382 | -22.0001 | -41.4654 | -47.4044 | -47.6614 | 0.37051 | -0.033582 | -0.50001 | -1.2648 | -2.2109 | -3.4257 | -5.0203 | -7.1088 | -9.5618 | -12.1344 | -15.0952 | -30.0303 | -34.5833 | -34.7685 | -0.40343 | -0.82512 | -1.2353 | -1.8253 | -2.4978 | -3.411 | -5.1847 | -7.7372 | -10.7431 | -13.9631 | -17.5622 | -36.3296 | -42.0542 | -42.2949
|  | BURGHMUIR | FS |  |  |  | 4.085 | -1.7378 | -2.0408 | -2.3506 | -2.7753 | -3.2706 | -3.9765 | -4.9962 | -6.3095 | -7.795 | -9.3343 | -11.1696 | -23.2402 | -36.4698 | -43.0779 | 0.67554 | 0.43623 | 0.2158 | -0.082143 | -0.43262 | -1.0252 | -1.8223 | -2.8599 | -4.0326 | -5.2168 | -6.6706 | -15.9627 | -26.1024 | -31.1694 | -0.08319 | -0.36013 | -0.63599 | -1.0131 | -1.4535 | -1.9444 | -2.5794 | -3.4692 | -4.4158 | -5.3831 | -7.1127 | -18.7096 | -31.4589 | -37.8265
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.10938 | 0.10877 | 0.10799 | 0.10676 | 0.10583 | 0.10473 | 0.10287 | 0.1013 | 0.10014 | 0.098928 | 0.097876 | 0.093979 | 0.093006 | 0.092699 | 0.10318 | 0.10273 | 0.10222 | 0.10151 | 0.10086 | 0.10006 | 0.098616 | 0.097339 | 0.096402 | 0.095398 | 0.09451 | 0.091308 | 0.090619 | 0.090326 | 0.10644 | 0.10592 | 0.10529 | 0.10437 | 0.10338 | 0.10228 | 0.10061 | 0.099179 | 0.098133 | 0.097027 | 0.096011 | 0.092235 | 0.091294 | 0.090998
|  | BUTTERBRIDGE | CT |  |  |  | 0 | 0.10938 | 0.10877 | 0.10799 | 0.10676 | 0.10583 | 0.10473 | 0.10287 | 0.1013 | 0.10014 | 0.098928 | 0.097876 | 0.095872 | 0.095862 | 0.095857 | 0.10318 | 0.10273 | 0.10222 | 0.10151 | 0.10086 | 0.10006 | 0.098616 | 0.097339 | 0.096402 | 0.095398 | 0.09451 | 0.09275 | 0.092733 | 0.092721 | 0.10644 | 0.10592 | 0.10529 | 0.10437 | 0.10338 | 0.10228 | 0.10061 | 0.099179 | 0.098133 | 0.097027 | 0.096011 | 0.09405 | 0.09404 | 0.094036
|  | BUTTERBRIDGE | LW |  |  |  | 0 | 0.10943 | 0.10898 | 0.1086 | 0.10806 | 0.10753 | 0.10662 | 0.10553 | 0.104 | 0.10204 | 0.10019 | 0.098414 | 0.093979 | 0.093006 | 0.093 | 0.10321 | 0.10285 | 0.10254 | 0.10211 | 0.10171 | 0.10102 | 0.1002 | 0.099304 | 0.097759 | 0.096195 | 0.094719 | 0.091308 | 0.090619 | 0.090614 | 0.10649 | 0.10608 | 0.1057 | 0.10519 | 0.1047 | 0.10388 | 0.10293 | 0.10165 | 0.099889 | 0.098233 | 0.096535 | 0.092235 | 0.091294 | 0.09129
|  | BUTTERBRIDGE | ST |  |  |  | 0 | 0.10959 | 0.10943 | 0.10921 | 0.10893 | 0.10858 | 0.10815 | 0.10761 | 0.10694 | 0.10603 | 0.10489 | 0.10346 | 0.095954 | 0.09397 | 0.093946 | 0.10333 | 0.10318 | 0.10299 | 0.10274 | 0.10246 | 0.10213 | 0.10173 | 0.10124 | 0.1006 | 0.099897 | 0.098962 | 0.092756 | 0.091186 | 0.091161 | 0.10661 | 0.10644 | 0.10619 | 0.10589 | 0.10556 | 0.10515 | 0.10468 | 0.10411 | 0.10337 | 0.10246 | 0.10119 | 0.09415 | 0.092227 | 0.092206
|  | BUTTERBRIDGE | FS |  |  |  | 0 | 0.10963 | 0.10952 | 0.10937 | 0.10918 | 0.10897 | 0.10872 | 0.10841 | 0.10803 | 0.10753 | 0.10698 | 0.10635 | 0.10126 | 0.095595 | 0.092699 | 0.10337 | 0.10327 | 0.10315 | 0.10299 | 0.10283 | 0.10263 | 0.1024 | 0.1021 | 0.10171 | 0.1013 | 0.10084 | 0.09707 | 0.092468 | 0.090326 | 0.10668 | 0.10656 | 0.10642 | 0.10625 | 0.10606 | 0.10584 | 0.10558 | 0.10523 | 0.10479 | 0.10432 | 0.10379 | 0.099159 | 0.093791 | 0.090998
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0.114 | 2.4286 | 2.356 | 2.2885 | 1.9995 | 1.5444 | 1.1372 | 0.64048 | 0.2383 | -0.08282 | -0.4623 | -0.84061 | -2.2094 | -2.9732 | -3.6719 | 3.4204 | 3.3522 | 3.2891 | 3.129 | 2.8591 | 2.6588 | 2.3881 | 2.1745 | 2.0175 | 1.8558 | 1.6413 | 0.91795 | 0.60503 | 0.38047 | 3.1991 | 3.0991 | 2.9562 | 2.6838 | 2.3626 | 2.1051 | 1.7304 | 1.3944 | 1.1301 | 0.85569 | 0.52957 | -0.67187 | -1.3374 | -1.9348
|  | CALLANDER | CT |  |  |  | 0.114 | 2.478 | 2.3953 | 2.2993 | 1.9995 | 1.5444 | 1.1372 | 0.64048 | 0.2383 | -0.08282 | -0.39763 | -0.67293 | -1.9554 | -2.8449 | -3.5383 | 3.4751 | 3.3959 | 3.2996 | 3.129 | 2.8591 | 2.6588 | 2.3881 | 2.1745 | 2.0175 | 1.8558 | 1.7153 | 1.2316 | 0.92878 | 0.68245 | 3.2438 | 3.1287 | 2.9562 | 2.6838 | 2.3626 | 2.1051 | 1.7304 | 1.3944 | 1.1301 | 0.87351 | 0.65227 | -0.4263 | -1.1931 | -1.7922
|  | CALLANDER | LW |  |  |  | 0.114 | 2.4286 | 2.356 | 2.2885 | 2.023 | 1.6122 | 1.2218 | 0.77761 | 0.36203 | -0.057734 | -0.4623 | -0.84061 | -2.2094 | -2.9732 | -3.6719 | 3.4204 | 3.3522 | 3.2891 | 3.1901 | 2.9578 | 2.7738 | 2.5543 | 2.3442 | 2.1103 | 1.8706 | 1.6413 | 0.91795 | 0.60503 | 0.38047 | 3.1991 | 3.0991 | 2.9686 | 2.8004 | 2.541 | 2.2709 | 1.9066 | 1.5636 | 1.2029 | 0.85569 | 0.52957 | -0.67187 | -1.3374 | -1.9348
|  | CALLANDER | ST |  |  |  | 0.114 | 2.4999 | 2.467 | 2.42 | 2.3626 | 2.1967 | 2.1106 | 1.9989 | 1.8556 | 1.7014 | 1.5267 | 1.3364 | 0.15416 | -0.7257 | -1.4573 | 3.4979 | 3.4683 | 3.4272 | 3.3769 | 3.2151 | 3.1335 | 3.0415 | 2.9417 | 2.8159 | 2.6684 | 2.5019 | 1.5822 | 1.154 | 0.92844 | 3.2797 | 3.2322 | 3.1646 | 3.0859 | 2.899 | 2.7849 | 2.656 | 2.5222 | 2.3643 | 2.182 | 1.9753 | 0.83794 | 0.25568 | -0.12193
|  | CALLANDER | FS |  |  |  | 0.114 | 2.5676 | 2.537 | 2.5065 | 2.4555 | 2.3294 | 2.2541 | 2.193 | 2.1274 | 2.0454 | 1.8915 | 1.7344 | 0.68758 | -0.47648 | -1.4296 | 3.5731 | 3.5467 | 3.5205 | 3.4757 | 3.3547 | 3.2875 | 3.2303 | 3.1715 | 3.0979 | 2.9985 | 2.8884 | 2.1631 | 1.4074 | 0.85877 | 3.3551 | 3.3175 | 3.276 | 3.2153 | 3.0805 | 2.9938 | 2.9161 | 2.8226 | 2.7082 | 2.5803 | 2.4475 | 1.5584 | 0.51942 | -0.28398
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0.031 | 2.6179 | 2.4791 | 2.3462 | 2.2127 | 2.0811 | 1.9286 | 1.7449 | 1.5779 | 1.4327 | 1.2841 | 1.1509 | 0.73635 | 0.48261 | 0.26094 | 2.9393 | 2.8287 | 2.7459 | 2.6695 | 2.6031 | 2.5203 | 2.4087 | 2.3124 | 2.2315 | 2.1384 | 2.0544 | 1.8469 | 1.7386 | 1.5987 | 2.8091 | 2.6843 | 2.6101 | 2.5388 | 2.4785 | 2.3988 | 2.2791 | 2.1578 | 2.0487 | 1.9395 | 1.8415 | 1.5302 | 1.345 | 1.1528
|  | CALLANISH | CT |  |  |  | 0.031 | 2.6179 | 2.5041 | 2.383 | 2.2452 | 2.1015 | 1.9588 | 1.7672 | 1.6018 | 1.4897 | 1.3679 | 1.2624 | 0.78745 | 0.48261 | 0.2975 | 2.9393 | 2.8559 | 2.7872 | 2.7093 | 2.6347 | 2.5756 | 2.4711 | 2.3696 | 2.317 | 2.2381 | 2.1651 | 1.9288 | 1.8026 | 1.6662 | 2.8091 | 2.7204 | 2.6611 | 2.5832 | 2.5225 | 2.4614 | 2.3289 | 2.2081 | 2.1212 | 2.0334 | 1.958 | 1.6159 | 1.3925 | 1.2629
|  | CALLANISH | LW |  |  |  | 0.031 | 2.6233 | 2.4791 | 2.3462 | 2.2127 | 2.0811 | 1.9286 | 1.7449 | 1.5779 | 1.4327 | 1.2841 | 1.1509 | 0.73635 | 0.50533 | 0.26094 | 2.9418 | 2.8287 | 2.7459 | 2.6695 | 2.6031 | 2.5203 | 2.4087 | 2.3124 | 2.2315 | 2.1384 | 2.0544 | 1.8469 | 1.7386 | 1.5987 | 2.8095 | 2.6843 | 2.6101 | 2.5388 | 2.4785 | 2.3988 | 2.2791 | 2.1578 | 2.0487 | 1.9395 | 1.8415 | 1.5302 | 1.345 | 1.1528
|  | CALLANISH | ST |  |  |  | 0.031 | 2.6445 | 2.5485 | 2.4808 | 2.4237 | 2.3714 | 2.3238 | 2.2635 | 2.2041 | 2.1544 | 2.0974 | 2.0341 | 1.588 | 1.223 | 0.91412 | 2.9574 | 2.8887 | 2.8391 | 2.7998 | 2.764 | 2.7346 | 2.6913 | 2.6425 | 2.605 | 2.5568 | 2.5011 | 2.1743 | 1.9686 | 1.7862 | 2.8207 | 2.7438 | 2.6977 | 2.6602 | 2.6312 | 2.6039 | 2.5675 | 2.5277 | 2.4873 | 2.4461 | 2.4006 | 2.1139 | 1.8354 | 1.5961
|  | CALLANISH | FS |  |  |  | 0.031 | 2.6539 | 2.583 | 2.5438 | 2.5009 | 2.4743 | 2.4344 | 2.3987 | 2.3354 | 2.2665 | 2.215 | 2.1522 | 1.7624 | 1.3384 | 0.98999 | 2.9587 | 2.9087 | 2.8796 | 2.8455 | 2.8281 | 2.7965 | 2.7681 | 2.7248 | 2.6737 | 2.6431 | 2.5983 | 2.3357 | 2.0575 | 1.8293 | 2.8237 | 2.7663 | 2.7407 | 2.7136 | 2.697 | 2.6718 | 2.6465 | 2.6114 | 2.5717 | 2.5393 | 2.505 | 2.2793 | 1.9624 | 1.6829
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.596 | -1.4575 | -1.4752 | -1.5063 | -1.5388 | -1.5679 | -1.6152 | -1.6818 | -1.704 | -1.7329 | -1.7649 | -1.7929 | -1.892 | -1.9631 | -2.0552 | -1.177 | -1.1986 | -1.2311 | -1.2642 | -1.2923 | -1.3312 | -1.384 | -1.3984 | -1.4218 | -1.4425 | -1.4552 | -1.5297 | -1.6006 | -1.6829 | -1.3876 | -1.4019 | -1.4273 | -1.4525 | -1.4718 | -1.508 | -1.5648 | -1.5886 | -1.6211 | -1.6509 | -1.6749 | -1.7673 | -1.8376 | -1.9102
|  | CALVINE | CT |  |  |  | 0.596 | -1.4524 | -1.4622 | -1.4786 | -1.5143 | -1.5411 | -1.579 | -1.6379 | -1.6614 | -1.6838 | -1.7048 | -1.7193 | -1.8053 | -1.85 | -1.9043 | -1.174 | -1.1816 | -1.1954 | -1.2311 | -1.2559 | -1.2801 | -1.322 | -1.339 | -1.3572 | -1.3761 | -1.3873 | -1.449 | -1.4857 | -1.5391 | -1.3784 | -1.383 | -1.3906 | -1.4199 | -1.4346 | -1.4587 | -1.5021 | -1.5263 | -1.5477 | -1.5691 | -1.5846 | -1.6433 | -1.6682 | -1.6997
|  | CALVINE | LW |  |  |  | 0.596 | -1.4503 | -1.4752 | -1.5063 | -1.5388 | -1.5679 | -1.6152 | -1.6818 | -1.704 | -1.7329 | -1.7649 | -1.7929 | -1.892 | -1.9631 | -2.0552 | -1.1718 | -1.1986 | -1.2311 | -1.2642 | -1.2923 | -1.3312 | -1.384 | -1.3984 | -1.4218 | -1.4425 | -1.4552 | -1.5297 | -1.6006 | -1.6829 | -1.3782 | -1.4019 | -1.4273 | -1.4525 | -1.4718 | -1.508 | -1.5648 | -1.5886 | -1.6211 | -1.6509 | -1.6749 | -1.7673 | -1.8376 | -1.9102
|  | CALVINE | ST |  |  |  | 0.596 | -1.4575 | -1.4572 | -1.475 | -1.4923 | -1.5062 | -1.5194 | -1.5343 | -1.5536 | -1.579 | -1.6053 | -1.631 | -1.8114 | -1.9099 | -1.9714 | -1.177 | -1.1772 | -1.1959 | -1.2138 | -1.2272 | -1.2396 | -1.254 | -1.2668 | -1.2853 | -1.3046 | -1.3158 | -1.4405 | -1.5332 | -1.614 | -1.3876 | -1.3788 | -1.393 | -1.4054 | -1.4138 | -1.4214 | -1.4304 | -1.4445 | -1.468 | -1.4931 | -1.5144 | -1.6827 | -1.783 | -1.8499
|  | CALVINE | FS |  |  |  | 0.596 | -1.4508 | -1.4651 | -1.4523 | -1.4588 | -1.4651 | -1.4736 | -1.4823 | -1.4951 | -1.5123 | -1.5269 | -1.5432 | -1.6552 | -1.7701 | -1.8355 | -1.1718 | -1.1853 | -1.1756 | -1.1838 | -1.1915 | -1.2021 | -1.2131 | -1.2268 | -1.2457 | -1.2611 | -1.2744 | -1.3432 | -1.4249 | -1.4915 | -1.3854 | -1.3966 | -1.3821 | -1.3889 | -1.3956 | -1.4041 | -1.4141 | -1.4234 | -1.4371 | -1.4494 | -1.458 | -1.5447 | -1.6351 | -1.6917
| CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 1.021 | 5.9275 | 2.926 | -0.45306 | -3.6899 | -5.9992 | -9.4461 | -14.1758 | -14.9137 | -15.5234 | -16.1605 | -16.7485 | -22.086 | -30.7234 | -40.4581 | 7.7696 | 4.1509 | 0.26154 | -3.3998 | -5.9248 | -9.7728 | -15.1815 | -15.7707 | -16.2211 | -16.7402 | -17.2294 | -23.2696 | -33.8701 | -45.8066 | 6.8074 | 3.1556 | -0.80593 | -4.5376 | -7.1116 | -11.0255 | -16.707 | -17.4481 | -18.0751 | -18.7511 | -19.3798 | -25.7635 | -36.4676 | -48.541
|  | CAMPBELTOWN | CT |  |  |  | 1.021 | 5.9275 | 5.6245 | 5.2705 | 2.1036 | 1.1567 | -0.18978 | -2.9818 | -3.7665 | -4.633 | -5.4409 | -6.247 | -9.2722 | -12.3461 | -15.7791 | 7.7696 | 7.5445 | 7.4256 | 3.8223 | 3.035 | 1.7769 | -1.229 | -1.8447 | -2.6811 | -3.4751 | -4.3107 | -7.5064 | -11.0541 | -15.3215 | 6.8074 | 6.5439 | 6.3448 | 2.6557 | 1.7969 | 0.47536 | -2.6894 | -3.4994 | -4.4667 | -5.3778 | -6.3075 | -9.7805 | -13.4089 | -17.564
|  | CAMPBELTOWN | LW |  |  |  | 1.021 | 5.9401 | 2.926 | -0.45306 | -3.6899 | -5.9992 | -9.4461 | -14.1758 | -14.9137 | -15.5234 | -16.1605 | -16.7485 | -22.086 | -30.7234 | -40.4581 | 7.7725 | 4.1509 | 0.26154 | -3.3998 | -5.9248 | -9.7728 | -15.1815 | -15.7707 | -16.2211 | -16.7402 | -17.2294 | -23.2696 | -33.8701 | -45.8066 | 6.8124 | 3.1556 | -0.80593 | -4.5376 | -7.1116 | -11.0255 | -16.707 | -17.4481 | -18.0751 | -18.7511 | -19.3798 | -25.7635 | -36.4676 | -48.541
|  | CAMPBELTOWN | ST |  |  |  | 1.021 | 5.9987 | 5.7884 | 3.8874 | 2.5901 | 1.7324 | 1.3332 | 0.84759 | 0.1509 | -0.52597 | -1.1428 | -1.4436 | -9.8068 | -19.2572 | -28.4694 | 7.7993 | 7.6322 | 5.3381 | 3.7984 | 2.8229 | 2.4128 | 1.909 | 1.1457 | 0.43673 | -0.19446 | -0.4636 | -10.3093 | -22.057 | -33.3655 | 6.8541 | 6.6661 | 4.3435 | 2.7737 | 1.7667 | 1.3274 | 0.7964 | 0.0030941 | -0.74984 | -1.4284 | -1.7475 | -11.8425 | -23.6925 | -34.863
|  | CAMPBELTOWN | FS |  |  |  | 1.021 | 6.0551 | 5.9899 | 5.416 | 4.8319 | 4.1375 | 3.4209 | 2.2961 | 1.385 | 0.43175 | -0.54201 | -0.78655 | -2.2749 | -3.4564 | -5.7023 | 7.8075 | 7.7864 | 7.1119 | 6.4374 | 5.6114 | 4.7718 | 3.4248 | 2.4335 | 1.3637 | 0.29082 | 0.13694 | -0.89846 | -1.9238 | -4.6766 | 6.8764 | 6.8431 | 6.1512 | 5.4574 | 4.612 | 3.7509 | 2.3861 | 1.3597 | 0.25698 | -0.85157 | -1.044 | -2.178 | -3.1801 | -5.5929
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 0.475 | 6.6644 | 6.5383 | 6.3143 | 5.9841 | 5.6557 | 5.2847 | 4.8048 | 4.4967 | 4.2056 | 3.6785 | 3.3638 | 2.5431 | 2.1844 | 1.7694 | 8.3267 | 8.2538 | 8.1749 | 8.0429 | 7.9286 | 7.7865 | 7.5522 | 7.3607 | 7.1688 | 6.7649 | 6.5529 | 6.0347 | 5.8466 | 5.4636 | 6.9867 | 6.8683 | 6.7124 | 6.4906 | 6.2937 | 6.0729 | 5.6734 | 5.3942 | 5.0784 | 4.609 | 4.3098 | 3.5874 | 3.2899 | 2.8916
|  | CAPUTH | CT |  |  |  | 0.475 | 6.6644 | 6.5383 | 6.3143 | 5.9841 | 5.6557 | 5.2847 | 4.8048 | 4.4967 | 4.2291 | 3.7866 | 3.5553 | 2.7691 | 2.4059 | 2.0428 | 8.3308 | 8.2569 | 8.1749 | 8.0429 | 7.9286 | 7.7865 | 7.5522 | 7.3607 | 7.1844 | 6.8302 | 6.665 | 6.1218 | 5.8466 | 5.4636 | 6.9867 | 6.8683 | 6.7124 | 6.4906 | 6.2937 | 6.0729 | 5.6734 | 5.3942 | 5.1413 | 4.7479 | 4.5196 | 3.7989 | 3.5048 | 3.1653
|  | CAPUTH | LW |  |  |  | 0.475 | 6.6686 | 6.5516 | 6.3635 | 6.0803 | 5.7786 | 5.4163 | 4.9159 | 4.6046 | 4.2056 | 3.6785 | 3.3638 | 2.5431 | 2.1844 | 1.7694 | 8.3267 | 8.2538 | 8.1907 | 8.1073 | 8.0116 | 7.8635 | 7.6261 | 7.4316 | 7.1688 | 6.7649 | 6.5529 | 6.0347 | 5.8478 | 5.6006 | 6.99 | 6.8779 | 6.7464 | 6.5832 | 6.4141 | 6.1903 | 5.741 | 5.4614 | 5.0784 | 4.609 | 4.3098 | 3.5874 | 3.2899 | 2.8916
|  | CAPUTH | ST |  |  |  | 0.475 | 6.7046 | 6.6448 | 6.5537 | 6.4042 | 6.2541 | 6.0867 | 5.8726 | 5.7047 | 5.4921 | 5.0704 | 4.8473 | 3.6879 | 3.1662 | 2.8719 | 8.3526 | 8.3261 | 8.2848 | 8.2341 | 8.1806 | 8.1138 | 7.9874 | 7.8892 | 7.7539 | 7.3566 | 7.2092 | 6.3641 | 6.0638 | 5.8983 | 7.0243 | 6.9695 | 6.8873 | 6.7931 | 6.6953 | 6.5805 | 6.4138 | 6.2802 | 6.1003 | 5.6926 | 5.4963 | 4.3673 | 3.8897 | 3.6722
|  | CAPUTH | FS |  |  |  | 0.475 | 6.7429 | 6.7037 | 6.6568 | 6.6053 | 6.5453 | 6.4832 | 6.3862 | 6.2803 | 6.158 | 5.8925 | 5.7122 | 4.6299 | 3.5068 | 2.8264 | 8.368 | 8.3493 | 8.3218 | 8.2905 | 8.2527 | 8.2133 | 8.1369 | 8.0756 | 8.0032 | 7.7853 | 7.6829 | 6.9873 | 6.2106 | 5.4812 | 7.059 | 7.023 | 6.9787 | 6.9301 | 6.8733 | 6.8147 | 6.7218 | 6.6225 | 6.5101 | 6.2735 | 6.1286 | 5.2175 | 4.2519 | 3.612
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 1.101 | 4.6919 | 4.0595 | 3.192 | 2.2194 | 1.399 | 0.38151 | -0.46759 | -1.0576 | -1.9625 | -2.7742 | -3.5059 | -5.645 | -7.1216 | -8.116 | 6.0242 | 5.5476 | 5.0134 | 4.3971 | 3.8929 | 3.2483 | 2.7841 | 2.5784 | 2.0952 | 1.6628 | 1.2708 | 0.10146 | -0.77889 | -1.7438 | 5.6857 | 5.1089 | 4.3983 | 3.565 | 2.8759 | 1.96 | 1.168 | 0.68968 | -0.16751 | -0.93462 | -1.6274 | -3.5447 | -4.6535 | -5.5159
|  | CARNOUSTIE | CT |  |  |  | 1.101 | 4.9428 | 4.3833 | 3.5889 | 2.6411 | 1.6747 | 0.60899 | -0.34105 | -0.96738 | -1.7172 | -2.3912 | -3.0136 | -5.6001 | -7.1216 | -8.116 | 6.2356 | 5.8145 | 5.3217 | 4.7036 | 4.0701 | 3.3779 | 2.8338 | 2.5827 | 2.1928 | 1.8253 | 1.4766 | 0.10146 | -0.77889 | -1.7438 | 5.8922 | 5.3736 | 4.7145 | 3.9029 | 3.0719 | 2.1509 | 1.2915 | 0.77843 | 0.095756 | -0.53581 | -1.119 | -3.4007 | -4.6535 | -5.5159
|  | CARNOUSTIE | LW |  |  |  | 1.101 | 4.6919 | 4.0595 | 3.192 | 2.2194 | 1.399 | 0.38151 | -0.46759 | -1.0576 | -1.9625 | -2.7742 | -3.5059 | -5.645 | -6.43 | -7.2586 | 6.0242 | 5.5476 | 5.0134 | 4.3971 | 3.8929 | 3.2483 | 2.7841 | 2.5784 | 2.0952 | 1.6628 | 1.2708 | 0.23711 | -0.086376 | -0.52235 | 5.6857 | 5.1089 | 4.3983 | 3.565 | 2.8759 | 1.96 | 1.168 | 0.68968 | -0.16751 | -0.93462 | -1.6274 | -3.5447 | -4.1994 | -4.9621
|  | CARNOUSTIE | ST |  |  |  | 1.101 | 5.0279 | 4.6092 | 4.1687 | 3.6727 | 3.216 | 2.7102 | 2.4926 | 2.2584 | 1.9978 | 1.7456 | 1.7871 | -0.13161 | -1.6257 | -3.1628 | 6.2864 | 5.967 | 5.6232 | 5.2095 | 4.8042 | 4.3554 | 4.1689 | 3.9812 | 3.7695 | 3.5617 | 3.5955 | 2.3012 | 1.3293 | 0.20588 | 5.979 | 5.6247 | 5.242 | 4.7966 | 4.3911 | 3.9207 | 3.6967 | 3.4389 | 3.1362 | 2.8344 | 2.9142 | 1.0289 | -0.24943 | -1.4234
|  | CARNOUSTIE | FS |  |  |  | 1.101 | 5.3468 | 5.0043 | 4.6554 | 4.2102 | 3.8085 | 3.292 | 3.0459 | 2.7792 | 2.4523 | 2.1078 | 1.7124 | -0.076881 | -1.9485 | -3.7123 | 6.5543 | 6.2833 | 6.0211 | 5.6605 | 5.3217 | 4.8789 | 4.6828 | 4.4936 | 4.253 | 3.9906 | 3.6868 | 2.3797 | 0.82491 | -1.0311 | 6.2415 | 5.9473 | 5.6524 | 5.2645 | 4.918 | 4.4577 | 4.2189 | 3.9769 | 3.6597 | 3.3244 | 2.9426 | 1.3499 | -0.3172 | -1.8125
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0.018 | 0.73413 | 0.71801 | 0.70093 | 0.68188 | 0.68536 | 0.67228 | 0.65296 | 0.64563 | 0.63005 | 0.62194 | 0.61029 | 0.57544 | 0.53953 | 0.50835 | 0.79196 | 0.77353 | 0.75533 | 0.7353 | 0.74149 | 0.72655 | 0.70512 | 0.69761 | 0.68689 | 0.67862 | 0.66997 | 0.63528 | 0.5949 | 0.5618 | 0.85973 | 0.84062 | 0.82148 | 0.80029 | 0.79542 | 0.78133 | 0.75612 | 0.74796 | 0.73272 | 0.72488 | 0.71347 | 0.67659 | 0.62998 | 0.59422
|  | CASHLIE | CT |  |  |  | 0.018 | 0.73413 | 0.72352 | 0.71238 | 0.69199 | 0.69694 | 0.68944 | 0.67344 | 0.66629 | 0.65966 | 0.65497 | 0.64601 | 0.62075 | 0.60786 | 0.59006 | 0.79196 | 0.78092 | 0.77022 | 0.74825 | 0.75652 | 0.74836 | 0.73129 | 0.7222 | 0.71463 | 0.70811 | 0.70137 | 0.68212 | 0.67297 | 0.66046 | 0.85973 | 0.8476 | 0.83543 | 0.81135 | 0.81225 | 0.80766 | 0.78787 | 0.77689 | 0.76798 | 0.76019 | 0.7524 | 0.72845 | 0.71627 | 0.69721
|  | CASHLIE | LW |  |  |  | 0.018 | 0.73474 | 0.71801 | 0.70093 | 0.68188 | 0.68536 | 0.67228 | 0.65296 | 0.64563 | 0.63005 | 0.62194 | 0.61029 | 0.57544 | 0.54485 | 0.50835 | 0.79237 | 0.77353 | 0.75533 | 0.7353 | 0.74149 | 0.72655 | 0.70512 | 0.69761 | 0.68689 | 0.67862 | 0.66997 | 0.63528 | 0.60307 | 0.56997 | 0.86028 | 0.84062 | 0.82148 | 0.80029 | 0.79542 | 0.78133 | 0.75612 | 0.74796 | 0.73272 | 0.72488 | 0.71347 | 0.67659 | 0.64143 | 0.5996
|  | CASHLIE | ST |  |  |  | 0.018 | 0.73706 | 0.7326 | 0.72189 | 0.71159 | 0.70216 | 0.69212 | 0.69991 | 0.69654 | 0.68966 | 0.68106 | 0.67465 | 0.58844 | 0.53953 | 0.5088 | 0.79489 | 0.79063 | 0.77894 | 0.76784 | 0.75773 | 0.7469 | 0.75633 | 0.75051 | 0.7411 | 0.7301 | 0.72039 | 0.64253 | 0.5949 | 0.5618 | 0.863 | 0.85826 | 0.84587 | 0.83397 | 0.82294 | 0.81103 | 0.81648 | 0.81201 | 0.80085 | 0.78795 | 0.77605 | 0.68365 | 0.62998 | 0.59422
|  | CASHLIE | FS |  |  |  | 0.018 | 0.73869 | 0.73553 | 0.7305 | 0.72465 | 0.71845 | 0.7114 | 0.70254 | 0.71077 | 0.70673 | 0.69911 | 0.6952 | 0.65989 | 0.60509 | 0.56881 | 0.79604 | 0.79304 | 0.7872 | 0.7804 | 0.77309 | 0.76476 | 0.75419 | 0.76396 | 0.75735 | 0.74822 | 0.7426 | 0.70257 | 0.66343 | 0.63536 | 0.86439 | 0.86112 | 0.85493 | 0.84773 | 0.83995 | 0.83107 | 0.81987 | 0.82879 | 0.82112 | 0.81088 | 0.80403 | 0.75586 | 0.70471 | 0.66927
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | 0.75635 | 0.75291 | 0.74972 | 0.74611 | 0.74137 | 0.73662 | 0.72919 | 0.72459 | 0.73558 | 0.73002 | 0.73415 | 0.7326 | 0.72994 | 0.72499 | 0.76585 | 0.76243 | 0.75929 | 0.75569 | 0.75117 | 0.74676 | 0.7397 | 0.73432 | 0.74389 | 0.73792 | 0.74287 | 0.74245 | 0.74119 | 0.73985 | 0.86845 | 0.86485 | 0.86145 | 0.85751 | 0.85264 | 0.84786 | 0.84035 | 0.83454 | 0.8382 | 0.83874 | 0.83829 | 0.83177 | 0.82882 | 0.82438
|  | CHAORACH | CT |  |  |  | 0 | 0.75635 | 0.75291 | 0.74972 | 0.74611 | 0.74137 | 0.73662 | 0.72919 | 0.73998 | 0.74142 | 0.73919 | 0.73707 | 0.73328 | 0.72994 | 0.72544 | 0.76585 | 0.76243 | 0.75929 | 0.75569 | 0.75117 | 0.74676 | 0.7397 | 0.75304 | 0.75346 | 0.75139 | 0.74944 | 0.74589 | 0.74469 | 0.74336 | 0.86845 | 0.86485 | 0.86145 | 0.85751 | 0.85264 | 0.84786 | 0.84035 | 0.84377 | 0.84897 | 0.84382 | 0.83874 | 0.83177 | 0.82882 | 0.82468
|  | CHAORACH | LW |  |  |  | 0 | 0.75657 | 0.75352 | 0.75085 | 0.74722 | 0.74393 | 0.73812 | 0.73141 | 0.72459 | 0.73724 | 0.73852 | 0.73616 | 0.7326 | 0.7305 | 0.72499 | 0.76596 | 0.76289 | 0.76035 | 0.75686 | 0.75379 | 0.74811 | 0.74151 | 0.73432 | 0.74955 | 0.74935 | 0.74676 | 0.74245 | 0.74119 | 0.73985 | 0.86858 | 0.86533 | 0.86255 | 0.85877 | 0.85538 | 0.84926 | 0.84217 | 0.83454 | 0.8382 | 0.8434 | 0.83829 | 0.83241 | 0.82951 | 0.82438
|  | CHAORACH | ST |  |  |  | 0 | 0.75729 | 0.75588 | 0.75437 | 0.75245 | 0.75028 | 0.74767 | 0.74458 | 0.74078 | 0.73558 | 0.73002 | 0.74276 | 0.73946 | 0.73842 | 0.73932 | 0.76683 | 0.76558 | 0.76399 | 0.76195 | 0.75964 | 0.75684 | 0.75351 | 0.74945 | 0.74389 | 0.73792 | 0.75296 | 0.74535 | 0.74246 | 0.74197 | 0.86952 | 0.86817 | 0.86642 | 0.86421 | 0.86172 | 0.85871 | 0.85514 | 0.85085 | 0.84501 | 0.83874 | 0.84841 | 0.84353 | 0.84063 | 0.8399
|  | CHAORACH | FS |  |  |  | 0 | 0.75771 | 0.75665 | 0.75555 | 0.75416 | 0.75265 | 0.75087 | 0.74873 | 0.74591 | 0.74225 | 0.73843 | 0.73415 | 0.74174 | 0.73597 | 0.73318 | 0.76709 | 0.76611 | 0.76495 | 0.7635 | 0.76191 | 0.76004 | 0.75777 | 0.75493 | 0.75119 | 0.74727 | 0.74287 | 0.75156 | 0.74532 | 0.74175 | 0.86983 | 0.86878 | 0.86755 | 0.86602 | 0.86434 | 0.86237 | 0.85998 | 0.85699 | 0.85306 | 0.84896 | 0.84436 | 0.8494 | 0.84042 | 0.8366
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0.885 | 2.7454 | 2.5623 | 2.141 | 1.6641 | 1.1282 | 0.46372 | -0.64316 | -1.8196 | -2.8008 | -3.599 | -4.3256 | -6.3492 | -7.3208 | -8.1513 | 5.5585 | 5.4789 | 5.3642 | 5.1797 | 5.0158 | 4.7402 | 4.058 | 3.2538 | 2.6156 | 2.1397 | 1.7012 | 0.50014 | -0.33133 | -1.6027 | 4.4301 | 4.2407 | 3.8434 | 3.4005 | 2.8883 | 2.2873 | 1.2611 | 0.1138 | -0.78024 | -1.5267 | -2.2278 | -4.1219 | -4.8527 | -5.6022
|  | CHARLES AVENUE | CT |  |  |  | 0.885 | 2.7538 | 2.5716 | 2.1913 | 1.6983 | 1.1282 | 0.52636 | -0.51012 | -1.6769 | -2.4519 | -3.181 | -3.7963 | -6.1117 | -7.3208 | -8.1513 | 5.5585 | 5.4789 | 5.3642 | 5.1797 | 5.0158 | 4.7402 | 4.058 | 3.2565 | 2.7779 | 2.3154 | 1.9137 | 0.50014 | -0.33133 | -1.4003 | 4.4353 | 4.246 | 3.8912 | 3.4214 | 2.8883 | 2.3417 | 1.3843 | 0.25813 | -0.44026 | -1.1157 | -1.6914 | -3.8108 | -4.8527 | -5.6022
|  | CHARLES AVENUE | LW |  |  |  | 0.885 | 2.7454 | 2.5623 | 2.141 | 1.6641 | 1.1368 | 0.46372 | -0.64316 | -1.8196 | -2.8008 | -3.599 | -4.3256 | -6.3492 | -6.8774 | -7.5263 | 5.5607 | 5.482 | 5.3797 | 5.2602 | 5.134 | 4.7981 | 4.0598 | 3.2538 | 2.6156 | 2.1397 | 1.7012 | 0.5781 | 0.34172 | -0.091962 | 4.4301 | 4.2407 | 3.8434 | 3.4005 | 2.9061 | 2.2873 | 1.2611 | 0.1138 | -0.78024 | -1.5267 | -2.2278 | -4.1219 | -4.5858 | -5.2363
|  | CHARLES AVENUE | ST |  |  |  | 0.885 | 2.8345 | 2.7539 | 2.7011 | 2.6305 | 2.5447 | 2.4606 | 2.0908 | 1.6531 | 1.1359 | 0.81709 | 0.49384 | -1.1516 | -2.4361 | -3.762 | 5.5846 | 5.5544 | 5.5147 | 5.4657 | 5.3914 | 5.3055 | 4.9364 | 4.4938 | 3.9906 | 3.705 | 3.4145 | 2.117 | 1.39 | 0.21191 | 4.5191 | 4.4387 | 4.3794 | 4.2983 | 4.2007 | 4.111 | 3.7408 | 3.2753 | 2.7777 | 2.4399 | 2.0916 | 0.46913 | -0.70956 | -1.8409
|  | CHARLES AVENUE | FS |  |  |  | 0.885 | 2.8651 | 2.8069 | 2.7208 | 2.639 | 2.5437 | 2.4327 | 2.1708 | 1.8209 | 1.372 | 1.0928 | 0.75663 | -1.1511 | -3.174 | -4.9693 | 5.5898 | 5.5656 | 5.5338 | 5.5015 | 5.4617 | 5.4024 | 5.1725 | 4.8971 | 4.5719 | 4.3867 | 4.1677 | 2.6164 | 0.67077 | -1.6027 | 4.5472 | 4.4885 | 4.3998 | 4.3175 | 4.218 | 4.101 | 3.8473 | 3.4748 | 3.0508 | 2.7849 | 2.4635 | 0.63869 | -1.2692 | -2.8724
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 0 | 4.8316 | 4.7337 | 4.6138 | 4.434 | 4.2861 | 4.1357 | 3.9079 | 3.6709 | 3.4932 | 3.3205 | 2.841 | 1.8013 | 1.5804 | 1.3474 | 4.2866 | 4.193 | 4.0652 | 3.9032 | 3.7319 | 3.5673 | 3.3254 | 3.0444 | 2.8213 | 2.591 | 2.2134 | 1.5241 | 1.2198 | -0.14125 | 6.1608 | 6.0796 | 5.981 | 5.835 | 5.7125 | 5.5912 | 5.4037 | 5.2071 | 5.0596 | 4.9171 | 4.6084 | 3.7641 | 3.4912 | 3.3122
|  | CHARLESTON | CT |  |  |  | 0 | 4.8316 | 4.7337 | 4.6138 | 4.434 | 4.2861 | 4.1357 | 3.9079 | 3.6709 | 3.4932 | 3.3205 | 3.0223 | 2.1394 | 1.8412 | 1.5991 | 4.2866 | 4.193 | 4.0652 | 3.9032 | 3.7319 | 3.5673 | 3.3254 | 3.0444 | 2.8213 | 2.6185 | 2.3031 | 1.5817 | 1.2457 | 0.72073 | 6.1608 | 6.0796 | 5.981 | 5.835 | 5.7125 | 5.5912 | 5.4037 | 5.2071 | 5.0596 | 4.9171 | 4.6434 | 4.1017 | 3.8614 | 3.6383
|  | CHARLESTON | LW |  |  |  | 0 | 4.836 | 4.7541 | 4.6918 | 4.6042 | 4.5115 | 4.3574 | 4.1669 | 3.9428 | 3.6493 | 3.3506 | 2.841 | 1.8013 | 1.6993 | 1.4099 | 4.2927 | 4.2067 | 4.1159 | 3.9954 | 3.8632 | 3.672 | 3.4322 | 3.1759 | 2.8557 | 2.591 | 2.2134 | 1.5241 | 1.4546 | 1.2326 | 6.165 | 6.0962 | 6.0453 | 5.9729 | 5.8963 | 5.7701 | 5.6114 | 5.4253 | 5.1807 | 4.9638 | 4.6084 | 3.7641 | 3.672 | 3.3853
|  | CHARLESTON | ST |  |  |  | 0 | 4.8637 | 4.8327 | 4.7911 | 4.7352 | 4.6693 | 4.5833 | 4.4736 | 4.3302 | 4.1396 | 3.9225 | 3.5316 | 2.0995 | 1.5804 | 1.4467 | 4.3184 | 4.2818 | 4.2416 | 4.186 | 4.1287 | 4.0538 | 3.9555 | 3.8336 | 3.687 | 3.517 | 3.2124 | 2.0941 | 1.5184 | 0.97446 | 6.1879 | 6.1622 | 6.1278 | 6.0811 | 6.0271 | 5.9562 | 5.8655 | 5.7475 | 5.5937 | 5.4166 | 5.0712 | 3.9084 | 3.4912 | 3.3862
|  | CHARLESTON | FS |  |  |  | 0 | 4.8723 | 4.8509 | 4.8232 | 4.7873 | 4.7477 | 4.6957 | 4.6331 | 4.5578 | 4.4521 | 4.3451 | 4.1459 | 3.1632 | 2.1025 | 1.3474 | 4.3296 | 4.302 | 4.2666 | 4.2202 | 4.1751 | 4.1126 | 4.0357 | 3.947 | 3.8261 | 3.7151 | 3.5236 | 2.4963 | 1.2198 | -0.14125 | 6.1948 | 6.1768 | 6.154 | 6.1238 | 6.0913 | 6.0479 | 5.9955 | 5.9337 | 5.8462 | 5.7604 | 5.5836 | 4.7753 | 3.9141 | 3.3122
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 1.148 | 4.8543 | 4.7311 | 4.5721 | 4.3783 | 4.1744 | 4.0003 | 3.8126 | 3.6259 | 3.4633 | 3.2911 | 3.1362 | 2.7077 | 2.4794 | 2.2574 | 5.5492 | 5.4302 | 5.3137 | 5.1557 | 4.9979 | 4.8838 | 4.7794 | 4.6923 | 4.6054 | 4.5189 | 4.4407 | 4.2387 | 4.1056 | 3.9523 | 5.1497 | 5.0298 | 4.9128 | 4.7608 | 4.5993 | 4.4298 | 4.2636 | 4.1118 | 3.968 | 3.8284 | 3.703 | 3.3331 | 3.1073 | 2.8529
|  | CLACHAN | CT |  |  |  | 1.148 | 4.8543 | 4.7506 | 4.613 | 4.4001 | 4.1744 | 4.011 | 3.8144 | 3.6287 | 3.5143 | 3.3731 | 3.247 | 2.7716 | 2.4794 | 2.2744 | 5.5492 | 5.4621 | 5.3683 | 5.1953 | 5.0285 | 4.9319 | 4.8332 | 4.7411 | 4.6797 | 4.6122 | 4.5524 | 4.2942 | 4.1229 | 3.9628 | 5.1497 | 5.0597 | 4.9626 | 4.793 | 4.6109 | 4.4503 | 4.2778 | 4.1267 | 4.0175 | 3.9064 | 3.8104 | 3.4022 | 3.1169 | 2.9314
|  | CLACHAN | LW |  |  |  | 1.148 | 4.8589 | 4.7311 | 4.5721 | 4.3783 | 4.1765 | 4.0003 | 3.8126 | 3.6259 | 3.4633 | 3.2911 | 3.1362 | 2.7077 | 2.4999 | 2.2574 | 5.55 | 5.4302 | 5.3137 | 5.1557 | 4.9979 | 4.8838 | 4.7794 | 4.6923 | 4.6054 | 4.5189 | 4.4407 | 4.2387 | 4.1098 | 3.9523 | 5.1502 | 5.0298 | 4.9128 | 4.7608 | 4.5993 | 4.4298 | 4.2636 | 4.1118 | 3.968 | 3.8284 | 3.703 | 3.3331 | 3.1073 | 2.8529
|  | CLACHAN | ST |  |  |  | 1.148 | 4.8865 | 4.8076 | 4.7196 | 4.5991 | 4.4683 | 4.3938 | 4.3295 | 4.2819 | 4.2032 | 4.1318 | 4.0492 | 3.5078 | 3.1325 | 2.8429 | 5.5619 | 5.4896 | 5.4085 | 5.2764 | 5.1393 | 5.0686 | 5.0201 | 4.9712 | 4.9023 | 4.8358 | 4.7618 | 4.3226 | 4.1056 | 3.972 | 5.1643 | 5.0935 | 5.0127 | 4.8939 | 4.7697 | 4.696 | 4.6415 | 4.5849 | 4.5068 | 4.4303 | 4.3447 | 3.8352 | 3.476 | 3.2
|  | CLACHAN | FS |  |  |  | 1.148 | 4.8883 | 4.8298 | 4.7713 | 4.6754 | 4.5798 | 4.5025 | 4.4575 | 4.3868 | 4.3022 | 4.2441 | 4.1674 | 3.7328 | 3.2958 | 2.9702 | 5.5642 | 5.5107 | 5.4587 | 5.3648 | 5.2544 | 5.1821 | 5.1413 | 5.0927 | 5.0306 | 4.9803 | 4.926 | 4.5913 | 4.2974 | 4.0845 | 5.1673 | 5.1155 | 5.0634 | 4.9762 | 4.8778 | 4.8053 | 4.762 | 4.7085 | 4.6408 | 4.5825 | 4.5203 | 4.1086 | 3.6641 | 3.2894
| CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.18126 | 0.16908 | 0.15774 | 0.16726 | 0.16046 | 0.15877 | 0.1507 | 0.14101 | 0.13312 | 0.12536 | 0.11639 | 0.098899 | 0.094651 | 0.086315 | 0.22696 | 0.21599 | 0.20594 | 0.2161 | 0.20908 | 0.20902 | 0.20984 | 0.20327 | 0.19667 | 0.19042 | 0.18412 | 0.17211 | 0.17069 | 0.16738 | 0.18987 | 0.17787 | 0.16677 | 0.17731 | 0.16958 | 0.17064 | 0.16648 | 0.15671 | 0.14932 | 0.14169 | 0.13266 | 0.11591 | 0.11222 | 0.10434
|  | CLAONAIG | CT |  |  |  | 0 | 0.18126 | 0.16908 | 0.15774 | 0.17325 | 0.16487 | 0.15877 | 0.1507 | 0.14395 | 0.13638 | 0.13063 | 0.12332 | 0.1107 | 0.10572 | 0.099148 | 0.22708 | 0.21599 | 0.20594 | 0.22304 | 0.21831 | 0.21492 | 0.21046 | 0.20552 | 0.20104 | 0.19714 | 0.19237 | 0.18363 | 0.18104 | 0.17681 | 0.18988 | 0.17787 | 0.16677 | 0.1826 | 0.177 | 0.17272 | 0.16663 | 0.16008 | 0.15257 | 0.14676 | 0.1392 | 0.12751 | 0.12312 | 0.11716
|  | CLAONAIG | LW |  |  |  | 0 | 0.18126 | 0.16977 | 0.16021 | 0.16726 | 0.16869 | 0.16012 | 0.15179 | 0.14101 | 0.13312 | 0.12536 | 0.11639 | 0.098899 | 0.094651 | 0.086315 | 0.22696 | 0.21654 | 0.20819 | 0.22131 | 0.22038 | 0.21531 | 0.20984 | 0.20327 | 0.19667 | 0.19042 | 0.18412 | 0.17211 | 0.17069 | 0.16738 | 0.18987 | 0.17853 | 0.1692 | 0.18123 | 0.17939 | 0.17323 | 0.16648 | 0.15671 | 0.14932 | 0.14169 | 0.13266 | 0.11591 | 0.11222 | 0.10434
|  | CLAONAIG | ST |  |  |  | 0 | 0.18513 | 0.18091 | 0.17536 | 0.16835 | 0.16046 | 0.1711 | 0.171 | 0.16607 | 0.16107 | 0.15609 | 0.14918 | 0.1181 | 0.10871 | 0.10691 | 0.23054 | 0.227 | 0.22231 | 0.2161 | 0.20908 | 0.22256 | 0.22149 | 0.2174 | 0.21341 | 0.20955 | 0.20383 | 0.17856 | 0.17137 | 0.17056 | 0.19369 | 0.18957 | 0.18417 | 0.17731 | 0.16958 | 0.18221 | 0.1805 | 0.17578 | 0.17101 | 0.16628 | 0.15964 | 0.12983 | 0.12092 | 0.11933
|  | CLAONAIG | FS |  |  |  | 0 | 0.18597 | 0.1826 | 0.17861 | 0.17361 | 0.16822 | 0.1618 | 0.17623 | 0.17535 | 0.1712 | 0.16822 | 0.16512 | 0.14077 | 0.11934 | 0.10725 | 0.23093 | 0.22799 | 0.22441 | 0.21986 | 0.21496 | 0.20902 | 0.22478 | 0.22449 | 0.22105 | 0.21878 | 0.21648 | 0.19685 | 0.18004 | 0.17074 | 0.19446 | 0.19116 | 0.18723 | 0.1823 | 0.17698 | 0.17064 | 0.18519 | 0.18444 | 0.18047 | 0.17765 | 0.17473 | 0.15149 | 0.13117 | 0.11976
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 1.954 | 6.9612 | 6.7155 | 6.0743 | 5.107 | 4.0818 | 2.6197 | 0.89451 | -0.80631 | -2.8819 | -4.8318 | -6.6398 | -11.4671 | -11.5566 | -13.2439 | 9.9023 | 9.692 | 9.48 | 9.1618 | 8.878 | 8.433 | 7.2739 | 6.0922 | 4.6141 | 3.2564 | 1.9867 | -1.1939 | -3.3449 | -11.5127 | 8.9978 | 8.7537 | 8.1807 | 7.2816 | 6.3138 | 4.8711 | 3.1555 | 1.4477 | -0.60354 | -2.4808 | -4.2245 | -8.8221 | -8.9336 | -10.6207
|  | CLAYHILLS | CT |  |  |  | 1.954 | 6.9636 | 6.7155 | 6.282 | 5.3944 | 4.4507 | 3.4194 | 2.0344 | 0.28367 | -1.202 | -2.716 | -4.0814 | -9.1614 | -10.5529 | -11.9629 | 9.9023 | 9.692 | 9.48 | 9.1618 | 8.878 | 8.433 | 7.3906 | 6.1509 | 5.1148 | 4.0254 | 3.0033 | -1.0421 | -3.3119 | -7.178 | 8.9978 | 8.7537 | 8.3572 | 7.4707 | 6.5383 | 5.5214 | 4.1335 | 2.408 | 0.9832 | -0.45719 | -1.7607 | -6.5093 | -7.7599 | -9.1159
|  | CLAYHILLS | LW |  |  |  | 1.954 | 6.9612 | 6.7258 | 6.0743 | 5.107 | 4.0818 | 2.6197 | 0.89451 | -0.80631 | -2.8819 | -4.8318 | -6.6398 | -11.4671 | -11.5566 | -13.2439 | 9.9164 | 9.7256 | 9.571 | 9.3642 | 9.1708 | 8.4495 | 7.2739 | 6.0922 | 4.6141 | 3.2564 | 1.9867 | -1.1939 | -1.3647 | -2.7531 | 8.9995 | 8.7661 | 8.1807 | 7.2816 | 6.3138 | 4.8711 | 3.1555 | 1.4477 | -0.60354 | -2.4808 | -4.2245 | -8.8221 | -8.9336 | -10.6207
|  | CLAYHILLS | ST |  |  |  | 1.954 | 7.0257 | 6.9332 | 6.8284 | 6.6939 | 6.5364 | 6.3315 | 5.9081 | 5.4207 | 4.7432 | 4.0191 | 3.1882 | -1.3205 | -3.1125 | -4.5797 | 9.9578 | 9.8734 | 9.7584 | 9.6191 | 9.4602 | 9.2635 | 9.0204 | 8.7404 | 8.3556 | 7.9367 | 7.1727 | 2.5593 | -0.27221 | -3.819 | 9.0665 | 8.9789 | 8.8581 | 8.7091 | 8.5384 | 8.3238 | 7.8825 | 7.3627 | 6.6321 | 5.851 | 5.0169 | 0.57372 | -1.1365 | -2.4505
|  | CLAYHILLS | FS |  |  |  | 1.954 | 7.0516 | 6.9864 | 6.9141 | 6.8206 | 6.7141 | 6.5785 | 6.3344 | 5.8921 | 5.3735 | 4.8217 | 4.2224 | -0.69417 | -5.5581 | -9.0334 | 9.9719 | 9.9044 | 9.8177 | 9.7112 | 9.591 | 9.4424 | 9.2559 | 9.0366 | 8.7702 | 8.4715 | 7.8193 | 3.0733 | -3.3449 | -11.5127 | 9.0895 | 9.0277 | 8.9464 | 8.8443 | 8.7296 | 8.5861 | 8.363 | 7.9151 | 7.3887 | 6.8216 | 6.2033 | 1.427 | -3.1592 | -6.3924
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 1.046 | -0.79156 | -0.82363 | -0.87474 | -0.93054 | -0.98841 | -1.0545 | -1.1351 | -1.1715 | -1.2264 | -1.274 | -1.2978 | -1.4178 | -1.4862 | -1.5701 | -0.64366 | -0.67061 | -0.70131 | -0.73294 | -0.76461 | -0.8013 | -0.85684 | -0.88362 | -0.92632 | -0.96338 | -0.97545 | -1.0553 | -1.105 | -1.1594 | -0.72828 | -0.76204 | -0.80873 | -0.85757 | -0.9088 | -0.97047 | -1.0469 | -1.0818 | -1.1354 | -1.1818 | -1.1984 | -1.3142 | -1.4264 | -1.4907
|  | COLDBACKIE | CT |  |  |  | 1.046 | -0.79156 | -0.82363 | -0.86788 | -0.92411 | -0.98557 | -1.0462 | -1.1259 | -1.1609 | -1.1981 | -1.236 | -1.2691 | -1.3648 | -1.4174 | -1.4767 | -0.64363 | -0.66383 | -0.68702 | -0.71813 | -0.75404 | -0.77874 | -0.82875 | -0.8582 | -0.88675 | -0.91826 | -0.94746 | -1.0064 | -1.0361 | -1.0811 | -0.72828 | -0.75956 | -0.79866 | -0.84657 | -0.90313 | -0.95452 | -1.0286 | -1.0606 | -1.0966 | -1.1347 | -1.1688 | -1.2475 | -1.2901 | -1.3403
|  | COLDBACKIE | LW |  |  |  | 1.046 | -0.78819 | -0.82334 | -0.87474 | -0.93054 | -0.98841 | -1.0545 | -1.1351 | -1.1715 | -1.2264 | -1.274 | -1.2978 | -1.4178 | -1.4862 | -1.5701 | -0.64366 | -0.67061 | -0.70131 | -0.73294 | -0.76461 | -0.8013 | -0.85684 | -0.88362 | -0.92632 | -0.96338 | -0.97545 | -1.0553 | -1.0979 | -1.1594 | -0.7254 | -0.76204 | -0.80873 | -0.85757 | -0.9088 | -0.97047 | -1.0469 | -1.0818 | -1.1354 | -1.1818 | -1.1984 | -1.3053 | -1.3675 | -1.4452
|  | COLDBACKIE | ST |  |  |  | 1.046 | -0.78517 | -0.80561 | -0.84214 | -0.87837 | -0.9154 | -0.95177 | -0.99185 | -1.0274 | -1.0607 | -1.1004 | -1.136 | -1.3466 | -1.4596 | -1.5223 | -0.643 | -0.64731 | -0.66626 | -0.68475 | -0.70405 | -0.72123 | -0.7451 | -0.76988 | -0.78722 | -0.81657 | -0.83767 | -1.0169 | -1.105 | -1.1528 | -0.72517 | -0.73652 | -0.76863 | -0.80219 | -0.83617 | -0.86924 | -0.90596 | -0.94326 | -0.9833 | -1.0294 | -1.0738 | -1.3142 | -1.4264 | -1.4907
|  | COLDBACKIE | FS |  |  |  | 1.046 | -0.76385 | -0.77702 | -0.78872 | -0.80155 | -0.814 | -0.82884 | -0.8435 | -0.87172 | -0.90331 | -0.9301 | -0.96112 | -1.1389 | -1.314 | -1.4177 | -0.63433 | -0.63901 | -0.64807 | -0.65739 | -0.66633 | -0.67871 | -0.69013 | -0.70948 | -0.73368 | -0.74691 | -0.76888 | -0.88516 | -0.9927 | -1.0701 | -0.7104 | -0.71951 | -0.73194 | -0.74443 | -0.75644 | -0.77223 | -0.78643 | -0.81406 | -0.847 | -0.87672 | -0.91038 | -1.1001 | -1.2792 | -1.3766
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.45787 | 0.45601 | 0.44333 | 0.43636 | 0.42393 | 0.40839 | 0.39093 | 0.38434 | 0.376 | 0.36157 | 0.35746 | 0.34633 | 0.34045 | 0.33113 | 0.45837 | 0.45768 | 0.44763 | 0.45021 | 0.44411 | 0.43544 | 0.42573 | 0.42011 | 0.41065 | 0.40083 | 0.39762 | 0.38988 | 0.38533 | 0.3758 | 0.46722 | 0.46562 | 0.45348 | 0.44827 | 0.43704 | 0.4228 | 0.40676 | 0.40046 | 0.38747 | 0.37326 | 0.36947 | 0.35941 | 0.35402 | 0.3462
|  | COLINTRAIVE | CT |  |  |  | 0 | 0.45787 | 0.45722 | 0.44671 | 0.43636 | 0.42393 | 0.40839 | 0.39093 | 0.38434 | 0.37668 | 0.36764 | 0.35746 | 0.35236 | 0.34553 | 0.33692 | 0.45837 | 0.46035 | 0.45479 | 0.45021 | 0.44411 | 0.43544 | 0.42573 | 0.42011 | 0.41304 | 0.40503 | 0.39762 | 0.39133 | 0.38533 | 0.3758 | 0.46722 | 0.46711 | 0.45755 | 0.44827 | 0.43704 | 0.4228 | 0.40676 | 0.40046 | 0.39086 | 0.37963 | 0.36947 | 0.36506 | 0.35973 | 0.35312
|  | COLINTRAIVE | LW |  |  |  | 0 | 0.45868 | 0.45913 | 0.44979 | 0.4394 | 0.42657 | 0.41293 | 0.39621 | 0.38932 | 0.376 | 0.36157 | 0.36492 | 0.34633 | 0.34045 | 0.33113 | 0.45854 | 0.46124 | 0.45665 | 0.45162 | 0.44461 | 0.43724 | 0.42753 | 0.42222 | 0.41065 | 0.40083 | 0.40214 | 0.38988 | 0.38713 | 0.38238 | 0.4679 | 0.46882 | 0.46037 | 0.45098 | 0.43924 | 0.42676 | 0.41131 | 0.40433 | 0.38747 | 0.37326 | 0.37712 | 0.35941 | 0.35402 | 0.3462
|  | COLINTRAIVE | ST |  |  |  | 0 | 0.46596 | 0.45601 | 0.44333 | 0.45133 | 0.44284 | 0.43702 | 0.43156 | 0.42623 | 0.41822 | 0.40859 | 0.4032 | 0.37228 | 0.36297 | 0.3596 | 0.4656 | 0.45768 | 0.44763 | 0.4588 | 0.45298 | 0.44982 | 0.44713 | 0.44394 | 0.43818 | 0.43057 | 0.42709 | 0.40185 | 0.39286 | 0.38595 | 0.47515 | 0.46562 | 0.45348 | 0.46205 | 0.45411 | 0.44882 | 0.44389 | 0.439 | 0.43143 | 0.42118 | 0.41632 | 0.38346 | 0.37466 | 0.37212
|  | COLINTRAIVE | FS |  |  |  | 0 | 0.46922 | 0.46168 | 0.45413 | 0.4581 | 0.46026 | 0.45858 | 0.45414 | 0.4507 | 0.44629 | 0.43918 | 0.43334 | 0.39598 | 0.37259 | 0.36485 | 0.46718 | 0.4608 | 0.45366 | 0.45767 | 0.46044 | 0.45902 | 0.45473 | 0.45299 | 0.45018 | 0.44458 | 0.44048 | 0.41338 | 0.39307 | 0.3766 | 0.47808 | 0.4708 | 0.46336 | 0.4657 | 0.46942 | 0.46766 | 0.46225 | 0.45969 | 0.45562 | 0.44801 | 0.44225 | 0.40516 | 0.3836 | 0.37658
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0.187 | -0.24624 | -0.31617 | -0.47125 | -0.63288 | -0.80951 | -1.0265 | -1.2508 | -1.4706 | -1.6943 | -1.8936 | -2.0389 | -2.5948 | -3.0184 | -3.2675 | 0.5327 | 0.48444 | 0.40153 | 0.32013 | 0.23454 | 0.11988 | 0.0028367 | -0.10616 | -0.2242 | -0.35365 | -0.41671 | -0.67804 | -0.86976 | -1.0778 | 0.27007 | 0.20078 | 0.1059 | 0.011959 | -0.084877 | -0.22975 | -0.3942 | -0.57303 | -0.75049 | -0.90937 | -1.0268 | -1.5079 | -1.854 | -2.1016
|  | COLL | CT |  |  |  | 0.187 | -0.24624 | -0.31341 | -0.45265 | -0.61341 | -0.79908 | -1.009 | -1.2407 | -1.4542 | -1.6335 | -1.8012 | -1.9161 | -2.5838 | -3.0184 | -3.2675 | 0.5327 | 0.49446 | 0.4281 | 0.34646 | 0.25851 | 0.15869 | 0.046929 | -0.06341 | -0.15605 | -0.24844 | -0.30749 | -0.64276 | -0.86976 | -1.0778 | 0.27007 | 0.21246 | 0.13206 | 0.043367 | -0.063321 | -0.18007 | -0.36404 | -0.53537 | -0.68143 | -0.81499 | -0.90667 | -1.4673 | -1.854 | -2.0766
|  | COLL | LW |  |  |  | 0.187 | -0.24019 | -0.31617 | -0.47125 | -0.63288 | -0.80951 | -1.0265 | -1.2508 | -1.4706 | -1.6943 | -1.8936 | -2.0389 | -2.5948 | -2.9067 | -3.2246 | 0.53597 | 0.48444 | 0.40153 | 0.32013 | 0.23454 | 0.11988 | 0.0028367 | -0.10616 | -0.2242 | -0.35365 | -0.41671 | -0.67804 | -0.81913 | -0.99322 | 0.27176 | 0.20078 | 0.1059 | 0.011959 | -0.084877 | -0.22975 | -0.3942 | -0.57303 | -0.75049 | -0.90937 | -1.0268 | -1.5079 | -1.8086 | -2.1016
|  | COLL | ST |  |  |  | 0.187 | -0.21599 | -0.26024 | -0.32192 | -0.39164 | -0.45185 | -0.5216 | -0.5788 | -0.64247 | -0.72206 | -0.7777 | -0.85786 | -1.4426 | -1.9285 | -2.3511 | 0.54916 | 0.52539 | 0.48826 | 0.44591 | 0.41193 | 0.37133 | 0.34063 | 0.29977 | 0.24582 | 0.21116 | 0.15608 | -0.26712 | -0.52031 | -0.8025 | 0.29403 | 0.26522 | 0.22334 | 0.17108 | 0.12877 | 0.074204 | 0.033083 | -0.028044 | -0.1113 | -0.16825 | -0.25464 | -0.74055 | -1.0263 | -1.4401
|  | COLL | FS |  |  |  | 0.187 | -0.19585 | -0.22781 | -0.2696 | -0.30398 | -0.34086 | -0.38657 | -0.43826 | -0.50108 | -0.58606 | -0.66681 | -0.7514 | -1.2732 | -1.8498 | -2.3539 | 0.55725 | 0.53946 | 0.51324 | 0.49271 | 0.46941 | 0.43886 | 0.40127 | 0.36619 | 0.31236 | 0.2618 | 0.20957 | -0.12138 | -0.48203 | -0.89211 | 0.30265 | 0.28128 | 0.24937 | 0.22437 | 0.1961 | 0.15679 | 0.10917 | 0.07016 | 0.0022407 | -0.062061 | -0.13093 | -0.52786 | -0.86502 | -1.2795
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 2.033 | 7.36 | 5.9577 | 4.4527 | 3.0136 | 1.9939 | 0.43097 | -1.7176 | -2.0726 | -2.5494 | -3.2576 | -3.9457 | -7.7563 | -12.0161 | -16.4204 | 8.4565 | 6.7521 | 4.9126 | 3.1711 | 1.9595 | 0.10446 | -2.4616 | -2.7692 | -3.0739 | -3.4239 | -3.7674 | -7.1288 | -12.1943 | -17.6624 | 8.4224 | 6.6923 | 4.8367 | 3.0712 | 1.8294 | -0.070501 | -2.6901 | -3.0505 | -3.4221 | -4.083 | -4.7616 | -9.0208 | -14.2424 | -19.7266
|  | COMMERCE STREET | CT |  |  |  | 2.033 | 7.36 | 7.1852 | 6.9958 | 5.4104 | 4.9618 | 4.3227 | 2.9511 | 2.5185 | 1.9369 | 1.3866 | 0.87379 | -0.80831 | -2.0355 | -3.4878 | 8.4565 | 8.2921 | 8.1373 | 6.2962 | 5.8275 | 5.1323 | 3.5769 | 3.2514 | 2.8188 | 2.4119 | 1.9967 | -0.012276 | -2.3646 | -6.2131 | 8.4224 | 8.2397 | 8.0572 | 6.1651 | 5.6661 | 4.9368 | 3.3253 | 2.964 | 2.3773 | 1.7952 | 1.2417 | -0.65558 | -2.1736 | -3.9683
|  | COMMERCE STREET | LW |  |  |  | 2.033 | 7.3665 | 5.9577 | 4.4527 | 3.0136 | 1.9939 | 0.43097 | -1.7176 | -2.0726 | -2.5494 | -3.2576 | -3.9457 | -7.7563 | -12.0161 | -16.4204 | 8.468 | 6.7521 | 4.9126 | 3.1711 | 1.9595 | 0.10446 | -2.4616 | -2.7692 | -3.0739 | -3.4239 | -3.7674 | -7.1288 | -12.1943 | -17.6624 | 8.4289 | 6.6923 | 4.8367 | 3.0712 | 1.8294 | -0.070501 | -2.6901 | -3.0505 | -3.4221 | -4.083 | -4.7616 | -9.0208 | -14.2424 | -19.7266
|  | COMMERCE STREET | ST |  |  |  | 2.033 | 7.4057 | 7.3062 | 6.4356 | 5.8155 | 5.3957 | 5.1708 | 4.9065 | 4.5421 | 4.1312 | 3.7274 | 3.4216 | -2.5034 | -7.6557 | -11.8012 | 8.4923 | 8.3811 | 7.305 | 6.551 | 6.0534 | 5.8073 | 5.5238 | 5.1257 | 4.6919 | 4.2767 | 3.9995 | -1.4648 | -7.6622 | -14.5162 | 8.4662 | 8.3553 | 7.278 | 6.5222 | 6.0212 | 5.7692 | 5.4761 | 5.0653 | 4.6111 | 4.173 | 3.8684 | -2.6783 | -8.8701 | -14.0328
|  | COMMERCE STREET | FS |  |  |  | 2.033 | 7.4194 | 7.3855 | 7.1248 | 6.8477 | 6.5057 | 6.15 | 5.6067 | 5.2032 | 4.7283 | 4.2516 | 4.1012 | 2.8153 | 0.72175 | -1.2838 | 8.5011 | 8.4629 | 8.1396 | 7.799 | 7.3794 | 6.9452 | 6.2753 | 5.7774 | 5.2002 | 4.623 | 4.4607 | 3.0578 | 0.36766 | -5.2756 | 8.4796 | 8.4468 | 8.1269 | 7.7927 | 7.3796 | 6.9523 | 6.2944 | 5.8141 | 5.2525 | 4.6908 | 4.5426 | 3.404 | 1.3812 | -0.72551
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | NO | 0 | 0.042305 | 0.032593 | 0.021917 | 0.011334 | 0.0034886 | -0.0087121 | -0.024875 | -0.030061 | -0.036512 | -0.03455 | -0.038657 | -0.044002 | -0.06708 | -0.092867 | 0.0038215 | -0.0074895 | -0.019356 | -0.030841 | -0.038863 | -0.051808 | -0.069438 | -0.074281 | -0.080483 | -0.071378 | -0.074477 | -0.084215 | -0.11216 | -0.14354 | 0.041713 | 0.030192 | 0.017892 | 0.0059138 | -0.0026452 | -0.016384 | -0.034959 | -0.039998 | -0.04629 | -0.046333 | -0.050391 | -0.058664 | -0.087128 | -0.11894
|  | COMRIE | CT |  |  |  | 0 | 0.042305 | 0.039467 | 0.03671 | 0.026377 | 0.020843 | 0.014481 | 0.0032239 | -0.003151 | -0.0080849 | -0.0065035 | -0.011125 | -0.011671 | -0.01846 | -0.027733 | 0.0038215 | 0.0014997 | -0.00048684 | -0.011783 | -0.016711 | -0.02253 | -0.033958 | -0.040208 | -0.045059 | -0.037201 | -0.041117 | -0.043952 | -0.051531 | -0.062329 | 0.041713 | 0.039067 | 0.036659 | 0.02487 | 0.019395 | 0.012766 | 0.00031428 | -0.0061302 | -0.011167 | -0.011766 | -0.016557 | -0.01838 | -0.026475 | -0.037693
|  | COMRIE | LW |  |  |  | 0 | 0.042519 | 0.032593 | 0.021917 | 0.011334 | 0.0034886 | -0.0087121 | -0.024875 | -0.030061 | -0.036512 | -0.03455 | -0.038657 | -0.044002 | -0.06708 | -0.092867 | 0.0038445 | -0.0074895 | -0.019356 | -0.030841 | -0.038863 | -0.051808 | -0.069438 | -0.074281 | -0.080483 | -0.071378 | -0.074477 | -0.084215 | -0.11216 | -0.14354 | 0.04181 | 0.030192 | 0.017892 | 0.0059138 | -0.0026452 | -0.016384 | -0.034959 | -0.039998 | -0.04629 | -0.046333 | -0.050391 | -0.058664 | -0.087128 | -0.11894
|  | COMRIE | ST |  |  |  | 0 | 0.043206 | 0.041957 | 0.035366 | 0.03014 | 0.026409 | 0.023203 | 0.019684 | 0.01592 | 0.011356 | 0.0065988 | 0.0023187 | -0.0167 | -0.043747 | -0.067406 | 0.0045781 | 0.0038212 | -0.0032879 | -0.0086325 | -0.012088 | -0.014825 | -0.017892 | -0.021399 | -0.025747 | -0.030298 | -0.034188 | -0.051426 | -0.083584 | -0.11244 | 0.04257 | 0.041569 | 0.034106 | 0.0284 | 0.024577 | 0.021414 | 0.017815 | 0.013943 | 0.0092798 | 0.0044271 | 0.0002599 | -0.02529 | -0.058305 | -0.087581
|  | COMRIE | FS |  |  |  | 0 | 0.043769 | 0.042881 | 0.040371 | 0.03768 | 0.034929 | 0.031999 | 0.028057 | 0.024348 | 0.019329 | 0.014247 | 0.011392 | 0.00070427 | 0.00098658 | -0.0038929 | 0.0047253 | 0.0041267 | 0.0013751 | -0.0015619 | -0.0045657 | -0.0077547 | -0.012166 | -0.015867 | -0.021105 | -0.026405 | -0.028876 | -0.030427 | -0.029373 | -0.034368 | 0.042901 | 0.042153 | 0.039298 | 0.036254 | 0.033138 | 0.029833 | 0.025299 | 0.021345 | 0.015842 | 0.010274 | 0.0075285 | -0.0037621 | -0.003161 | -0.008721
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0.146 | -0.98528 | -1.05 | -1.1287 | -1.2182 | -1.3316 | -1.4495 | -1.568 | -1.6453 | -1.7076 | -1.7737 | -1.8268 | -2.0013 | -2.0865 | -2.1806 | -0.18767 | -0.22866 | -0.26746 | -0.31233 | -0.37379 | -0.43644 | -0.50028 | -0.55421 | -0.60253 | -0.65413 | -0.69403 | -0.80801 | -0.86175 | -0.99214 | -0.40586 | -0.45344 | -0.52986 | -0.6163 | -0.71558 | -0.82102 | -0.93153 | -0.97515 | -1.0359 | -1.1011 | -1.1559 | -1.322 | -1.3978 | -1.4846
|  | CONNEL | CT |  |  |  | 0.146 | -0.98528 | -1.05 | -1.1287 | -1.2182 | -1.3316 | -1.4495 | -1.568 | -1.6453 | -1.7076 | -1.7737 | -1.7937 | -1.9531 | -2.0337 | -2.1269 | -0.18767 | -0.22866 | -0.26746 | -0.31233 | -0.37379 | -0.43644 | -0.50028 | -0.55421 | -0.60154 | -0.65413 | -0.67175 | -0.79984 | -0.86175 | -0.95431 | -0.40586 | -0.45344 | -0.52986 | -0.6163 | -0.71558 | -0.82102 | -0.93153 | -0.97515 | -1.0359 | -1.1011 | -1.1208 | -1.2745 | -1.3464 | -1.4309
|  | CONNEL | LW |  |  |  | 0.146 | -0.97684 | -1.0348 | -1.1032 | -1.1872 | -1.2795 | -1.4039 | -1.5148 | -1.5957 | -1.6995 | -1.7517 | -1.8268 | -2.0013 | -2.0865 | -2.1806 | -0.18399 | -0.22072 | -0.25255 | -0.29473 | -0.34158 | -0.4123 | -0.47008 | -0.52643 | -0.60253 | -0.63842 | -0.69403 | -0.80801 | -0.84432 | -0.8951 | -0.39647 | -0.43818 | -0.50589 | -0.58334 | -0.66829 | -0.77007 | -0.87029 | -0.93111 | -1.0323 | -1.0826 | -1.1559 | -1.322 | -1.3978 | -1.4846
|  | CONNEL | ST |  |  |  | 0.146 | -0.96269 | -0.99389 | -1.0415 | -1.0987 | -1.1446 | -1.2058 | -1.2604 | -1.3232 | -1.3755 | -1.449 | -1.5208 | -1.8415 | -1.9653 | -2.0271 | -0.17474 | -0.19141 | -0.21509 | -0.24658 | -0.26917 | -0.30416 | -0.33395 | -0.37382 | -0.40532 | -0.45402 | -0.50151 | -0.72708 | -0.81873 | -0.89016 | -0.38725 | -0.41587 | -0.46179 | -0.51202 | -0.55774 | -0.61001 | -0.65934 | -0.7072 | -0.75211 | -0.80602 | -0.86268 | -1.1678 | -1.2813 | -1.3384
|  | CONNEL | FS |  |  |  | 0.146 | -0.94335 | -0.96586 | -0.99086 | -1.0141 | -1.0445 | -1.0636 | -1.0975 | -1.136 | -1.1916 | -1.2483 | -1.2843 | -1.5937 | -1.8545 | -1.9817 | -0.16682 | -0.18044 | -0.19621 | -0.21069 | -0.23115 | -0.24263 | -0.26669 | -0.28964 | -0.32668 | -0.36462 | -0.38605 | -0.60641 | -0.81222 | -0.99214 | -0.37125 | -0.38556 | -0.40509 | -0.42365 | -0.44555 | -0.46272 | -0.48623 | -0.52019 | -0.56211 | -0.61287 | -0.64567 | -0.93895 | -1.1818 | -1.2993
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 0.523 | 1.634 | 1.207 | 0.86988 | 0.51968 | 0.14813 | -0.30405 | -0.88007 | -1.2495 | -1.6227 | -1.9767 | -2.128 | -2.827 | -3.3934 | -3.8471 | 2.9547 | 2.7272 | 2.5672 | 2.3965 | 2.2345 | 2.0185 | 1.7499 | 1.5371 | 1.3001 | 1.0928 | 1.0185 | 0.72411 | 0.37326 | -0.02719 | 2.3465 | 2.0006 | 1.7014 | 1.3828 | 1.0434 | 0.638 | 0.12856 | -0.21258 | -0.5635 | -0.89342 | -1.0195 | -1.6421 | -2.1146 | -2.5191
|  | CONON BRIDGE | CT |  |  |  | 0.523 | 1.6416 | 1.2356 | 0.91463 | 0.55038 | 0.14813 | -0.30405 | -0.88007 | -1.2495 | -1.5426 | -1.8202 | -2.128 | -2.7855 | -3.3934 | -3.8471 | 2.961 | 2.75 | 2.5982 | 2.4197 | 2.2345 | 2.0218 | 1.7504 | 1.5392 | 1.3726 | 1.203 | 1.0185 | 0.72411 | 0.37326 | -0.02719 | 2.3481 | 2.0167 | 1.7307 | 1.4012 | 1.0434 | 0.638 | 0.12856 | -0.21258 | -0.48264 | -0.74132 | -1.0195 | -1.5807 | -2.1146 | -2.5191
|  | CONON BRIDGE | LW |  |  |  | 0.523 | 1.634 | 1.207 | 0.86988 | 0.51968 | 0.17118 | -0.27658 | -0.8295 | -1.2191 | -1.6227 | -1.9767 | -1.9855 | -2.827 | -3.2907 | -3.7354 | 2.9547 | 2.7272 | 2.5672 | 2.3965 | 2.2446 | 2.0185 | 1.7499 | 1.5371 | 1.3001 | 1.0928 | 1.1562 | 0.74025 | 0.54356 | 0.32019 | 2.3465 | 2.0006 | 1.7014 | 1.3828 | 1.0731 | 0.66378 | 0.17109 | -0.18713 | -0.5635 | -0.89342 | -0.88033 | -1.6421 | -2.0543 | -2.4602
|  | CONON BRIDGE | ST |  |  |  | 0.523 | 1.7049 | 1.3716 | 1.2019 | 1.0447 | 0.8628 | 0.67405 | 0.45475 | 0.27629 | 0.074321 | -0.094795 | -0.34953 | -1.2455 | -1.9473 | -2.476 | 2.9944 | 2.8268 | 2.7418 | 2.6638 | 2.5697 | 2.4685 | 2.3556 | 2.2494 | 2.123 | 2.0223 | 1.8653 | 1.3383 | 0.91012 | 0.49054 | 2.4062 | 2.1431 | 1.9921 | 1.8511 | 1.689 | 1.5187 | 1.33 | 1.1656 | 0.97728 | 0.82168 | 0.5924 | -0.22136 | -0.84811 | -1.318
|  | CONON BRIDGE | FS |  |  |  | 0.523 | 1.821 | 1.5848 | 1.5084 | 1.4184 | 1.3347 | 1.2335 | 1.0948 | 0.9257 | 0.77374 | 0.59647 | 0.37662 | -0.66368 | -1.4248 | -2.0708 | 3.045 | 2.9195 | 2.8742 | 2.8171 | 2.7672 | 2.703 | 2.6129 | 2.5125 | 2.4232 | 2.3128 | 2.1787 | 1.512 | 0.98486 | 0.28175 | 2.5019 | 2.3193 | 2.2514 | 2.1699 | 2.0975 | 2.0077 | 1.8877 | 1.7342 | 1.5965 | 1.4332 | 1.2387 | 0.27663 | -0.37174 | -0.94548
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0 | 0.46154 | 0.45544 | 0.43544 | 0.4149 | 0.39405 | 0.3694 | 0.33822 | 0.32885 | 0.31266 | 0.29573 | 0.29656 | 0.25715 | 0.22332 | 0.18546 | 0.46712 | 0.46227 | 0.4466 | 0.43133 | 0.41639 | 0.39818 | 0.3729 | 0.36633 | 0.3516 | 0.33904 | 0.34125 | 0.30911 | 0.27785 | 0.24092 | 0.48489 | 0.47145 | 0.45127 | 0.43116 | 0.41045 | 0.38608 | 0.35359 | 0.34402 | 0.32456 | 0.30801 | 0.31062 | 0.27058 | 0.23457 | 0.19361
|  | CONON FALLS | CT |  |  |  | 0 | 0.46154 | 0.45997 | 0.44749 | 0.42727 | 0.41048 | 0.38934 | 0.3627 | 0.35265 | 0.342 | 0.32861 | 0.32896 | 0.29491 | 0.27748 | 0.25725 | 0.46737 | 0.47018 | 0.46363 | 0.44914 | 0.43985 | 0.42601 | 0.40689 | 0.39865 | 0.38824 | 0.37659 | 0.37741 | 0.34826 | 0.3327 | 0.30933 | 0.48489 | 0.47838 | 0.46724 | 0.44816 | 0.43349 | 0.41301 | 0.38657 | 0.37552 | 0.36214 | 0.34754 | 0.35001 | 0.31535 | 0.2997 | 0.28048
|  | CONON FALLS | LW |  |  |  | 0 | 0.46298 | 0.45544 | 0.43544 | 0.4149 | 0.39405 | 0.3694 | 0.33822 | 0.32885 | 0.31266 | 0.29573 | 0.29656 | 0.25715 | 0.22332 | 0.18546 | 0.46712 | 0.46227 | 0.4466 | 0.43133 | 0.41639 | 0.39818 | 0.3729 | 0.36633 | 0.3516 | 0.33904 | 0.34125 | 0.30911 | 0.27785 | 0.24092 | 0.48525 | 0.47145 | 0.45127 | 0.43116 | 0.41045 | 0.38608 | 0.35359 | 0.34402 | 0.32456 | 0.30801 | 0.31062 | 0.27058 | 0.23457 | 0.19361
|  | CONON FALLS | ST |  |  |  | 0 | 0.47038 | 0.45798 | 0.45005 | 0.44095 | 0.43068 | 0.42143 | 0.40903 | 0.40049 | 0.3893 | 0.37634 | 0.36822 | 0.30466 | 0.26358 | 0.23367 | 0.47483 | 0.46662 | 0.46154 | 0.45732 | 0.45123 | 0.44661 | 0.43751 | 0.43239 | 0.42386 | 0.41274 | 0.40828 | 0.34978 | 0.30636 | 0.26776 | 0.49322 | 0.48292 | 0.46763 | 0.46142 | 0.45223 | 0.44467 | 0.43162 | 0.424 | 0.41218 | 0.39718 | 0.39037 | 0.32264 | 0.27823 | 0.24477
|  | CONON FALLS | FS |  |  |  | 0 | 0.47537 | 0.46634 | 0.45583 | 0.45613 | 0.45828 | 0.4538 | 0.44447 | 0.43855 | 0.42975 | 0.41737 | 0.4095 | 0.35883 | 0.3237 | 0.30569 | 0.47626 | 0.46968 | 0.45986 | 0.46252 | 0.46389 | 0.4599 | 0.45123 | 0.44691 | 0.44012 | 0.42977 | 0.4243 | 0.38723 | 0.35919 | 0.33166 | 0.49621 | 0.48836 | 0.4777 | 0.47187 | 0.47418 | 0.46958 | 0.45926 | 0.45347 | 0.44503 | 0.43186 | 0.42445 | 0.37611 | 0.34507 | 0.32991
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 0.6 | 15.3708 | 15.1125 | 14.621 | 14.008 | 13.302 | 12.2643 | 10.8255 | 9.3894 | 7.6614 | 6.0768 | 4.6043 | 0.83129 | 0.7777 | -0.65331 | 17.7749 | 17.6109 | 17.3812 | 17.0671 | 16.7441 | 16.3802 | 15.6641 | 14.7925 | 13.5789 | 12.4491 | 11.3898 | 8.817 | 8.1331 | 4.141 | 16.8926 | 16.6972 | 16.161 | 15.4705 | 14.7308 | 13.6448 | 12.3537 | 11.0659 | 9.5283 | 8.1194 | 6.8118 | 3.4378 | 3.4055 | 2.1426
|  | CONSTABLE STREET | CT |  |  |  | 0.6 | 15.4101 | 15.1555 | 14.7389 | 14.1771 | 13.5149 | 12.6773 | 11.4916 | 10.06 | 8.8873 | 7.7039 | 6.6401 | 2.8966 | 1.9174 | 0.74663 | 17.7764 | 17.6109 | 17.3812 | 17.0671 | 16.7441 | 16.3869 | 15.7269 | 14.8348 | 14.0583 | 13.2067 | 12.4139 | 9.5071 | 8.1331 | 5.6847 | 16.9111 | 16.7202 | 16.2204 | 15.5472 | 14.8213 | 14.0318 | 12.9661 | 11.6749 | 10.6192 | 9.5599 | 8.6109 | 5.2367 | 4.339 | 3.3166
|  | CONSTABLE STREET | LW |  |  |  | 0.6 | 15.3708 | 15.1125 | 14.621 | 14.008 | 13.302 | 12.2643 | 10.8255 | 9.3894 | 7.6614 | 6.0768 | 4.6043 | 0.83129 | 0.7777 | -0.65331 | 17.7749 | 17.6286 | 17.407 | 17.1228 | 16.8201 | 16.3802 | 15.6641 | 14.7925 | 13.5789 | 12.4491 | 11.3898 | 8.817 | 8.723 | 7.5593 | 16.8926 | 16.6972 | 16.161 | 15.4705 | 14.7308 | 13.6448 | 12.3537 | 11.0659 | 9.5283 | 8.1194 | 6.8118 | 3.4378 | 3.4055 | 2.1426
|  | CONSTABLE STREET | ST |  |  |  | 0.6 | 15.4814 | 15.3727 | 15.3369 | 15.283 | 15.1987 | 15.0734 | 14.9157 | 14.5866 | 14.0167 | 13.3928 | 12.7297 | 9.3402 | 8.3794 | 7.6583 | 17.8216 | 17.7493 | 17.6961 | 17.6301 | 17.5425 | 17.4236 | 17.2818 | 17.0905 | 16.839 | 16.4583 | 15.9493 | 12.7174 | 11.0674 | 9.13 | 16.9507 | 16.8817 | 16.8643 | 16.802 | 16.6722 | 16.4437 | 16.1683 | 15.7999 | 15.307 | 14.773 | 14.1985 | 11.2958 | 10.3691 | 9.652
|  | CONSTABLE STREET | FS |  |  |  | 0.6 | 15.5643 | 15.5047 | 15.4427 | 15.3678 | 15.2705 | 15.1567 | 15.0146 | 14.7791 | 14.4842 | 14.0897 | 13.6028 | 9.8454 | 6.2983 | 3.8169 | 17.8404 | 17.7994 | 17.7401 | 17.6703 | 17.5829 | 17.4792 | 17.3439 | 17.1554 | 16.9346 | 16.702 | 16.3497 | 13.2289 | 9.0666 | 4.141 | 16.9931 | 16.9511 | 16.9248 | 16.873 | 16.8006 | 16.6276 | 16.4051 | 16.0977 | 15.7302 | 15.3416 | 14.9092 | 11.5209 | 8.3039 | 6.0314
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0 | 0.090967 | 0.080522 | 0.069188 | 0.057715 | 0.049106 | 0.035498 | 0.017691 | 0.017035 | 0.02132 | 0.017219 | 0.013596 | 0.00051995 | -0.022756 | -0.048912 | 0.09226 | 0.080288 | 0.067699 | 0.055267 | 0.046395 | 0.032027 | 0.012742 | 0.016514 | 0.019965 | 0.016856 | 0.014079 | -0.0016081 | -0.029637 | -0.061236 | 0.090219 | 0.078012 | 0.064847 | 0.051755 | 0.042101 | 0.026854 | 0.0066106 | 0.0062483 | 0.010423 | 0.0064613 | 0.0029271 | -0.013186 | -0.041829 | -0.07404
|  | CONTULLICH | CT |  |  |  | 0 | 0.090967 | 0.087463 | 0.083875 | 0.072633 | 0.065955 | 0.058456 | 0.045415 | 0.043687 | 0.038191 | 0.045006 | 0.040895 | 0.033243 | 0.02631 | 0.016736 | 0.09226 | 0.089221 | 0.086436 | 0.074279 | 0.068213 | 0.061225 | 0.047998 | 0.050487 | 0.045771 | 0.050849 | 0.047239 | 0.038482 | 0.030348 | 0.018527 | 0.090219 | 0.086838 | 0.083468 | 0.070598 | 0.063705 | 0.055808 | 0.041574 | 0.039911 | 0.034255 | 0.040815 | 0.036558 | 0.027574 | 0.019343 | 0.0078154
|  | CONTULLICH | LW |  |  |  | 0 | 0.091131 | 0.080522 | 0.069188 | 0.057715 | 0.049106 | 0.035498 | 0.017691 | 0.017035 | 0.02132 | 0.017219 | 0.013596 | 0.00051995 | -0.022756 | -0.048912 | 0.092316 | 0.080288 | 0.067699 | 0.055267 | 0.046395 | 0.032027 | 0.012742 | 0.016514 | 0.019965 | 0.016856 | 0.014079 | -0.0016081 | -0.029637 | -0.061236 | 0.090352 | 0.078012 | 0.064847 | 0.051755 | 0.042101 | 0.026854 | 0.0066106 | 0.0062483 | 0.010423 | 0.0064613 | 0.0029271 | -0.013186 | -0.041829 | -0.07404
|  | CONTULLICH | ST |  |  |  | 0 | 0.09202 | 0.090523 | 0.08371 | 0.078159 | 0.07405 | 0.070353 | 0.066218 | 0.061617 | 0.055876 | 0.049849 | 0.050204 | 0.029357 | 0.0023933 | -0.020939 | 0.093169 | 0.092047 | 0.084502 | 0.078629 | 0.07461 | 0.071212 | 0.067381 | 0.062989 | 0.057469 | 0.051298 | 0.056737 | 0.031392 | -0.0013057 | -0.030902 | 0.09124 | 0.089852 | 0.081951 | 0.07572 | 0.071325 | 0.067524 | 0.063285 | 0.058562 | 0.0527 | 0.046552 | 0.047238 | 0.02168 | -0.011274 | -0.040261
|  | CONTULLICH | FS |  |  |  | 0 | 0.092595 | 0.091498 | 0.088789 | 0.085828 | 0.082786 | 0.079493 | 0.075096 | 0.070801 | 0.064991 | 0.059074 | 0.055254 | 0.052108 | 0.045952 | 0.04105 | 0.093436 | 0.092555 | 0.089536 | 0.086266 | 0.082914 | 0.079313 | 0.074395 | 0.069997 | 0.063884 | 0.05759 | 0.053989 | 0.056324 | 0.051424 | 0.044573 | 0.091726 | 0.090694 | 0.087604 | 0.084262 | 0.080837 | 0.077163 | 0.072179 | 0.067567 | 0.061234 | 0.054795 | 0.051085 | 0.048572 | 0.042755 | 0.037169
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | 0.127 | -0.45923 | -0.50562 | -0.55993 | -0.64135 | -0.7065 | -0.79026 | -0.88919 | -0.9603 | -0.9941 | -1.0663 | -1.1259 | -1.3158 | -1.4057 | -1.4937 | -0.14764 | -0.17075 | -0.19659 | -0.25052 | -0.28344 | -0.32427 | -0.38172 | -0.42054 | -0.44626 | -0.47828 | -0.52412 | -0.68624 | -0.7623 | -0.80199 | -0.33315 | -0.37771 | -0.43409 | -0.51898 | -0.58845 | -0.67461 | -0.77739 | -0.83985 | -0.87066 | -0.9338 | -0.9885 | -1.178 | -1.28 | -1.3716
|  | CORRAN | CT |  |  |  | 0.127 | -0.45923 | -0.50562 | -0.55993 | -0.64135 | -0.7065 | -0.79026 | -0.88919 | -0.9603 | -0.9911 | -1.0437 | -1.0903 | -1.23 | -1.2885 | -1.3502 | -0.14764 | -0.16842 | -0.19638 | -0.25052 | -0.28344 | -0.32427 | -0.38172 | -0.42054 | -0.44626 | -0.47599 | -0.50229 | -0.58193 | -0.6113 | -0.63052 | -0.33315 | -0.37771 | -0.43409 | -0.51898 | -0.58845 | -0.67461 | -0.77739 | -0.83985 | -0.87066 | -0.9158 | -0.95476 | -1.0883 | -1.153 | -1.2167
|  | CORRAN | LW |  |  |  | 0.127 | -0.45342 | -0.50081 | -0.5542 | -0.62417 | -0.67783 | -0.76983 | -0.86365 | -0.93443 | -0.9941 | -1.0663 | -1.1259 | -1.3158 | -1.4057 | -1.4937 | -0.14564 | -0.17075 | -0.19659 | -0.22762 | -0.25355 | -0.29636 | -0.34623 | -0.38504 | -0.42994 | -0.47828 | -0.52412 | -0.68624 | -0.7623 | -0.80199 | -0.32607 | -0.37301 | -0.43069 | -0.50213 | -0.56242 | -0.65452 | -0.75153 | -0.81432 | -0.86976 | -0.9338 | -0.9885 | -1.178 | -1.28 | -1.3716
|  | CORRAN | ST |  |  |  | 0.127 | -0.44741 | -0.46874 | -0.50432 | -0.54256 | -0.57678 | -0.61983 | -0.65413 | -0.69971 | -0.74471 | -0.80177 | -0.86344 | -1.1278 | -1.2373 | -1.2785 | -0.1408 | -0.14753 | -0.16382 | -0.18023 | -0.19562 | -0.21399 | -0.23236 | -0.25603 | -0.28539 | -0.32065 | -0.36062 | -0.59502 | -0.70073 | -0.73632 | -0.32089 | -0.34393 | -0.38247 | -0.42264 | -0.45906 | -0.50193 | -0.53889 | -0.5824 | -0.62629 | -0.67993 | -0.73744 | -0.99558 | -1.1142 | -1.1653
|  | CORRAN | FS |  |  |  | 0.127 | -0.43223 | -0.44513 | -0.45844 | -0.47481 | -0.49437 | -0.50915 | -0.53337 | -0.55645 | -0.59676 | -0.63839 | -0.66901 | -0.88671 | -1.1318 | -1.2589 | -0.13724 | -0.14138 | -0.14846 | -0.15684 | -0.16672 | -0.17626 | -0.18982 | -0.20245 | -0.2229 | -0.2448 | -0.26352 | -0.40935 | -0.59635 | -0.74585 | -0.30408 | -0.31797 | -0.33101 | -0.34666 | -0.36465 | -0.37918 | -0.40132 | -0.42648 | -0.46519 | -0.50512 | -0.53575 | -0.74563 | -0.992 | -1.1288
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 1.366 | -0.10534 | -0.14038 | -0.22761 | -0.33738 | -0.4615 | -0.60415 | -0.77253 | -0.85054 | -0.93909 | -1.0328 | -1.1093 | -1.325 | -1.4394 | -1.5843 | 0.10892 | 0.068988 | 0.017091 | -0.037476 | -0.09786 | -0.17667 | -0.27657 | -0.3329 | -0.41426 | -0.4885 | -0.55307 | -0.70896 | -0.77245 | -0.87402 | 0.081998 | 0.049694 | -0.034377 | -0.13946 | -0.25081 | -0.37918 | -0.53392 | -0.60611 | -0.69913 | -0.78785 | -0.86164 | -1.0661 | -1.1761 | -1.3168
|  | COSHIEVILLE | CT |  |  |  | 1.366 | -0.10534 | -0.14038 | -0.22761 | -0.33738 | -0.4615 | -0.60415 | -0.77253 | -0.85054 | -0.92457 | -0.98819 | -1.0383 | -1.2255 | -1.3142 | -1.4257 | 0.10892 | 0.071418 | 0.022782 | -0.035343 | -0.096104 | -0.16737 | -0.26152 | -0.31729 | -0.37313 | -0.42534 | -0.47466 | -0.62136 | -0.67381 | -0.76123 | 0.081998 | 0.05178 | -0.034377 | -0.13946 | -0.25081 | -0.37918 | -0.53392 | -0.60611 | -0.67483 | -0.73505 | -0.78438 | -0.96174 | -1.0418 | -1.1451
|  | COSHIEVILLE | LW |  |  |  | 1.366 | -0.10068 | -0.13864 | -0.21849 | -0.31933 | -0.43822 | -0.58062 | -0.74672 | -0.8316 | -0.93909 | -1.0328 | -1.1093 | -1.325 | -1.4394 | -1.5843 | 0.11203 | 0.068988 | 0.017091 | -0.037476 | -0.09786 | -0.17667 | -0.27657 | -0.3329 | -0.41426 | -0.4885 | -0.55307 | -0.70896 | -0.77245 | -0.87402 | 0.084931 | 0.049694 | -0.029698 | -0.12749 | -0.23532 | -0.3658 | -0.52062 | -0.59832 | -0.69913 | -0.78785 | -0.86164 | -1.0661 | -1.1761 | -1.3168
|  | COSHIEVILLE | ST |  |  |  | 1.366 | -0.096965 | -0.11688 | -0.16025 | -0.21718 | -0.27627 | -0.33221 | -0.40036 | -0.46242 | -0.54196 | -0.62079 | -0.67933 | -1.0081 | -1.1391 | -1.2051 | 0.11837 | 0.10261 | 0.072249 | 0.040197 | 0.0038088 | -0.026244 | -0.067133 | -0.10359 | -0.15663 | -0.21069 | -0.24657 | -0.50836 | -0.61213 | -0.67927 | 0.091337 | 0.077401 | 0.040564 | -0.014633 | -0.074271 | -0.12857 | -0.19237 | -0.24802 | -0.3208 | -0.39376 | -0.44769 | -0.76444 | -0.89231 | -0.95771
|  | COSHIEVILLE | FS |  |  |  | 1.366 | -0.082683 | -0.096607 | -0.10676 | -0.1224 | -0.13691 | -0.15547 | -0.17923 | -0.23421 | -0.2888 | -0.34938 | -0.40657 | -0.70425 | -1.0057 | -1.13 | 0.12734 | 0.11388 | 0.10034 | 0.080898 | 0.063638 | 0.039217 | 0.021568 | -0.012831 | -0.047096 | -0.087755 | -0.12636 | -0.32697 | -0.53634 | -0.65895 | 0.099642 | 0.089494 | 0.07816 | 0.062914 | 0.047962 | 0.027362 | 0.0040682 | -0.045668 | -0.095053 | -0.15076 | -0.20354 | -0.47442 | -0.75427 | -0.87297
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 1.206 | -0.073782 | -0.35731 | -0.68007 | -1.0734 | -1.4569 | -1.9195 | -2.4469 | -2.9663 | -3.4695 | -4.3425 | -5.1325 | -6.1237 | -6.5304 | -6.9466 | 0.076042 | -0.17196 | -0.39639 | -0.66106 | -0.91576 | -1.2161 | -1.5574 | -1.8818 | -2.2017 | -2.9121 | -3.5856 | -4.1791 | -4.5104 | -4.9132 | 0.47829 | 0.18454 | -0.14247 | -0.52747 | -0.91416 | -1.3712 | -1.8833 | -2.3702 | -2.8419 | -3.7096 | -4.504 | -5.4744 | -5.9179 | -6.3234
|  | COUPAR ANGUS | CT |  |  |  | 1.206 | -0.063648 | -0.31079 | -0.61303 | -1.0132 | -1.4233 | -1.8521 | -2.3672 | -2.89 | -3.2901 | -4.1149 | -4.8571 | -5.9727 | -6.5024 | -6.9029 | 0.089721 | -0.11196 | -0.31665 | -0.59784 | -0.87005 | -1.1547 | -1.4848 | -1.8186 | -2.0862 | -2.7824 | -3.4436 | -4.1382 | -4.5104 | -4.9132 | 0.48978 | 0.23872 | -0.056254 | -0.45106 | -0.8531 | -1.2866 | -1.786 | -2.2756 | -2.6698 | -3.4989 | -4.2485 | -5.3417 | -5.9179 | -6.3234
|  | COUPAR ANGUS | LW |  |  |  | 1.206 | -0.073782 | -0.35731 | -0.68007 | -1.0734 | -1.4569 | -1.9195 | -2.4469 | -2.9663 | -3.4695 | -4.3425 | -5.1325 | -6.1237 | -6.5304 | -6.9466 | 0.076042 | -0.17196 | -0.39639 | -0.66106 | -0.91576 | -1.2161 | -1.5574 | -1.8818 | -2.2017 | -2.9121 | -3.5856 | -4.1791 | -4.4132 | -4.6594 | 0.47829 | 0.18454 | -0.14247 | -0.52747 | -0.91416 | -1.3712 | -1.8833 | -2.3702 | -2.8419 | -3.7096 | -4.504 | -5.4744 | -5.9099 | -6.3149
|  | COUPAR ANGUS | ST |  |  |  | 1.206 | -0.027008 | -0.20214 | -0.41149 | -0.64823 | -0.85412 | -1.114 | -1.3511 | -1.6221 | -1.8839 | -2.5752 | -3.2451 | -4.449 | -5.0875 | -5.5584 | 0.11022 | -0.050026 | -0.21392 | -0.40047 | -0.56751 | -0.76855 | -0.94863 | -1.1523 | -1.3575 | -2.0121 | -2.6512 | -3.4482 | -3.9167 | -4.3615 | 0.51954 | 0.32573 | 0.12196 | -0.10493 | -0.31063 | -0.55732 | -0.7822 | -1.0323 | -1.2775 | -1.975 | -2.6535 | -3.7615 | -4.3875 | -4.8958
|  | COUPAR ANGUS | FS |  |  |  | 1.206 | 0.034812 | -0.095103 | -0.22397 | -0.38857 | -0.55805 | -0.74455 | -0.90895 | -1.1169 | -1.3613 | -1.7623 | -2.204 | -3.6809 | -4.8198 | -5.489 | 0.14925 | 0.026708 | -0.079341 | -0.21363 | -0.35787 | -0.52282 | -0.65674 | -0.81538 | -1.0007 | -1.379 | -1.7891 | -2.9588 | -3.8716 | -4.6554 | 0.58503 | 0.44363 | 0.32055 | 0.16785 | 0.0034762 | -0.18109 | -0.33353 | -0.53043 | -0.76141 | -1.1676 | -1.6132 | -3.0296 | -4.1298 | -4.8345
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 10.141 | 1.954 | 1.7321 | 1.3549 | 0.89434 | 0.46678 | -0.056143 | -0.74523 | -1.4623 | -1.8265 | -2.4345 | -2.9871 | -4.4427 | -5.2409 | -5.8219 | 8.2563 | 8.0887 | 7.893 | 7.6303 | 7.348 | 7.0938 | 6.676 | 6.2487 | 6.2203 | 5.8871 | 5.5749 | 4.3384 | 3.3361 | 0.60358 | 7.8699 | 7.6638 | 7.3264 | 6.9072 | 6.5148 | 6.0289 | 5.3914 | 4.7295 | 4.4146 | 3.8519 | 3.3403 | 2.0057 | 1.3571 | 0.82958
|  | CRAIGIEBUCKLER | CT |  |  |  | 10.141 | 1.9831 | 1.7835 | 1.4197 | 0.96302 | 0.46855 | -0.0216 | -0.73223 | -1.4062 | -1.6145 | -2.0901 | -2.5177 | -4.3451 | -5.2409 | -5.8219 | 8.2623 | 8.0996 | 7.9044 | 7.6401 | 7.348 | 7.0938 | 6.676 | 6.2487 | 6.2203 | 5.9164 | 5.6289 | 4.3384 | 3.3361 | 1.9105 | 7.8933 | 7.7103 | 7.3878 | 6.9716 | 6.5189 | 6.0741 | 5.4251 | 4.8021 | 4.6361 | 4.1965 | 3.8012 | 2.1492 | 1.3571 | 0.82958
|  | CRAIGIEBUCKLER | LW |  |  |  | 10.141 | 1.954 | 1.7321 | 1.3549 | 0.89434 | 0.46678 | -0.056143 | -0.74523 | -1.4623 | -1.8265 | -2.4345 | -2.9871 | -4.4427 | -4.8178 | -5.3488 | 8.2563 | 8.0887 | 7.893 | 7.6303 | 7.3981 | 7.1029 | 6.6847 | 6.2678 | 6.2287 | 5.8871 | 5.5749 | 4.8111 | 4.6137 | 4.2813 | 7.8699 | 7.6638 | 7.3264 | 6.9072 | 6.5148 | 6.0289 | 5.3914 | 4.7295 | 4.4146 | 3.8519 | 3.3403 | 2.0057 | 1.6593 | 1.1537
|  | CRAIGIEBUCKLER | ST |  |  |  | 10.141 | 2.0666 | 1.9629 | 1.853 | 1.7346 | 1.6264 | 1.5452 | 1.3786 | 1.2492 | 1.048 | 0.84028 | 0.60625 | -0.43608 | -1.3676 | -2.4225 | 8.3163 | 8.2308 | 8.136 | 8.0231 | 7.9046 | 7.8099 | 7.6473 | 7.5098 | 7.2936 | 7.0658 | 6.8128 | 5.8104 | 4.7278 | 3.1673 | 7.9714 | 7.8813 | 7.7833 | 7.6747 | 7.5704 | 7.487 | 7.3092 | 7.1791 | 6.9519 | 6.716 | 6.4537 | 5.5862 | 4.7473 | 3.8029
|  | CRAIGIEBUCKLER | FS |  |  |  | 10.141 | 2.0795 | 1.9899 | 1.8787 | 1.7474 | 1.6327 | 1.4999 | 1.3673 | 1.1697 | 0.94308 | 0.76056 | 0.53077 | -0.6148 | -2.0345 | -3.2541 | 8.3255 | 8.2486 | 8.1645 | 8.0537 | 7.9486 | 7.8217 | 7.6941 | 7.5091 | 7.2908 | 7.1116 | 6.8858 | 5.7109 | 3.6226 | 0.60358 | 7.9803 | 7.9028 | 7.8062 | 7.6883 | 7.5822 | 7.458 | 7.3402 | 7.1577 | 6.9379 | 6.776 | 6.5487 | 5.5153 | 4.2101 | 3.1151
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 4.044 | 6.795 | 4.5219 | 2.0994 | -0.20364 | -1.8274 | -4.565 | -8.3321 | -9.2682 | -10.1075 | -10.9503 | -11.755 | -17.1523 | -23.5158 | -30.8709 | 8.8003 | 6.0418 | 3.0928 | 0.31968 | -1.6422 | -4.6768 | -8.8464 | -9.4371 | -10.0579 | -10.727 | -11.3552 | -16.8559 | -24.8816 | -33.7171 | 7.9476 | 5.1155 | 2.1075 | -0.74574 | -2.7468 | -5.8918 | -10.2713 | -11.0578 | -11.8363 | -12.657 | -13.4284 | -19.3554 | -27.4383 | -36.3149
|  | CRAIGINCHES | CT |  |  |  | 4.044 | 6.795 | 6.5415 | 6.3024 | 3.8742 | 3.2203 | 2.1798 | -0.014682 | -0.83288 | -1.7361 | -2.5815 | -3.3764 | -6.9355 | -9.4644 | -12.1034 | 8.8003 | 8.5817 | 8.4285 | 5.6249 | 4.9767 | 3.9797 | 1.5733 | 0.91847 | 0.14037 | -0.58934 | -1.3106 | -4.2346 | -7.4783 | -11.5963 | 7.9476 | 7.6492 | 7.3894 | 4.4133 | 3.642 | 2.5127 | -0.023905 | -0.81656 | -1.6981 | -2.5275 | -3.3305 | -6.4622 | -9.0677 | -12.1498
|  | CRAIGINCHES | LW |  |  |  | 4.044 | 6.7992 | 4.5219 | 2.0994 | -0.20364 | -1.8274 | -4.565 | -8.3321 | -9.2682 | -10.1075 | -10.9503 | -11.755 | -17.1523 | -23.5158 | -30.8709 | 8.8062 | 6.0418 | 3.0928 | 0.31968 | -1.6422 | -4.6768 | -8.8464 | -9.4371 | -10.0579 | -10.727 | -11.3552 | -16.8559 | -24.8816 | -33.7171 | 7.9502 | 5.1155 | 2.1075 | -0.74574 | -2.7468 | -5.8918 | -10.2713 | -11.0578 | -11.8363 | -12.657 | -13.4284 | -19.3554 | -27.4383 | -36.3149
|  | CRAIGINCHES | ST |  |  |  | 4.044 | 6.8424 | 6.7142 | 5.2933 | 4.3003 | 3.6378 | 3.2899 | 2.893 | 2.2978 | 1.6211 | 0.88915 | 0.31645 | -7.8966 | -15.8059 | -22.6763 | 8.8384 | 8.6976 | 6.9538 | 5.7683 | 5.0077 | 4.6601 | 4.2711 | 3.6857 | 3.0746 | 2.5058 | 2.0665 | -6.7836 | -16.2324 | -24.8379 | 8.0118 | 7.8477 | 6.072 | 4.8445 | 4.0321 | 3.6174 | 3.1451 | 2.445 | 1.6861 | 0.9541 | 0.44722 | -8.8699 | -18.5299 | -27.1167
|  | CRAIGINCHES | FS |  |  |  | 4.044 | 6.8538 | 6.8217 | 6.3905 | 5.952 | 5.4053 | 4.8386 | 3.9687 | 3.3048 | 2.5476 | 1.7852 | 1.5282 | -0.76024 | -3.3415 | -6.1848 | 8.8466 | 8.8189 | 8.2966 | 7.7747 | 7.1307 | 6.4712 | 5.4422 | 4.6948 | 3.8424 | 2.9861 | 2.7753 | 1.2201 | -1.1119 | -5.5265 | 8.0267 | 7.9844 | 7.4416 | 6.8952 | 6.2218 | 5.5258 | 4.4538 | 3.6508 | 2.7275 | 1.7998 | 1.542 | -0.51465 | -2.8104 | -5.6626
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | YES | YES | 0.539 | 4.1672 | 3.1734 | 1.2151 | -0.060916 | -1.3141 | -2.1518 | -3.0916 | -3.9836 | -4.8005 | -5.5151 | -6.1893 | -7.574 | -8.3158 | -8.8778 | 8.3579 | 7.1723 | 5.0876 | 3.8851 | 2.63 | 2.1756 | 1.6691 | 1.0609 | 0.48879 | 0.073936 | -0.32408 | -0.94637 | -1.44 | -1.9685 | 8.8487 | 7.9393 | 6.0136 | 4.8006 | 3.4935 | 2.7558 | 1.9323 | 1.1128 | 0.30831 | -0.32712 | -0.92731 | -2.1659 | -2.8214 | -3.3152
|  | CRAIGTON | CT |  |  |  | 0.539 | 4.4056 | 3.5894 | 1.8742 | 0.47539 | -0.95529 | -1.8934 | -2.8913 | -3.9836 | -4.4734 | -5.1337 | -5.7328 | -7.4361 | -8.3158 | -8.8778 | 8.6137 | 7.6688 | 5.8876 | 4.5046 | 3.0907 | 2.4867 | 1.8864 | 1.1154 | 0.69057 | 0.25729 | -0.1372 | -0.94562 | -1.44 | -1.9685 | 9.0542 | 8.3105 | 6.7892 | 5.3581 | 3.8864 | 3.0185 | 2.1195 | 1.1128 | 0.5812 | -0.017644 | -0.55596 | -2.05 | -2.8214 | -3.3152
|  | CRAIGTON | LW |  |  |  | 0.539 | 4.1672 | 3.1734 | 1.2151 | -0.060916 | -1.3141 | -2.1518 | -3.0916 | -3.869 | -4.8005 | -5.5151 | -6.1893 | -7.574 | -8.0138 | -8.5341 | 8.3579 | 7.1723 | 5.0876 | 3.8851 | 2.63 | 2.1756 | 1.6691 | 1.0609 | 0.48879 | 0.073936 | -0.32408 | -0.94637 | -1.1771 | -1.4223 | 8.8487 | 7.9393 | 6.0136 | 4.8006 | 3.4935 | 2.7558 | 1.9323 | 1.1411 | 0.30831 | -0.32712 | -0.92731 | -2.1659 | -2.602 | -3.0683
|  | CRAIGTON | ST |  |  |  | 0.539 | 4.4738 | 3.7396 | 2.24 | 1.1504 | 0.089511 | -0.44202 | -0.91964 | -1.5244 | -2.0927 | -2.5536 | -3.0199 | -4.2136 | -5.1564 | -6.0536 | 8.639 | 7.728 | 5.9517 | 4.6142 | 3.2968 | 2.8345 | 2.4558 | 1.8758 | 1.406 | 1.0446 | 0.69282 | -0.037504 | -0.50542 | -1.1601 | 9.1177 | 8.4529 | 6.8598 | 5.653 | 4.4901 | 4.0265 | 3.6555 | 3.1085 | 2.6443 | 2.2857 | 1.9325 | 0.96821 | 0.065889 | -0.82224
|  | CRAIGTON | FS |  |  |  | 0.539 | 4.7375 | 4.1766 | 3.0773 | 2.2829 | 1.3489 | 0.89568 | 0.43659 | -0.12728 | -0.68444 | -1.1514 | -1.6484 | -3.7592 | -5.141 | -6.2299 | 8.8951 | 8.2002 | 6.9157 | 5.963 | 4.8151 | 4.3865 | 3.9855 | 3.5043 | 3.0116 | 2.6459 | 2.2507 | 0.44302 | -0.50854 | -1.7259 | 9.342 | 8.8351 | 7.8032 | 6.9619 | 5.9642 | 5.564 | 5.1667 | 4.71 | 4.2303 | 3.8142 | 3.3579 | 1.3241 | 0.10359 | -0.91812
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 1.491 | 5.4296 | 4.9784 | 4.3938 | 3.7358 | 3.0422 | 2.2382 | 1.3307 | 0.41067 | -0.58727 | -1.1078 | -1.8896 | -4.0932 | -4.7589 | -5.6022 | 7.0664 | 6.0389 | 5.7214 | 5.3653 | 4.9625 | 4.5553 | 4.0425 | 3.5103 | 2.9275 | 2.6759 | 2.2157 | 0.99038 | 0.4459 | -0.36583 | 6.7271 | 5.955 | 5.4284 | 4.8318 | 4.1951 | 3.4715 | 2.6414 | 1.8101 | 0.91277 | 0.45212 | -0.24979 | -2.2406 | -2.8608 | -3.6452
|  | CRIEFF | CT |  |  |  | 1.491 | 5.4537 | 5.0267 | 4.4511 | 3.7951 | 3.0422 | 2.2888 | 1.3818 | 0.47156 | -0.29142 | -0.68527 | -1.3244 | -3.6986 | -4.7476 | -5.6022 | 7.083 | 6.0782 | 5.7556 | 5.3831 | 4.9625 | 4.5557 | 4.043 | 3.5103 | 3.0648 | 2.8733 | 2.4843 | 1.1214 | 0.4459 | -0.36583 | 6.744 | 5.9943 | 5.4778 | 4.8778 | 4.1951 | 3.5104 | 2.6805 | 1.8595 | 1.1707 | 0.82371 | 0.25372 | -1.8885 | -2.8608 | -3.6452
|  | CRIEFF | LW |  |  |  | 1.491 | 5.4296 | 4.9784 | 4.3938 | 3.7358 | 3.0448 | 2.2382 | 1.3307 | 0.41067 | -0.58727 | -1.1078 | -1.8896 | -4.0932 | -4.7589 | -5.537 | 7.0664 | 6.0389 | 5.7214 | 5.3653 | 4.997 | 4.5553 | 4.0425 | 3.5186 | 2.9275 | 2.6759 | 2.2157 | 0.99038 | 0.6839 | 0.21295 | 6.7271 | 5.955 | 5.4284 | 4.8318 | 4.2033 | 3.4715 | 2.6414 | 1.8101 | 0.91277 | 0.45212 | -0.24979 | -2.2406 | -2.8558 | -3.5603
|  | CRIEFF | ST |  |  |  | 1.491 | 5.5768 | 5.2933 | 5.0077 | 4.6818 | 4.3441 | 4.0243 | 3.6822 | 3.3022 | 2.8993 | 2.4467 | 1.9604 | 0.003215 | -1.1478 | -2.1892 | 7.1499 | 6.2353 | 6.0594 | 5.8526 | 5.6361 | 5.4259 | 5.1977 | 4.9406 | 4.6693 | 4.3554 | 4.0184 | 2.7121 | 1.9066 | 1.071 | 6.856 | 6.2348 | 5.9849 | 5.6984 | 5.4014 | 5.1144 | 4.8072 | 4.47 | 4.1167 | 3.7137 | 3.2825 | 1.486 | 0.45028 | -0.50988
|  | CRIEFF | FS |  |  |  | 1.491 | 5.6783 | 5.4702 | 5.2546 | 5.0267 | 4.7781 | 4.5062 | 4.2818 | 3.947 | 3.5646 | 3.1787 | 2.8098 | 0.77396 | -1.1869 | -2.5666 | 7.206 | 6.3364 | 6.1979 | 6.049 | 5.8813 | 5.6913 | 5.532 | 5.3111 | 5.0534 | 4.7918 | 4.5456 | 3.1725 | 1.6368 | 0.10516 | 6.9436 | 6.3905 | 6.2037 | 6.0073 | 5.7896 | 5.5489 | 5.3472 | 5.0492 | 4.7092 | 4.3651 | 4.0421 | 2.2279 | 0.43757 | -0.84848
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.039 | 0.10621 | 0.087573 | 0.053161 | 0.011729 | -0.028743 | -0.077472 | -0.12884 | -0.14834 | -0.16131 | -0.16155 | -0.17418 | -0.25141 | -0.27851 | -0.31963 | 0.24828 | 0.22801 | 0.20163 | 0.16831 | 0.13712 | 0.098297 | 0.056498 | 0.018719 | -0.013486 | -0.035573 | -0.068795 | -0.2833 | -0.82333 | -1.7246 | 0.14144 | 0.12605 | 0.10114 | 0.063832 | 0.027903 | -0.015847 | -0.06179 | -0.08069 | -0.093396 | -0.093726 | -0.10335 | -0.16309 | -0.19312 | -0.23732
|  | CRINAN | CT |  |  |  | 0.039 | 0.10621 | 0.087573 | 0.053161 | 0.011729 | -0.028743 | -0.077472 | -0.12884 | -0.14834 | -0.16131 | -0.16155 | -0.16875 | -0.21726 | -0.24252 | -0.27693 | 0.24828 | 0.22801 | 0.20163 | 0.16831 | 0.13712 | 0.098297 | 0.056498 | 0.018719 | -0.013486 | -0.035573 | -0.068795 | -0.26269 | -0.5094 | -0.94433 | 0.14173 | 0.12605 | 0.10114 | 0.063832 | 0.027903 | -0.015847 | -0.06179 | -0.08069 | -0.093396 | -0.093726 | -0.1013 | -0.13167 | -0.1541 | -0.19123
|  | CRINAN | LW |  |  |  | 0.039 | 0.10886 | 0.093691 | 0.064079 | 0.026605 | -0.012165 | -0.052321 | -0.097817 | -0.1203 | -0.14553 | -0.15307 | -0.17418 | -0.25141 | -0.27851 | -0.31963 | 0.25421 | 0.24083 | 0.22367 | 0.19896 | 0.17452 | 0.14803 | 0.11654 | 0.088445 | 0.053879 | 0.038241 | 0.010773 | -0.048809 | -0.062913 | -0.091677 | 0.14144 | 0.1272 | 0.1109 | 0.077012 | 0.042172 | 0.0062934 | -0.034574 | -0.056015 | -0.080367 | -0.087311 | -0.10335 | -0.16309 | -0.19312 | -0.23732
|  | CRINAN | ST |  |  |  | 0.039 | 0.11305 | 0.10012 | 0.085096 | 0.069359 | 0.052318 | 0.036768 | 0.016768 | 0.004108 | -0.017169 | -0.033329 | -0.055424 | -0.12989 | -0.16068 | -0.16749 | 0.25488 | 0.24008 | 0.22431 | 0.20684 | 0.18643 | 0.16647 | 0.14015 | 0.11877 | 0.085707 | 0.05681 | 0.018781 | -0.21096 | -0.46439 | -0.88178 | 0.15107 | 0.14214 | 0.13012 | 0.11592 | 0.10043 | 0.08642 | 0.067981 | 0.056631 | 0.036718 | 0.02191 | 0.0011991 | -0.10395 | -0.12192 | -0.12287
|  | CRINAN | FS |  |  |  | 0.039 | 0.11494 | 0.11205 | 0.10974 | 0.10691 | 0.10203 | 0.095305 | 0.09164 | 0.076411 | 0.065852 | 0.049695 | 0.032719 | -0.050207 | -0.13091 | -0.17281 | 0.25262 | 0.2443 | 0.23193 | 0.21777 | 0.2011 | 0.18047 | 0.15795 | 0.12254 | 0.089141 | 0.049037 | 0.0059637 | -0.2833 | -0.82333 | -1.7246 | 0.1467 | 0.14583 | 0.14061 | 0.13397 | 0.12546 | 0.11253 | 0.10621 | 0.090042 | 0.084242 | 0.065637 | 0.045087 | -0.056639 | -0.11065 | -0.11616
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.0731 | 2.0416 | 1.9912 | 1.9362 | 1.8709 | 1.834 | 1.7045 | 1.6695 | 1.5156 | 1.4657 | 1.4281 | 1.2808 | 1.1964 | 1.1524 | 2.188 | 2.1755 | 2.147 | 2.1142 | 2.0779 | 2.0552 | 1.9426 | 1.9151 | 1.7236 | 1.7005 | 1.6719 | 1.5412 | 1.4805 | 1.4413 | 1.6888 | 1.656 | 1.6077 | 1.5532 | 1.491 | 1.4513 | 1.3256 | 1.2903 | 1.1052 | 1.0705 | 1.0363 | 0.97677 | 0.92096 | 0.87801
|  | CROMALT | CT |  |  |  | 0 | 2.0798 | 2.0416 | 1.9912 | 1.9362 | 1.8709 | 1.834 | 1.7045 | 1.6695 | 1.5156 | 1.4657 | 1.4281 | 1.3726 | 1.359 | 1.345 | 2.1953 | 2.1755 | 2.147 | 2.1142 | 2.0779 | 2.0552 | 1.9426 | 1.9151 | 1.7435 | 1.7036 | 1.6719 | 1.6277 | 1.6143 | 1.5815 | 1.6908 | 1.656 | 1.6077 | 1.5532 | 1.491 | 1.4513 | 1.3256 | 1.2903 | 1.1175 | 1.0719 | 1.0363 | 0.99017 | 0.97108 | 0.94711
|  | CROMALT | LW |  |  |  | 0 | 2.0824 | 2.0451 | 1.9998 | 1.9492 | 1.8905 | 1.8525 | 1.726 | 1.7004 | 1.5165 | 1.4778 | 1.4546 | 1.3473 | 1.3149 | 1.3021 | 2.1961 | 2.1764 | 2.1523 | 2.1264 | 2.0956 | 2.074 | 1.95 | 1.934 | 1.7236 | 1.7005 | 1.6849 | 1.6038 | 1.5844 | 1.5799 | 1.6939 | 1.661 | 1.6186 | 1.5708 | 1.5154 | 1.4769 | 1.3459 | 1.3209 | 1.1052 | 1.0705 | 1.0556 | 0.97677 | 0.94711 | 0.91974
|  | CROMALT | ST |  |  |  | 0 | 2.0832 | 2.0597 | 2.0331 | 2.005 | 1.9745 | 1.9583 | 1.8762 | 1.835 | 1.6641 | 1.6003 | 1.5421 | 1.2808 | 1.1964 | 1.1741 | 2.1963 | 2.1859 | 2.1711 | 2.1551 | 2.1374 | 2.1273 | 2.037 | 2.0112 | 1.8425 | 1.7874 | 1.7399 | 1.5412 | 1.4805 | 1.4665 | 1.6951 | 1.6733 | 1.6488 | 1.6232 | 1.5952 | 1.5788 | 1.4921 | 1.4585 | 1.2909 | 1.24 | 1.202 | 1.0016 | 0.92096 | 0.90007
|  | CROMALT | FS |  |  |  | 0 | 2.0731 | 2.0721 | 2.056 | 2.0405 | 2.0246 | 2.0149 | 1.963 | 1.9382 | 1.8232 | 1.7857 | 1.7357 | 1.4772 | 1.2767 | 1.1524 | 2.188 | 2.1901 | 2.1797 | 2.1698 | 2.1599 | 2.1526 | 2.104 | 2.087 | 1.9696 | 1.9441 | 1.9058 | 1.6858 | 1.5336 | 1.4413 | 1.6888 | 1.6868 | 1.6738 | 1.6609 | 1.6478 | 1.6389 | 1.5903 | 1.5676 | 1.4478 | 1.4204 | 1.3764 | 1.1807 | 0.99684 | 0.87801
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 1.05 | 5.7788 | 5.0315 | 3.8877 | 3.4606 | 3.0381 | 2.496 | 1.8004 | 1.086 | 0.54087 | -0.0083732 | -0.26752 | -1.6939 | -2.4878 | -3.1471 | 6.8934 | 6.0952 | 5.0673 | 4.9387 | 4.8324 | 4.5666 | 4.2796 | 3.8812 | 3.6009 | 3.3401 | 3.1861 | 2.4547 | 1.9264 | 1.5712 | 5.9089 | 5.1901 | 4.2497 | 3.8717 | 3.494 | 2.9957 | 2.3856 | 1.7379 | 1.2496 | 0.75092 | 0.50301 | -0.77797 | -1.4378 | -2.0145
|  | CROSSHILLS | CT |  |  |  | 1.05 | 6.013 | 5.3518 | 4.2977 | 3.7831 | 3.1998 | 2.5353 | 1.8004 | 1.086 | 0.54087 | 0.050987 | -0.090695 | -1.5742 | -2.4878 | -3.1471 | 7.208 | 6.5341 | 5.6129 | 5.3802 | 5.1339 | 4.7214 | 4.2856 | 3.8812 | 3.6009 | 3.3608 | 3.2924 | 2.5813 | 2.0923 | 1.5712 | 6.1755 | 5.5626 | 4.6985 | 4.2261 | 3.6841 | 3.0635 | 2.3856 | 1.7379 | 1.2496 | 0.81474 | 0.67444 | -0.63793 | -1.4378 | -2.0145
|  | CROSSHILLS | LW |  |  |  | 1.05 | 5.7788 | 5.0315 | 3.8877 | 3.4606 | 3.0381 | 2.496 | 1.9098 | 1.267 | 0.5936 | -0.0083732 | -0.26752 | -1.6939 | -2.2768 | -2.8061 | 6.8934 | 6.0952 | 5.0673 | 4.9387 | 4.8324 | 4.5666 | 4.2796 | 3.9704 | 3.6378 | 3.3401 | 3.1861 | 2.4547 | 2.2591 | 2.0207 | 5.9089 | 5.1901 | 4.2497 | 3.8717 | 3.494 | 2.9957 | 2.4633 | 1.8898 | 1.2885 | 0.75092 | 0.50301 | -0.77797 | -1.3041 | -1.7759
|  | CROSSHILLS | ST |  |  |  | 1.05 | 6.0785 | 5.5095 | 4.6916 | 4.4782 | 4.2396 | 3.9422 | 3.6679 | 3.3939 | 3.1206 | 2.887 | 2.5943 | 0.57832 | -0.47354 | -1.2648 | 7.2324 | 6.615 | 5.737 | 5.5773 | 5.3931 | 5.1429 | 4.9119 | 4.6948 | 4.501 | 4.3078 | 4.0201 | 2.5202 | 1.9264 | 1.6989 | 6.2056 | 5.6615 | 4.8643 | 4.7078 | 4.5263 | 4.2834 | 4.0557 | 3.7991 | 3.5357 | 3.3187 | 3.0511 | 1.4851 | 0.31196 | -0.56764
|  | CROSSHILLS | FS |  |  |  | 1.05 | 6.3787 | 5.9518 | 5.3559 | 5.2028 | 5.0389 | 4.8629 | 4.6349 | 4.4 | 4.1268 | 3.8702 | 3.5711 | 1.5509 | 0.24698 | -1.0089 | 7.5593 | 7.0875 | 6.4417 | 6.3291 | 6.1944 | 6.0535 | 5.857 | 5.7097 | 5.541 | 5.3911 | 5.1903 | 3.54 | 2.5787 | 1.7051 | 6.4847 | 6.0699 | 5.4854 | 5.3751 | 5.2475 | 5.1103 | 4.9206 | 4.7741 | 4.5484 | 4.3041 | 4.0157 | 2.128 | 0.93559 | -0.19154
| KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0.396 | -0.23029 | -0.34446 | -0.57029 | -0.83985 | -1.1197 | -1.4605 | -1.8701 | -2.2118 | -2.5324 | -2.8456 | -3.131 | -3.9776 | -4.4347 | -4.8571 | 0.60007 | 0.52356 | 0.40097 | 0.26175 | 0.12155 | -0.066593 | -0.31806 | -0.50183 | -0.67701 | -0.85535 | -1.0188 | -1.464 | -1.7965 | -2.2063 | 0.29545 | 0.18936 | -0.015899 | -0.2553 | -0.50403 | -0.81615 | -1.1962 | -1.5099 | -1.8049 | -2.0953 | -2.3599 | -3.1374 | -3.5275 | -3.8986
|  | CULLEN | CT |  |  |  | 0.396 | -0.23029 | -0.34317 | -0.53675 | -0.817 | -1.1078 | -1.4234 | -1.8209 | -2.1689 | -2.4609 | -2.6925 | -2.9238 | -3.8499 | -4.4347 | -4.8571 | 0.60007 | 0.52857 | 0.43034 | 0.27346 | 0.12155 | -0.043003 | -0.27815 | -0.47585 | -0.63997 | -0.76973 | -0.91116 | -1.4415 | -1.7965 | -2.2063 | 0.29545 | 0.19326 | 0.022238 | -0.23073 | -0.48995 | -0.77302 | -1.1372 | -1.457 | -1.724 | -1.9354 | -2.1497 | -2.9897 | -3.5066 | -3.8865
|  | CULLEN | LW |  |  |  | 0.396 | -0.22509 | -0.34446 | -0.57029 | -0.83985 | -1.1197 | -1.4605 | -1.8701 | -2.2118 | -2.5324 | -2.8456 | -3.131 | -3.9776 | -4.4062 | -4.8004 | 0.60467 | 0.52356 | 0.40097 | 0.26175 | 0.12176 | -0.066593 | -0.31806 | -0.50183 | -0.67701 | -0.85535 | -1.0188 | -1.464 | -1.6752 | -1.9101 | 0.30106 | 0.18936 | -0.015899 | -0.2553 | -0.50403 | -0.81615 | -1.1962 | -1.5099 | -1.8049 | -2.0953 | -2.3599 | -3.1374 | -3.5275 | -3.8986
|  | CULLEN | ST |  |  |  | 0.396 | -0.19087 | -0.26231 | -0.35002 | -0.45808 | -0.56992 | -0.66468 | -0.82591 | -0.94034 | -1.0508 | -1.1814 | -1.317 | -2.1818 | -2.8333 | -3.3548 | 0.62468 | 0.58225 | 0.52577 | 0.4588 | 0.38753 | 0.32933 | 0.20777 | 0.12538 | 0.046422 | -0.050248 | -0.15064 | -0.76313 | -1.2062 | -1.655 | 0.3327 | 0.27052 | 0.19159 | 0.097585 | -0.0011139 | -0.083473 | -0.23229 | -0.33964 | -0.44251 | -0.56634 | -0.69473 | -1.5118 | -2.1088 | -2.5803
|  | CULLEN | FS |  |  |  | 0.396 | -0.16209 | -0.21356 | -0.26943 | -0.3498 | -0.42114 | -0.49909 | -0.60213 | -0.71384 | -0.83962 | -0.97158 | -1.0785 | -1.781 | -2.5099 | -3.0983 | 0.63724 | 0.60458 | 0.56843 | 0.51511 | 0.46735 | 0.41173 | 0.32768 | 0.25043 | 0.16074 | 0.065532 | -0.0087837 | -0.53478 | -1.1796 | -1.8979 | 0.35738 | 0.31302 | 0.2645 | 0.19486 | 0.13329 | 0.063176 | -0.03156 | -0.13372 | -0.24923 | -0.37106 | -0.4671 | -1.1187 | -1.7908 | -2.3183
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 3.059 | 6.3257 | 7.5632 | 9.3231 | 8.739 | 8.0102 | 7.2153 | 6.2271 | 5.6966 | 4.9773 | 4.1384 | 3.3795 | 1.2945 | -0.014148 | -1.1029 | 9.6329 | 9.4534 | 11.7589 | 11.4589 | 11.0743 | 10.667 | 10.1318 | 9.9142 | 9.4958 | 9.0149 | 8.5771 | 7.4628 | 6.6013 | 5.5986 | 8.2006 | 7.9523 | 10.6577 | 10.1258 | 9.4599 | 8.7366 | 7.8284 | 7.3636 | 6.6688 | 5.8884 | 5.1825 | 3.2877 | 2.2443 | 1.3052
|  | CULLODEN | CT |  |  |  | 3.059 | 6.3257 | 7.5632 | 9.3231 | 8.739 | 8.0102 | 7.2153 | 6.2271 | 5.6966 | 4.9977 | 4.3344 | 3.7649 | 1.4946 | -0.014148 | -1.1029 | 9.6329 | 9.4534 | 11.7589 | 11.4589 | 11.0743 | 10.667 | 10.1318 | 9.9142 | 9.5263 | 9.1333 | 8.7798 | 7.4628 | 6.6013 | 5.5986 | 8.2006 | 7.9523 | 10.6577 | 10.1258 | 9.4599 | 8.7366 | 7.8284 | 7.3636 | 6.7212 | 6.1056 | 5.5737 | 3.513 | 2.2443 | 1.3052
|  | CULLODEN | LW |  |  |  | 3.059 | 6.3314 | 7.5744 | 9.3646 | 8.8123 | 8.2102 | 7.4025 | 6.8185 | 5.9201 | 4.9773 | 4.1384 | 3.3795 | 1.2945 | 0.40087 | -0.59252 | 9.64 | 9.4669 | 11.7964 | 11.5154 | 11.2146 | 10.7676 | 10.5191 | 10.0374 | 9.4958 | 9.0149 | 8.5771 | 7.501 | 7.1322 | 6.6153 | 8.206 | 7.961 | 10.6933 | 10.1888 | 9.6405 | 8.8927 | 8.3726 | 7.5462 | 6.6688 | 5.8884 | 5.1825 | 3.2877 | 2.5031 | 1.598
|  | CULLODEN | ST |  |  |  | 3.059 | 6.4465 | 7.8272 | 9.9831 | 9.8303 | 9.7042 | 9.5169 | 9.3403 | 9.0925 | 8.7765 | 8.4427 | 8.4823 | 6.3615 | 4.8958 | 3.6547 | 9.7021 | 9.6235 | 12.1096 | 11.9921 | 11.8958 | 11.7507 | 11.6129 | 11.4178 | 11.1657 | 10.8974 | 10.927 | 9.3901 | 8.4153 | 7.3954 | 8.3132 | 8.2034 | 11.2646 | 11.1176 | 10.998 | 10.8181 | 10.6488 | 10.409 | 10.1011 | 9.7755 | 9.8217 | 7.8196 | 6.5057 | 5.4139
|  | CULLODEN | FS |  |  |  | 3.059 | 6.4738 | 7.859 | 10.0368 | 9.908 | 9.7976 | 9.6426 | 9.468 | 9.2365 | 8.9304 | 8.6193 | 8.2922 | 6.7852 | 4.8266 | 3.1611 | 9.7154 | 9.6346 | 12.1417 | 12.0457 | 11.9633 | 11.844 | 11.7022 | 11.542 | 11.318 | 11.0893 | 10.846 | 9.7234 | 8.0334 | 6.1667 | 8.3376 | 8.2308 | 11.3156 | 11.194 | 11.0911 | 10.944 | 10.7773 | 10.5632 | 10.2746 | 9.9809 | 9.6715 | 8.2761 | 6.4742 | 4.9869
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 0.914 | 9.4198 | 9.1769 | 8.7358 | 8.3144 | 7.8477 | 7.2703 | 6.5742 | 5.7451 | 5.1984 | 4.5734 | 3.9979 | 2.3432 | 1.6444 | 0.9799 | 11.705 | 11.5352 | 11.2987 | 11.0749 | 10.8092 | 10.5011 | 10.0831 | 9.6157 | 9.3064 | 9.0257 | 8.6763 | 7.7812 | 7.234 | 6.4326 | 10.812 | 10.5854 | 10.1872 | 9.7997 | 9.3706 | 8.8334 | 8.1804 | 7.4274 | 6.9547 | 6.368 | 5.8286 | 4.2989 | 3.7494 | 3.0691
|  | CULTER | CT |  |  |  | 0.914 | 9.4466 | 9.2217 | 8.8014 | 8.3847 | 7.8651 | 7.3518 | 6.6703 | 5.8721 | 5.1984 | 5.0057 | 4.5528 | 2.658 | 1.6444 | 0.9799 | 11.7152 | 11.5577 | 11.3281 | 11.1001 | 10.8092 | 10.5446 | 10.1503 | 9.6894 | 9.3064 | 9.2906 | 9.0044 | 7.9004 | 7.234 | 6.4708 | 10.8327 | 10.6255 | 10.2487 | 9.8652 | 9.3889 | 8.921 | 8.2895 | 7.5639 | 6.9547 | 6.7958 | 6.3736 | 4.649 | 3.7494 | 3.1447
|  | CULTER | LW |  |  |  | 0.914 | 9.4198 | 9.1769 | 8.7358 | 8.3144 | 7.8477 | 7.2703 | 6.5742 | 5.7451 | 5.2046 | 4.5734 | 3.9979 | 2.3432 | 1.7538 | 1.0187 | 11.705 | 11.5352 | 11.2987 | 11.0749 | 10.8279 | 10.5011 | 10.0831 | 9.6157 | 9.4053 | 9.0257 | 8.6763 | 7.7812 | 7.5046 | 7.0713 | 10.812 | 10.5854 | 10.1872 | 9.7997 | 9.3706 | 8.8334 | 8.1804 | 7.4274 | 6.9585 | 6.368 | 5.8286 | 4.2989 | 3.7609 | 3.0691
|  | CULTER | ST |  |  |  | 0.914 | 9.5221 | 9.3938 | 9.2375 | 9.1029 | 8.9446 | 8.8106 | 8.6244 | 8.3465 | 8.0591 | 7.7923 | 7.4944 | 5.9808 | 4.8172 | 3.8353 | 11.7643 | 11.6816 | 11.5789 | 11.4769 | 11.357 | 11.257 | 11.1103 | 10.9058 | 10.6953 | 10.4722 | 10.2239 | 9.1254 | 8.3051 | 7.4841 | 10.904 | 10.7909 | 10.6523 | 10.5251 | 10.3766 | 10.2511 | 10.0739 | 9.8231 | 9.5619 | 9.2975 | 8.9935 | 7.5901 | 6.5226 | 5.6415
|  | CULTER | FS |  |  |  | 0.914 | 9.5815 | 9.4859 | 9.3509 | 9.2471 | 9.121 | 8.9766 | 8.8516 | 8.5955 | 8.3035 | 8.0988 | 7.8454 | 6.0981 | 4.716 | 3.2049 | 11.7916 | 11.7253 | 11.6332 | 11.5597 | 11.4653 | 11.3539 | 11.2542 | 11.0769 | 10.866 | 10.7145 | 10.5196 | 9.2225 | 8.0993 | 6.4326 | 10.9529 | 10.869 | 10.7496 | 10.6548 | 10.5387 | 10.4041 | 10.2882 | 10.0603 | 9.7967 | 9.6048 | 9.3669 | 7.7393 | 6.4844 | 5.1105
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.579 | 8.1008 | 7.952 | 7.7357 | 7.4383 | 7.2288 | 7.015 | 6.7278 | 6.2017 | 5.6355 | 5.1213 | 4.5398 | 3.2054 | 2.768 | 2.236 | 10.2873 | 10.1828 | 10.0398 | 9.8373 | 9.6962 | 9.5375 | 9.2162 | 8.7837 | 8.4145 | 8.0187 | 7.6532 | 6.7443 | 5.8967 | 3.3631 | 9.9742 | 9.84 | 9.6584 | 9.2216 | 8.8081 | 8.2944 | 7.7817 | 7.2203 | 6.6254 | 6.0875 | 5.5955 | 4.4079 | 4.066 | 3.6666
|  | CUMMING STREET | CT |  |  |  | 0.579 | 8.1027 | 7.9558 | 7.7357 | 7.4383 | 7.2288 | 7.015 | 6.7401 | 6.288 | 5.8284 | 5.4095 | 5.0119 | 3.5357 | 2.768 | 2.236 | 10.2873 | 10.1835 | 10.0398 | 9.8373 | 9.6962 | 9.5375 | 9.2162 | 8.7837 | 8.4262 | 8.074 | 7.7495 | 6.7443 | 5.8967 | 4.6693 | 9.9752 | 9.8484 | 9.6584 | 9.2867 | 8.8789 | 8.4362 | 7.9375 | 7.3426 | 6.85 | 6.403 | 6.0145 | 4.7544 | 4.095 | 3.6666
|  | CUMMING STREET | LW |  |  |  | 0.579 | 8.1008 | 7.952 | 7.7573 | 7.5135 | 7.3438 | 7.0823 | 6.7278 | 6.2017 | 5.6355 | 5.1213 | 4.5398 | 3.2054 | 2.8473 | 2.4221 | 10.2907 | 10.1828 | 10.0522 | 9.8901 | 9.7803 | 9.5862 | 9.2335 | 8.8519 | 8.4145 | 8.0187 | 7.6532 | 6.9664 | 6.7772 | 6.4572 | 9.9742 | 9.84 | 9.6633 | 9.2216 | 8.8081 | 8.2944 | 7.7817 | 7.2203 | 6.6254 | 6.0875 | 5.5955 | 4.4079 | 4.066 | 3.7273
|  | CUMMING STREET | ST |  |  |  | 0.579 | 8.14 | 8.0756 | 7.9274 | 7.7684 | 7.6346 | 7.4905 | 7.3447 | 7.1468 | 6.8859 | 6.6152 | 6.2673 | 4.2634 | 3.5082 | 3.2304 | 10.3136 | 10.2667 | 10.1651 | 10.0582 | 9.9626 | 9.8586 | 9.7553 | 9.6127 | 9.3738 | 9.0533 | 8.6823 | 6.7515 | 6.045 | 5.5677 | 10.0078 | 9.9515 | 9.8173 | 9.6763 | 9.5593 | 9.4351 | 9.3159 | 9.149 | 8.9 | 8.5665 | 8.1716 | 5.9888 | 5.1465 | 4.8735
|  | CUMMING STREET | FS |  |  |  | 0.579 | 8.1522 | 8.1056 | 7.9991 | 7.8789 | 7.7884 | 7.6945 | 7.5842 | 7.4512 | 7.2895 | 7.1173 | 6.933 | 5.6478 | 4.1983 | 2.8953 | 10.3204 | 10.2842 | 10.2111 | 10.1267 | 10.0592 | 9.9846 | 9.8923 | 9.7827 | 9.6564 | 9.5176 | 9.3709 | 7.9716 | 6.0921 | 3.3631 | 10.0181 | 9.977 | 9.8819 | 9.774 | 9.6959 | 9.614 | 9.5169 | 9.4017 | 9.268 | 9.1209 | 8.9646 | 7.4661 | 5.8484 | 4.6235
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | NO | 0.459 | 4.8512 | 4.7567 | 4.6152 | 4.4305 | 4.263 | 4.0746 | 3.8511 | 3.6679 | 3.4747 | 3.277 | 3.0998 | 2.6376 | 2.3635 | 2.1302 | 4.9217 | 4.8542 | 4.7805 | 4.6782 | 4.6048 | 4.5006 | 4.3695 | 4.2752 | 4.1322 | 4.0065 | 3.8934 | 3.681 | 3.5452 | 3.3531 | 4.8922 | 4.8494 | 4.81 | 4.7563 | 4.6173 | 4.4477 | 4.24 | 4.0721 | 3.8844 | 3.6994 | 3.5331 | 3.1087 | 2.8745 | 2.6568
|  | DALCHONZIE | CT |  |  |  | 0.459 | 4.8646 | 4.7746 | 4.635 | 4.4445 | 4.263 | 4.0746 | 3.8511 | 3.6679 | 3.4956 | 3.3319 | 3.1853 | 2.6842 | 2.3635 | 2.1302 | 4.9281 | 4.8665 | 4.7956 | 4.6916 | 4.6048 | 4.5082 | 4.379 | 4.2786 | 4.1765 | 4.0699 | 3.9705 | 3.7113 | 3.5452 | 3.3531 | 4.9016 | 4.867 | 4.8303 | 4.7682 | 4.6173 | 4.4477 | 4.24 | 4.0721 | 3.914 | 3.7614 | 3.6244 | 3.1699 | 2.8745 | 2.6568
|  | DALCHONZIE | LW |  |  |  | 0.459 | 4.8512 | 4.7567 | 4.6152 | 4.4305 | 4.2785 | 4.0858 | 3.8746 | 3.6964 | 3.4747 | 3.277 | 3.0998 | 2.6376 | 2.3984 | 2.1613 | 4.9217 | 4.8542 | 4.7805 | 4.6782 | 4.6118 | 4.5006 | 4.3695 | 4.2752 | 4.1322 | 4.0065 | 3.8934 | 3.681 | 3.5716 | 3.44 | 4.8922 | 4.8494 | 4.81 | 4.7563 | 4.6322 | 4.4542 | 4.2551 | 4.0921 | 3.8844 | 3.6994 | 3.5331 | 3.1087 | 2.891 | 2.6689
|  | DALCHONZIE | ST |  |  |  | 0.459 | 4.889 | 4.8373 | 4.7671 | 4.698 | 4.631 | 4.5639 | 4.5197 | 4.4493 | 4.37 | 4.2809 | 4.2184 | 3.6268 | 3.3217 | 3.0394 | 4.9448 | 4.9152 | 4.8677 | 4.8275 | 4.7864 | 4.7383 | 4.7094 | 4.6544 | 4.5917 | 4.5198 | 4.4733 | 4.0348 | 3.8577 | 3.6513 | 4.9082 | 4.8898 | 4.8606 | 4.8313 | 4.8031 | 4.7762 | 4.7591 | 4.7295 | 4.6834 | 4.5915 | 4.5324 | 3.9622 | 3.7053 | 3.4684
|  | DALCHONZIE | FS |  |  |  | 0.459 | 4.9264 | 4.8886 | 4.8406 | 4.7904 | 4.732 | 4.6864 | 4.6354 | 4.5643 | 4.501 | 4.4275 | 4.3459 | 3.9064 | 3.4279 | 3.0632 | 4.9619 | 4.939 | 4.9056 | 4.8759 | 4.8359 | 4.8051 | 4.7638 | 4.7128 | 4.6734 | 4.6209 | 4.5604 | 4.2307 | 3.8538 | 3.5087 | 4.9221 | 4.9073 | 4.888 | 4.8655 | 4.8394 | 4.8189 | 4.7966 | 4.7736 | 4.7519 | 4.7253 | 4.6587 | 4.2372 | 3.8007 | 3.5016
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 2.236 | 7.8893 | 7.7146 | 7.5136 | 7.2591 | 6.9688 | 6.5602 | 6.0924 | 5.6402 | 5.2277 | 4.8346 | 4.7349 | 4.3155 | 4.1324 | 4.0011 | 8.2791 | 8.1649 | 8.0081 | 7.8149 | 7.6179 | 7.3342 | 7.0694 | 6.8082 | 6.5758 | 6.3501 | 6.2741 | 5.8933 | 5.5585 | 5.4668 | 8.3417 | 8.1512 | 7.9124 | 7.615 | 7.2711 | 6.8189 | 6.396 | 5.9971 | 5.6346 | 5.2873 | 5.1946 | 4.8113 | 4.6253 | 4.4968
|  | DALCROSS | CT |  |  |  | 2.236 | 7.951 | 7.7725 | 7.5527 | 7.2591 | 6.9688 | 6.5602 | 6.0924 | 5.6402 | 5.2277 | 4.8346 | 4.7349 | 4.3155 | 4.1983 | 4.0874 | 8.338 | 8.2205 | 8.057 | 7.8367 | 7.6179 | 7.3342 | 7.0694 | 6.8082 | 6.5758 | 6.3501 | 6.2881 | 6.0236 | 5.9443 | 5.8367 | 8.3977 | 8.203 | 7.9518 | 7.6195 | 7.2711 | 6.8189 | 6.396 | 5.9971 | 5.6346 | 5.2873 | 5.1946 | 4.8118 | 4.7099 | 4.6091
|  | DALCROSS | LW |  |  |  | 2.236 | 7.8893 | 7.7146 | 7.5136 | 7.2681 | 7.0125 | 6.6454 | 6.2554 | 5.7981 | 5.3372 | 4.8866 | 4.7563 | 4.3377 | 4.1324 | 4.0011 | 8.2791 | 8.1649 | 8.0081 | 7.8149 | 7.6187 | 7.3626 | 7.1469 | 6.8898 | 6.62 | 6.3571 | 6.2741 | 5.9916 | 5.8711 | 5.7872 | 8.3417 | 8.1512 | 7.9124 | 7.615 | 7.2992 | 6.8899 | 6.5353 | 6.1337 | 5.7236 | 5.3236 | 5.2017 | 4.8113 | 4.6253 | 4.4968
|  | DALCROSS | ST |  |  |  | 2.236 | 7.9721 | 7.8355 | 7.6825 | 7.5171 | 7.3369 | 7.1085 | 6.9241 | 6.6897 | 6.4492 | 6.1751 | 6.0191 | 4.8629 | 4.4103 | 4.2885 | 8.3509 | 8.2696 | 8.149 | 8.0183 | 7.8786 | 7.6983 | 7.5553 | 7.3727 | 7.1949 | 7.0056 | 6.9012 | 5.8933 | 5.5585 | 5.4744 | 8.4238 | 8.2737 | 8.1007 | 7.9153 | 7.7171 | 7.4704 | 7.2719 | 7.0266 | 6.7821 | 6.5253 | 6.3806 | 5.6962 | 5.3845 | 5.2646
|  | DALCROSS | FS |  |  |  | 2.236 | 8.0771 | 7.9812 | 7.8816 | 7.7713 | 7.6353 | 7.4944 | 7.3607 | 7.188 | 6.9961 | 6.8004 | 6.6816 | 5.9902 | 5.0371 | 4.4102 | 8.4194 | 8.3717 | 8.3068 | 8.2202 | 8.1107 | 8.0013 | 7.8931 | 7.7589 | 7.6085 | 7.4559 | 7.3683 | 6.6621 | 5.9469 | 5.4668 | 8.5407 | 8.4425 | 8.3436 | 8.2363 | 8.1035 | 7.9681 | 7.8376 | 7.6656 | 7.4747 | 7.2809 | 7.1633 | 6.4788 | 5.9563 | 5.3852
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.003 | 0.82709 | 0.82211 | 0.81111 | 0.80248 | 0.78649 | 0.77511 | 0.75781 | 0.74892 | 0.73451 | 0.72031 | 0.70775 | 0.69673 | 0.68894 | 0.67747 | 0.86718 | 0.86626 | 0.85641 | 0.85804 | 0.84863 | 0.84252 | 0.83239 | 0.82643 | 0.81754 | 0.80805 | 0.7996 | 0.79328 | 0.78256 | 0.75628 | 0.80299 | 0.79851 | 0.7881 | 0.78051 | 0.7655 | 0.75516 | 0.73903 | 0.73046 | 0.71602 | 0.70209 | 0.68975 | 0.67969 | 0.67282 | 0.66213
|  | DALMALLY | CT |  |  |  | 0.003 | 0.82709 | 0.82211 | 0.81195 | 0.80248 | 0.78649 | 0.77511 | 0.75781 | 0.74892 | 0.73866 | 0.72759 | 0.71763 | 0.70457 | 0.69667 | 0.68703 | 0.86718 | 0.86899 | 0.86324 | 0.85804 | 0.84863 | 0.84252 | 0.83239 | 0.82643 | 0.81943 | 0.8117 | 0.80454 | 0.79341 | 0.78422 | 0.76934 | 0.80299 | 0.79851 | 0.78912 | 0.78051 | 0.7655 | 0.75516 | 0.73903 | 0.73046 | 0.72045 | 0.70955 | 0.69969 | 0.68755 | 0.68052 | 0.67167
|  | DALMALLY | LW |  |  |  | 0.003 | 0.82785 | 0.82393 | 0.81111 | 0.80456 | 0.79152 | 0.77737 | 0.75996 | 0.75109 | 0.73451 | 0.72031 | 0.70775 | 0.69673 | 0.68894 | 0.67747 | 0.8675 | 0.87013 | 0.86273 | 0.85966 | 0.85236 | 0.84441 | 0.83422 | 0.82855 | 0.81754 | 0.80805 | 0.7996 | 0.79328 | 0.78965 | 0.78296 | 0.80362 | 0.80014 | 0.7881 | 0.78239 | 0.77028 | 0.75711 | 0.74078 | 0.73227 | 0.71602 | 0.70209 | 0.68975 | 0.67969 | 0.67282 | 0.66213
|  | DALMALLY | ST |  |  |  | 0.003 | 0.8345 | 0.82519 | 0.81296 | 0.80695 | 0.80656 | 0.80013 | 0.79434 | 0.7841 | 0.77688 | 0.76783 | 0.75564 | 0.71235 | 0.71248 | 0.70848 | 0.87394 | 0.86626 | 0.85641 | 0.85992 | 0.86027 | 0.85654 | 0.85315 | 0.84661 | 0.84209 | 0.83614 | 0.82811 | 0.79693 | 0.79289 | 0.78125 | 0.81026 | 0.80134 | 0.78982 | 0.78423 | 0.78435 | 0.77843 | 0.77315 | 0.76335 | 0.75654 | 0.74792 | 0.73616 | 0.69432 | 0.69524 | 0.69173
|  | DALMALLY | FS |  |  |  | 0.003 | 0.83761 | 0.83058 | 0.8234 | 0.82142 | 0.8242 | 0.81854 | 0.81635 | 0.81286 | 0.80393 | 0.79961 | 0.79077 | 0.75384 | 0.71314 | 0.70283 | 0.87564 | 0.8695 | 0.86267 | 0.86728 | 0.86901 | 0.86502 | 0.86326 | 0.86088 | 0.85478 | 0.85182 | 0.84572 | 0.81806 | 0.78256 | 0.75628 | 0.81306 | 0.80626 | 0.7992 | 0.79741 | 0.80029 | 0.79475 | 0.79267 | 0.78953 | 0.78095 | 0.77698 | 0.7685 | 0.7333 | 0.69473 | 0.68523
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.19823 | 0.19823 | 0.18541 | 0.17675 | 0.17102 | 0.15135 | 0.14587 | 0.13108 | 0.12583 | 0.12138 | 0.11428 | 0.08659 | 0.045637 | -0.0067559 | 0.29743 | 0.29743 | 0.28462 | 0.27595 | 0.27022 | 0.25055 | 0.24508 | 0.23028 | 0.22503 | 0.22059 | 0.21348 | 0.1829 | 0.14365 | 0.081182 | 0.14936 | 0.14936 | 0.13334 | 0.12251 | 0.11535 | 0.090758 | 0.083917 | 0.065418 | 0.058859 | 0.053305 | 0.044428 | 0.0098109 | -0.04138 | -0.10687
|  | DALMALLY SCHOOL | CT |  |  |  | 0 | 0.19823 | 0.19823 | 0.19656 | 0.1936 | 0.17935 | 0.16415 | 0.1603 | 0.15357 | 0.14682 | 0.14098 | 0.13457 | 0.10661 | 0.075203 | 0.04011 | 0.29743 | 0.29743 | 0.29534 | 0.29164 | 0.27383 | 0.25484 | 0.25002 | 0.24161 | 0.23317 | 0.22587 | 0.21785 | 0.1829 | 0.14365 | 0.099781 | 0.14936 | 0.14936 | 0.14727 | 0.14357 | 0.12576 | 0.10677 | 0.10195 | 0.093541 | 0.085103 | 0.077803 | 0.069781 | 0.034834 | -0.0044223 | -0.048289
|  | DALMALLY SCHOOL | LW |  |  |  | 0 | 0.19823 | 0.19823 | 0.19823 | 0.19823 | 0.19823 | 0.19823 | 0.19823 | 0.1956 | 0.19287 | 0.19062 | 0.1881 | 0.17756 | 0.13489 | 0.045658 | 0.29743 | 0.29743 | 0.29743 | 0.29743 | 0.29743 | 0.29743 | 0.29743 | 0.29414 | 0.29073 | 0.28792 | 0.28476 | 0.27159 | 0.21826 | 0.10672 | 0.14936 | 0.14936 | 0.14936 | 0.14936 | 0.14936 | 0.14936 | 0.14936 | 0.14607 | 0.14266 | 0.13985 | 0.13669 | 0.12352 | 0.070186 | -0.041354
|  | DALMALLY SCHOOL | ST |  |  |  | 0 | 0.19823 | 0.19823 | 0.18541 | 0.17675 | 0.17102 | 0.15135 | 0.14587 | 0.13108 | 0.12583 | 0.12138 | 0.11428 | 0.08659 | 0.045637 | -0.0067559 | 0.29743 | 0.29743 | 0.28462 | 0.27595 | 0.27022 | 0.25055 | 0.24508 | 0.23028 | 0.22503 | 0.22059 | 0.21348 | 0.18579 | 0.14484 | 0.081182 | 0.14936 | 0.14936 | 0.13334 | 0.12251 | 0.11535 | 0.090758 | 0.083917 | 0.065418 | 0.058859 | 0.053305 | 0.044428 | 0.0098109 | -0.04138 | -0.10687
|  | DALMALLY SCHOOL | FS |  |  |  | 0 | 0.19823 | 0.19823 | 0.19561 | 0.19299 | 0.18993 | 0.18688 | 0.18426 | 0.1789 | 0.17527 | 0.17164 | 0.168 | 0.16375 | 0.16086 | 0.15651 | 0.29743 | 0.29743 | 0.29416 | 0.29088 | 0.28706 | 0.28324 | 0.27997 | 0.27327 | 0.26873 | 0.26419 | 0.25965 | 0.25434 | 0.25072 | 0.24528 | 0.14936 | 0.14936 | 0.14609 | 0.14281 | 0.13899 | 0.13517 | 0.1319 | 0.1252 | 0.12066 | 0.11612 | 0.11158 | 0.10627 | 0.10265 | 0.097211
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 2.351 | -0.60985 | -0.94142 | -1.485 | -2.1999 | -2.9889 | -3.8872 | -5.0312 | -5.8765 | -7.1226 | -8.2611 | -9.3065 | -12.1404 | -12.9063 | -14.042 | 2.4591 | 2.2439 | 1.9437 | 1.5323 | 1.1044 | 0.61386 | -0.031462 | -0.43816 | -1.0631 | -1.7521 | -2.39 | -3.9972 | -4.9234 | -6.3136 | 0.88154 | 0.58741 | 0.081886 | -0.56656 | -1.2839 | -2.1072 | -3.1553 | -3.9183 | -5.0901 | -6.1591 | -7.1413 | -9.7585 | -10.3699 | -11.3797
|  | DALNEIGH | CT |  |  |  | 2.351 | -0.58108 | -0.92557 | -1.4733 | -2.1999 | -2.9889 | -3.8872 | -5.0312 | -5.8765 | -6.8234 | -7.7343 | -8.5292 | -11.4503 | -12.9063 | -14.042 | 2.4755 | 2.2439 | 1.9437 | 1.5323 | 1.1044 | 0.61386 | -0.031462 | -0.43816 | -0.9849 | -1.5426 | -2.0495 | -3.8815 | -4.9234 | -6.3136 | 0.90993 | 0.60703 | 0.10211 | -0.56656 | -1.2839 | -2.1072 | -3.1553 | -3.9183 | -4.7938 | -5.6436 | -6.3892 | -9.067 | -10.3472 | -11.3797
|  | DALNEIGH | LW |  |  |  | 2.351 | -0.60985 | -0.94142 | -1.485 | -2.1863 | -2.8783 | -3.8636 | -4.9978 | -5.8646 | -7.1226 | -8.2611 | -9.3065 | -12.1404 | -12.8291 | -13.8253 | 2.4591 | 2.2448 | 1.9695 | 1.6001 | 1.2594 | 0.72447 | 0.098684 | -0.30404 | -1.0631 | -1.7521 | -2.39 | -3.9972 | -4.3211 | -4.9617 | 0.88154 | 0.58741 | 0.081886 | -0.56212 | -1.1957 | -2.0922 | -3.1256 | -3.9092 | -5.0901 | -6.1591 | -7.1413 | -9.7585 | -10.3699 | -11.3102
|  | DALNEIGH | ST |  |  |  | 2.351 | -0.42893 | -0.5654 | -0.66065 | -0.81094 | -0.95362 | -1.1641 | -1.377 | -1.6669 | -2.0487 | -2.457 | -2.5391 | -5.0838 | -6.6377 | -8.1673 | 2.5602 | 2.4641 | 2.3854 | 2.2664 | 2.1464 | 1.9791 | 1.8124 | 1.5923 | 1.3044 | 0.9596 | 0.87226 | -1.1795 | -2.4173 | -3.8269 | 1.0452 | 0.92578 | 0.84435 | 0.71547 | 0.58921 | 0.40047 | 0.19234 | -0.091562 | -0.46699 | -0.86865 | -0.94559 | -3.3874 | -4.7969 | -6.1416
|  | DALNEIGH | FS |  |  |  | 2.351 | -0.37639 | -0.48129 | -0.60208 | -0.76094 | -0.93545 | -1.0993 | -1.3163 | -1.6262 | -1.948 | -2.3213 | -2.7228 | -4.9929 | -7.623 | -9.7418 | 2.6014 | 2.5221 | 2.4381 | 2.3206 | 2.1924 | 2.0629 | 1.8895 | 1.6631 | 1.4278 | 1.1491 | 0.84691 | -0.91298 | -3.3725 | -6.1267 | 1.0945 | 1.0028 | 0.89756 | 0.75618 | 0.60301 | 0.45487 | 0.26373 | -0.020185 | -0.32435 | -0.67929 | -1.0618 | -3.1864 | -5.628 | -7.5447
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | YES | 0.047 | 0.71759 | 0.68554 | 0.65378 | 0.62387 | 0.59875 | 0.55276 | 0.4749 | 0.3832 | 0.2851 | 0.19424 | 0.11394 | -0.078176 | -0.21398 | -0.37478 | 1.0406 | 0.99449 | 0.93367 | 0.87507 | 0.82133 | 0.73682 | 0.64867 | 0.59273 | 0.52975 | 0.47156 | 0.41439 | 0.28546 | 0.19257 | 0.071105 | 0.92919 | 0.89492 | 0.86005 | 0.82677 | 0.79943 | 0.75182 | 0.69733 | 0.66197 | 0.61969 | 0.57996 | 0.54356 | 0.45041 | 0.38341 | 0.23285
|  | DALRULZION | CT |  |  |  | 0.047 | 0.71836 | 0.69987 | 0.68409 | 0.6447 | 0.61965 | 0.58995 | 0.49793 | 0.40722 | 0.3448 | 0.27602 | 0.21641 | 0.047133 | -0.046197 | -0.15978 | 1.0406 | 1.0051 | 0.96722 | 0.89822 | 0.84308 | 0.77727 | 0.6999 | 0.64176 | 0.60048 | 0.55378 | 0.5115 | 0.38999 | 0.31825 | 0.20745 | 0.92956 | 0.91232 | 0.89655 | 0.85423 | 0.82902 | 0.79952 | 0.75785 | 0.72101 | 0.69522 | 0.66558 | 0.63858 | 0.58035 | 0.56094 | 0.46537
|  | DALRULZION | LW |  |  |  | 0.047 | 0.71759 | 0.68554 | 0.65378 | 0.62387 | 0.59875 | 0.55276 | 0.4749 | 0.3832 | 0.2851 | 0.19424 | 0.11394 | -0.078176 | -0.21398 | -0.37478 | 1.0446 | 0.99449 | 0.93367 | 0.87507 | 0.82133 | 0.73682 | 0.64867 | 0.59273 | 0.52975 | 0.47156 | 0.41439 | 0.28546 | 0.19257 | 0.071105 | 0.92919 | 0.89492 | 0.86005 | 0.82677 | 0.79943 | 0.75182 | 0.69733 | 0.66197 | 0.61969 | 0.57996 | 0.54356 | 0.45041 | 0.38341 | 0.23285
|  | DALRULZION | ST |  |  |  | 0.047 | 0.72178 | 0.71573 | 0.69798 | 0.68326 | 0.66782 | 0.65611 | 0.63805 | 0.61935 | 0.59091 | 0.56831 | 0.52083 | 0.15814 | 0.032865 | -0.059727 | 1.0494 | 1.0321 | 0.99374 | 0.95965 | 0.92411 | 0.89557 | 0.8572 | 0.82497 | 0.77884 | 0.74432 | 0.69742 | 0.43167 | 0.31093 | 0.19126 | 0.93391 | 0.92868 | 0.90763 | 0.8902 | 0.87344 | 0.85994 | 0.84103 | 0.82155 | 0.79351 | 0.7698 | 0.74011 | 0.54454 | 0.45643 | 0.39426
|  | DALRULZION | FS |  |  |  | 0.047 | 0.72417 | 0.71836 | 0.71136 | 0.70299 | 0.69185 | 0.67899 | 0.66802 | 0.65166 | 0.63305 | 0.61105 | 0.5921 | 0.48672 | 0.22156 | 0.09746 | 1.06 | 1.0461 | 1.0324 | 1.0167 | 0.99696 | 0.97473 | 0.95639 | 0.92346 | 0.89033 | 0.85079 | 0.81504 | 0.62562 | 0.42745 | 0.26348 | 0.93575 | 0.93085 | 0.92177 | 0.91152 | 0.89895 | 0.88484 | 0.87114 | 0.85409 | 0.83382 | 0.81089 | 0.7923 | 0.68636 | 0.59813 | 0.5423
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.164 | 0.12285 | 0.1036 | 0.069367 | 0.032568 | -0.00097132 | -0.045438 | -0.10281 | -0.12511 | -0.15631 | -0.18088 | -0.20566 | -0.28787 | -0.34986 | -0.42216 | 0.28549 | 0.27052 | 0.23999 | 0.20883 | 0.18289 | 0.14706 | 0.098911 | 0.08527 | 0.065345 | 0.050892 | 0.034446 | -0.036035 | -0.10081 | -0.17954 | 0.25522 | 0.23349 | 0.19684 | 0.15825 | 0.12041 | 0.070456 | 0.005806 | -0.012714 | -0.04368 | -0.06402 | -0.090879 | -0.18169 | -0.25826 | -0.34893
|  | DALWHINNIE | CT |  |  |  | 0.164 | 0.12871 | 0.11594 | 0.096502 | 0.057436 | 0.027743 | -0.0018279 | -0.046425 | -0.068335 | -0.088586 | -0.10851 | -0.12236 | -0.18234 | -0.21897 | -0.26681 | 0.2949 | 0.28779 | 0.27663 | 0.24413 | 0.2245 | 0.20437 | 0.17042 | 0.15583 | 0.14195 | 0.12338 | 0.1132 | 0.05389 | 0.025079 | -0.016589 | 0.26147 | 0.24987 | 0.2321 | 0.19135 | 0.15877 | 0.12428 | 0.072707 | 0.053468 | 0.033605 | 0.0064579 | -0.0062458 | -0.083391 | -0.11969 | -0.16495
|  | DALWHINNIE | LW |  |  |  | 0.164 | 0.12993 | 0.1036 | 0.069367 | 0.032568 | -0.00097132 | -0.045438 | -0.10281 | -0.12511 | -0.15631 | -0.18088 | -0.20566 | -0.28787 | -0.34986 | -0.42216 | 0.29539 | 0.27052 | 0.23999 | 0.20883 | 0.18289 | 0.14706 | 0.098911 | 0.08527 | 0.065345 | 0.050892 | 0.034446 | -0.036035 | -0.10081 | -0.17954 | 0.26246 | 0.23349 | 0.19684 | 0.15825 | 0.12041 | 0.070456 | 0.005806 | -0.012714 | -0.04368 | -0.06402 | -0.090879 | -0.18169 | -0.25826 | -0.34893
|  | DALWHINNIE | ST |  |  |  | 0.164 | 0.12285 | 0.12403 | 0.10284 | 0.083847 | 0.064349 | 0.046758 | 0.026892 | 0.0084514 | -0.015909 | -0.041498 | -0.062087 | -0.21669 | -0.30713 | -0.36736 | 0.28549 | 0.29226 | 0.274 | 0.25908 | 0.24549 | 0.23438 | 0.2217 | 0.20964 | 0.19355 | 0.17665 | 0.16437 | 0.044714 | -0.040789 | -0.10541 | 0.25522 | 0.2573 | 0.23492 | 0.21558 | 0.19505 | 0.17592 | 0.15484 | 0.13673 | 0.11336 | 0.089145 | 0.071492 | -0.081726 | -0.18125 | -0.25113
|  | DALWHINNIE | FS |  |  |  | 0.164 | 0.12967 | 0.13337 | 0.12649 | 0.11738 | 0.10838 | 0.098493 | 0.084744 | 0.068856 | 0.050411 | 0.029847 | 0.013015 | -0.081447 | -0.1724 | -0.22366 | 0.28981 | 0.2975 | 0.29157 | 0.28396 | 0.27649 | 0.2685 | 0.25681 | 0.24528 | 0.23109 | 0.2154 | 0.20505 | 0.1465 | 0.086076 | 0.044915 | 0.2614 | 0.26567 | 0.25835 | 0.24883 | 0.23942 | 0.22917 | 0.21467 | 0.19892 | 0.18026 | 0.1595 | 0.14372 | 0.055138 | -0.029304 | -0.079027
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 0.194 | 6.6359 | 6.48 | 6.2746 | 5.7622 | 5.1928 | 4.4615 | 3.5924 | 2.6546 | 1.5273 | 0.49109 | -0.46144 | -3.4539 | -3.6258 | -4.7559 | 9.7636 | 9.5429 | 9.1994 | 8.7788 | 8.3522 | 7.8964 | 7.2677 | 6.4957 | 5.8209 | 5.0674 | 4.3348 | 0.56903 | -6.5091 | -19.6194 | 8.2332 | 8.0829 | 7.8561 | 7.529 | 7.0076 | 6.3009 | 5.3274 | 4.3967 | 3.3241 | 2.2575 | 1.2206 | -1.6717 | -1.8493 | -2.9811
|  | DENBURN | CT |  |  |  | 0.194 | 6.6394 | 6.483 | 6.2746 | 5.9812 | 5.508 | 4.999 | 4.319 | 3.3783 | 2.5335 | 1.7071 | 0.96778 | -1.9467 | -2.8754 | -3.8093 | 9.7636 | 9.5429 | 9.1994 | 8.7788 | 8.3522 | 7.8964 | 7.2677 | 6.4957 | 5.8209 | 5.0674 | 4.3348 | 0.56903 | -3.0325 | -9.2955 | 8.2351 | 8.0874 | 7.8955 | 7.5844 | 7.2749 | 6.7895 | 6.0138 | 5.0532 | 4.2656 | 3.4888 | 2.754 | -0.10768 | -0.91519 | -1.8714
|  | DENBURN | LW |  |  |  | 0.194 | 6.6359 | 6.48 | 6.2909 | 5.7622 | 5.1928 | 4.4615 | 3.5924 | 2.6546 | 1.5273 | 0.49109 | -0.46144 | -3.4539 | -3.6258 | -4.7559 | 9.7889 | 9.6372 | 9.3458 | 9.0212 | 8.676 | 8.1881 | 7.5886 | 6.9622 | 6.1939 | 5.4253 | 4.7266 | 2.823 | 2.632 | 1.6815 | 8.2332 | 8.0829 | 7.8561 | 7.529 | 7.0076 | 6.3009 | 5.3274 | 4.3967 | 3.3241 | 2.2575 | 1.2206 | -1.6717 | -1.8493 | -2.9811
|  | DENBURN | ST |  |  |  | 0.194 | 6.684 | 6.624 | 6.508 | 6.4095 | 6.2974 | 6.1591 | 5.9885 | 5.7858 | 5.5221 | 5.243 | 4.8779 | 2.627 | 1.5445 | 0.50458 | 9.803 | 9.6954 | 9.4932 | 9.2892 | 9.0603 | 8.7915 | 8.4814 | 8.1246 | 7.6916 | 7.2325 | 6.6735 | 2.7502 | -1.1181 | -7.1994 | 8.2779 | 8.2223 | 8.1146 | 8.0211 | 7.915 | 7.785 | 7.6241 | 7.4329 | 7.1816 | 6.9162 | 6.5114 | 4.0773 | 3.0226 | 2.1852
|  | DENBURN | FS |  |  |  | 0.194 | 6.6991 | 6.6578 | 6.5741 | 6.507 | 6.4248 | 6.3339 | 6.2127 | 6.0852 | 5.9157 | 5.6637 | 5.3843 | 2.7446 | 0.026782 | -1.9952 | 9.826 | 9.7312 | 9.5329 | 9.3286 | 9.0925 | 8.8235 | 8.4592 | 8.0101 | 7.4852 | 6.9523 | 6.375 | 1.7193 | -6.5091 | -19.6194 | 8.2906 | 8.2523 | 8.1767 | 8.1139 | 8.0369 | 7.9513 | 7.8371 | 7.7177 | 7.5311 | 7.333 | 7.1311 | 4.4647 | 1.9377 | 0.077677
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0.422 | 0.86101 | 0.75802 | 0.5719 | 0.34316 | 0.11086 | -0.1487 | -0.62325 | -0.87568 | -0.97 | -1.1307 | -1.2763 | -1.6435 | -1.7862 | -2.0478 | 1.7032 | 1.6372 | 1.5503 | 1.431 | 1.3202 | 1.191 | 0.87361 | 0.63786 | 0.48914 | 0.33228 | 0.18836 | -0.13428 | -0.20471 | -0.405 | 1.3397 | 1.2429 | 1.0939 | 0.90235 | 0.71485 | 0.50054 | 0.074391 | -0.17536 | -0.33543 | -0.53165 | -0.70942 | -1.1205 | -1.2333 | -1.5033
|  | DERVAIG | CT |  |  |  | 0.422 | 0.86101 | 0.75802 | 0.5719 | 0.34316 | 0.11086 | -0.1487 | -0.62325 | -0.87568 | -0.97 | -1.084 | -1.1696 | -1.4286 | -1.5446 | -1.7418 | 1.7032 | 1.6372 | 1.5503 | 1.431 | 1.3202 | 1.191 | 0.89144 | 0.66295 | 0.57067 | 0.44459 | 0.3358 | 0.03628 | -0.060661 | -0.26397 | 1.3397 | 1.2429 | 1.0939 | 0.90235 | 0.71485 | 0.50054 | 0.074391 | -0.17536 | -0.27511 | -0.41496 | -0.53595 | -0.86536 | -0.95733 | -1.1426
|  | DERVAIG | LW |  |  |  | 0.422 | 0.87765 | 0.77873 | 0.60812 | 0.41952 | 0.215 | -0.029752 | -0.52698 | -0.8032 | -0.967 | -1.1307 | -1.2763 | -1.6435 | -1.7862 | -2.0478 | 1.7093 | 1.6408 | 1.5522 | 1.4544 | 1.3503 | 1.2134 | 0.87361 | 0.63786 | 0.48914 | 0.33228 | 0.18836 | -0.13428 | -0.20471 | -0.405 | 1.3509 | 1.2543 | 1.1108 | 0.95198 | 0.78084 | 0.56668 | 0.13376 | -0.14683 | -0.33543 | -0.53165 | -0.70942 | -1.1205 | -1.2333 | -1.5033
|  | DERVAIG | ST |  |  |  | 0.422 | 0.90154 | 0.83585 | 0.7616 | 0.68731 | 0.60135 | 0.51821 | 0.2536 | 0.055315 | -0.089814 | -0.22996 | -0.37256 | -0.90763 | -1.0666 | -1.0988 | 1.7306 | 1.6952 | 1.6534 | 1.6123 | 1.559 | 1.5084 | 1.3097 | 1.164 | 1.0515 | 0.9438 | 0.83074 | 0.33481 | 0.15823 | 0.049259 | 1.3788 | 1.3226 | 1.2595 | 1.197 | 1.1191 | 1.0447 | 0.81534 | 0.64277 | 0.49765 | 0.358 | 0.2099 | -0.38425 | -0.54879 | -0.57848
|  | DERVAIG | FS |  |  |  | 0.422 | 0.93993 | 0.89625 | 0.87288 | 0.84038 | 0.81559 | 0.77738 | 0.637 | 0.49039 | 0.39406 | 0.27725 | 0.1596 | -0.43046 | -0.96826 | -1.2049 | 1.7433 | 1.7168 | 1.6956 | 1.6645 | 1.642 | 1.6046 | 1.4858 | 1.3749 | 1.305 | 1.2145 | 1.1247 | 0.63766 | 0.18271 | -0.13721 | 1.4061 | 1.3669 | 1.3419 | 1.305 | 1.2791 | 1.235 | 1.1097 | 0.97758 | 0.88968 | 0.77717 | 0.66543 | 0.075134 | -0.44523 | -0.66321
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 0.954 | 4.6712 | 4.4567 | 4.0489 | 3.5291 | 2.9506 | 2.2038 | 1.3572 | 0.70688 | 0.20725 | -0.12606 | -0.63379 | -2.142 | -2.7773 | -3.4355 | 6.679 | 6.5239 | 6.2965 | 6.0162 | 5.6947 | 5.3126 | 4.8343 | 4.4231 | 4.0907 | 3.9631 | 3.6288 | 2.742 | 2.291 | 1.6133 | 5.8373 | 5.7158 | 5.5772 | 5.3627 | 4.9839 | 4.3832 | 3.6029 | 3.0106 | 2.5397 | 2.2464 | 1.7778 | 0.40384 | -0.16005 | -0.73858
|  | DINGWALL | CT |  |  |  | 0.954 | 4.6712 | 4.4567 | 4.0489 | 3.5291 | 2.9506 | 2.2038 | 1.3572 | 0.70688 | 0.2116 | -0.012118 | -0.3657 | -1.8452 | -2.7587 | -3.4355 | 6.679 | 6.5239 | 6.2965 | 6.0162 | 5.6947 | 5.3126 | 4.8343 | 4.4231 | 4.1086 | 4.0434 | 3.7919 | 2.8496 | 2.291 | 1.6133 | 5.8432 | 5.7201 | 5.5772 | 5.3627 | 4.9839 | 4.3832 | 3.6029 | 3.0106 | 2.557 | 2.3668 | 2.0392 | 0.70061 | -0.10076 | -0.70426
|  | DINGWALL | LW |  |  |  | 0.954 | 4.6842 | 4.4773 | 4.0874 | 3.6041 | 3.0839 | 2.3109 | 1.5366 | 0.85807 | 0.20725 | -0.12606 | -0.63379 | -2.142 | -2.7773 | -3.3799 | 6.6877 | 6.5378 | 6.3341 | 6.0846 | 5.8171 | 5.3785 | 4.943 | 4.5326 | 4.0907 | 3.9631 | 3.6288 | 2.742 | 2.4548 | 2.0804 | 5.8373 | 5.7158 | 5.6129 | 5.4753 | 5.1697 | 4.4767 | 3.7601 | 3.1448 | 2.5397 | 2.2464 | 1.7778 | 0.40384 | -0.16005 | -0.73858
|  | DINGWALL | ST |  |  |  | 0.954 | 4.7559 | 4.629 | 4.4835 | 4.3146 | 4.1362 | 3.8686 | 3.6084 | 3.3801 | 3.1646 | 2.9145 | 2.6455 | 1.291 | 0.31413 | -0.49352 | 6.7359 | 6.6592 | 6.5607 | 6.4518 | 6.3269 | 6.1532 | 5.9654 | 5.786 | 5.6068 | 5.3909 | 5.1554 | 4.1381 | 3.4639 | 2.8181 | 5.8812 | 5.8355 | 5.7697 | 5.6865 | 5.5884 | 5.4397 | 5.2759 | 5.1064 | 4.8617 | 4.5422 | 4.1871 | 2.411 | 1.5761 | 1.1192
|  | DINGWALL | FS |  |  |  | 0.954 | 4.8341 | 4.743 | 4.6707 | 4.5777 | 4.4765 | 4.3165 | 4.1612 | 3.9592 | 3.737 | 3.5019 | 3.2928 | 1.7875 | 0.42829 | -0.78414 | 6.7692 | 6.7047 | 6.6465 | 6.5742 | 6.4887 | 6.3605 | 6.2253 | 6.0876 | 5.9125 | 5.7274 | 5.5658 | 4.3545 | 3.2778 | 1.934 | 5.8968 | 5.8604 | 5.8186 | 5.7607 | 5.6927 | 5.5869 | 5.4759 | 5.3768 | 5.2446 | 5.1013 | 4.9609 | 3.3924 | 1.9473 | 0.75698
| CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0 | 0.22678 | 0.21571 | 0.19042 | 0.1466 | 0.092922 | 0.044229 | -0.020479 | -0.037106 | -0.052783 | -0.075853 | -0.085119 | -0.15049 | -0.17307 | -0.20891 | 0.8933 | 0.87732 | 0.85577 | 0.83553 | 0.80605 | 0.78606 | 0.74953 | 0.73054 | 0.70996 | 0.68281 | 0.67781 | 0.62918 | 0.60396 | 0.53719 | 0.32978 | 0.31947 | 0.30305 | 0.28549 | 0.24599 | 0.21174 | 0.14992 | 0.12486 | 0.098151 | 0.064379 | 0.057619 | -0.0038033 | -0.022897 | -0.056473
|  | DIPPEN | CT |  |  |  | 0 | 0.22678 | 0.21571 | 0.19042 | 0.1466 | 0.092922 | 0.044229 | -0.020479 | -0.037106 | -0.052783 | -0.073045 | -0.074708 | -0.13464 | -0.15567 | -0.18471 | 0.8933 | 0.87732 | 0.85577 | 0.83553 | 0.80605 | 0.78606 | 0.74953 | 0.73054 | 0.70996 | 0.6869 | 0.683 | 0.62918 | 0.60396 | 0.56046 | 0.32978 | 0.31947 | 0.30305 | 0.28549 | 0.24599 | 0.21174 | 0.14992 | 0.12486 | 0.098151 | 0.068806 | 0.068861 | 0.010141 | -0.0078006 | -0.032808
|  | DIPPEN | LW |  |  |  | 0 | 0.22847 | 0.21887 | 0.20397 | 0.16477 | 0.12075 | 0.073738 | 0.015522 | -0.0038476 | -0.03765 | -0.075853 | -0.085119 | -0.15049 | -0.17307 | -0.20891 | 0.89534 | 0.88162 | 0.86405 | 0.84535 | 0.82356 | 0.80068 | 0.76618 | 0.74703 | 0.71346 | 0.68281 | 0.67781 | 0.63241 | 0.62203 | 0.60044 | 0.33127 | 0.32231 | 0.30882 | 0.29413 | 0.27069 | 0.23226 | 0.17624 | 0.14927 | 0.10342 | 0.064379 | 0.057619 | -0.0038033 | -0.022897 | -0.056473
|  | DIPPEN | ST |  |  |  | 0 | 0.22913 | 0.22503 | 0.2163 | 0.20707 | 0.18739 | 0.16725 | 0.14264 | 0.11936 | 0.10019 | 0.073715 | 0.052633 | -0.065733 | -0.10243 | -0.11303 | 0.89396 | 0.89117 | 0.88144 | 0.87078 | 0.85843 | 0.84735 | 0.83101 | 0.81282 | 0.80096 | 0.77871 | 0.76286 | 0.66862 | 0.63001 | 0.59673 | 0.33184 | 0.32829 | 0.32041 | 0.31202 | 0.30265 | 0.29367 | 0.28205 | 0.26378 | 0.24639 | 0.21577 | 0.19403 | 0.07779 | 0.043344 | 0.03386
|  | DIPPEN | FS |  |  |  | 0 | 0.23309 | 0.22995 | 0.22748 | 0.22241 | 0.21858 | 0.21378 | 0.20944 | 0.2005 | 0.18503 | 0.17399 | 0.15021 | 0.027031 | -0.071896 | -0.11184 | 0.89824 | 0.89503 | 0.89295 | 0.88431 | 0.87924 | 0.87177 | 0.86556 | 0.85156 | 0.8342 | 0.82677 | 0.80935 | 0.71297 | 0.62065 | 0.53719 | 0.33538 | 0.33259 | 0.33038 | 0.32558 | 0.32203 | 0.3175 | 0.31346 | 0.30512 | 0.29477 | 0.28822 | 0.27735 | 0.1635 | 0.070849 | 0.0335
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 1.469 | -1.3246 | -1.4319 | -1.5944 | -1.7922 | -2.0202 | -2.3075 | -2.6178 | -2.7618 | -2.8635 | -2.9559 | -3.0642 | -3.4673 | -3.718 | -3.9782 | 0.093918 | 0.030312 | -0.05226 | -0.14471 | -0.24016 | -0.37009 | -0.51814 | -0.65451 | -0.80146 | -0.90081 | -1.0189 | -1.2986 | -1.4078 | -1.5999 | -0.69408 | -0.79818 | -0.9587 | -1.1352 | -1.325 | -1.5658 | -1.8289 | -1.9599 | -2.0585 | -2.1557 | -2.2579 | -2.5756 | -2.7808 | -2.9524
|  | DORNOCH | CT |  |  |  | 1.469 | -1.2856 | -1.405 | -1.5675 | -1.7671 | -2.0202 | -2.3075 | -2.6178 | -2.7618 | -2.8635 | -2.9559 | -3.0034 | -3.3379 | -3.5751 | -3.8007 | 0.15877 | 0.09068 | 0.013218 | -0.082457 | -0.20812 | -0.35731 | -0.51515 | -0.65451 | -0.75625 | -0.86689 | -0.92955 | -1.2338 | -1.3831 | -1.5999 | -0.65747 | -0.77134 | -0.92872 | -1.1111 | -1.3239 | -1.5658 | -1.8289 | -1.9599 | -2.0515 | -2.1361 | -2.1786 | -2.4518 | -2.6296 | -2.785
|  | DORNOCH | LW |  |  |  | 1.469 | -1.3246 | -1.4319 | -1.5944 | -1.7922 | -2.016 | -2.2783 | -2.5587 | -2.6994 | -2.849 | -2.9546 | -3.0642 | -3.4673 | -3.718 | -3.9782 | 0.093918 | 0.030312 | -0.05226 | -0.14471 | -0.24016 | -0.37009 | -0.51814 | -0.64577 | -0.80146 | -0.90081 | -1.0189 | -1.2986 | -1.4078 | -1.5659 | -0.69408 | -0.79818 | -0.9587 | -1.1352 | -1.325 | -1.5492 | -1.7904 | -1.9188 | -2.0585 | -2.1557 | -2.2579 | -2.5756 | -2.7808 | -2.9524
|  | DORNOCH | ST |  |  |  | 1.469 | -1.2485 | -1.335 | -1.4415 | -1.553 | -1.6822 | -1.8259 | -1.9658 | -2.0909 | -2.2296 | -2.359 | -2.5096 | -3.1792 | -3.4667 | -3.6033 | 0.1774 | 0.12994 | 0.077551 | 0.021238 | -0.052659 | -0.14033 | -0.22338 | -0.29944 | -0.38217 | -0.45694 | -0.5482 | -1.0445 | -1.2597 | -1.4275 | -0.62296 | -0.70729 | -0.80873 | -0.91412 | -1.0358 | -1.1702 | -1.2968 | -1.4108 | -1.5368 | -1.6519 | -1.786 | -2.3524 | -2.6091 | -2.7382
|  | DORNOCH | FS |  |  |  | 1.469 | -1.131 | -1.1868 | -1.2247 | -1.2733 | -1.3257 | -1.3857 | -1.4513 | -1.5406 | -1.6438 | -1.7552 | -1.8795 | -2.5196 | -3.143 | -3.4732 | 0.27587 | 0.24309 | 0.21872 | 0.1839 | 0.14475 | 0.099484 | 0.044767 | -0.0072192 | -0.080856 | -0.16466 | -0.25938 | -0.74547 | -1.211 | -1.5795 | -0.50824 | -0.5626 | -0.5956 | -0.63966 | -0.6855 | -0.73916 | -0.79802 | -0.87964 | -0.97288 | -1.0757 | -1.1896 | -1.7622 | -2.3112 | -2.6067
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0.069 | 0.079629 | 0.07072 | 0.074068 | 0.036021 | -0.011171 | -0.053112 | -0.11486 | -0.14891 | -0.19266 | -0.23172 | -0.27517 | -0.37685 | -0.40078 | -0.4624 | 0.36089 | 0.35269 | 0.34711 | 0.3306 | 0.31079 | 0.2923 | 0.267 | 0.25567 | 0.24419 | 0.23214 | 0.2181 | 0.18351 | 0.1715 | 0.14627 | 0.14811 | 0.1407 | 0.11586 | 0.082198 | 0.042874 | 0.0036148 | -0.046085 | -0.065865 | -0.086727 | -0.12502 | -0.16786 | -0.26672 | -0.28803 | -0.34725
|  | DOUGLAS PIER | CT |  |  |  | 0.069 | 0.088029 | 0.085544 | 0.074068 | 0.036021 | -0.011171 | -0.053112 | -0.11486 | -0.14891 | -0.1827 | -0.21869 | -0.24037 | -0.33531 | -0.3634 | -0.41005 | 0.36765 | 0.36086 | 0.34711 | 0.3306 | 0.31079 | 0.2923 | 0.267 | 0.25567 | 0.24419 | 0.23254 | 0.22646 | 0.19274 | 0.17543 | 0.15059 | 0.15296 | 0.14247 | 0.11586 | 0.082198 | 0.042874 | 0.0036148 | -0.046085 | -0.065865 | -0.083814 | -0.11092 | -0.13248 | -0.22519 | -0.25066 | -0.29487
|  | DOUGLAS PIER | LW |  |  |  | 0.069 | 0.087768 | 0.085647 | 0.081768 | 0.047585 | 0.009071 | -0.039135 | -0.10125 | -0.1366 | -0.19266 | -0.23172 | -0.27517 | -0.37685 | -0.40078 | -0.4624 | 0.36889 | 0.36327 | 0.35116 | 0.336 | 0.31955 | 0.29977 | 0.27517 | 0.26325 | 0.24457 | 0.23214 | 0.2181 | 0.18351 | 0.1715 | 0.14627 | 0.15496 | 0.14603 | 0.1237 | 0.092725 | 0.059006 | 0.01949 | -0.027518 | -0.049216 | -0.086727 | -0.12502 | -0.16786 | -0.26672 | -0.28803 | -0.34725
|  | DOUGLAS PIER | ST |  |  |  | 0.069 | 0.079629 | 0.087888 | 0.087178 | 0.084204 | 0.074762 | 0.056623 | 0.034381 | 0.0082187 | -0.016586 | -0.04904 | -0.07135 | -0.20507 | -0.24128 | -0.24657 | 0.36089 | 0.3652 | 0.36017 | 0.353 | 0.34604 | 0.33848 | 0.32946 | 0.31921 | 0.30944 | 0.29706 | 0.28851 | 0.23842 | 0.21936 | 0.20877 | 0.14811 | 0.14802 | 0.14074 | 0.12736 | 0.1135 | 0.098696 | 0.081926 | 0.064445 | 0.047364 | 0.027043 | 0.010909 | -0.10247 | -0.13712 | -0.14176
|  | DOUGLAS PIER | FS |  |  |  | 0.069 | 0.081386 | 0.07072 | 0.089091 | 0.087036 | 0.085278 | 0.081664 | 0.07914 | 0.075358 | 0.053344 | 0.036453 | 0.012076 | -0.11306 | -0.22552 | -0.27516 | 0.36556 | 0.35269 | 0.37003 | 0.36725 | 0.36474 | 0.3604 | 0.35711 | 0.34989 | 0.34057 | 0.33338 | 0.32366 | 0.27393 | 0.22092 | 0.1845 | 0.15544 | 0.1407 | 0.15763 | 0.15514 | 0.15305 | 0.14884 | 0.1441 | 0.1311 | 0.11554 | 0.10263 | 0.086565 | -0.015032 | -0.1221 | -0.16933
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0.133 | 1.4816 | 1.4447 | 1.3914 | 1.3258 | 1.2755 | 1.1909 | 1.1013 | 1.0193 | 0.94925 | 0.87371 | 0.80554 | 0.60994 | 0.49105 | 0.35616 | 1.8192 | 1.7947 | 1.7695 | 1.7401 | 1.7122 | 1.6524 | 1.5894 | 1.5397 | 1.5028 | 1.4553 | 1.4124 | 1.303 | 1.2227 | 1.1236 | 1.8897 | 1.8628 | 1.8356 | 1.7836 | 1.736 | 1.6666 | 1.5885 | 1.5145 | 1.4562 | 1.3852 | 1.3214 | 1.1511 | 1.0398 | 0.90971
|  | DRIMORE | CT |  |  |  | 0.133 | 1.4828 | 1.4523 | 1.4112 | 1.3432 | 1.289 | 1.2158 | 1.1295 | 1.049 | 1.0004 | 0.93747 | 0.88138 | 0.67206 | 0.54243 | 0.45405 | 1.8203 | 1.8115 | 1.8051 | 1.7683 | 1.7413 | 1.6992 | 1.6466 | 1.5946 | 1.5727 | 1.5304 | 1.4909 | 1.3773 | 1.313 | 1.2465 | 1.8912 | 1.8797 | 1.8708 | 1.8116 | 1.7662 | 1.7098 | 1.6375 | 1.5594 | 1.5224 | 1.4611 | 1.4055 | 1.2243 | 1.1192 | 1.0425
|  | DRIMORE | LW |  |  |  | 0.133 | 1.4816 | 1.4447 | 1.3914 | 1.3258 | 1.2755 | 1.1909 | 1.1013 | 1.0193 | 0.94925 | 0.87371 | 0.80554 | 0.60994 | 0.49105 | 0.35616 | 1.8192 | 1.7947 | 1.7695 | 1.7401 | 1.7122 | 1.6524 | 1.5894 | 1.5397 | 1.5028 | 1.4553 | 1.4124 | 1.303 | 1.2227 | 1.1236 | 1.8897 | 1.8628 | 1.8356 | 1.7836 | 1.736 | 1.6666 | 1.5885 | 1.5145 | 1.4562 | 1.3852 | 1.3214 | 1.1511 | 1.0398 | 0.90971
|  | DRIMORE | ST |  |  |  | 0.133 | 1.494 | 1.4832 | 1.4577 | 1.432 | 1.4113 | 1.3858 | 1.3568 | 1.3397 | 1.3039 | 1.2786 | 1.2427 | 1.0033 | 0.82223 | 0.6743 | 1.8224 | 1.8195 | 1.8041 | 1.7916 | 1.7826 | 1.7742 | 1.7628 | 1.7511 | 1.7216 | 1.7023 | 1.6737 | 1.4989 | 1.3737 | 1.2593 | 1.894 | 1.8903 | 1.8738 | 1.8598 | 1.8492 | 1.8386 | 1.8209 | 1.804 | 1.7785 | 1.7574 | 1.7251 | 1.4991 | 1.3323 | 1.1961
|  | DRIMORE | FS |  |  |  | 0.133 | 1.4968 | 1.485 | 1.4714 | 1.4567 | 1.4395 | 1.4242 | 1.3995 | 1.3688 | 1.3461 | 1.3117 | 1.2892 | 1.1134 | 0.93356 | 0.7841 | 1.8229 | 1.8205 | 1.8152 | 1.8093 | 1.8018 | 1.7946 | 1.7823 | 1.7706 | 1.7556 | 1.729 | 1.7148 | 1.5937 | 1.4729 | 1.3628 | 1.8947 | 1.8915 | 1.8854 | 1.8785 | 1.8699 | 1.8615 | 1.8474 | 1.8332 | 1.8109 | 1.7843 | 1.7656 | 1.6077 | 1.4443 | 1.3265
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | YES | 1.559 | 0.95374 | 0.90614 | 0.86825 | 0.80626 | 0.7481 | 0.59862 | 0.39244 | 0.30514 | 0.25828 | 0.15091 | 0.028161 | -0.28009 | -0.41621 | -0.60835 | 2.6037 | 2.5466 | 2.4812 | 2.3941 | 2.3124 | 2.214 | 2.084 | 1.9816 | 1.8933 | 1.7908 | 1.6984 | 1.495 | 1.4223 | 1.3007 | 1.7242 | 1.6795 | 1.6423 | 1.587 | 1.5421 | 1.4792 | 1.354 | 1.2673 | 1.2135 | 1.1177 | 1.0316 | 0.82392 | 0.6612 | 0.48812
|  | DRUMNADROCHIT | CT |  |  |  | 1.559 | 0.9581 | 0.91509 | 0.87931 | 0.82407 | 0.7481 | 0.59862 | 0.39244 | 0.30514 | 0.25828 | 0.20402 | 0.14611 | -0.13426 | -0.25397 | -0.4023 | 2.6038 | 2.5505 | 2.4876 | 2.399 | 2.3195 | 2.2208 | 2.0973 | 1.9937 | 1.9503 | 1.8699 | 1.7962 | 1.583 | 1.4947 | 1.3547 | 1.7285 | 1.6908 | 1.6583 | 1.6069 | 1.5653 | 1.511 | 1.354 | 1.2673 | 1.2196 | 1.1634 | 1.1204 | 0.92162 | 0.78499 | 0.64157
|  | DRUMNADROCHIT | LW |  |  |  | 1.559 | 0.95374 | 0.90614 | 0.86825 | 0.80626 | 0.75727 | 0.63804 | 0.44513 | 0.35187 | 0.26848 | 0.15091 | 0.028161 | -0.28009 | -0.41621 | -0.60835 | 2.6037 | 2.5466 | 2.4812 | 2.3941 | 2.3124 | 2.214 | 2.084 | 1.9816 | 1.8933 | 1.7908 | 1.6984 | 1.495 | 1.4223 | 1.3007 | 1.7242 | 1.6795 | 1.6423 | 1.587 | 1.5421 | 1.4792 | 1.389 | 1.2971 | 1.2135 | 1.1177 | 1.0316 | 0.82392 | 0.6612 | 0.48812
|  | DRUMNADROCHIT | ST |  |  |  | 1.559 | 0.98035 | 0.95736 | 0.93182 | 0.90939 | 0.87193 | 0.84329 | 0.76317 | 0.69039 | 0.59432 | 0.4962 | 0.38903 | -0.10295 | -0.30194 | -0.39706 | 2.6267 | 2.5924 | 2.5498 | 2.5101 | 2.4575 | 2.4104 | 2.3491 | 2.3064 | 2.2319 | 2.1619 | 2.08 | 1.7192 | 1.5719 | 1.4626 | 1.7462 | 1.7278 | 1.7044 | 1.6831 | 1.6511 | 1.6233 | 1.582 | 1.5521 | 1.492 | 1.4359 | 1.3684 | 1.0583 | 0.90275 | 0.81112
|  | DRUMNADROCHIT | FS |  |  |  | 1.559 | 0.98811 | 0.96935 | 0.95241 | 0.92226 | 0.90929 | 0.8765 | 0.85382 | 0.81364 | 0.78808 | 0.73904 | 0.6963 | 0.34701 | -0.060843 | -0.26495 | 2.6478 | 2.6225 | 2.6028 | 2.5721 | 2.5534 | 2.5185 | 2.4894 | 2.4398 | 2.3997 | 2.3413 | 2.2885 | 1.9797 | 1.6419 | 1.422 | 1.7533 | 1.7382 | 1.7229 | 1.6978 | 1.6837 | 1.6551 | 1.6314 | 1.5969 | 1.5693 | 1.5257 | 1.4872 | 1.2582 | 1.0621 | 0.96573
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | YES | 0 | -0.0056211 | -0.030124 | -0.035678 | -0.052783 | -0.070538 | -0.094249 | -0.12309 | -0.13757 | -0.15457 | -0.1647 | -0.1793 | -0.22708 | -0.26361 | -0.30822 | 0.20038 | 0.1771 | 0.1647 | 0.15398 | 0.14246 | 0.12429 | 0.10091 | 0.08883 | 0.076578 | 0.069648 | 0.059069 | 0.021077 | -0.011502 | -0.05331 | 0.014796 | -0.010737 | -0.030168 | -0.045167 | -0.063681 | -0.089729 | -0.12197 | -0.1381 | -0.15454 | -0.1655 | -0.17932 | -0.23037 | -0.27123 | -0.32062
|  | DRUMRUNIE | CT |  |  |  | 0 | -0.0056211 | -0.026849 | -0.018893 | -0.040134 | -0.055424 | -0.071821 | -0.094505 | -0.11011 | -0.1247 | -0.133 | -0.14621 | -0.19097 | -0.21003 | -0.23446 | 0.20038 | 0.18308 | 0.18967 | 0.17072 | 0.16092 | 0.1517 | 0.13473 | 0.1229 | 0.11225 | 0.1061 | 0.095776 | 0.062627 | 0.047829 | 0.025472 | 0.014796 | -0.0059966 | -0.0046772 | -0.029164 | -0.045648 | -0.062493 | -0.088053 | -0.10384 | -0.11752 | -0.12663 | -0.13886 | -0.1838 | -0.20491 | -0.23078
|  | DRUMRUNIE | LW |  |  |  | 0 | -0.0037572 | -0.030124 | -0.035678 | -0.052783 | -0.070538 | -0.094249 | -0.12309 | -0.13757 | -0.15457 | -0.1647 | -0.1793 | -0.22708 | -0.26361 | -0.30822 | 0.20165 | 0.1771 | 0.1647 | 0.15398 | 0.14246 | 0.12429 | 0.10091 | 0.08883 | 0.076578 | 0.069648 | 0.059069 | 0.021077 | -0.011502 | -0.05331 | 0.016886 | -0.010737 | -0.030168 | -0.045167 | -0.063681 | -0.089729 | -0.12197 | -0.1381 | -0.15454 | -0.1655 | -0.17932 | -0.23037 | -0.27123 | -0.32062
|  | DRUMRUNIE | ST |  |  |  | 0 | 0.0010335 | -0.0087155 | -0.027062 | -0.045701 | -0.04228 | -0.051 | -0.06208 | -0.073433 | -0.084491 | -0.095906 | -0.10863 | -0.18265 | -0.23048 | -0.26419 | 0.2059 | 0.19907 | 0.18391 | 0.16898 | 0.1679 | 0.16744 | 0.16149 | 0.15206 | 0.14582 | 0.13945 | 0.12959 | 0.06816 | 0.024019 | -0.013164 | 0.021393 | 0.011962 | -0.0069951 | -0.025789 | -0.03289 | -0.038259 | -0.04914 | -0.062106 | -0.072631 | -0.08348 | -0.097291 | -0.17543 | -0.22769 | -0.26643
|  | DRUMRUNIE | FS |  |  |  | 0 | 0.0054588 | -0.0014995 | -0.0098649 | -0.01955 | -0.029738 | -0.020281 | -0.022858 | -0.031158 | -0.042345 | -0.051827 | -0.06084 | -0.10938 | -0.16455 | -0.18618 | 0.20807 | 0.20289 | 0.19535 | 0.18653 | 0.17726 | 0.17787 | 0.17824 | 0.17295 | 0.16226 | 0.15636 | 0.1488 | 0.11712 | 0.08034 | 0.057517 | 0.025545 | 0.018863 | 0.010301 | 0.00043047 | -0.0099333 | -0.013335 | -0.012728 | -0.02042 | -0.034539 | -0.042846 | -0.053665 | -0.10149 | -0.15443 | -0.1783
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.591 | -2.4635 | -2.5303 | -2.6411 | -2.778 | -2.9263 | -3.0932 | -3.2851 | -3.4406 | -3.5932 | -3.7534 | -3.8996 | -4.3632 | -4.7518 | -5.1356 | -2.1504 | -2.1891 | -2.2447 | -2.3148 | -2.388 | -2.472 | -2.5681 | -2.6558 | -2.7469 | -2.838 | -2.9213 | -3.1644 | -3.306 | -3.4367 | -3.2375 | -3.3182 | -3.4271 | -3.5629 | -3.7025 | -3.8724 | -4.0719 | -4.2584 | -4.4249 | -4.6119 | -4.7826 | -5.2624 | -5.5324 | -5.8232
|  | DRYMEN | CT |  |  |  | 0.591 | -2.4635 | -2.5303 | -2.6411 | -2.778 | -2.9263 | -3.0932 | -3.2851 | -3.4406 | -3.5549 | -3.6755 | -3.7814 | -4.2593 | -4.7088 | -5.0817 | -2.1504 | -2.1891 | -2.2447 | -2.3148 | -2.388 | -2.472 | -2.5681 | -2.6556 | -2.715 | -2.7841 | -2.846 | -3.0869 | -3.2483 | -3.3781 | -3.2375 | -3.3182 | -3.4271 | -3.5629 | -3.7025 | -3.8724 | -4.0719 | -4.2584 | -4.3671 | -4.5169 | -4.6543 | -5.1566 | -5.4678 | -5.7399
|  | DRYMEN | LW |  |  |  | 0.591 | -2.4594 | -2.5221 | -2.6266 | -2.756 | -2.8975 | -3.0678 | -3.2603 | -3.4277 | -3.5932 | -3.7534 | -3.8996 | -4.3632 | -4.7518 | -5.1356 | -2.1495 | -2.1864 | -2.2382 | -2.3055 | -2.3774 | -2.464 | -2.5628 | -2.6558 | -2.7469 | -2.838 | -2.9213 | -3.1644 | -3.306 | -3.4367 | -3.2339 | -3.3096 | -3.4118 | -3.5497 | -3.693 | -3.8582 | -4.0584 | -4.2514 | -4.4249 | -4.6119 | -4.7826 | -5.2624 | -5.5324 | -5.8232
|  | DRYMEN | ST |  |  |  | 0.591 | -2.4416 | -2.48 | -2.5344 | -2.59 | -2.655 | -2.7209 | -2.795 | -2.8619 | -2.9482 | -3.0395 | -3.1376 | -3.6463 | -3.9514 | -4.1736 | -2.1389 | -2.1592 | -2.1891 | -2.2187 | -2.2556 | -2.2919 | -2.335 | -2.3727 | -2.4235 | -2.4792 | -2.5394 | -2.8403 | -3.0036 | -3.1166 | -3.2128 | -3.2541 | -3.3154 | -3.3698 | -3.4436 | -3.5122 | -3.598 | -3.6613 | -3.7587 | -3.8665 | -3.9825 | -4.5246 | -4.8129 | -5.0241
|  | DRYMEN | FS |  |  |  | 0.591 | -2.4222 | -2.45 | -2.4783 | -2.5082 | -2.5447 | -2.5849 | -2.6225 | -2.6851 | -2.7491 | -2.8198 | -2.8921 | -3.3282 | -3.7919 | -4.1278 | -2.1299 | -2.1462 | -2.1626 | -2.18 | -2.2029 | -2.2284 | -2.2508 | -2.287 | -2.3224 | -2.364 | -2.4047 | -2.6561 | -2.913 | -3.0837 | -3.1951 | -3.2306 | -3.2633 | -3.2952 | -3.342 | -3.3946 | -3.4373 | -3.5112 | -3.5725 | -3.6558 | -3.7354 | -4.2086 | -4.6922 | -4.9745
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 0.288 | 1.0978 | 1.012 | 0.9003 | 0.75789 | 0.60269 | 0.43526 | 0.24765 | 0.14478 | 0.064634 | -0.016216 | -0.11362 | -0.41218 | -0.54949 | -0.71272 | 1.4123 | 1.3793 | 1.3416 | 1.2743 | 1.2222 | 1.1649 | 1.0896 | 1.0269 | 0.9428 | 0.88068 | 0.8002 | 0.59431 | 0.51729 | 0.40703 | 1.3238 | 1.243 | 1.1548 | 1.0392 | 0.90592 | 0.76426 | 0.61426 | 0.51476 | 0.40671 | 0.33486 | 0.23624 | -0.014163 | -0.12304 | -0.28039
|  | DRYNOCH | CT |  |  |  | 0.288 | 1.0978 | 1.012 | 0.9003 | 0.75789 | 0.60269 | 0.43526 | 0.24765 | 0.14478 | 0.064634 | -0.016216 | -0.049563 | -0.27251 | -0.37513 | -0.50089 | 1.4123 | 1.381 | 1.3416 | 1.2743 | 1.2222 | 1.1649 | 1.0896 | 1.0269 | 0.96385 | 0.89585 | 0.86554 | 0.69186 | 0.61984 | 0.50318 | 1.3238 | 1.243 | 1.1548 | 1.0392 | 0.90592 | 0.76426 | 0.61426 | 0.51476 | 0.43553 | 0.35189 | 0.32483 | 0.1181 | 0.040609 | -0.060376
|  | DRYNOCH | LW |  |  |  | 0.288 | 1.1108 | 1.0285 | 0.92514 | 0.80287 | 0.67076 | 0.49658 | 0.31996 | 0.21119 | 0.076464 | -0.0096692 | -0.11362 | -0.41218 | -0.54949 | -0.71272 | 1.4146 | 1.3793 | 1.3442 | 1.3027 | 1.2603 | 1.1977 | 1.1244 | 1.0458 | 0.9428 | 0.88068 | 0.8002 | 0.59431 | 0.51729 | 0.40703 | 1.3332 | 1.2518 | 1.1662 | 1.061 | 0.94824 | 0.79065 | 0.64247 | 0.53961 | 0.40671 | 0.33486 | 0.23624 | -0.014163 | -0.12304 | -0.28039
|  | DRYNOCH | ST |  |  |  | 0.288 | 1.1241 | 1.0767 | 1.01 | 0.93591 | 0.87108 | 0.79205 | 0.71632 | 0.63535 | 0.55799 | 0.46229 | 0.36733 | -0.058139 | -0.22825 | -0.29985 | 1.4226 | 1.4107 | 1.3881 | 1.3635 | 1.3415 | 1.3139 | 1.2848 | 1.2497 | 1.2095 | 1.1614 | 1.1099 | 0.81658 | 0.67899 | 0.58771 | 1.3474 | 1.3075 | 1.2505 | 1.184 | 1.133 | 1.0632 | 0.99991 | 0.92535 | 0.86241 | 0.77439 | 0.6899 | 0.30755 | 0.16593 | 0.10539
|  | DRYNOCH | FS |  |  |  | 0.288 | 1.1552 | 1.1232 | 1.0973 | 1.0722 | 1.0401 | 1.0162 | 0.97796 | 0.92523 | 0.85516 | 0.78356 | 0.72927 | 0.33457 | -0.045483 | -0.22258 | 1.4281 | 1.4197 | 1.4086 | 1.397 | 1.3826 | 1.3695 | 1.3503 | 1.3297 | 1.3003 | 1.2696 | 1.2437 | 1.0264 | 0.75731 | 0.55658 | 1.3716 | 1.3429 | 1.3177 | 1.2941 | 1.2618 | 1.243 | 1.2046 | 1.1597 | 1.0937 | 1.0262 | 0.98605 | 0.62995 | 0.32271 | 0.19389
| KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0.407 | 0.99976 | 0.92346 | 0.82226 | 0.72124 | 0.5513 | 0.27557 | -0.019289 | -0.2314 | -0.46213 | -0.66938 | -0.82745 | -1.3979 | -1.7034 | -1.9625 | 2.0323 | 1.9706 | 1.9024 | 1.8394 | 1.7642 | 1.6596 | 1.536 | 1.4432 | 1.3222 | 1.2104 | 1.1182 | 0.8362 | 0.70137 | 0.59814 | 1.2459 | 1.1468 | 0.97347 | 0.8084 | 0.5972 | 0.33922 | 0.057956 | -0.13942 | -0.36336 | -0.56456 | -0.71712 | -1.2546 | -1.5361 | -1.7801
|  | DUFFTOWN | CT |  |  |  | 0.407 | 0.99976 | 0.93574 | 0.837 | 0.72124 | 0.56777 | 0.30425 | 0.019046 | -0.20503 | -0.39155 | -0.56629 | -0.68997 | -1.2968 | -1.6884 | -1.9625 | 2.0323 | 1.9886 | 1.929 | 1.8499 | 1.7759 | 1.6924 | 1.5917 | 1.492 | 1.4073 | 1.3233 | 1.2589 | 1.0188 | 0.87296 | 0.6227 | 1.2459 | 1.1578 | 0.99592 | 0.82756 | 0.61778 | 0.37733 | 0.11427 | -0.10001 | -0.27784 | -0.44731 | -0.5675 | -1.137 | -1.4881 | -1.7403
|  | DUFFTOWN | LW |  |  |  | 0.407 | 1.0015 | 0.92346 | 0.82226 | 0.72654 | 0.5513 | 0.27557 | -0.019289 | -0.2314 | -0.46213 | -0.66938 | -0.82745 | -1.3979 | -1.7034 | -1.9513 | 2.0325 | 1.9706 | 1.9024 | 1.8394 | 1.7642 | 1.6596 | 1.536 | 1.4432 | 1.3222 | 1.2104 | 1.1182 | 0.8362 | 0.70137 | 0.59814 | 1.2535 | 1.1468 | 0.97347 | 0.8084 | 0.5972 | 0.33922 | 0.057956 | -0.13942 | -0.36336 | -0.56456 | -0.71712 | -1.2546 | -1.5361 | -1.7801
|  | DUFFTOWN | ST |  |  |  | 0.407 | 1.0197 | 0.98218 | 0.92792 | 0.88344 | 0.82628 | 0.75985 | 0.69781 | 0.63575 | 0.5538 | 0.47642 | 0.38019 | -0.18985 | -0.69123 | -1.1072 | 2.0454 | 2.021 | 1.9811 | 1.949 | 1.9095 | 1.864 | 1.8216 | 1.7766 | 1.716 | 1.6595 | 1.589 | 1.1758 | 0.95221 | 0.81733 | 1.2737 | 1.2138 | 1.1341 | 1.068 | 0.99012 | 0.90035 | 0.8249 | 0.75215 | 0.66164 | 0.58519 | 0.48743 | -0.12778 | -0.58202 | -0.95504
|  | DUFFTOWN | FS |  |  |  | 0.407 | 1.0303 | 1.004 | 0.96925 | 0.94593 | 0.90905 | 0.86648 | 0.8185 | 0.77268 | 0.70938 | 0.64679 | 0.57812 | 0.13767 | -0.40458 | -0.86883 | 2.0506 | 2.033 | 2.0082 | 1.992 | 1.9652 | 1.9338 | 1.8969 | 1.8662 | 1.8213 | 1.7769 | 1.7298 | 1.4474 | 1.1473 | 0.8344 | 1.2971 | 1.2571 | 1.208 | 1.1763 | 1.1292 | 1.0741 | 1.0133 | 0.94903 | 0.86281 | 0.78043 | 0.69143 | 0.18907 | -0.32509 | -0.75033
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 2.573 | -0.51058 | -0.7839 | -1.2787 | -1.928 | -2.6639 | -3.4915 | -4.478 | -5.5343 | -6.2688 | -7.2397 | -8.1714 | -11.3133 | -13.2293 | -15.1586 | 1.9552 | 1.7708 | 1.512 | 1.1559 | 0.76784 | 0.34353 | -0.19329 | -0.7586 | -1.0511 | -1.5889 | -2.115 | -3.6893 | -4.7265 | -5.9903 | 1.5771 | 1.3246 | 0.88796 | 0.30211 | -0.35152 | -1.0825 | -1.9738 | -2.927 | -3.5598 | -4.4353 | -5.2741 | -8.0358 | -9.7038 | -11.3431
|  | DUNBLANE | CT |  |  |  | 2.573 | -0.50304 | -0.77675 | -1.2738 | -1.928 | -2.6639 | -3.4859 | -4.4729 | -5.484 | -5.9911 | -6.776 | -7.5115 | -10.7777 | -13.2293 | -15.0972 | 1.9552 | 1.7708 | 1.512 | 1.1559 | 0.76784 | 0.34353 | -0.19329 | -0.7586 | -0.93801 | -1.3726 | -1.7974 | -3.5019 | -4.7265 | -5.9903 | 1.5828 | 1.3305 | 0.88926 | 0.30211 | -0.35152 | -1.0825 | -1.9738 | -2.8907 | -3.3248 | -4.0222 | -4.674 | -7.5956 | -9.6967 | -11.2709
|  | DUNBLANE | LW |  |  |  | 2.573 | -0.51058 | -0.7839 | -1.2787 | -1.917 | -2.6342 | -3.4915 | -4.478 | -5.5343 | -6.2688 | -7.2397 | -8.1714 | -11.3133 | -13.2192 | -15.1586 | 1.9562 | 1.7763 | 1.5335 | 1.2029 | 0.83846 | 0.38859 | -0.15112 | -0.72635 | -1.0511 | -1.5889 | -2.115 | -3.6893 | -4.5335 | -5.4456 | 1.5771 | 1.3246 | 0.88796 | 0.31936 | -0.31377 | -1.0792 | -1.972 | -2.927 | -3.5598 | -4.4353 | -5.2741 | -8.0358 | -9.7038 | -11.3431
|  | DUNBLANE | ST |  |  |  | 2.573 | -0.42107 | -0.57457 | -0.75559 | -0.97908 | -1.2244 | -1.5068 | -1.8059 | -2.0952 | -2.4945 | -2.9084 | -3.3824 | -5.7347 | -7.7579 | -9.4832 | 2.011 | 1.9169 | 1.8041 | 1.6615 | 1.504 | 1.3209 | 1.12 | 0.92529 | 0.64606 | 0.35276 | 0.0088285 | -1.4865 | -2.695 | -3.8792 | 1.6615 | 1.5267 | 1.3693 | 1.1742 | 0.96368 | 0.71701 | 0.45095 | 0.19494 | -0.16604 | -0.5423 | -0.97504 | -3.0497 | -4.7752 | -6.2153
|  | DUNBLANE | FS |  |  |  | 2.573 | -0.36866 | -0.48121 | -0.63104 | -0.81377 | -1.0384 | -1.2372 | -1.4699 | -1.7781 | -2.1009 | -2.4552 | -2.841 | -4.8672 | -7.3642 | -9.6222 | 2.0335 | 1.9587 | 1.8655 | 1.7478 | 1.5972 | 1.4703 | 1.3077 | 1.1056 | 0.89242 | 0.65242 | 0.38594 | -0.94776 | -2.8047 | -4.817 | 1.7077 | 1.6095 | 1.4813 | 1.3237 | 1.1293 | 0.96143 | 0.75714 | 0.48517 | 0.20219 | -0.11308 | -0.45728 | -2.2291 | -4.4315 | -6.3784
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0.034 | 16.682 | 16.4974 | 16.0985 | 15.6387 | 15.1257 | 14.4874 | 13.6359 | 12.638 | 11.5019 | 10.9312 | 10.293 | 8.3855 | 7.5273 | 6.7968 | 18.9023 | 18.7353 | 18.5173 | 18.2799 | 17.9745 | 17.6659 | 17.1656 | 16.5065 | 15.7011 | 15.3095 | 14.9576 | 13.7886 | 13.0075 | 11.7585 | 18.0297 | 17.8556 | 17.4965 | 17.0819 | 16.6183 | 16.0279 | 15.2413 | 14.3109 | 13.2402 | 12.7206 | 12.1225 | 10.3648 | 9.6504 | 8.9843
|  | DUNOON | CT |  |  |  | 0.034 | 16.6968 | 16.5089 | 16.1458 | 15.7268 | 15.22 | 14.6968 | 13.9449 | 12.9494 | 12.0146 | 11.1923 | 10.9486 | 8.6183 | 7.5273 | 6.7968 | 18.9023 | 18.7353 | 18.5173 | 18.2799 | 17.9745 | 17.6659 | 17.1766 | 16.517 | 15.8864 | 15.3095 | 15.2037 | 13.7886 | 13.0075 | 11.9781 | 18.0414 | 17.8623 | 17.5304 | 17.1481 | 16.6831 | 16.2011 | 15.5061 | 14.5804 | 13.7102 | 12.9408 | 12.7338 | 10.6151 | 9.6504 | 8.9843
|  | DUNOON | LW |  |  |  | 0.034 | 16.682 | 16.4974 | 16.0985 | 15.6387 | 15.1257 | 14.4874 | 13.6359 | 12.638 | 11.5019 | 10.9312 | 10.293 | 8.3855 | 7.9278 | 7.2905 | 18.909 | 18.7605 | 18.5621 | 18.3337 | 18.0762 | 17.7022 | 17.1656 | 16.5065 | 15.7011 | 15.3693 | 14.9576 | 13.8812 | 13.6872 | 13.2661 | 18.0297 | 17.8556 | 17.4965 | 17.0819 | 16.6183 | 16.0279 | 15.2413 | 14.3109 | 13.2402 | 12.7206 | 12.1225 | 10.3648 | 9.9567 | 9.3574
|  | DUNOON | ST |  |  |  | 0.034 | 16.7465 | 16.6543 | 16.565 | 16.4781 | 16.3661 | 16.2453 | 15.9955 | 15.6169 | 15.1061 | 14.7141 | 14.4168 | 13.1369 | 12.168 | 11.171 | 18.9538 | 18.8818 | 18.7979 | 18.7153 | 18.6076 | 18.4802 | 18.2488 | 17.9084 | 17.4516 | 17.0938 | 16.8014 | 15.6215 | 14.8108 | 13.8225 | 18.0911 | 18.007 | 17.9241 | 17.8436 | 17.7382 | 17.6195 | 17.382 | 17.0196 | 16.528 | 16.1505 | 15.8264 | 14.5031 | 13.6779 | 12.8754
|  | DUNOON | FS |  |  |  | 0.034 | 16.7927 | 16.7371 | 16.6472 | 16.5543 | 16.4393 | 16.3281 | 16.109 | 15.8195 | 15.4174 | 15.077 | 14.8115 | 12.6978 | 11.05 | 9.435 | 18.9649 | 18.9103 | 18.8388 | 18.7631 | 18.664 | 18.5611 | 18.3567 | 18.1204 | 17.7769 | 17.4813 | 17.2474 | 15.5 | 13.8997 | 11.7585 | 18.1308 | 18.0797 | 17.9983 | 17.9139 | 17.8077 | 17.702 | 17.4955 | 17.2252 | 16.8453 | 16.5234 | 16.274 | 14.2912 | 12.7934 | 11.3345
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 0.49 | -1.7738 | -1.8456 | -1.9775 | -2.1281 | -2.2962 | -2.4659 | -2.6759 | -2.7457 | -2.8001 | -2.8717 | -2.9639 | -3.2278 | -3.3645 | -3.5512 | 1.1822 | 1.1353 | 1.0677 | 0.99081 | 0.89986 | 0.82376 | 0.70168 | 0.61613 | 0.50786 | 0.4452 | 0.36232 | 0.16401 | 0.094233 | -0.036407 | 0.75749 | 0.68415 | 0.56609 | 0.43847 | 0.28431 | 0.15162 | -0.047033 | -0.15548 | -0.26993 | -0.34432 | -0.44864 | -0.70302 | -0.80773 | -0.97524
|  | DUNVEGAN | CT |  |  |  | 0.49 | -1.7738 | -1.8456 | -1.9775 | -2.1281 | -2.2962 | -2.4659 | -2.6759 | -2.7457 | -2.8001 | -2.8466 | -2.9039 | -3.1232 | -3.2405 | -3.3878 | 1.1822 | 1.1353 | 1.0677 | 0.99081 | 0.89986 | 0.82376 | 0.70168 | 0.61613 | 0.54737 | 0.50273 | 0.43696 | 0.23592 | 0.15379 | 0.015485 | 0.75749 | 0.68415 | 0.56609 | 0.43847 | 0.28431 | 0.15162 | -0.047033 | -0.15548 | -0.24126 | -0.28713 | -0.36237 | -0.59173 | -0.67676 | -0.79685
|  | DUNVEGAN | LW |  |  |  | 0.49 | -1.7596 | -1.83 | -1.9553 | -2.0916 | -2.2377 | -2.4056 | -2.6031 | -2.6816 | -2.7924 | -2.8717 | -2.9639 | -3.2278 | -3.3645 | -3.5512 | 1.1876 | 1.137 | 1.0694 | 0.9976 | 0.92257 | 0.82858 | 0.70214 | 0.61836 | 0.50786 | 0.4452 | 0.36232 | 0.16401 | 0.094233 | -0.036407 | 0.76772 | 0.69349 | 0.58053 | 0.46091 | 0.33275 | 0.18302 | -0.013642 | -0.12497 | -0.26993 | -0.34432 | -0.44864 | -0.70302 | -0.80773 | -0.97524
|  | DUNVEGAN | ST |  |  |  | 0.49 | -1.7508 | -1.8018 | -1.8697 | -1.9416 | -2.0067 | -2.076 | -2.1531 | -2.2253 | -2.2949 | -2.3719 | -2.4554 | -2.8382 | -2.9947 | -3.0611 | 1.1988 | 1.1738 | 1.1369 | 1.0929 | 1.0594 | 1.0198 | 0.9681 | 0.91279 | 0.86303 | 0.79983 | 0.72761 | 0.3984 | 0.2604 | 0.16377 | 0.78344 | 0.73945 | 0.67973 | 0.60894 | 0.55557 | 0.49282 | 0.4132 | 0.33164 | 0.26339 | 0.17551 | 0.074825 | -0.33019 | -0.46891 | -0.52343
|  | DUNVEGAN | FS |  |  |  | 0.49 | -1.7138 | -1.7454 | -1.7645 | -1.788 | -1.8067 | -1.8326 | -1.8621 | -1.9146 | -1.9785 | -2.0325 | -2.0953 | -2.4655 | -2.8447 | -3.0093 | 1.2111 | 1.1935 | 1.1763 | 1.1521 | 1.1355 | 1.1077 | 1.0742 | 1.0391 | 0.9863 | 0.94959 | 0.89775 | 0.59039 | 0.3131 | 0.10591 | 0.80967 | 0.78062 | 0.75817 | 0.72556 | 0.70666 | 0.67063 | 0.62837 | 0.57893 | 0.50519 | 0.45756 | 0.38568 | -0.014997 | -0.34012 | -0.4693
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.935 | 3.4244 | -0.93539 | -3.8844 | -6.9728 | -9.2474 | -12.1166 | -16.2203 | -17.2714 | -18.2531 | -19.3245 | -20.3253 | -25.5737 | -32.0108 | -39.0887 | 6.5198 | 1.4159 | -2.0002 | -5.5141 | -7.9771 | -11.0615 | -15.5019 | -16.2488 | -16.9654 | -17.7893 | -18.525 | -23.9315 | -31.8467 | -40.5885 | 5.6775 | 0.74857 | -2.6385 | -6.0928 | -8.5416 | -11.8459 | -16.626 | -17.644 | -18.5699 | -19.6054 | -20.522 | -26.4773 | -34.462 | -43.2612
|  | DYCE NORTH | CT |  |  |  | 0.935 | 4.1246 | 2.2218 | 1.4353 | -1.7262 | -3.1595 | -4.6585 | -7.6204 | -8.8449 | -9.8417 | -10.8113 | -11.6748 | -14.9284 | -17.2244 | -19.6804 | 7.2934 | 5.1922 | 4.5323 | 1.0094 | -0.33398 | -1.7695 | -4.7629 | -5.7232 | -6.6132 | -7.4596 | -8.2622 | -11.1793 | -13.7077 | -16.5887 | 6.3832 | 4.4098 | 3.7637 | 0.28195 | -1.0577 | -2.665 | -5.9365 | -7.1296 | -8.1586 | -9.1576 | -10.0764 | -13.5356 | -16.2573 | -19.2419
|  | DYCE NORTH | LW |  |  |  | 0.935 | 3.4244 | -0.93539 | -3.8844 | -6.9728 | -9.2474 | -12.1166 | -16.2203 | -17.2714 | -18.2531 | -19.3245 | -20.3253 | -25.5737 | -32.0108 | -39.0887 | 6.5198 | 1.4159 | -2.0002 | -5.5141 | -7.9771 | -11.0615 | -15.5019 | -16.2488 | -16.9654 | -17.7893 | -18.525 | -23.9315 | -31.8467 | -40.5885 | 5.6775 | 0.74857 | -2.6385 | -6.0928 | -8.5416 | -11.8459 | -16.626 | -17.644 | -18.5699 | -19.6054 | -20.522 | -26.4773 | -34.462 | -43.2612
|  | DYCE NORTH | ST |  |  |  | 0.935 | 4.1666 | 2.3787 | 0.55186 | -1.0983 | -2.4498 | -3.3113 | -4.4802 | -5.5815 | -6.6982 | -7.7307 | -8.5805 | -17.8467 | -26.0262 | -32.9812 | 7.3392 | 5.3553 | 3.1262 | 1.2038 | -0.24504 | -1.0447 | -2.0708 | -3.0703 | -4.0711 | -4.9668 | -5.6215 | -15.2051 | -24.7658 | -33.1838 | 6.4398 | 4.6105 | 2.4223 | 0.58105 | -0.82441 | -1.6445 | -2.7362 | -3.7933 | -4.8689 | -5.9045 | -6.7344 | -17.1481 | -26.9837 | -35.5415
|  | DYCE NORTH | FS |  |  |  | 0.935 | 4.9207 | 3.607 | 2.851 | 1.8485 | 0.75107 | -0.24721 | -1.6032 | -2.6765 | -3.8296 | -4.9968 | -5.7267 | -9.9567 | -12.8172 | -15.7891 | 8.175 | 6.7178 | 5.8193 | 4.6421 | 3.4088 | 2.3597 | 0.93616 | -0.13587 | -1.2677 | -2.4363 | -3.0514 | -6.4725 | -8.6326 | -11.2691 | 7.2041 | 5.8687 | 5.0001 | 3.8939 | 2.7072 | 1.653 | 0.18751 | -0.91831 | -2.0992 | -3.3025 | -3.9686 | -8.0102 | -10.7477 | -13.8176
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0.012 | 0.71625 | 0.70569 | 0.69133 | 0.67671 | 0.65965 | 0.63776 | 0.61231 | 0.59723 | 0.57715 | 0.55592 | 0.54942 | 0.51028 | 0.49535 | 0.4787 | 0.81327 | 0.80971 | 0.80008 | 0.79428 | 0.78527 | 0.7727 | 0.75821 | 0.74878 | 0.73444 | 0.71951 | 0.71459 | 0.69491 | 0.68889 | 0.68046 | 0.79484 | 0.78468 | 0.77122 | 0.75765 | 0.74172 | 0.721 | 0.69694 | 0.68286 | 0.66283 | 0.64239 | 0.63667 | 0.60095 | 0.58773 | 0.57267
|  | EDAY | CT |  |  |  | 0.012 | 0.71625 | 0.70569 | 0.69133 | 0.67671 | 0.65965 | 0.63776 | 0.61231 | 0.59723 | 0.58132 | 0.56457 | 0.54942 | 0.52249 | 0.5087 | 0.49452 | 0.81327 | 0.80971 | 0.80171 | 0.79428 | 0.78527 | 0.7727 | 0.75821 | 0.74878 | 0.73786 | 0.7258 | 0.71459 | 0.7008 | 0.69275 | 0.68166 | 0.79484 | 0.78468 | 0.77122 | 0.75765 | 0.74172 | 0.721 | 0.69694 | 0.68286 | 0.66758 | 0.65138 | 0.63667 | 0.61232 | 0.59992 | 0.58723
|  | EDAY | LW |  |  |  | 0.012 | 0.71802 | 0.70928 | 0.69593 | 0.68104 | 0.6623 | 0.64161 | 0.61621 | 0.60141 | 0.57715 | 0.55592 | 0.55144 | 0.51028 | 0.49535 | 0.4787 | 0.81396 | 0.81154 | 0.80463 | 0.79691 | 0.78645 | 0.77515 | 0.76059 | 0.75159 | 0.73444 | 0.71951 | 0.71905 | 0.69491 | 0.68889 | 0.68046 | 0.79649 | 0.78805 | 0.77553 | 0.76146 | 0.74368 | 0.72421 | 0.70005 | 0.68624 | 0.66283 | 0.64239 | 0.63911 | 0.60095 | 0.58773 | 0.57267
|  | EDAY | ST |  |  |  | 0.012 | 0.72535 | 0.71292 | 0.69601 | 0.69373 | 0.67862 | 0.66723 | 0.65646 | 0.64625 | 0.63176 | 0.61446 | 0.6029 | 0.53791 | 0.51324 | 0.50274 | 0.82105 | 0.81199 | 0.80008 | 0.80534 | 0.79624 | 0.79042 | 0.78511 | 0.77959 | 0.77065 | 0.75922 | 0.75291 | 0.71172 | 0.69668 | 0.68803 | 0.80377 | 0.79174 | 0.77545 | 0.77362 | 0.75911 | 0.74846 | 0.73833 | 0.72883 | 0.715 | 0.69838 | 0.6878 | 0.6269 | 0.60421 | 0.59453
|  | EDAY | FS |  |  |  | 0.012 | 0.73063 | 0.72172 | 0.71268 | 0.70672 | 0.70879 | 0.70474 | 0.6965 | 0.69003 | 0.68177 | 0.66938 | 0.65893 | 0.59237 | 0.5405 | 0.51885 | 0.82362 | 0.81668 | 0.80901 | 0.8078 | 0.81058 | 0.8082 | 0.80217 | 0.79893 | 0.79432 | 0.78614 | 0.77982 | 0.73602 | 0.70443 | 0.68413 | 0.80529 | 0.79992 | 0.7912 | 0.78524 | 0.78757 | 0.78382 | 0.7758 | 0.76975 | 0.76206 | 0.75015 | 0.7402 | 0.67692 | 0.62918 | 0.60959
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0 | -0.031165 | -0.031703 | -0.032216 | -0.032775 | -0.033509 | -0.034246 | -0.035304 | -0.036404 | -0.037534 | -0.038611 | -0.039562 | -0.040977 | -0.041246 | -0.041614 | 0.66366 | 0.66321 | 0.66281 | 0.66238 | 0.66179 | 0.66122 | 0.66034 | 0.65933 | 0.6583 | 0.65731 | 0.65644 | 0.6553 | 0.65519 | 0.65502 | 0.77089 | 0.77036 | 0.76986 | 0.76932 | 0.76861 | 0.7679 | 0.76687 | 0.76579 | 0.76467 | 0.76361 | 0.76268 | 0.76131 | 0.76108 | 0.76076
|  | EDAY TIDAL | CT |  |  |  | 0 | -0.031165 | -0.031703 | -0.032216 | -0.032775 | -0.033509 | -0.034246 | -0.035304 | -0.036404 | -0.037228 | -0.038175 | -0.039069 | -0.040925 | -0.041207 | -0.041514 | 0.66366 | 0.66321 | 0.66281 | 0.66238 | 0.66179 | 0.66122 | 0.66034 | 0.65933 | 0.65859 | 0.6577 | 0.65686 | 0.6553 | 0.65519 | 0.65505 | 0.77089 | 0.77036 | 0.76986 | 0.76932 | 0.76861 | 0.7679 | 0.76687 | 0.76579 | 0.76498 | 0.76404 | 0.76316 | 0.76135 | 0.76111 | 0.76085
|  | EDAY TIDAL | LW |  |  |  | 0 | -0.031123 | -0.031613 | -0.032085 | -0.032697 | -0.033254 | -0.03418 | -0.035245 | -0.036263 | -0.037534 | -0.038611 | -0.039562 | -0.040977 | -0.041246 | -0.041614 | 0.66368 | 0.66327 | 0.66291 | 0.66244 | 0.66203 | 0.66128 | 0.6604 | 0.65948 | 0.6583 | 0.65731 | 0.65644 | 0.6553 | 0.6552 | 0.65502 | 0.77092 | 0.77044 | 0.76999 | 0.7694 | 0.76886 | 0.76796 | 0.76693 | 0.76593 | 0.76467 | 0.76361 | 0.76268 | 0.76131 | 0.76108 | 0.76076
|  | EDAY TIDAL | ST |  |  |  | 0 | -0.030996 | -0.031233 | -0.031557 | -0.031932 | -0.032333 | -0.032791 | -0.033309 | -0.033873 | -0.034594 | -0.035353 | -0.036179 | -0.040128 | -0.040898 | -0.041106 | 0.66381 | 0.66364 | 0.66342 | 0.66314 | 0.66285 | 0.6625 | 0.66208 | 0.66161 | 0.66097 | 0.66031 | 0.65957 | 0.656 | 0.65545 | 0.65537 | 0.77105 | 0.77082 | 0.77051 | 0.77015 | 0.76976 | 0.76932 | 0.76882 | 0.76827 | 0.76756 | 0.76682 | 0.766 | 0.76212 | 0.76139 | 0.7612
|  | EDAY TIDAL | FS |  |  |  | 0 | -0.030891 | -0.03106 | -0.031229 | -0.031433 | -0.031648 | -0.031899 | -0.032188 | -0.032587 | -0.033081 | -0.03359 | -0.034144 | -0.037558 | -0.040356 | -0.040719 | 0.66386 | 0.66373 | 0.66359 | 0.66341 | 0.66323 | 0.66301 | 0.66275 | 0.66242 | 0.662 | 0.66156 | 0.66108 | 0.65806 | 0.6557 | 0.65553 | 0.77115 | 0.77098 | 0.77082 | 0.77062 | 0.77041 | 0.77016 | 0.76988 | 0.76949 | 0.76901 | 0.76851 | 0.76797 | 0.76462 | 0.76189 | 0.76156
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 0.696 | 1.6214 | 1.5453 | 1.4499 | 1.3558 | 1.192 | 0.95767 | 0.71911 | 0.42069 | -0.050869 | -0.47127 | -0.90168 | -2.5808 | -3.2059 | -3.4331 | 1.6223 | 1.5591 | 1.4851 | 1.4191 | 1.3475 | 1.2457 | 1.1429 | 0.91194 | 0.48545 | 0.081502 | -0.32523 | -1.8733 | -2.3297 | -2.4028 | 1.871 | 1.776 | 1.6153 | 1.4581 | 1.2835 | 1.0629 | 0.84087 | 0.54445 | 0.074698 | -0.34422 | -0.77353 | -2.4185 | -3.0041 | -3.2162
|  | EDZELL | CT |  |  |  | 0.696 | 1.6214 | 1.5488 | 1.4559 | 1.3558 | 1.1942 | 0.97265 | 0.73224 | 0.4565 | 0.072862 | -0.37899 | -0.77787 | -2.491 | -3.1578 | -3.3905 | 1.6223 | 1.5673 | 1.4987 | 1.4237 | 1.348 | 1.2648 | 1.172 | 0.97035 | 0.63239 | 0.207 | -0.18918 | -1.7181 | -2.1635 | -2.2251 | 1.8728 | 1.776 | 1.6209 | 1.467 | 1.287 | 1.0829 | 0.86203 | 0.58944 | 0.2097 | -0.24198 | -0.64094 | -2.3183 | -2.9371 | -3.1456
|  | EDZELL | LW |  |  |  | 0.696 | 1.6231 | 1.5453 | 1.4499 | 1.3619 | 1.192 | 0.95767 | 0.71911 | 0.42069 | -0.050869 | -0.47127 | -0.90168 | -2.5808 | -3.2059 | -3.4331 | 1.6223 | 1.5591 | 1.4851 | 1.4191 | 1.3475 | 1.2457 | 1.1429 | 0.91194 | 0.48545 | 0.081502 | -0.32523 | -1.8733 | -2.3297 | -2.4028 | 1.871 | 1.7838 | 1.6153 | 1.4581 | 1.2835 | 1.0629 | 0.84087 | 0.54445 | 0.074698 | -0.34422 | -0.77353 | -2.4185 | -3.0041 | -3.2162
|  | EDZELL | ST |  |  |  | 0.696 | 1.6399 | 1.5943 | 1.5318 | 1.4828 | 1.4259 | 1.3688 | 1.2721 | 1.0802 | 0.73185 | 0.31699 | -0.10973 | -1.8912 | -2.6146 | -2.878 | 1.6358 | 1.6022 | 1.555 | 1.5177 | 1.4747 | 1.4342 | 1.3841 | 1.2201 | 0.88654 | 0.47329 | 0.053293 | -1.6644 | -2.1994 | -2.288 | 1.8862 | 1.8348 | 1.7294 | 1.6453 | 1.5513 | 1.4637 | 1.3643 | 1.1734 | 0.82618 | 0.41533 | -0.0094476 | -1.7668 | -2.4441 | -2.6815
|  | EDZELL | FS |  |  |  | 0.696 | 1.6587 | 1.6268 | 1.5942 | 1.5671 | 1.5386 | 1.504 | 1.47 | 1.3539 | 1.1346 | 0.89784 | 0.63408 | -0.9743 | -2.2123 | -2.5796 | 1.6487 | 1.6246 | 1.5995 | 1.5777 | 1.5549 | 1.5269 | 1.5013 | 1.3897 | 1.174 | 0.93988 | 0.67941 | -0.9 | -1.9666 | -2.1819 | 1.8944 | 1.8717 | 1.8468 | 1.8215 | 1.7844 | 1.7386 | 1.699 | 1.5545 | 1.3168 | 1.0611 | 0.78019 | -0.87261 | -2.0814 | -2.419
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 0 | 8.8054 | 8.6983 | 8.5174 | 8.2873 | 8.046 | 7.7506 | 7.3765 | 7.0156 | 6.5761 | 6.1849 | 5.8325 | 4.9667 | 4.5246 | 4.1572 | 8.8474 | 8.7643 | 8.6579 | 8.514 | 8.366 | 8.19 | 7.9633 | 7.7498 | 7.5463 | 7.3364 | 7.1264 | 6.1639 | 4.9508 | 1.9764 | 9.0492 | 8.9431 | 8.7764 | 8.5629 | 8.3406 | 8.0747 | 7.7291 | 7.3838 | 6.9727 | 6.6071 | 6.2775 | 5.4796 | 5.1221 | 4.7884
|  | EDZELL STREET | CT |  |  |  | 0 | 8.8092 | 8.707 | 8.5272 | 8.2953 | 8.0478 | 7.7506 | 7.3765 | 7.0199 | 6.7014 | 6.3926 | 6.121 | 5.0575 | 4.5246 | 4.1572 | 8.8474 | 8.7643 | 8.6579 | 8.514 | 8.366 | 8.19 | 7.9633 | 7.7498 | 7.5463 | 7.3364 | 7.1264 | 6.1639 | 5.229 | 3.7866 | 9.0525 | 8.953 | 8.789 | 8.5742 | 8.3484 | 8.076 | 7.7291 | 7.4003 | 7.1058 | 6.8175 | 6.5629 | 5.5935 | 5.1221 | 4.7884
|  | EDZELL STREET | LW |  |  |  | 0 | 8.8054 | 8.6983 | 8.5174 | 8.2873 | 8.046 | 7.7593 | 7.3957 | 7.0156 | 6.5761 | 6.1849 | 5.8325 | 4.9667 | 4.7353 | 4.4319 | 8.86 | 8.7866 | 8.6947 | 8.5721 | 8.4487 | 8.2948 | 8.0926 | 7.9038 | 7.6441 | 7.4088 | 7.1959 | 6.7368 | 6.6277 | 6.4389 | 9.0492 | 8.9431 | 8.7764 | 8.5629 | 8.3406 | 8.0747 | 7.7332 | 7.3838 | 6.9727 | 6.6071 | 6.2775 | 5.4796 | 5.2676 | 4.9787
|  | EDZELL STREET | ST |  |  |  | 0 | 8.8321 | 8.821 | 8.7968 | 8.7482 | 8.7156 | 8.6636 | 8.5939 | 8.5418 | 8.4362 | 8.3241 | 8.2393 | 7.386 | 6.828 | 6.2293 | 8.8747 | 8.8379 | 8.7928 | 8.7349 | 8.6868 | 8.6215 | 8.5418 | 8.4687 | 8.356 | 8.216 | 8.0979 | 7.0544 | 6.1254 | 4.6416 | 9.0993 | 9.0707 | 9.0368 | 8.9876 | 8.9547 | 8.9026 | 8.833 | 8.7812 | 8.6761 | 8.5646 | 8.4806 | 7.631 | 7.1501 | 6.6169
|  | EDZELL STREET | FS |  |  |  | 0 | 8.8299 | 8.8189 | 8.7689 | 8.7175 | 8.654 | 8.6046 | 8.5367 | 8.4326 | 8.3097 | 8.2245 | 8.1016 | 7.3274 | 6.4991 | 5.8395 | 8.8698 | 8.8298 | 8.7718 | 8.7131 | 8.6419 | 8.5767 | 8.4808 | 8.3522 | 8.2025 | 8.0746 | 7.9186 | 6.851 | 4.9508 | 1.9764 | 9.0948 | 9.067 | 9.0144 | 8.9657 | 8.9049 | 8.8581 | 8.7926 | 8.6941 | 8.5768 | 8.4969 | 8.3802 | 7.6537 | 6.886 | 6.2965
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 2.479 | 5.5098 | 4.8932 | 4.125 | 3.252 | 2.5466 | 1.6921 | 0.77476 | -0.13883 | -0.95444 | -1.4435 | -2.2113 | -5.8069 | -6.6096 | -7.1424 | 7.1816 | 6.6023 | 6.0601 | 5.4741 | 5.3028 | 4.9181 | 4.3619 | 3.784 | 3.2794 | 3.0101 | 2.5448 | -0.20667 | -0.84775 | -1.1642 | 6.6383 | 6.0773 | 5.3872 | 4.607 | 3.979 | 3.2298 | 2.3994 | 1.5651 | 0.79578 | 0.35263 | -0.35987 | -3.7206 | -4.3259 | -4.8022
|  | ELGIN | CT |  |  |  | 2.479 | 5.5301 | 4.9891 | 4.2434 | 3.3101 | 2.5466 | 1.6921 | 0.77476 | -0.13883 | -0.87881 | -1.2831 | -1.923 | -5.6618 | -6.6096 | -7.1424 | 7.1897 | 6.7243 | 6.21 | 5.53 | 5.3028 | 4.9181 | 4.3619 | 3.784 | 3.3246 | 3.0866 | 2.679 | -0.024202 | -0.57225 | -1.1043 | 6.6505 | 6.1604 | 5.4912 | 4.6498 | 3.979 | 3.2298 | 2.3994 | 1.5651 | 0.87894 | 0.51452 | -0.08096 | -3.5312 | -4.3259 | -4.8022
|  | ELGIN | LW |  |  |  | 2.479 | 5.5098 | 4.8932 | 4.125 | 3.252 | 2.5768 | 1.7257 | 0.84983 | -0.0595 | -0.95444 | -1.4435 | -2.2113 | -5.8069 | -6.3487 | -6.8272 | 7.1816 | 6.6023 | 6.0601 | 5.4741 | 5.318 | 4.9295 | 4.387 | 3.8284 | 3.2794 | 3.0101 | 2.5448 | -0.20667 | -0.42577 | -0.63276 | 6.6383 | 6.0773 | 5.3872 | 4.607 | 4.0207 | 3.265 | 2.4669 | 1.6384 | 0.79578 | 0.35263 | -0.35987 | -3.7206 | -4.1946 | -4.6505
|  | ELGIN | ST |  |  |  | 2.479 | 5.6354 | 5.229 | 4.7378 | 4.1559 | 3.8118 | 3.4194 | 3.0302 | 2.5874 | 2.1545 | 1.6773 | 1.1431 | -2.6331 | -3.9189 | -4.9529 | 7.2246 | 6.8328 | 6.3693 | 5.7873 | 5.6285 | 5.4401 | 5.1343 | 4.7734 | 4.4357 | 4.0727 | 3.6795 | -0.0070121 | -0.84775 | -1.1642 | 6.7482 | 6.3868 | 5.945 | 5.4242 | 5.1311 | 4.7954 | 4.4449 | 4.0391 | 3.6263 | 3.163 | 2.6518 | -1.1925 | -2.357 | -3.0616
|  | ELGIN | FS |  |  |  | 2.479 | 5.7143 | 5.3958 | 5.0577 | 4.6383 | 4.3779 | 4.1127 | 3.8089 | 3.4598 | 3.0485 | 2.6311 | 2.2182 | -1.3405 | -3.434 | -4.8689 | 7.2472 | 6.9416 | 6.6181 | 6.1975 | 6.0675 | 5.9346 | 5.7065 | 5.4657 | 5.1967 | 4.9279 | 4.6582 | 1.9502 | 0.19824 | -1.1012 | 6.8119 | 6.5289 | 6.2278 | 5.8554 | 5.6356 | 5.4106 | 5.1375 | 4.8261 | 4.4451 | 4.0581 | 3.682 | 0.30981 | -1.6252 | -2.9376
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 3.739 | -10.0543 | -10.4735 | -10.8833 | -11.0022 | -11.0812 | -11.1506 | -11.2868 | -11.4704 | -11.6119 | -11.7266 | -11.8104 | -12.2879 | -12.4278 | -12.4885 | -9.2291 | -9.6696 | -10.096 | -10.2049 | -10.2752 | -10.3485 | -10.5109 | -10.6371 | -10.7194 | -10.7815 | -10.8256 | -11.1699 | -11.2767 | -11.3266 | -9.3709 | -9.7913 | -10.2014 | -10.3145 | -10.3894 | -10.4613 | -10.6078 | -10.7301 | -10.8107 | -10.9922 | -11.1529 | -11.6951 | -11.848 | -11.9995
|  | ELLIOT DEPOT | CT |  |  |  | 3.739 | -9.8166 | -10.1632 | -10.5395 | -10.7159 | -10.8972 | -11.0864 | -11.2868 | -11.4704 | -11.6119 | -11.7266 | -11.8104 | -12.0926 | -12.2519 | -12.4329 | -8.9669 | -9.3297 | -9.721 | -9.9006 | -10.086 | -10.2913 | -10.5109 | -10.6371 | -10.7194 | -10.7815 | -10.8227 | -10.9914 | -11.0393 | -11.0822 | -9.1296 | -9.4758 | -9.8515 | -10.0272 | -10.207 | -10.4012 | -10.6078 | -10.7301 | -10.8107 | -10.9701 | -11.0887 | -11.5994 | -11.8333 | -11.9995
|  | ELLIOT DEPOT | LW |  |  |  | 3.739 | -10.0543 | -10.4735 | -10.8833 | -11.0022 | -11.0812 | -11.1506 | -11.2235 | -11.3032 | -11.476 | -11.6494 | -11.7992 | -12.2879 | -12.4278 | -12.4885 | -9.2291 | -9.6696 | -10.096 | -10.2049 | -10.2752 | -10.3485 | -10.4297 | -10.5142 | -10.6175 | -10.723 | -10.8256 | -11.1699 | -11.2767 | -11.3266 | -9.3709 | -9.7913 | -10.2014 | -10.3145 | -10.3894 | -10.4613 | -10.5382 | -10.6193 | -10.7736 | -10.9922 | -11.1529 | -11.6951 | -11.848 | -11.9923
|  | ELLIOT DEPOT | ST |  |  |  | 3.739 | -9.8026 | -10.122 | -10.4623 | -10.5739 | -10.7145 | -10.859 | -10.9864 | -11.0683 | -11.1449 | -11.1975 | -11.2708 | -11.6629 | -11.9201 | -12.0509 | -8.9526 | -9.2863 | -9.6408 | -9.7443 | -9.886 | -10.0433 | -10.1853 | -10.272 | -10.3527 | -10.412 | -10.4901 | -10.9113 | -11.0735 | -11.1231 | -9.1155 | -9.4338 | -9.7733 | -9.8782 | -10.0149 | -10.1612 | -10.2918 | -10.3735 | -10.4497 | -10.5024 | -10.5751 | -10.9668 | -11.1153 | -11.1603
|  | ELLIOT DEPOT | FS |  |  |  | 3.739 | -9.5118 | -9.7752 | -10.0263 | -10.1372 | -10.217 | -10.3189 | -10.4103 | -10.4771 | -10.5444 | -10.6421 | -10.7743 | -11.3765 | -11.8377 | -12.2192 | -8.6324 | -8.9076 | -9.1669 | -9.2755 | -9.3525 | -9.4633 | -9.5602 | -9.632 | -9.7001 | -9.8041 | -9.9448 | -10.6076 | -10.9302 | -11.1691 | -8.8205 | -9.0826 | -9.3318 | -9.438 | -9.5143 | -9.6176 | -9.7094 | -9.7771 | -9.8431 | -9.9411 | -10.073 | -10.6846 | -10.9778 | -11.2413
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 2.477 | -2.1665 | -2.5956 | -3.3627 | -4.3523 | -5.4947 | -6.4825 | -8.2052 | -9.8614 | -11.4564 | -13.0123 | -14.3472 | -18.1006 | -20.1143 | -21.2739 | 1.1917 | 0.90539 | 0.5038 | -0.023644 | -0.63055 | -1.01 | -1.9926 | -3.0325 | -4.0469 | -5.0119 | -5.8259 | -7.8276 | -8.977 | -10.0387 | -0.16645 | -0.56028 | -1.2485 | -2.1399 | -3.1721 | -4.0159 | -5.5666 | -7.0671 | -8.5106 | -9.922 | -11.1327 | -14.4432 | -16.1031 | -17.104
|  | ELLON | CT |  |  |  | 2.477 | -2.1665 | -2.5956 | -3.3627 | -4.3523 | -5.4947 | -6.4825 | -8.2052 | -9.8614 | -11.3473 | -12.7203 | -13.8134 | -17.9765 | -20.1143 | -21.2739 | 1.1917 | 0.90539 | 0.5038 | -0.023644 | -0.63055 | -1.01 | -1.9926 | -3.0325 | -3.9663 | -4.8624 | -5.5793 | -7.8276 | -8.977 | -10.0387 | -0.16645 | -0.56028 | -1.2485 | -2.1399 | -3.1721 | -4.0159 | -5.5666 | -7.0671 | -8.4077 | -9.652 | -10.6444 | -14.2965 | -16.1031 | -17.104
|  | ELLON | LW |  |  |  | 2.477 | -2.1638 | -2.5711 | -3.2843 | -4.2064 | -5.2043 | -6.1553 | -7.7988 | -9.6182 | -11.4564 | -13.0123 | -14.3472 | -18.1006 | -19.452 | -20.4928 | 1.195 | 0.93143 | 0.58162 | 0.10132 | -0.39755 | -0.79256 | -1.7689 | -2.8773 | -4.0469 | -5.0119 | -5.8259 | -7.7864 | -8.3676 | -8.8838 | -0.1621 | -0.53358 | -1.1682 | -1.9946 | -2.8883 | -3.7077 | -5.1937 | -6.8371 | -8.5106 | -9.922 | -11.1327 | -14.4432 | -15.5817 | -16.5088
|  | ELLON | ST |  |  |  | 2.477 | -2.007 | -2.2289 | -2.4913 | -2.8247 | -3.1515 | -3.611 | -4.3547 | -5.273 | -5.9448 | -6.8815 | -7.7118 | -11.63 | -13.9454 | -15.7778 | 1.2795 | 1.1447 | 0.98727 | 0.77225 | 0.56239 | 0.26192 | -0.29117 | -0.9972 | -1.4865 | -2.2138 | -2.8582 | -5.6615 | -7.1499 | -8.467 | -0.019959 | -0.21522 | -0.44758 | -0.74599 | -1.0386 | -1.4445 | -2.1195 | -2.9583 | -3.5485 | -4.4071 | -5.1732 | -8.8122 | -10.8023 | -12.379
|  | ELLON | FS |  |  |  | 2.477 | -1.9421 | -2.122 | -2.3333 | -2.5558 | -2.8079 | -3.083 | -3.5841 | -4.3219 | -5.139 | -5.601 | -6.3246 | -10.2687 | -13.8329 | -16.3166 | 1.3131 | 1.1978 | 1.0585 | 0.91631 | 0.74147 | 0.55579 | 0.17158 | -0.35683 | -0.95702 | -1.2475 | -1.7732 | -4.5916 | -7.3222 | -9.7543 | 0.035978 | -0.12215 | -0.311 | -0.50739 | -0.73692 | -0.97748 | -1.4296 | -2.0919 | -2.831 | -3.2173 | -3.8696 | -7.4229 | -10.6305 | -12.8618
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.15672 | 0.14638 | 0.13576 | 0.13209 | 0.13127 | 0.1258 | 0.11452 | 0.11103 | 0.1069 | 0.099076 | 0.094928 | 0.08284 | 0.079847 | 0.07436 | 0.15748 | 0.1481 | 0.13936 | 0.1443 | 0.14182 | 0.13481 | 0.13468 | 0.13223 | 0.12893 | 0.12353 | 0.12047 | 0.11233 | 0.11093 | 0.10756 | 0.13631 | 0.12616 | 0.11605 | 0.11273 | 0.11236 | 0.10738 | 0.096667 | 0.093263 | 0.088992 | 0.081272 | 0.07719 | 0.065457 | 0.062807 | 0.057617
|  | EREDINE | CT |  |  |  | 0 | 0.15672 | 0.14638 | 0.13576 | 0.13209 | 0.13127 | 0.1258 | 0.11452 | 0.11103 | 0.10949 | 0.10369 | 0.098478 | 0.088871 | 0.085813 | 0.081428 | 0.1575 | 0.1481 | 0.13936 | 0.1443 | 0.14441 | 0.14148 | 0.13468 | 0.13223 | 0.13116 | 0.12712 | 0.12342 | 0.11665 | 0.11486 | 0.11184 | 0.13631 | 0.12616 | 0.11605 | 0.11273 | 0.11236 | 0.10738 | 0.096667 | 0.093263 | 0.091782 | 0.086024 | 0.080816 | 0.071469 | 0.068725 | 0.064641
|  | EREDINE | LW |  |  |  | 0 | 0.15693 | 0.14706 | 0.13777 | 0.13314 | 0.13452 | 0.12727 | 0.12047 | 0.11223 | 0.1069 | 0.099076 | 0.094928 | 0.08284 | 0.079847 | 0.07436 | 0.15748 | 0.14845 | 0.14077 | 0.14485 | 0.14638 | 0.14213 | 0.13816 | 0.13259 | 0.12893 | 0.12353 | 0.12047 | 0.11233 | 0.11093 | 0.10756 | 0.13647 | 0.12676 | 0.11782 | 0.11365 | 0.11542 | 0.10862 | 0.10231 | 0.094209 | 0.088992 | 0.081272 | 0.07719 | 0.065457 | 0.062807 | 0.057617
|  | EREDINE | ST |  |  |  | 0 | 0.16 | 0.15596 | 0.15081 | 0.14426 | 0.13694 | 0.12849 | 0.12874 | 0.132 | 0.12856 | 0.12169 | 0.11976 | 0.099863 | 0.094307 | 0.093231 | 0.16049 | 0.15718 | 0.15297 | 0.14767 | 0.14182 | 0.13481 | 0.14224 | 0.14458 | 0.14243 | 0.13794 | 0.13672 | 0.12313 | 0.11935 | 0.11829 | 0.13954 | 0.13565 | 0.13072 | 0.12467 | 0.11807 | 0.11029 | 0.10954 | 0.11295 | 0.10969 | 0.103 | 0.10124 | 0.081907 | 0.076637 | 0.075686
|  | EREDINE | FS |  |  |  | 0 | 0.16136 | 0.15833 | 0.15518 | 0.15128 | 0.14712 | 0.14225 | 0.1366 | 0.13696 | 0.14043 | 0.13518 | 0.13367 | 0.11741 | 0.099624 | 0.094498 | 0.16127 | 0.15868 | 0.15578 | 0.15213 | 0.14824 | 0.14363 | 0.13826 | 0.14633 | 0.14878 | 0.14538 | 0.1445 | 0.13392 | 0.12225 | 0.11802 | 0.14076 | 0.13783 | 0.13474 | 0.13089 | 0.12679 | 0.12196 | 0.11636 | 0.11693 | 0.12054 | 0.11544 | 0.11408 | 0.098546 | 0.081642 | 0.076849
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0.017 | 0.85121 | 0.83759 | 0.82407 | 0.8061 | 0.79198 | 0.77136 | 0.74474 | 0.73362 | 0.72591 | 0.71542 | 0.70473 | 0.67056 | 0.64041 | 0.60561 | 0.89704 | 0.88636 | 0.87488 | 0.86048 | 0.85055 | 0.83462 | 0.81271 | 0.80489 | 0.79856 | 0.7886 | 0.77971 | 0.74967 | 0.71921 | 0.6833 | 0.87332 | 0.85599 | 0.84212 | 0.8233 | 0.8095 | 0.78812 | 0.75997 | 0.74823 | 0.74004 | 0.72794 | 0.71657 | 0.68027 | 0.6463 | 0.607
|  | ERROGIE | CT |  |  |  | 0.017 | 0.85121 | 0.84338 | 0.83692 | 0.81905 | 0.80575 | 0.79139 | 0.7678 | 0.75819 | 0.7546 | 0.74665 | 0.73977 | 0.71303 | 0.69931 | 0.68227 | 0.89704 | 0.89469 | 0.89252 | 0.87824 | 0.87052 | 0.86198 | 0.8449 | 0.83736 | 0.83434 | 0.82666 | 0.8183 | 0.79246 | 0.77718 | 0.75373 | 0.87332 | 0.86395 | 0.85912 | 0.84064 | 0.82837 | 0.81498 | 0.79103 | 0.78081 | 0.77694 | 0.76801 | 0.75908 | 0.73065 | 0.7171 | 0.69963
|  | ERROGIE | LW |  |  |  | 0.017 | 0.85177 | 0.83759 | 0.82407 | 0.8061 | 0.79198 | 0.77136 | 0.74474 | 0.73362 | 0.72591 | 0.71542 | 0.70473 | 0.67056 | 0.64041 | 0.60561 | 0.89707 | 0.88636 | 0.87488 | 0.86048 | 0.85055 | 0.83462 | 0.81271 | 0.80489 | 0.79856 | 0.7886 | 0.77971 | 0.74967 | 0.71921 | 0.6833 | 0.87369 | 0.85599 | 0.84212 | 0.8233 | 0.8095 | 0.78812 | 0.75997 | 0.74823 | 0.74004 | 0.72794 | 0.71657 | 0.68027 | 0.6463 | 0.607
|  | ERROGIE | ST |  |  |  | 0.017 | 0.85791 | 0.84908 | 0.83258 | 0.82837 | 0.82423 | 0.81709 | 0.80699 | 0.80101 | 0.79385 | 0.7852 | 0.77554 | 0.71923 | 0.68172 | 0.65282 | 0.90295 | 0.89613 | 0.88126 | 0.88189 | 0.87964 | 0.87536 | 0.86866 | 0.86478 | 0.85993 | 0.85382 | 0.8472 | 0.79241 | 0.74965 | 0.71004 | 0.87983 | 0.87163 | 0.85478 | 0.84849 | 0.84525 | 0.83854 | 0.82851 | 0.82292 | 0.81586 | 0.80728 | 0.79753 | 0.73496 | 0.69276 | 0.65997
|  | ERROGIE | FS |  |  |  | 0.017 | 0.8612 | 0.85465 | 0.84639 | 0.83662 | 0.84008 | 0.84061 | 0.83608 | 0.82767 | 0.8211 | 0.8114 | 0.80748 | 0.7758 | 0.73975 | 0.72619 | 0.90449 | 0.89904 | 0.89091 | 0.88124 | 0.88804 | 0.88776 | 0.88308 | 0.87632 | 0.87061 | 0.86236 | 0.85981 | 0.83597 | 0.8022 | 0.77016 | 0.8826 | 0.87643 | 0.86797 | 0.85798 | 0.85895 | 0.85981 | 0.85473 | 0.84599 | 0.83933 | 0.82904 | 0.82553 | 0.79495 | 0.75964 | 0.74699
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.098 | 3.6362 | 3.4768 | 3.2578 | 2.9474 | 2.5908 | 2.2665 | 1.8209 | 1.4458 | 1.0694 | 0.66977 | 0.30301 | -0.78772 | -1.3244 | -1.751 | 4.0521 | 3.9581 | 3.8344 | 3.6599 | 3.4684 | 3.2958 | 3.0551 | 2.8541 | 2.6562 | 2.4362 | 2.2321 | 1.6386 | 1.2486 | 0.87586 | 4.3218 | 4.2316 | 4.0513 | 3.7959 | 3.4936 | 3.1899 | 2.7686 | 2.4328 | 2.0742 | 1.7028 | 1.3617 | 0.36799 | -0.078637 | -0.45695
|  | ERROL | CT |  |  |  | 0.098 | 3.6362 | 3.4768 | 3.2578 | 2.9474 | 2.5908 | 2.2665 | 1.8209 | 1.4458 | 1.1068 | 0.77969 | 0.48949 | -0.67414 | -1.3244 | -1.751 | 4.0521 | 3.9581 | 3.8344 | 3.6599 | 3.4684 | 3.2958 | 3.0551 | 2.8541 | 2.6695 | 2.4864 | 2.3186 | 1.6476 | 1.2486 | 0.87586 | 4.3218 | 4.2316 | 4.0513 | 3.7959 | 3.4936 | 3.1899 | 2.7686 | 2.4328 | 2.1225 | 1.82 | 1.5495 | 0.49549 | -0.072732 | -0.45695
|  | ERROL | LW |  |  |  | 0.098 | 3.6469 | 3.4909 | 3.2812 | 2.977 | 2.6591 | 2.3071 | 1.8819 | 1.5106 | 1.0694 | 0.66977 | 0.30301 | -0.78772 | -1.2851 | -1.6929 | 4.0602 | 3.9654 | 3.8457 | 3.6827 | 3.5148 | 3.3259 | 3.0938 | 2.8973 | 2.6562 | 2.4362 | 2.2321 | 1.6386 | 1.3793 | 1.1691 | 4.3223 | 4.2379 | 4.0714 | 3.8329 | 3.5558 | 3.2335 | 2.8306 | 2.4847 | 2.0742 | 1.7028 | 1.3617 | 0.36799 | -0.078637 | -0.45406
|  | ERROL | ST |  |  |  | 0.098 | 3.6903 | 3.6125 | 3.502 | 3.3586 | 3.2279 | 3.0804 | 2.9179 | 2.7741 | 2.5635 | 2.3425 | 2.1531 | 0.80376 | 0.11309 | -0.3194 | 4.0844 | 4.0369 | 3.9692 | 3.8835 | 3.8077 | 3.7225 | 3.6275 | 3.5397 | 3.4118 | 3.2759 | 3.1543 | 2.2894 | 1.8032 | 1.4076 | 4.3595 | 4.3293 | 4.2564 | 4.1473 | 4.0393 | 3.9162 | 3.7768 | 3.6295 | 3.43 | 3.2136 | 2.989 | 1.6038 | 0.97562 | 0.68959
|  | ERROL | FS |  |  |  | 0.098 | 3.7308 | 3.6775 | 3.6052 | 3.5274 | 3.4349 | 3.3683 | 3.2789 | 3.1328 | 2.9568 | 2.8197 | 2.6416 | 1.5939 | 0.46669 | -0.36539 | 4.1058 | 4.0715 | 4.026 | 3.9766 | 3.918 | 3.8728 | 3.8122 | 3.7189 | 3.6088 | 3.5202 | 3.4085 | 2.7155 | 1.8507 | 0.99771 | 4.3695 | 4.3483 | 4.3155 | 4.2762 | 4.2149 | 4.151 | 4.0719 | 3.9532 | 3.7973 | 3.6767 | 3.5114 | 2.5127 | 1.3625 | 0.44074
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | NO | 0.006 | 0.46301 | 0.44187 | 0.41053 | 0.37251 | 0.34174 | 0.29174 | 0.24437 | 0.21711 | 0.19233 | 0.16207 | 0.13527 | 0.06904 | 0.026183 | -0.024546 | 0.63078 | 0.6225 | 0.60249 | 0.57867 | 0.56357 | 0.53145 | 0.50442 | 0.4829 | 0.46515 | 0.44254 | 0.42243 | 0.37287 | 0.33719 | 0.29351 | 0.57147 | 0.54725 | 0.51621 | 0.47931 | 0.45178 | 0.40244 | 0.35989 | 0.32982 | 0.30653 | 0.27812 | 0.25305 | 0.18848 | 0.1418 | 0.088051
|  | FASNAKYLE | CT |  |  |  | 0.006 | 0.46723 | 0.44563 | 0.42295 | 0.38278 | 0.3477 | 0.30487 | 0.26039 | 0.23602 | 0.2255 | 0.20486 | 0.18457 | 0.12581 | 0.099845 | 0.067701 | 0.64235 | 0.63077 | 0.62152 | 0.59688 | 0.5816 | 0.56032 | 0.54004 | 0.51713 | 0.50929 | 0.49104 | 0.47424 | 0.43047 | 0.41377 | 0.39067 | 0.57275 | 0.55325 | 0.53281 | 0.49416 | 0.46445 | 0.42625 | 0.38944 | 0.3596 | 0.34894 | 0.32693 | 0.30734 | 0.25082 | 0.22503 | 0.19425
|  | FASNAKYLE | LW |  |  |  | 0.006 | 0.46889 | 0.44187 | 0.41053 | 0.37251 | 0.34174 | 0.29174 | 0.24437 | 0.21711 | 0.19233 | 0.16207 | 0.13527 | 0.06904 | 0.026183 | -0.024546 | 0.64243 | 0.6225 | 0.60249 | 0.57867 | 0.56357 | 0.53145 | 0.50442 | 0.4829 | 0.46515 | 0.44254 | 0.42243 | 0.37287 | 0.33719 | 0.29351 | 0.57421 | 0.54725 | 0.51621 | 0.47931 | 0.45178 | 0.40244 | 0.35989 | 0.32982 | 0.30653 | 0.27812 | 0.25305 | 0.18848 | 0.1418 | 0.088051
|  | FASNAKYLE | ST |  |  |  | 0.006 | 0.46301 | 0.46166 | 0.44032 | 0.42034 | 0.40147 | 0.38118 | 0.3624 | 0.34147 | 0.31441 | 0.30202 | 0.27619 | 0.15598 | 0.10094 | 0.065717 | 0.63078 | 0.64064 | 0.62711 | 0.61604 | 0.60718 | 0.59662 | 0.58808 | 0.574 | 0.55637 | 0.55062 | 0.53438 | 0.44298 | 0.39435 | 0.35859 | 0.57147 | 0.56811 | 0.54703 | 0.52854 | 0.51226 | 0.49363 | 0.47756 | 0.4555 | 0.42891 | 0.41755 | 0.39248 | 0.27318 | 0.21322 | 0.17197
|  | FASNAKYLE | FS |  |  |  | 0.006 | 0.47322 | 0.47374 | 0.4657 | 0.45833 | 0.4514 | 0.43901 | 0.42786 | 0.41545 | 0.39339 | 0.37097 | 0.36536 | 0.27542 | 0.18132 | 0.15371 | 0.63301 | 0.64518 | 0.63922 | 0.63375 | 0.62855 | 0.61947 | 0.61063 | 0.60359 | 0.58914 | 0.57444 | 0.57254 | 0.52088 | 0.46405 | 0.44289 | 0.57883 | 0.57872 | 0.57051 | 0.56292 | 0.55566 | 0.54344 | 0.53194 | 0.52002 | 0.49888 | 0.47742 | 0.47152 | 0.38777 | 0.30131 | 0.27434
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.045777 | 0.034408 | 0.020952 | 0.0068077 | -0.0044535 | -0.021747 | -0.032962 | -0.029555 | -0.037131 | -0.038502 | -0.043511 | -0.059883 | -0.085949 | -0.11569 | 0.073123 | 0.060131 | 0.046259 | 0.03216 | 0.021756 | 0.0048879 | -0.003985 | -0.0015137 | -0.0065949 | -0.0075556 | -0.010963 | -0.028372 | -0.05748 | -0.090566 | 0.062115 | 0.048603 | 0.033584 | 0.018175 | 0.0063211 | -0.012216 | -0.025349 | -0.023828 | -0.030035 | -0.031845 | -0.036086 | -0.0566 | -0.088105 | -0.12335
|  | FINCASTLE | CT |  |  |  | 0 | 0.045777 | 0.040442 | 0.034585 | 0.020787 | 0.010869 | -4.684e-05 | -0.0070017 | -0.0044 | -0.0062576 | -0.012523 | -0.013055 | -0.030779 | -0.040062 | -0.052087 | 0.073123 | 0.068333 | 0.063966 | 0.05008 | 0.041718 | 0.032414 | 0.029846 | 0.031253 | 0.029578 | 0.024864 | 0.024014 | 0.0090605 | -0.00042071 | -0.014149 | 0.062115 | 0.056526 | 0.051117 | 0.036001 | 0.026235 | 0.015362 | 0.0085155 | 0.0090415 | 0.0066075 | 0.0011568 | -0.00016723 | -0.01802 | -0.028897 | -0.043185
|  | FINCASTLE | LW |  |  |  | 0 | 0.04618 | 0.034408 | 0.020952 | 0.0068077 | -0.0044535 | -0.021747 | -0.032962 | -0.029555 | -0.037131 | -0.038502 | -0.043511 | -0.059883 | -0.085949 | -0.11569 | 0.0735 | 0.060131 | 0.046259 | 0.03216 | 0.021756 | 0.0048879 | -0.003985 | -0.0015137 | -0.0065949 | -0.0075556 | -0.010963 | -0.028372 | -0.05748 | -0.090566 | 0.062682 | 0.048603 | 0.033584 | 0.018175 | 0.0063211 | -0.012216 | -0.025349 | -0.023828 | -0.030035 | -0.031845 | -0.036086 | -0.0566 | -0.088105 | -0.12335
|  | FINCASTLE | ST |  |  |  | 0 | 0.047228 | 0.045082 | 0.036297 | 0.028525 | 0.022108 | 0.015897 | 0.0090943 | 0.0017487 | 0.0029222 | 0.0059506 | 0.00025441 | -0.0332 | -0.063657 | -0.089395 | 0.074529 | 0.072606 | 0.063943 | 0.056765 | 0.051346 | 0.046339 | 0.040716 | 0.03431 | 0.038687 | 0.040496 | 0.036841 | 0.0032104 | -0.031383 | -0.06256 | 0.063765 | 0.061216 | 0.051616 | 0.043493 | 0.037119 | 0.03114 | 0.024543 | 0.017331 | 0.018388 | 0.019338 | 0.014633 | -0.022787 | -0.059204 | -0.090739
|  | FINCASTLE | FS |  |  |  | 0 | 0.048025 | 0.046444 | 0.043161 | 0.039499 | 0.035716 | 0.031337 | 0.025598 | 0.019163 | 0.010799 | 0.0022115 | 0.0042079 | -0.001832 | -0.019335 | -0.026983 | 0.075106 | 0.073633 | 0.069989 | 0.065961 | 0.061809 | 0.057278 | 0.051215 | 0.045226 | 0.03709 | 0.028728 | 0.035804 | 0.032075 | 0.020127 | 0.01053 | 0.064847 | 0.06301 | 0.059133 | 0.054869 | 0.050474 | 0.045698 | 0.039406 | 0.032838 | 0.024111 | 0.015158 | 0.019314 | 0.012502 | -0.002948 | -0.011715
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0.15 | -2.1601 | -3.1186 | -4.0418 | -5.0343 | -6.0072 | -6.9886 | -7.982 | -8.9759 | -9.9809 | -10.9769 | -11.0459 | -11.211 | -11.3015 | -11.3662 | -1.8936 | -2.9474 | -3.9858 | -5.1036 | -6.1989 | -7.2876 | -8.3859 | -9.4736 | -10.5587 | -11.6398 | -11.6631 | -11.742 | -11.7836 | -11.8361 | -1.8324 | -2.7977 | -3.725 | -4.7183 | -5.6958 | -6.6842 | -7.6828 | -8.6788 | -9.6712 | -10.6571 | -10.7004 | -10.8456 | -10.9218 | -11.0008
|  | FIRTH | CT |  |  |  | 0.15 | -1.8466 | -2.6092 | -3.4214 | -4.4868 | -5.5652 | -6.6932 | -7.6447 | -8.6297 | -9.5996 | -10.7505 | -10.8942 | -11.0842 | -11.128 | -11.1584 | -1.5485 | -2.381 | -3.2728 | -4.4666 | -5.6779 | -6.9442 | -7.995 | -9.0716 | -10.1442 | -11.4257 | -11.5567 | -11.6857 | -11.723 | -11.763 | -1.5171 | -2.2796 | -3.0887 | -4.1564 | -5.2439 | -6.39 | -7.3508 | -8.3324 | -9.3057 | -10.4602 | -10.5907 | -10.785 | -10.8669 | -10.9216
|  | FIRTH | LW |  |  |  | 0.15 | -2.1601 | -3.1186 | -4.0418 | -5.0343 | -6.0072 | -6.9886 | -7.982 | -8.9759 | -9.9809 | -10.9769 | -11.0459 | -11.211 | -11.2545 | -11.3027 | -1.8936 | -2.9474 | -3.9858 | -5.1036 | -6.1989 | -7.2876 | -8.3859 | -9.4736 | -10.5587 | -11.6398 | -11.6631 | -11.742 | -11.7836 | -11.8308 | -1.8324 | -2.7977 | -3.725 | -4.7183 | -5.6958 | -6.6842 | -7.6828 | -8.6788 | -9.6712 | -10.6571 | -10.7004 | -10.8456 | -10.9218 | -11.0008
|  | FIRTH | ST |  |  |  | 0.15 | -1.8449 | -2.5937 | -3.3968 | -4.4394 | -5.5007 | -6.6171 | -7.5348 | -8.4932 | -9.46 | -10.6169 | -10.7771 | -11.1629 | -11.3015 | -11.3662 | -1.5473 | -2.3713 | -3.258 | -4.4362 | -5.6348 | -6.8902 | -7.9189 | -8.9824 | -10.0453 | -11.3224 | -11.4577 | -11.6712 | -11.766 | -11.8361 | -1.5155 | -2.2684 | -3.077 | -4.126 | -5.1935 | -6.3142 | -7.2334 | -8.1852 | -9.1389 | -10.2829 | -10.4122 | -10.6764 | -10.7785 | -10.8743
|  | FIRTH | FS |  |  |  | 0.15 | -1.5077 | -2.0903 | -2.677 | -3.467 | -4.3818 | -5.5114 | -6.1621 | -6.8178 | -7.5687 | -8.3627 | -8.7928 | -10.7538 | -11.1633 | -11.332 | -1.176 | -1.8173 | -2.4628 | -3.3386 | -4.3727 | -5.6462 | -6.3785 | -7.1154 | -7.9497 | -8.8321 | -9.2976 | -11.3667 | -11.6853 | -11.7794 | -1.1764 | -1.7622 | -2.3525 | -3.1471 | -4.0672 | -5.2023 | -5.856 | -6.5137 | -7.2588 | -8.0478 | -8.4643 | -10.3234 | -10.6486 | -10.7508
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | YES | 0 | 0.23142 | 0.23123 | 0.23107 | 0.23077 | 0.23052 | 0.23028 | 0.22984 | 0.22934 | 0.22869 | 0.22806 | 0.22748 | 0.22636 | 0.22587 | 0.22585 | -3.1899 | -3.19 | -3.1901 | -3.1904 | -3.1905 | -3.1907 | -3.191 | -3.1914 | -3.1919 | -3.1923 | -3.1927 | -3.1935 | -3.1938 | -3.1938 | 0.22218 | 0.22198 | 0.22182 | 0.22151 | 0.22126 | 0.22101 | 0.22055 | 0.22004 | 0.21939 | 0.21879 | 0.21823 | 0.21716 | 0.21668 | 0.21666
|  | FISHNISH | CT |  |  |  | 0 | 0.23145 | 0.23127 | 0.23107 | 0.23077 | 0.23052 | 0.23029 | 0.22998 | 0.22954 | 0.2292 | 0.22887 | 0.22855 | 0.22781 | 0.22781 | 0.22781 | -3.1899 | -3.19 | -3.1901 | -3.1904 | -3.1905 | -3.1907 | -3.1909 | -3.1913 | -3.1915 | -3.1918 | -3.192 | -3.1925 | -3.1925 | -3.1925 | 0.22221 | 0.22202 | 0.22182 | 0.22151 | 0.22126 | 0.22102 | 0.2207 | 0.22025 | 0.21991 | 0.21956 | 0.21926 | 0.21855 | 0.21855 | 0.21855
|  | FISHNISH | LW |  |  |  | 0 | 0.23142 | 0.23123 | 0.23108 | 0.23087 | 0.23065 | 0.23028 | 0.22984 | 0.22934 | 0.22869 | 0.22806 | 0.22748 | 0.22636 | 0.22636 | 0.22636 | -3.1899 | -3.19 | -3.1901 | -3.1903 | -3.1904 | -3.1907 | -3.191 | -3.1914 | -3.1919 | -3.1923 | -3.1927 | -3.1935 | -3.1935 | -3.1935 | 0.22218 | 0.22198 | 0.22182 | 0.22161 | 0.22139 | 0.22101 | 0.22055 | 0.22004 | 0.21939 | 0.21879 | 0.21823 | 0.21716 | 0.21716 | 0.21716
|  | FISHNISH | ST |  |  |  | 0 | 0.2315 | 0.23143 | 0.23134 | 0.23123 | 0.23108 | 0.2309 | 0.23068 | 0.2304 | 0.23002 | 0.22962 | 0.22915 | 0.22659 | 0.22587 | 0.22586 | -3.1898 | -3.1899 | -3.1899 | -3.19 | -3.1901 | -3.1903 | -3.1904 | -3.1906 | -3.1909 | -3.1912 | -3.1915 | -3.1933 | -3.1938 | -3.1938 | 0.22226 | 0.22219 | 0.2221 | 0.22198 | 0.22183 | 0.22165 | 0.22142 | 0.22113 | 0.22075 | 0.22033 | 0.21986 | 0.21738 | 0.21668 | 0.21667
|  | FISHNISH | FS |  |  |  | 0 | 0.23151 | 0.23146 | 0.23139 | 0.23131 | 0.23122 | 0.2311 | 0.23096 | 0.2308 | 0.23059 | 0.23037 | 0.23011 | 0.22842 | 0.22682 | 0.22585 | -3.1898 | -3.1899 | -3.1899 | -3.19 | -3.19 | -3.1901 | -3.1902 | -3.1903 | -3.1905 | -3.1907 | -3.1908 | -3.1921 | -3.1932 | -3.1938 | 0.22227 | 0.22221 | 0.22215 | 0.22207 | 0.22197 | 0.22185 | 0.22171 | 0.22154 | 0.22132 | 0.2211 | 0.22084 | 0.21913 | 0.21759 | 0.21666
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0 | 0.84001 | 0.82039 | 0.8182 | 0.81293 | 0.79796 | 0.78693 | 0.77165 | 0.75957 | 0.74913 | 0.74298 | 0.73159 | 0.70269 | 0.69135 | 0.68149 | 0.93755 | 0.92089 | 0.92223 | 0.9198 | 0.91393 | 0.90978 | 0.90231 | 0.89426 | 0.8866 | 0.88302 | 0.87487 | 0.85459 | 0.85002 | 0.83854 | 0.88851 | 0.87038 | 0.86434 | 0.86209 | 0.84827 | 0.83999 | 0.82749 | 0.81571 | 0.80514 | 0.79905 | 0.78785 | 0.76343 | 0.75522 | 0.74729
|  | FLOTTA | CT |  |  |  | 0 | 0.84001 | 0.82039 | 0.82365 | 0.81293 | 0.79796 | 0.78693 | 0.77165 | 0.75957 | 0.74913 | 0.74373 | 0.73497 | 0.70788 | 0.69762 | 0.68854 | 0.93755 | 0.92089 | 0.92847 | 0.92345 | 0.91393 | 0.90978 | 0.90231 | 0.89426 | 0.8866 | 0.88384 | 0.87692 | 0.85951 | 0.85303 | 0.84383 | 0.88851 | 0.87038 | 0.87119 | 0.86251 | 0.84827 | 0.83999 | 0.82749 | 0.81571 | 0.80514 | 0.80092 | 0.79157 | 0.76641 | 0.75871 | 0.75161
|  | FLOTTA | LW |  |  |  | 0 | 0.8417 | 0.82436 | 0.8182 | 0.81461 | 0.80514 | 0.79219 | 0.77775 | 0.76612 | 0.75089 | 0.74298 | 0.73159 | 0.70269 | 0.69135 | 0.68149 | 0.9385 | 0.92372 | 0.92223 | 0.92269 | 0.91923 | 0.91289 | 0.90593 | 0.89843 | 0.88685 | 0.88302 | 0.87487 | 0.85459 | 0.85002 | 0.84815 | 0.88985 | 0.87373 | 0.86434 | 0.86209 | 0.85496 | 0.84401 | 0.83198 | 0.82092 | 0.80525 | 0.79905 | 0.78785 | 0.76343 | 0.75522 | 0.74729
|  | FLOTTA | ST |  |  |  | 0 | 0.84636 | 0.83818 | 0.82703 | 0.81402 | 0.81164 | 0.80905 | 0.80149 | 0.79524 | 0.78418 | 0.77666 | 0.765 | 0.72035 | 0.70207 | 0.69386 | 0.94302 | 0.93712 | 0.92938 | 0.9198 | 0.92031 | 0.92241 | 0.91898 | 0.91619 | 0.90825 | 0.90462 | 0.89643 | 0.86321 | 0.85019 | 0.84694 | 0.89441 | 0.88722 | 0.87756 | 0.86518 | 0.8588 | 0.85924 | 0.85314 | 0.84821 | 0.83715 | 0.83114 | 0.81972 | 0.77802 | 0.75908 | 0.75426
|  | FLOTTA | FS |  |  |  | 0 | 0.84934 | 0.84392 | 0.83813 | 0.83098 | 0.82341 | 0.82376 | 0.82727 | 0.82306 | 0.81444 | 0.81088 | 0.80233 | 0.76508 | 0.72102 | 0.70395 | 0.94466 | 0.94014 | 0.93509 | 0.92881 | 0.92213 | 0.92467 | 0.92887 | 0.92667 | 0.9203 | 0.91873 | 0.91251 | 0.89036 | 0.8588 | 0.83854 | 0.89717 | 0.89191 | 0.88646 | 0.87979 | 0.87274 | 0.86966 | 0.87414 | 0.87036 | 0.86163 | 0.85855 | 0.84997 | 0.81733 | 0.77794 | 0.75761
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 3.205 | 4.4962 | 4.2548 | 3.9285 | 3.469 | 3.0685 | 2.6242 | 1.1449 | -0.56083 | -1.4843 | -2.3448 | -3.166 | -5.7694 | -6.4635 | -6.9374 | 5.2118 | 5.0936 | 4.9682 | 4.765 | 4.5348 | 4.2758 | 2.8782 | 1.1964 | 0.44916 | -0.25655 | -0.93721 | -3.3914 | -4.1092 | -4.3147 | 5.4262 | 5.2139 | 4.9685 | 4.5943 | 4.2951 | 3.8813 | 2.4348 | 0.72854 | -0.14041 | -0.97225 | -1.7673 | -4.2968 | -5.1284 | -5.4561
|  | FOCHABERS | CT |  |  |  | 3.205 | 4.4962 | 4.2548 | 3.9285 | 3.469 | 3.0685 | 2.6242 | 1.1449 | -0.50774 | -1.3641 | -2.2472 | -3.0018 | -5.3454 | -5.7155 | -5.9942 | 5.2118 | 5.0958 | 4.9682 | 4.765 | 4.5348 | 4.2758 | 2.9649 | 1.3988 | 0.66035 | -0.11832 | -0.78105 | -2.7669 | -2.9184 | -3.0334 | 5.4262 | 5.2139 | 4.9685 | 4.5943 | 4.2951 | 3.8813 | 2.4428 | 0.82949 | -7.2753e-05 | -0.85997 | -1.5951 | -3.863 | -4.231 | -4.6375
|  | FOCHABERS | LW |  |  |  | 3.205 | 4.5073 | 4.2758 | 4.0115 | 3.6751 | 3.3447 | 2.8887 | 1.2301 | -0.56083 | -1.4843 | -2.3448 | -3.166 | -5.7694 | -6.1472 | -6.4365 | 5.2132 | 5.0936 | 4.9982 | 4.8624 | 4.6659 | 4.393 | 2.8782 | 1.1964 | 0.44916 | -0.25655 | -0.93721 | -3.1575 | -3.3791 | -3.5633 | 5.4294 | 5.2269 | 5.0547 | 4.828 | 4.5149 | 4.0698 | 2.4348 | 0.72854 | -0.14041 | -0.97225 | -1.7673 | -4.2968 | -4.6537 | -4.9331
|  | FOCHABERS | ST |  |  |  | 3.205 | 4.5686 | 4.4526 | 4.288 | 4.0952 | 3.8986 | 3.6628 | 2.4917 | 1.0688 | 0.23523 | -0.66932 | -1.5296 | -5.3918 | -6.4635 | -6.9374 | 5.2454 | 5.2007 | 5.1304 | 5.0453 | 4.9582 | 4.85 | 3.7133 | 2.3123 | 1.5684 | 0.73719 | -0.047059 | -3.3914 | -4.1092 | -4.3147 | 5.489 | 5.4066 | 5.2853 | 5.1355 | 4.9733 | 4.7717 | 3.6279 | 2.2155 | 1.3873 | 0.48324 | -0.39 | -4.2357 | -5.1284 | -5.4561
|  | FOCHABERS | FS |  |  |  | 3.205 | 4.6247 | 4.5474 | 4.4574 | 4.3478 | 4.2386 | 4.105 | 3.3807 | 2.4765 | 1.9473 | 1.3374 | 0.67005 | -2.9415 | -5.1865 | -6.3837 | 5.2589 | 5.2268 | 5.184 | 5.1292 | 5.0736 | 5.0038 | 4.2806 | 3.4108 | 2.9858 | 2.4817 | 1.9142 | -1.294 | -3.0295 | -3.8569 | 5.5168 | 5.459 | 5.3855 | 5.2918 | 5.193 | 5.0704 | 4.3537 | 3.4824 | 2.9786 | 2.3956 | 1.7536 | -1.7434 | -3.8137 | -4.8921
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 1.857 | 1.8491 | 1.0064 | -0.083534 | -1.3917 | -2.9131 | -4.5441 | -6.4209 | -7.9899 | -9.8168 | -11.5478 | -12.9467 | -17.3797 | -19.7526 | -20.9204 | 5.452 | 4.8236 | 4.1667 | 3.3464 | 2.4229 | 1.4445 | 0.23589 | -0.71496 | -1.9454 | -3.1386 | -4.0489 | -7.8888 | -10.3584 | -10.8472 | 3.7886 | 3.0113 | 2.0657 | 0.89375 | -0.44774 | -1.8763 | -3.5834 | -4.9403 | -6.6283 | -8.2453 | -9.5595 | -13.5297 | -15.3932 | -16.4382
|  | FORRES | CT |  |  |  | 1.857 | 1.9379 | 1.1427 | 0.047724 | -1.3733 | -2.9131 | -4.5441 | -6.4209 | -7.9899 | -9.7124 | -11.3444 | -12.5591 | -17.0863 | -19.7526 | -20.9204 | 5.5109 | 4.9267 | 4.2549 | 3.3464 | 2.4229 | 1.4445 | 0.23589 | -0.71496 | -1.8563 | -3.0661 | -3.8339 | -6.589 | -8.2417 | -9.2675 | 3.8567 | 3.1207 | 2.1623 | 0.89375 | -0.44774 | -1.8763 | -3.5834 | -4.9403 | -6.4799 | -7.9756 | -9.1049 | -13.0791 | -15.3932 | -16.4382
|  | FORRES | LW |  |  |  | 1.857 | 1.8491 | 1.0064 | -0.083534 | -1.3917 | -2.7779 | -4.3961 | -6.2417 | -7.7919 | -9.8168 | -11.5478 | -12.9467 | -17.3797 | -19.4348 | -20.5477 | 5.452 | 4.8236 | 4.1667 | 3.3709 | 2.582 | 1.5757 | 0.35804 | -0.5671 | -1.9454 | -3.1386 | -4.0489 | -6.8357 | -8.0296 | -8.6992 | 3.7886 | 3.0113 | 2.0657 | 0.91806 | -0.26094 | -1.7209 | -3.4148 | -4.751 | -6.6283 | -8.2453 | -9.5595 | -13.5297 | -15.2669 | -16.3239
|  | FORRES | ST |  |  |  | 1.857 | 2.0913 | 1.5528 | 0.91157 | 0.14838 | -0.66574 | -1.5297 | -2.4141 | -3.4257 | -4.6829 | -5.9834 | -6.711 | -13.284 | -16.2344 | -17.4008 | 5.6128 | 5.2324 | 4.7725 | 4.2109 | 3.6302 | 2.9236 | 2.0512 | 1.0448 | -0.21288 | -1.5755 | -2.5429 | -7.8888 | -10.3584 | -10.8472 | 4.0069 | 3.5389 | 2.9726 | 2.2918 | 1.5802 | 0.80213 | -0.011409 | -0.95189 | -2.126 | -3.3528 | -4.507 | -10.9776 | -13.8479 | -14.4862
|  | FORRES | FS |  |  |  | 1.857 | 2.3108 | 1.9163 | 1.48 | 0.93919 | 0.28177 | -0.39784 | -1.0409 | -1.8125 | -2.7339 | -3.6539 | -4.5276 | -9.3428 | -14.1303 | -16.9261 | 5.7316 | 5.4401 | 5.1204 | 4.7175 | 4.2262 | 3.7075 | 3.1783 | 2.5502 | 1.7415 | 0.93942 | 0.2136 | -4.1408 | -8.1824 | -10.0613 | 4.1846 | 3.8381 | 3.4546 | 2.9773 | 2.3985 | 1.8012 | 1.2122 | 0.51166 | -0.32405 | -1.1701 | -1.9745 | -6.4125 | -11.2046 | -13.7929
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0.206 | -0.20238 | -0.2436 | -0.34328 | -0.40805 | -0.47377 | -0.56872 | -0.67997 | -0.76947 | -0.87132 | -0.96937 | -1.0719 | -1.3093 | -1.4004 | -1.4468 | -1.7178 | -1.7485 | -1.8281 | -1.8698 | -1.8931 | -1.9461 | -1.9988 | -2.0406 | -2.0698 | -2.11 | -2.1464 | -2.2249 | -2.2696 | -2.324 | -2.0939 | -2.1342 | -2.2289 | -2.2914 | -2.3332 | -2.4123 | -2.5096 | -2.5833 | -2.6614 | -2.7381 | -2.8082 | -3.034 | -3.1203 | -3.1695
|  | FORSS | CT |  |  |  | 0.206 | -0.20238 | -0.2436 | -0.33041 | -0.39888 | -0.47377 | -0.55845 | -0.65382 | -0.72748 | -0.79085 | -0.84428 | -0.89642 | -1.0558 | -1.1059 | -1.1477 | -1.7178 | -1.7432 | -1.8072 | -1.8527 | -1.8818 | -1.923 | -1.9671 | -2.0098 | -2.0425 | -2.0543 | -2.084 | -2.1604 | -2.1937 | -2.2383 | -2.0939 | -2.1326 | -2.212 | -2.2778 | -2.327 | -2.3928 | -2.4749 | -2.5423 | -2.5942 | -2.6348 | -2.6766 | -2.808 | -2.8573 | -2.9004
|  | FORSS | LW |  |  |  | 0.206 | -0.19775 | -0.24249 | -0.34328 | -0.40805 | -0.46798 | -0.56872 | -0.67997 | -0.76947 | -0.87132 | -0.96937 | -1.0719 | -1.3093 | -1.3669 | -1.4155 | -1.7161 | -1.7485 | -1.8281 | -1.8698 | -1.8931 | -1.9461 | -1.9988 | -2.0406 | -2.0698 | -2.11 | -2.1464 | -2.2249 | -2.2696 | -2.324 | -2.0898 | -2.1342 | -2.2289 | -2.2914 | -2.3332 | -2.4123 | -2.5096 | -2.5833 | -2.6614 | -2.7381 | -2.8082 | -3.034 | -3.0932 | -3.1452
|  | FORSS | ST |  |  |  | 0.206 | -0.19238 | -0.21785 | -0.29038 | -0.33222 | -0.36793 | -0.41398 | -0.46951 | -0.51913 | -0.58551 | -0.66087 | -0.74792 | -1.2243 | -1.4004 | -1.4468 | -1.7121 | -1.726 | -1.7836 | -1.8104 | -1.8313 | -1.8579 | -1.8851 | -1.8994 | -1.9322 | -1.9556 | -1.9897 | -2.1486 | -2.2345 | -2.2735 | -2.0846 | -2.108 | -2.1753 | -2.2148 | -2.2478 | -2.2883 | -2.3302 | -2.354 | -2.4128 | -2.4735 | -2.5438 | -2.9466 | -3.1203 | -3.1695
|  | FORSS | FS |  |  |  | 0.206 | -0.17805 | -0.19518 | -0.23922 | -0.25437 | -0.27172 | -0.28536 | -0.31075 | -0.34531 | -0.37065 | -0.42157 | -0.47618 | -0.82097 | -1.1694 | -1.3741 | -1.7061 | -1.7161 | -1.7548 | -1.7662 | -1.7793 | -1.7893 | -1.8097 | -1.8332 | -1.8498 | -1.8767 | -1.9019 | -2.0205 | -2.1492 | -2.2223 | -2.0718 | -2.0877 | -2.1287 | -2.1435 | -2.1604 | -2.1737 | -2.1987 | -2.2318 | -2.2554 | -2.2922 | -2.3276 | -2.5782 | -2.8898 | -3.0852
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 0.792 | 4.6146 | 4.5214 | 4.374 | 4.2574 | 4.1293 | 3.9843 | 3.812 | 3.6419 | 3.4949 | 3.3414 | 3.2039 | 2.7838 | 2.571 | 2.3739 | 4.6985 | 4.6386 | 4.5531 | 4.49 | 4.4202 | 4.3432 | 4.238 | 4.1348 | 4.0438 | 3.9413 | 3.8484 | 3.6153 | 3.5216 | 3.3821 | 4.9072 | 4.8247 | 4.6888 | 4.5827 | 4.4648 | 4.3329 | 4.1687 | 4.0075 | 3.8635 | 3.7108 | 3.5732 | 3.1846 | 3.0053 | 2.82
|  | FORTEVIOT | CT |  |  |  | 0.792 | 4.6146 | 4.5275 | 4.3865 | 4.2668 | 4.1293 | 3.9934 | 3.8141 | 3.6419 | 3.5068 | 3.4073 | 3.291 | 2.8512 | 2.5776 | 2.3739 | 4.6985 | 4.6456 | 4.5656 | 4.498 | 4.4202 | 4.3562 | 4.2527 | 4.1437 | 4.0597 | 4.0041 | 3.9235 | 3.6721 | 3.5415 | 3.3821 | 4.9072 | 4.8305 | 4.702 | 4.5918 | 4.4648 | 4.3461 | 4.1798 | 4.0137 | 3.884 | 3.7925 | 3.6771 | 3.2781 | 3.0594 | 2.8829
|  | FORTEVIOT | LW |  |  |  | 0.792 | 4.6152 | 4.5214 | 4.374 | 4.2574 | 4.1312 | 3.9843 | 3.812 | 3.6451 | 3.4949 | 3.3414 | 3.2039 | 2.7838 | 2.571 | 2.3759 | 4.6989 | 4.6386 | 4.5531 | 4.49 | 4.4243 | 4.3432 | 4.238 | 4.1348 | 4.0438 | 3.9413 | 3.8484 | 3.6153 | 3.5216 | 3.4057 | 4.9087 | 4.8247 | 4.6888 | 4.5827 | 4.4691 | 4.3329 | 4.1687 | 4.0075 | 3.8635 | 3.7108 | 3.5732 | 3.1846 | 3.0053 | 2.82
|  | FORTEVIOT | ST |  |  |  | 0.792 | 4.6381 | 4.5742 | 4.4936 | 4.454 | 4.4038 | 4.3559 | 4.2944 | 4.2229 | 4.1652 | 4.09 | 3.9974 | 3.5168 | 3.2303 | 3.0237 | 4.7145 | 4.6782 | 4.6282 | 4.6022 | 4.5677 | 4.5363 | 4.4936 | 4.443 | 4.4022 | 4.3469 | 4.2793 | 3.9336 | 3.7401 | 3.5728 | 4.9293 | 4.8744 | 4.8032 | 4.7651 | 4.7172 | 4.6726 | 4.6155 | 4.5498 | 4.4945 | 4.425 | 4.3399 | 3.8874 | 3.611 | 3.4084
|  | FORTEVIOT | FS |  |  |  | 0.792 | 4.6531 | 4.6104 | 4.5601 | 4.5276 | 4.5044 | 4.4669 | 4.4311 | 4.3709 | 4.2994 | 4.2533 | 4.1813 | 3.8081 | 3.4169 | 3.1578 | 4.7199 | 4.6951 | 4.6624 | 4.6379 | 4.6213 | 4.593 | 4.5655 | 4.5237 | 4.472 | 4.4397 | 4.3887 | 4.1161 | 3.7993 | 3.523 | 4.9432 | 4.9075 | 4.8644 | 4.8341 | 4.8121 | 4.7774 | 4.7445 | 4.6885 | 4.6219 | 4.5765 | 4.5102 | 4.1601 | 3.7866 | 3.5304
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0.244 | 0.30825 | 0.30033 | 0.27852 | 0.25591 | 0.23609 | 0.20665 | 0.17452 | 0.15692 | 0.13709 | 0.12983 | 0.11575 | 0.063902 | 0.022604 | -0.021946 | 0.44666 | 0.44257 | 0.42595 | 0.40956 | 0.39704 | 0.37623 | 0.35235 | 0.34104 | 0.32755 | 0.32385 | 0.31442 | 0.27717 | 0.24189 | 0.20136 | 0.38767 | 0.37684 | 0.35456 | 0.33199 | 0.31315 | 0.28371 | 0.25104 | 0.23332 | 0.21277 | 0.20644 | 0.19207 | 0.14032 | 0.097248 | 0.048916
|  | FOYERS | CT |  |  |  | 0.244 | 0.30825 | 0.30483 | 0.29057 | 0.26858 | 0.24946 | 0.22703 | 0.19959 | 0.1814 | 0.16723 | 0.1529 | 0.15061 | 0.10632 | 0.080546 | 0.05426 | 0.44666 | 0.45025 | 0.44296 | 0.42681 | 0.41617 | 0.40316 | 0.38532 | 0.37255 | 0.36246 | 0.35166 | 0.34993 | 0.31586 | 0.29256 | 0.25973 | 0.38767 | 0.38355 | 0.37065 | 0.34883 | 0.33123 | 0.31051 | 0.28397 | 0.26527 | 0.25073 | 0.23558 | 0.23383 | 0.19025 | 0.16674 | 0.14091
|  | FOYERS | LW |  |  |  | 0.244 | 0.30954 | 0.30033 | 0.27852 | 0.25591 | 0.23609 | 0.20665 | 0.17452 | 0.15692 | 0.13709 | 0.12983 | 0.11575 | 0.063902 | 0.022604 | -0.021946 | 0.44703 | 0.44257 | 0.42595 | 0.40956 | 0.39704 | 0.37623 | 0.35235 | 0.34104 | 0.32755 | 0.32385 | 0.31442 | 0.27717 | 0.24189 | 0.20136 | 0.38869 | 0.37684 | 0.35456 | 0.33199 | 0.31315 | 0.28371 | 0.25104 | 0.23332 | 0.21277 | 0.20644 | 0.19207 | 0.14032 | 0.097248 | 0.048916
|  | FOYERS | ST |  |  |  | 0.244 | 0.31873 | 0.30489 | 0.29492 | 0.28497 | 0.2733 | 0.26259 | 0.24814 | 0.23823 | 0.22502 | 0.21457 | 0.2005 | 0.12736 | 0.078245 | 0.042296 | 0.45577 | 0.44544 | 0.44192 | 0.4356 | 0.42861 | 0.42274 | 0.41383 | 0.40777 | 0.39899 | 0.39239 | 0.38311 | 0.32108 | 0.27038 | 0.22236 | 0.39781 | 0.38509 | 0.37324 | 0.36424 | 0.35335 | 0.34381 | 0.32997 | 0.32065 | 0.3078 | 0.29785 | 0.28393 | 0.20771 | 0.15559 | 0.11645
|  | FOYERS | FS |  |  |  | 0.244 | 0.32396 | 0.31366 | 0.30178 | 0.31061 | 0.30286 | 0.29763 | 0.29189 | 0.28023 | 0.27013 | 0.25852 | 0.24751 | 0.19428 | 0.14654 | 0.12148 | 0.45814 | 0.44988 | 0.43871 | 0.45029 | 0.44386 | 0.43943 | 0.43405 | 0.42546 | 0.41768 | 0.40867 | 0.40113 | 0.3628 | 0.3224 | 0.27751 | 0.40217 | 0.39257 | 0.38067 | 0.38795 | 0.37971 | 0.37427 | 0.36832 | 0.35669 | 0.34667 | 0.33513 | 0.32441 | 0.27308 | 0.23068 | 0.20783
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 2.267 | 18.204 | 17.6418 | 16.7622 | 15.6551 | 14.4113 | 13.3523 | 11.7244 | 10.0491 | 8.3182 | 6.562 | 5.1568 | 1.3648 | -0.28312 | -1.7028 | 21.7998 | 21.6023 | 21.3924 | 20.8664 | 20.2002 | 19.765 | 18.8598 | 17.8337 | 16.7661 | 15.6697 | 14.7733 | 12.5661 | 11.309 | 9.7115 | 20.7706 | 20.4067 | 19.9591 | 19.2814 | 18.5743 | 17.816 | 16.3592 | 14.8533 | 13.2815 | 11.6657 | 10.3765 | 6.9556 | 5.5989 | 4.3808
|  | FRASERBURGH | CT |  |  |  | 2.267 | 18.204 | 17.6418 | 16.7622 | 15.6551 | 14.4113 | 13.3523 | 11.7244 | 10.0491 | 8.4108 | 6.8261 | 5.6341 | 1.7864 | -0.28312 | -1.7028 | 21.7998 | 21.6023 | 21.3924 | 20.8664 | 20.2002 | 19.765 | 18.8598 | 17.8337 | 16.7661 | 15.6722 | 14.868 | 12.5661 | 11.309 | 9.8362 | 20.7706 | 20.4067 | 19.9591 | 19.2814 | 18.5743 | 17.816 | 16.3592 | 14.8533 | 13.3521 | 11.8895 | 10.7975 | 7.388 | 5.5989 | 4.3808
|  | FRASERBURGH | LW |  |  |  | 2.267 | 18.2247 | 17.7032 | 16.8425 | 15.815 | 14.6845 | 13.5878 | 12.0422 | 10.3198 | 8.3182 | 6.562 | 5.1568 | 1.3648 | 0.049708 | -1.111 | 21.8036 | 21.6361 | 21.5107 | 21.0792 | 20.5318 | 20.0615 | 19.2132 | 18.1745 | 16.8349 | 15.6697 | 14.7733 | 12.6443 | 12.0653 | 11.4302 | 20.7752 | 20.4646 | 20.1713 | 19.7245 | 19.0321 | 18.0625 | 16.68 | 15.1242 | 13.2815 | 11.6657 | 10.3765 | 6.9556 | 5.7994 | 4.7709
|  | FRASERBURGH | ST |  |  |  | 2.267 | 18.404 | 18.0866 | 17.7639 | 17.4519 | 17.0676 | 16.6789 | 16.1545 | 15.4227 | 14.6949 | 13.6559 | 12.8121 | 8.9258 | 6.5328 | 4.409 | 21.8523 | 21.7703 | 21.6788 | 21.5811 | 21.4483 | 21.3023 | 20.938 | 20.3544 | 19.7464 | 18.8414 | 18.1577 | 14.7628 | 13.5803 | 11.9618 | 20.8794 | 20.7334 | 20.5591 | 20.3656 | 20.1128 | 19.8158 | 19.3681 | 18.6708 | 17.7555 | 16.6323 | 15.6583 | 11.4016 | 9.7446 | 8.6484
|  | FRASERBURGH | FS |  |  |  | 2.267 | 18.5367 | 18.3062 | 18.0898 | 17.8773 | 17.6147 | 17.3309 | 17.012 | 16.389 | 15.5686 | 15.043 | 14.3269 | 10.2357 | 6.2953 | 3.3175 | 21.8737 | 21.8093 | 21.7438 | 21.6741 | 21.5815 | 21.4742 | 21.291 | 20.9266 | 20.2853 | 19.9092 | 19.3615 | 16.2535 | 12.976 | 9.7115 | 20.9229 | 20.8162 | 20.6962 | 20.565 | 20.3975 | 20.2036 | 19.9333 | 19.4978 | 18.8438 | 18.3216 | 17.6816 | 13.9694 | 10.4164 | 7.6449
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0.006 | 2.8188 | 2.7825 | 2.7476 | 2.7141 | 2.5138 | 2.2559 | 2.008 | 1.7891 | 1.5584 | 1.3895 | 1.2139 | 0.70514 | 0.46636 | 0.21634 | 3.4113 | 3.3557 | 3.2689 | 3.1809 | 3.0684 | 2.9282 | 2.7982 | 2.6649 | 2.5101 | 2.409 | 2.2923 | 2.0171 | 1.8776 | 1.6541 | 3.1093 | 3.0186 | 2.8734 | 2.717 | 2.5185 | 2.281 | 2.0568 | 1.8442 | 1.6099 | 1.447 | 1.2697 | 0.8044 | 0.60538 | 0.39162
|  | FRIOCKHEIM | CT |  |  |  | 0.006 | 2.821 | 2.7918 | 2.7601 | 2.7236 | 2.5138 | 2.2574 | 2.009 | 1.7966 | 1.6244 | 1.4917 | 1.3576 | 0.79692 | 0.46665 | 0.21634 | 3.4113 | 3.3557 | 3.2714 | 3.184 | 3.0684 | 2.9401 | 2.8167 | 2.6806 | 2.5726 | 2.4906 | 2.3926 | 2.0605 | 1.8776 | 1.6541 | 3.1093 | 3.0186 | 2.8734 | 2.7196 | 2.5185 | 2.2934 | 2.0739 | 1.8646 | 1.6974 | 1.5698 | 1.4303 | 0.92035 | 0.65619 | 0.44143
|  | FRIOCKHEIM | LW |  |  |  | 0.006 | 2.8188 | 2.7825 | 2.7476 | 2.7141 | 2.5294 | 2.2559 | 2.008 | 1.7891 | 1.5584 | 1.3895 | 1.2139 | 0.70514 | 0.46636 | 0.23786 | 3.4164 | 3.357 | 3.2689 | 3.1809 | 3.079 | 2.9282 | 2.7982 | 2.6649 | 2.5101 | 2.409 | 2.2923 | 2.0171 | 1.9139 | 1.7823 | 3.1186 | 3.0264 | 2.8744 | 2.717 | 2.5319 | 2.281 | 2.0568 | 1.8442 | 1.6099 | 1.447 | 1.2697 | 0.8044 | 0.60538 | 0.39162
|  | FRIOCKHEIM | ST |  |  |  | 0.006 | 2.8307 | 2.8174 | 2.7996 | 2.7791 | 2.7471 | 2.718 | 2.688 | 2.6038 | 2.4925 | 2.4068 | 2.2919 | 1.6931 | 1.3146 | 1.006 | 3.4325 | 3.3991 | 3.3572 | 3.3127 | 3.2543 | 3.2036 | 3.1418 | 3.0805 | 2.9976 | 2.9414 | 2.8543 | 2.4038 | 2.1553 | 1.9162 | 3.1452 | 3.0885 | 3.019 | 2.9448 | 2.851 | 2.7679 | 2.674 | 2.5848 | 2.4691 | 2.387 | 2.2672 | 1.6606 | 1.3296 | 1.0748
|  | FRIOCKHEIM | FS |  |  |  | 0.006 | 2.8335 | 2.8231 | 2.8122 | 2.7958 | 2.7745 | 2.7482 | 2.7327 | 2.708 | 2.6768 | 2.6419 | 2.6168 | 2.0561 | 1.4953 | 1.1267 | 3.4463 | 3.4215 | 3.3996 | 3.3679 | 3.3361 | 3.2927 | 3.2631 | 3.2053 | 3.1409 | 3.0696 | 3.0228 | 2.6043 | 2.1779 | 1.7835 | 3.1741 | 3.1347 | 3.1025 | 3.057 | 3.013 | 2.9556 | 2.9179 | 2.8345 | 2.744 | 2.6451 | 2.5764 | 2.0153 | 1.504 | 1.1979
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.149 | 5.0468 | 4.91 | 4.7263 | 4.4947 | 4.2361 | 3.9735 | 3.6529 | 3.4179 | 3.2742 | 3.1485 | 3.008 | 2.6252 | 2.3905 | 2.1602 | 3.7609 | 3.712 | 3.6335 | 3.5197 | 3.3935 | 3.2752 | 3.1154 | 2.9474 | 2.8532 | 2.7845 | 2.6923 | 2.4617 | 2.303 | 1.98 | 5.58 | 5.4704 | 5.3049 | 5.096 | 4.8637 | 4.6302 | 4.3417 | 4.1263 | 3.9981 | 3.8829 | 3.7567 | 3.4097 | 3.2009 | 3.0004
|  | FYVIE | CT |  |  |  | 0.149 | 5.0468 | 4.91 | 4.7263 | 4.4947 | 4.2361 | 3.9735 | 3.6529 | 3.4179 | 3.2742 | 3.1824 | 3.0774 | 2.7005 | 2.4906 | 2.2755 | 3.7609 | 3.712 | 3.6335 | 3.5197 | 3.3935 | 3.2752 | 3.1154 | 2.9474 | 2.8532 | 2.7933 | 2.7147 | 2.4617 | 2.303 | 2.0758 | 5.58 | 5.4704 | 5.3049 | 5.096 | 4.8637 | 4.6302 | 4.3417 | 4.1263 | 3.9981 | 3.9129 | 3.8198 | 3.4813 | 3.2936 | 3.1052
|  | FYVIE | LW |  |  |  | 0.149 | 5.0724 | 4.9524 | 4.7551 | 4.5389 | 4.2988 | 4.0241 | 3.7144 | 3.4621 | 3.3082 | 3.1485 | 3.008 | 2.6252 | 2.3905 | 2.1602 | 3.7616 | 3.7161 | 3.6476 | 3.5501 | 3.4413 | 3.3128 | 3.1589 | 2.9819 | 2.8879 | 2.7845 | 2.6923 | 2.477 | 2.386 | 2.2816 | 5.5853 | 5.5095 | 5.3321 | 5.1386 | 4.9233 | 4.6788 | 4.399 | 4.1678 | 4.0265 | 3.8829 | 3.7567 | 3.4097 | 3.2009 | 3.0004
|  | FYVIE | ST |  |  |  | 0.149 | 5.0975 | 4.993 | 4.8582 | 4.7143 | 4.5588 | 4.4139 | 4.2594 | 4.0581 | 3.9212 | 3.7609 | 3.595 | 2.9772 | 2.7113 | 2.5623 | 3.7789 | 3.7527 | 3.7075 | 3.6404 | 3.5637 | 3.4959 | 3.4181 | 3.2843 | 3.2064 | 3.1104 | 3.0089 | 2.5873 | 2.3847 | 2.1863 | 5.6073 | 5.5452 | 5.425 | 5.2968 | 5.1582 | 5.0295 | 4.8915 | 4.7066 | 4.5837 | 4.439 | 4.289 | 3.727 | 3.4727 | 3.3596
|  | FYVIE | FS |  |  |  | 0.149 | 5.1611 | 5.0978 | 5.0533 | 5.0022 | 4.9426 | 4.8789 | 4.8336 | 4.6889 | 4.5641 | 4.4354 | 4.3301 | 3.6866 | 3.0125 | 2.7468 | 3.7883 | 3.7709 | 3.753 | 3.7311 | 3.7045 | 3.6737 | 3.6442 | 3.5484 | 3.4722 | 3.3924 | 3.3305 | 2.9022 | 2.3962 | 1.98 | 5.6281 | 5.5998 | 5.5735 | 5.5424 | 5.5056 | 5.4529 | 5.4136 | 5.2813 | 5.1692 | 5.0535 | 4.9612 | 4.3759 | 3.7623 | 3.5134
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | YES | 0 | 0.1141 | 0.10655 | 0.098216 | 0.09063 | 0.085478 | 0.077697 | 0.066566 | 0.065984 | 0.065243 | 0.064558 | 0.063921 | 0.050452 | 0.028411 | 0.0039213 | 0.10756 | 0.098199 | 0.087858 | 0.078485 | 0.072164 | 0.062639 | 0.048965 | 0.048507 | 0.047925 | 0.047386 | 0.046885 | 0.030616 | 0.0030652 | -0.027547 | 0.11037 | 0.10108 | 0.090714 | 0.081314 | 0.074963 | 0.065388 | 0.051655 | 0.051131 | 0.050447 | 0.049789 | 0.049177 | 0.032695 | 0.0051439 | -0.025468
|  | GARBAT FOREST | CT |  |  |  | 0 | 0.11413 | 0.11395 | 0.11372 | 0.10602 | 0.1041 | 0.10138 | 0.095301 | 0.093973 | 0.092766 | 0.091559 | 0.090396 | 0.083875 | 0.07816 | 0.069997 | 0.10759 | 0.10742 | 0.10724 | 0.097778 | 0.095512 | 0.092237 | 0.084808 | 0.083386 | 0.082058 | 0.08073 | 0.079437 | 0.07166 | 0.064517 | 0.054313 | 0.11037 | 0.1103 | 0.11009 | 0.10059 | 0.098294 | 0.094988 | 0.087517 | 0.086036 | 0.084663 | 0.083285 | 0.081933 | 0.074014 | 0.066872 | 0.056667
|  | GARBAT FOREST | LW |  |  |  | 0 | 0.1141 | 0.10655 | 0.098216 | 0.09063 | 0.085478 | 0.077697 | 0.066566 | 0.065984 | 0.065243 | 0.064558 | 0.063921 | 0.050452 | 0.028411 | 0.0039213 | 0.10756 | 0.098199 | 0.087858 | 0.078485 | 0.072164 | 0.062639 | 0.048965 | 0.048507 | 0.047925 | 0.047386 | 0.046885 | 0.030616 | 0.0030652 | -0.027547 | 0.11037 | 0.10108 | 0.090714 | 0.081314 | 0.074963 | 0.065388 | 0.051655 | 0.051131 | 0.050447 | 0.049789 | 0.049177 | 0.032695 | 0.0051439 | -0.025468
|  | GARBAT FOREST | ST |  |  |  | 0 | 0.11417 | 0.11411 | 0.10913 | 0.10574 | 0.10394 | 0.10291 | 0.10183 | 0.10069 | 0.099439 | 0.098147 | 0.097607 | 0.075194 | 0.049913 | 0.027045 | 0.10763 | 0.10757 | 0.10137 | 0.097182 | 0.095008 | 0.093821 | 0.092593 | 0.091318 | 0.089955 | 0.08856 | 0.088136 | 0.061427 | 0.030193 | 0.0016124 | 0.11038 | 0.11037 | 0.10424 | 0.10006 | 0.097865 | 0.096653 | 0.095396 | 0.094084 | 0.09267 | 0.091221 | 0.090734 | 0.06355 | 0.032178 | 0.0035954
|  | GARBAT FOREST | FS |  |  |  | 0 | 0.11418 | 0.11414 | 0.11244 | 0.11074 | 0.10899 | 0.10723 | 0.10462 | 0.1028 | 0.1001 | 0.097388 | 0.097095 | 0.095147 | 0.093399 | 0.089074 | 0.10764 | 0.10759 | 0.10549 | 0.10338 | 0.10125 | 0.099105 | 0.095918 | 0.09373 | 0.090471 | 0.087207 | 0.086976 | 0.085444 | 0.084069 | 0.079155 | 0.11038 | 0.11037 | 0.10833 | 0.10627 | 0.10413 | 0.10196 | 0.098759 | 0.096549 | 0.093262 | 0.089968 | 0.089703 | 0.087914 | 0.086234 | 0.081136
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0.093 | -0.95403 | -0.98754 | -1.0443 | -1.1215 | -1.1899 | -1.2576 | -1.3599 | -1.4262 | -1.4996 | -1.5606 | -1.6291 | -1.862 | -1.9942 | -2.1221 | -0.76298 | -0.79592 | -0.83625 | -0.89141 | -0.9298 | -0.97843 | -1.0495 | -1.0889 | -1.1453 | -1.1796 | -1.226 | -1.3703 | -1.4589 | -1.557 | -0.70111 | -0.72959 | -0.7641 | -0.83547 | -0.87446 | -0.91751 | -0.99168 | -1.0494 | -1.1287 | -1.1862 | -1.2527 | -1.4768 | -1.6088 | -1.742
|  | GISLA | CT |  |  |  | 0.093 | -0.95403 | -0.98159 | -1.0311 | -1.1215 | -1.1899 | -1.2576 | -1.3599 | -1.4262 | -1.4873 | -1.5454 | -1.5797 | -1.7771 | -1.8975 | -1.9791 | -0.76298 | -0.78354 | -0.81093 | -0.87569 | -0.91595 | -0.94972 | -1.0166 | -1.0563 | -1.0957 | -1.137 | -1.1555 | -1.2648 | -1.3194 | -1.3793 | -0.70111 | -0.72143 | -0.75242 | -0.83547 | -0.87446 | -0.91751 | -0.99168 | -1.0388 | -1.0973 | -1.1542 | -1.1864 | -1.3695 | -1.4764 | -1.5545
|  | GISLA | LW |  |  |  | 0.093 | -0.95087 | -0.98754 | -1.0443 | -1.1192 | -1.1808 | -1.2538 | -1.349 | -1.4178 | -1.4996 | -1.5606 | -1.6291 | -1.862 | -1.9942 | -2.1221 | -0.76148 | -0.79592 | -0.83625 | -0.89141 | -0.9298 | -0.97843 | -1.0495 | -1.0889 | -1.1453 | -1.1796 | -1.226 | -1.3703 | -1.4589 | -1.557 | -0.69865 | -0.72959 | -0.7641 | -0.81508 | -0.84813 | -0.89428 | -0.98496 | -1.0494 | -1.1287 | -1.1862 | -1.2527 | -1.4768 | -1.6088 | -1.742
|  | GISLA | ST |  |  |  | 0.093 | -0.94705 | -0.95537 | -0.98178 | -1.0212 | -1.0453 | -1.0666 | -1.0943 | -1.115 | -1.149 | -1.1847 | -1.2143 | -1.4764 | -1.6703 | -1.8165 | -0.7613 | -0.76372 | -0.78506 | -0.81874 | -0.83676 | -0.85079 | -0.87209 | -0.88726 | -0.91691 | -0.94779 | -0.97048 | -1.1728 | -1.3043 | -1.4049 | -0.69567 | -0.69977 | -0.71905 | -0.75086 | -0.76692 | -0.78166 | -0.8011 | -0.8214 | -0.85295 | -0.88739 | -0.92222 | -1.1736 | -1.3071 | -1.4454
|  | GISLA | FS |  |  |  | 0.093 | -0.94174 | -0.94899 | -0.9591 | -0.98363 | -1.0014 | -1.0182 | -1.036 | -1.0639 | -1.0973 | -1.1218 | -1.1524 | -1.3416 | -1.5487 | -1.7303 | -0.75832 | -0.76126 | -0.76747 | -0.78875 | -0.80401 | -0.81791 | -0.83331 | -0.8541 | -0.88085 | -0.8971 | -0.91966 | -1.053 | -1.1823 | -1.2974 | -0.69367 | -0.69603 | -0.70225 | -0.72151 | -0.73315 | -0.74469 | -0.75977 | -0.77578 | -0.79772 | -0.81698 | -0.83752 | -0.981 | -1.1614 | -1.3265
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 0.107 | -1.3025 | -1.3355 | -1.4209 | -1.566 | -1.6846 | -1.8303 | -2.0427 | -2.1007 | -2.1454 | -2.1903 | -2.2386 | -2.4082 | -2.5135 | -2.6436 | -0.52623 | -0.58016 | -0.63929 | -0.72687 | -0.78577 | -0.86833 | -0.95139 | -0.99951 | -1.0585 | -1.0913 | -1.1364 | -1.2517 | -1.3124 | -1.408 | -0.83747 | -0.89591 | -0.9774 | -1.0909 | -1.173 | -1.2753 | -1.4057 | -1.44 | -1.4653 | -1.4887 | -1.5191 | -1.6784 | -1.7621 | -1.8837
|  | GLASTULLICH | CT |  |  |  | 0.107 | -1.1276 | -1.154 | -1.2566 | -1.4036 | -1.6103 | -1.8268 | -2.0427 | -2.1007 | -2.1454 | -2.1903 | -2.1981 | -2.3268 | -2.4104 | -2.5123 | -0.37734 | -0.42646 | -0.47338 | -0.55598 | -0.68709 | -0.82194 | -0.95139 | -0.99951 | -1.0374 | -1.0784 | -1.093 | -1.2116 | -1.2874 | -1.408 | -0.67084 | -0.72455 | -0.79417 | -0.9052 | -1.0685 | -1.2387 | -1.4057 | -1.44 | -1.4639 | -1.4862 | -1.4863 | -1.5916 | -1.6525 | -1.7337
|  | GLASTULLICH | LW |  |  |  | 0.107 | -1.3025 | -1.3355 | -1.4209 | -1.566 | -1.6846 | -1.8303 | -1.9799 | -2.0495 | -2.1341 | -2.1799 | -2.2386 | -2.4082 | -2.5135 | -2.6436 | -0.52623 | -0.58016 | -0.63929 | -0.72687 | -0.78577 | -0.86833 | -0.948 | -0.99616 | -1.0585 | -1.0913 | -1.1364 | -1.2517 | -1.3124 | -1.3993 | -0.83747 | -0.89591 | -0.9774 | -1.0909 | -1.173 | -1.2753 | -1.3801 | -1.4192 | -1.4653 | -1.4887 | -1.5191 | -1.6784 | -1.7621 | -1.8837
|  | GLASTULLICH | ST |  |  |  | 0.107 | -1.1237 | -1.1401 | -1.1664 | -1.2488 | -1.3693 | -1.498 | -1.6113 | -1.6692 | -1.7244 | -1.7949 | -1.8635 | -2.155 | -2.2791 | -2.3425 | -0.36615 | -0.39591 | -0.42627 | -0.48105 | -0.56868 | -0.66499 | -0.74728 | -0.78514 | -0.81731 | -0.86208 | -0.90538 | -1.1255 | -1.2441 | -1.3532 | -0.65961 | -0.69832 | -0.73695 | -0.80066 | -0.90407 | -1.0132 | -1.1086 | -1.1478 | -1.1832 | -1.227 | -1.2696 | -1.4513 | -1.5468 | -1.6011
|  | GLASTULLICH | FS |  |  |  | 0.107 | -0.89546 | -0.92879 | -0.93551 | -1.0001 | -1.0322 | -1.0961 | -1.1307 | -1.1783 | -1.2339 | -1.3353 | -1.4416 | -1.8704 | -2.1376 | -2.2432 | -0.15563 | -0.19586 | -0.21071 | -0.27582 | -0.31489 | -0.37881 | -0.42273 | -0.4585 | -0.49596 | -0.5751 | -0.65975 | -0.99156 | -1.2062 | -1.3995 | -0.41448 | -0.46094 | -0.47303 | -0.54214 | -0.57967 | -0.64738 | -0.6877 | -0.72684 | -0.76225 | -0.84433 | -0.93823 | -1.2535 | -1.4245 | -1.5066
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | YES | 0.478 | 0.874 | 0.81446 | 0.74273 | 0.66491 | 0.57837 | 0.47536 | 0.30858 | 0.24991 | 0.16362 | 0.082834 | 0.0088453 | -0.15975 | -0.24207 | -0.34935 | 1.4124 | 1.3781 | 1.3311 | 1.2871 | 1.2383 | 1.1761 | 1.0777 | 1.0385 | 0.98192 | 0.92863 | 0.87949 | 0.76381 | 0.70704 | 0.62723 | 1.1875 | 1.1471 | 1.0857 | 1.0153 | 0.93719 | 0.84572 | 0.69847 | 0.64327 | 0.55985 | 0.48151 | 0.40988 | 0.24684 | 0.1663 | 0.063913
|  | GLEDFIELD | CT |  |  |  | 0.478 | 0.874 | 0.81446 | 0.75368 | 0.66491 | 0.57837 | 0.47557 | 0.33105 | 0.25361 | 0.19937 | 0.13462 | 0.077155 | -0.050239 | -0.12108 | -0.21073 | 1.4124 | 1.3791 | 1.3469 | 1.294 | 1.2471 | 1.191 | 1.1121 | 1.0577 | 1.0212 | 0.97699 | 0.93637 | 0.837 | 0.77603 | 0.68422 | 1.1875 | 1.1471 | 1.0949 | 1.0169 | 0.94035 | 0.85227 | 0.72949 | 0.65634 | 0.60412 | 0.54084 | 0.4842 | 0.36351 | 0.30298 | 0.2321
|  | GLEDFIELD | LW |  |  |  | 0.478 | 0.88275 | 0.82254 | 0.74273 | 0.66845 | 0.58092 | 0.47536 | 0.30858 | 0.24991 | 0.16362 | 0.082834 | 0.0088453 | -0.15975 | -0.24207 | -0.34935 | 1.4167 | 1.3781 | 1.3311 | 1.2871 | 1.2383 | 1.1761 | 1.0777 | 1.0385 | 0.98192 | 0.92863 | 0.87949 | 0.76381 | 0.70704 | 0.62723 | 1.195 | 1.1501 | 1.0857 | 1.0153 | 0.93719 | 0.84572 | 0.69847 | 0.64327 | 0.55985 | 0.48151 | 0.40988 | 0.24684 | 0.1663 | 0.063913
|  | GLEDFIELD | ST |  |  |  | 0.478 | 0.88941 | 0.85906 | 0.80902 | 0.76173 | 0.70734 | 0.66676 | 0.58793 | 0.54132 | 0.47331 | 0.42925 | 0.36059 | 0.063326 | -0.040229 | -0.090986 | 1.4209 | 1.4056 | 1.3759 | 1.3487 | 1.318 | 1.2947 | 1.2491 | 1.221 | 1.1792 | 1.1497 | 1.1067 | 0.89034 | 0.78857 | 0.70354 | 1.1996 | 1.1736 | 1.1302 | 1.0884 | 1.0436 | 1.0023 | 0.94315 | 0.90361 | 0.8546 | 0.81295 | 0.75475 | 0.46352 | 0.35982 | 0.30196
|  | GLEDFIELD | FS |  |  |  | 0.478 | 0.9113 | 0.88758 | 0.87373 | 0.84929 | 0.83266 | 0.80569 | 0.77937 | 0.7319 | 0.69038 | 0.63787 | 0.58474 | 0.33164 | 0.070686 | -0.0086437 | 1.4307 | 1.4179 | 1.4075 | 1.3911 | 1.3787 | 1.36 | 1.3393 | 1.3093 | 1.2815 | 1.2471 | 1.2134 | 1.0387 | 0.84045 | 0.70061 | 1.2186 | 1.2014 | 1.1886 | 1.1723 | 1.1579 | 1.14 | 1.1181 | 1.0834 | 1.0491 | 1.0069 | 0.95665 | 0.71785 | 0.47354 | 0.39992
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.10776 | 0.10039 | 0.092214 | 0.084846 | 0.079924 | 0.072507 | 0.061627 | 0.061283 | 0.060781 | 0.060316 | 0.059884 | 0.046805 | 0.024764 | 0.00027407 | 0.087558 | 0.078361 | 0.068147 | 0.05895 | 0.052813 | 0.043605 | 0.03031 | 0.030277 | 0.030235 | 0.030188 | 0.029848 | 0.013889 | -0.013662 | -0.044274 | 0.10567 | 0.096445 | 0.086201 | 0.076961 | 0.070778 | 0.061492 | 0.048033 | 0.047654 | 0.047171 | 0.046725 | 0.04631 | 0.030206 | 0.002655 | -0.027957
|  | GLEN LAOGH | CT |  |  |  | 0 | 0.10776 | 0.10774 | 0.10772 | 0.10034 | 0.098686 | 0.096185 | 0.090283 | 0.089197 | 0.088115 | 0.087034 | 0.085983 | 0.079721 | 0.074007 | 0.065843 | 0.08756 | 0.087548 | 0.087534 | 0.078331 | 0.076274 | 0.073197 | 0.066034 | 0.064984 | 0.063942 | 0.062899 | 0.061859 | 0.054531 | 0.047388 | 0.037184 | 0.10568 | 0.10564 | 0.10559 | 0.09632 | 0.094211 | 0.091086 | 0.083854 | 0.082501 | 0.081225 | 0.07995 | 0.078704 | 0.071035 | 0.063893 | 0.053688
|  | GLEN LAOGH | LW |  |  |  | 0 | 0.10776 | 0.10039 | 0.092214 | 0.084846 | 0.079924 | 0.072507 | 0.061627 | 0.061283 | 0.060781 | 0.060316 | 0.059884 | 0.046805 | 0.024764 | 0.00027407 | 0.087558 | 0.078361 | 0.068147 | 0.05895 | 0.052813 | 0.043605 | 0.03031 | 0.030277 | 0.030235 | 0.030188 | 0.029848 | 0.013889 | -0.013662 | -0.044274 | 0.10567 | 0.096445 | 0.086201 | 0.076961 | 0.070778 | 0.061492 | 0.048033 | 0.047654 | 0.047171 | 0.046725 | 0.04631 | 0.030206 | 0.002655 | -0.027957
|  | GLEN LAOGH | ST |  |  |  | 0 | 0.10777 | 0.10776 | 0.10286 | 0.099578 | 0.09793 | 0.097094 | 0.096254 | 0.095408 | 0.094394 | 0.093332 | 0.092975 | 0.071469 | 0.046415 | 0.02355 | 0.087563 | 0.087558 | 0.08143 | 0.077341 | 0.075291 | 0.074258 | 0.073223 | 0.072184 | 0.071139 | 0.070092 | 0.070061 | 0.044636 | 0.013602 | -0.014975 | 0.10569 | 0.10568 | 0.099534 | 0.095425 | 0.093346 | 0.092276 | 0.091193 | 0.090096 | 0.088972 | 0.087663 | 0.087311 | 0.060983 | 0.029855 | 0.0012763
|  | GLEN LAOGH | FS |  |  |  | 0 | 0.10777 | 0.10777 | 0.10613 | 0.10448 | 0.10284 | 0.1012 | 0.098733 | 0.097083 | 0.094611 | 0.092139 | 0.091999 | 0.090781 | 0.089595 | 0.085583 | 0.087563 | 0.08756 | 0.085515 | 0.083469 | 0.081422 | 0.079373 | 0.076303 | 0.074252 | 0.071176 | 0.0681 | 0.068084 | 0.067973 | 0.067216 | 0.062569 | 0.1057 | 0.10568 | 0.10363 | 0.10157 | 0.099504 | 0.097433 | 0.094334 | 0.092248 | 0.089128 | 0.086005 | 0.085936 | 0.084731 | 0.083592 | 0.07882
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0.308 | 0.89679 | 0.80666 | 0.72369 | 0.61345 | 0.50729 | 0.3834 | 0.24533 | 0.14993 | 0.079654 | -0.021398 | -0.11438 | -0.3423 | -0.46404 | -0.59956 | 1.5122 | 1.4584 | 1.4048 | 1.3479 | 1.2895 | 1.2195 | 1.1396 | 1.0696 | 1.0019 | 0.92737 | 0.85825 | 0.70466 | 0.62853 | 0.53405 | 1.3369 | 1.255 | 1.1741 | 1.0746 | 0.9765 | 0.86148 | 0.73248 | 0.63978 | 0.5619 | 0.46348 | 0.37287 | 0.15483 | 0.037992 | -0.09549
|  | GLENCOE | CT |  |  |  | 0.308 | 0.89679 | 0.80666 | 0.72702 | 0.61345 | 0.50729 | 0.3834 | 0.24533 | 0.14993 | 0.084766 | 0.011139 | -0.060251 | -0.23868 | -0.32914 | -0.43068 | 1.5122 | 1.4596 | 1.4175 | 1.3479 | 1.2895 | 1.2195 | 1.1396 | 1.0696 | 1.0215 | 0.96424 | 0.90869 | 0.7784 | 0.71206 | 0.61592 | 1.3369 | 1.255 | 1.1821 | 1.0746 | 0.9765 | 0.86148 | 0.73248 | 0.63978 | 0.57651 | 0.50419 | 0.43445 | 0.26454 | 0.182 | 0.086523
|  | GLENCOE | LW |  |  |  | 0.308 | 0.90571 | 0.81352 | 0.72369 | 0.63682 | 0.54665 | 0.41397 | 0.28327 | 0.18713 | 0.079654 | -0.021398 | -0.11438 | -0.3423 | -0.46404 | -0.59956 | 1.5164 | 1.4584 | 1.4048 | 1.3557 | 1.3078 | 1.2266 | 1.1479 | 1.0802 | 1.0019 | 0.92737 | 0.85825 | 0.70466 | 0.62853 | 0.53405 | 1.3449 | 1.2592 | 1.1741 | 1.0924 | 1.0091 | 0.88317 | 0.75915 | 0.66635 | 0.5619 | 0.46348 | 0.37287 | 0.15483 | 0.037992 | -0.09549
|  | GLENCOE | ST |  |  |  | 0.308 | 0.91461 | 0.85851 | 0.80471 | 0.7528 | 0.69347 | 0.64375 | 0.57674 | 0.52185 | 0.44382 | 0.38459 | 0.2969 | -0.10164 | -0.21679 | -0.27942 | 1.5228 | 1.4951 | 1.4635 | 1.434 | 1.3993 | 1.3727 | 1.3321 | 1.2983 | 1.2457 | 1.2083 | 1.1494 | 0.84988 | 0.75315 | 0.67198 | 1.3536 | 1.3048 | 1.254 | 1.2056 | 1.1502 | 1.1046 | 1.0419 | 0.99043 | 0.91598 | 0.86029 | 0.77723 | 0.38942 | 0.27736 | 0.21427
|  | GLENCOE | FS |  |  |  | 0.308 | 0.93762 | 0.89563 | 0.8783 | 0.85763 | 0.83052 | 0.79973 | 0.7787 | 0.72904 | 0.68156 | 0.62342 | 0.55974 | 0.24379 | -0.10634 | -0.26719 | 1.5324 | 1.5095 | 1.4975 | 1.4828 | 1.4629 | 1.4399 | 1.4239 | 1.3911 | 1.3594 | 1.3191 | 1.2764 | 1.0553 | 0.79399 | 0.6107 | 1.374 | 1.3371 | 1.3205 | 1.3006 | 1.2742 | 1.2443 | 1.2239 | 1.1768 | 1.1318 | 1.0761 | 1.0163 | 0.71747 | 0.38803 | 0.23641
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.023 | 0.21448 | 0.21169 | 0.19628 | 0.17989 | 0.15878 | 0.14075 | 0.11651 | 0.10824 | 0.099807 | 0.090071 | 0.077646 | 0.059808 | 0.049579 | 0.036214 | 0.2998 | 0.29915 | 0.28885 | 0.28493 | 0.27286 | 0.26471 | 0.25135 | 0.2436 | 0.23421 | 0.22133 | 0.20967 | 0.19821 | 0.19411 | 0.1857 | 0.25757 | 0.25543 | 0.24143 | 0.2266 | 0.20717 | 0.19092 | 0.16862 | 0.16054 | 0.15218 | 0.13903 | 0.12445 | 0.10813 | 0.099804 | 0.086855
|  | GLENDARUEL | CT |  |  |  | 0.023 | 0.21448 | 0.21169 | 0.19628 | 0.17989 | 0.15878 | 0.14075 | 0.11651 | 0.10824 | 0.099807 | 0.091036 | 0.083682 | 0.072805 | 0.064365 | 0.053057 | 0.2998 | 0.3004 | 0.2926 | 0.28493 | 0.27286 | 0.26471 | 0.25135 | 0.2436 | 0.23511 | 0.22565 | 0.21696 | 0.20605 | 0.19899 | 0.18629 | 0.25757 | 0.25543 | 0.24143 | 0.2266 | 0.20717 | 0.19092 | 0.16862 | 0.16054 | 0.15218 | 0.14297 | 0.13384 | 0.12249 | 0.11552 | 0.10498
|  | GLENDARUEL | LW |  |  |  | 0.023 | 0.21592 | 0.21433 | 0.20169 | 0.18753 | 0.17079 | 0.15213 | 0.12984 | 0.1202 | 0.10407 | 0.090071 | 0.077646 | 0.059808 | 0.049579 | 0.036214 | 0.30048 | 0.30179 | 0.29574 | 0.28889 | 0.28001 | 0.26985 | 0.2569 | 0.24891 | 0.23421 | 0.22133 | 0.20967 | 0.19821 | 0.19411 | 0.18591 | 0.25885 | 0.25782 | 0.24639 | 0.23356 | 0.21825 | 0.20112 | 0.18048 | 0.17118 | 0.15485 | 0.13903 | 0.12445 | 0.10813 | 0.099804 | 0.086855
|  | GLENDARUEL | ST |  |  |  | 0.023 | 0.22294 | 0.21241 | 0.19874 | 0.19747 | 0.19427 | 0.18652 | 0.17886 | 0.17143 | 0.15942 | 0.14873 | 0.13557 | 0.094762 | 0.079507 | 0.074827 | 0.30721 | 0.29915 | 0.28885 | 0.29135 | 0.29203 | 0.2878 | 0.2838 | 0.27925 | 0.27006 | 0.26251 | 0.25227 | 0.22049 | 0.20769 | 0.19947 | 0.26584 | 0.25581 | 0.24283 | 0.24229 | 0.23976 | 0.23268 | 0.22569 | 0.21881 | 0.20738 | 0.19727 | 0.1847 | 0.14442 | 0.13004 | 0.12601
|  | GLENDARUEL | FS |  |  |  | 0.023 | 0.22687 | 0.21913 | 0.21147 | 0.21433 | 0.21542 | 0.21025 | 0.20761 | 0.20278 | 0.1937 | 0.18813 | 0.17891 | 0.13497 | 0.096521 | 0.07988 | 0.30913 | 0.30282 | 0.2958 | 0.29907 | 0.30102 | 0.29637 | 0.2942 | 0.29152 | 0.28446 | 0.28101 | 0.27381 | 0.23923 | 0.20939 | 0.1857 | 0.26939 | 0.26195 | 0.25444 | 0.25727 | 0.25874 | 0.25374 | 0.25125 | 0.24686 | 0.23777 | 0.23282 | 0.22325 | 0.17881 | 0.1442 | 0.12939
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.01 | 3.5007 | 3.4201 | 3.3169 | 3.1811 | 3.0187 | 2.8501 | 2.6491 | 2.5404 | 2.4154 | 2.1858 | 1.969 | 1.6715 | 1.5391 | 1.414 | 3.6033 | 3.5602 | 3.509 | 3.4437 | 3.3668 | 3.2828 | 3.1813 | 3.1079 | 3.0186 | 2.8307 | 2.6182 | 2.3743 | 2.32 | 2.2491 | 3.7304 | 3.6563 | 3.566 | 3.4458 | 3.303 | 3.1594 | 2.9797 | 2.8701 | 2.7474 | 2.5387 | 2.3363 | 2.0556 | 1.9352 | 1.8151
|  | GLENDEVON | CT |  |  |  | 0.01 | 3.5007 | 3.4201 | 3.3169 | 3.1811 | 3.0187 | 2.8501 | 2.6491 | 2.5404 | 2.4483 | 2.241 | 2.0509 | 1.7532 | 1.6474 | 1.5453 | 3.6033 | 3.5602 | 3.5139 | 3.4457 | 3.3668 | 3.291 | 3.1895 | 3.1239 | 3.0638 | 2.8785 | 2.6894 | 2.4688 | 2.3855 | 2.2682 | 3.7304 | 3.6563 | 3.566 | 3.4458 | 3.303 | 3.1594 | 2.9797 | 2.8782 | 2.7931 | 2.605 | 2.4267 | 2.1487 | 2.057 | 1.9647
|  | GLENDEVON | LW |  |  |  | 0.01 | 3.5137 | 3.4426 | 3.3282 | 3.1957 | 3.0412 | 2.8638 | 2.669 | 2.5446 | 2.4154 | 2.1858 | 1.969 | 1.6715 | 1.5391 | 1.414 | 3.6082 | 3.5672 | 3.509 | 3.4437 | 3.3697 | 3.2828 | 3.1813 | 3.1079 | 3.0186 | 2.8307 | 2.6182 | 2.3743 | 2.32 | 2.2705 | 3.7409 | 3.6739 | 3.5699 | 3.4523 | 3.3173 | 3.1614 | 2.9848 | 2.8701 | 2.7474 | 2.5387 | 2.3363 | 2.0556 | 1.9352 | 1.8151
|  | GLENDEVON | ST |  |  |  | 0.01 | 3.523 | 3.4706 | 3.3915 | 3.2996 | 3.211 | 3.1124 | 3.0108 | 2.9146 | 2.8263 | 2.5824 | 2.3491 | 1.8825 | 1.7026 | 1.5976 | 3.6147 | 3.5908 | 3.5519 | 3.5052 | 3.4636 | 3.4159 | 3.3639 | 3.3106 | 3.2636 | 3.0542 | 2.8487 | 2.4678 | 2.3462 | 2.2491 | 3.751 | 3.7053 | 3.635 | 3.5535 | 3.4779 | 3.3941 | 3.3048 | 3.2191 | 3.1423 | 2.9228 | 2.7096 | 2.2651 | 2.0976 | 2.0005
|  | GLENDEVON | FS |  |  |  | 0.01 | 3.5605 | 3.5279 | 3.5023 | 3.4663 | 3.4331 | 3.3888 | 3.3442 | 3.2768 | 3.196 | 3.0544 | 2.9058 | 2.3704 | 1.9712 | 1.8293 | 3.629 | 3.613 | 3.5975 | 3.5745 | 3.5548 | 3.5266 | 3.4962 | 3.4589 | 3.4081 | 3.2936 | 3.1682 | 2.7709 | 2.4681 | 2.2549 | 3.7827 | 3.754 | 3.7303 | 3.697 | 3.6683 | 3.6284 | 3.5869 | 3.529 | 3.4562 | 3.3318 | 3.1972 | 2.707 | 2.3461 | 2.221
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0.092 | 1.0409 | 1.0184 | 0.98033 | 0.93703 | 0.8935 | 0.83715 | 0.5347 | 0.4691 | 0.40483 | 0.3462 | 0.28477 | 0.17401 | 0.11532 | 0.03183 | 1.2113 | 1.1937 | 1.17 | 1.1435 | 1.1193 | 1.0842 | 0.94367 | 0.91043 | 0.86743 | 0.82864 | 0.79566 | 0.71834 | 0.67846 | 0.61442 | 1.2512 | 1.2326 | 1.1965 | 1.1564 | 1.117 | 1.0641 | 0.82169 | 0.76626 | 0.70607 | 0.65147 | 0.5988 | 0.4906 | 0.43326 | 0.34803
|  | GLENDOE | CT |  |  |  | 0.092 | 1.0409 | 1.0184 | 0.99019 | 0.94282 | 0.89663 | 0.85075 | 0.55183 | 0.50215 | 0.45327 | 0.40354 | 0.36642 | 0.22994 | 0.18376 | 0.12636 | 1.2113 | 1.1993 | 1.1877 | 1.1571 | 1.1316 | 1.1086 | 0.97475 | 0.94668 | 0.91584 | 0.88266 | 0.86037 | 0.77471 | 0.74934 | 0.70857 | 1.2535 | 1.2355 | 1.2108 | 1.167 | 1.1255 | 1.0851 | 0.84788 | 0.80409 | 0.75955 | 0.71337 | 0.68009 | 0.55538 | 0.51479 | 0.4604
|  | GLENDOE | LW |  |  |  | 0.092 | 1.0452 | 1.0184 | 0.98033 | 0.93703 | 0.8935 | 0.83715 | 0.5347 | 0.4691 | 0.40483 | 0.3462 | 0.28477 | 0.17401 | 0.11532 | 0.03183 | 1.2131 | 1.1937 | 1.17 | 1.1435 | 1.1193 | 1.0842 | 0.94367 | 0.91043 | 0.86743 | 0.82864 | 0.79566 | 0.71834 | 0.67846 | 0.61442 | 1.2574 | 1.2326 | 1.1965 | 1.1564 | 1.117 | 1.0641 | 0.82169 | 0.76626 | 0.70607 | 0.65147 | 0.5988 | 0.4906 | 0.43326 | 0.34803
|  | GLENDOE | ST |  |  |  | 0.092 | 1.0484 | 1.0339 | 1.0124 | 0.98753 | 0.9648 | 0.94116 | 0.7713 | 0.73303 | 0.69581 | 0.65245 | 0.61822 | 0.44365 | 0.36889 | 0.32304 | 1.2169 | 1.2094 | 1.1983 | 1.1839 | 1.1723 | 1.1602 | 1.0809 | 1.0575 | 1.0361 | 1.0083 | 0.99141 | 0.86319 | 0.80353 | 0.76177 | 1.2512 | 1.2461 | 1.2241 | 1.2017 | 1.1816 | 1.1616 | 1.0378 | 1.0037 | 0.97093 | 0.93145 | 0.90255 | 0.73282 | 0.65759 | 0.61101
|  | GLENDOE | FS |  |  |  | 0.092 | 1.0593 | 1.0415 | 1.0451 | 1.0353 | 1.0224 | 1.0127 | 0.90997 | 0.87129 | 0.83606 | 0.80598 | 0.77238 | 0.59499 | 0.46977 | 0.40912 | 1.2213 | 1.2084 | 1.2135 | 1.2061 | 1.1956 | 1.1887 | 1.1372 | 1.1158 | 1.0927 | 1.0751 | 1.0544 | 0.94558 | 0.8682 | 0.82076 | 1.2608 | 1.2455 | 1.2561 | 1.2483 | 1.2363 | 1.2269 | 1.1485 | 1.1162 | 1.0842 | 1.0578 | 1.0279 | 0.87056 | 0.75742 | 0.70284
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 3.978 | -2.4184 | -3.0874 | -3.9399 | -4.4871 | -5.0697 | -5.8599 | -6.6023 | -7.3906 | -8.2139 | -8.6007 | -9.1235 | -10.7295 | -11.375 | -12.04 | 0.54798 | 0.044057 | -0.54148 | -0.84534 | -1.1385 | -1.5613 | -1.9598 | -2.4055 | -2.8991 | -3.0522 | -3.3728 | -4.3207 | -4.733 | -5.3194 | -0.68427 | -1.2894 | -2.0568 | -2.5457 | -3.0594 | -3.7632 | -4.4328 | -5.1449 | -5.8994 | -6.2208 | -6.7083 | -8.1864 | -8.7619 | -9.3737
|  | GLENEAGLES | CT |  |  |  | 3.978 | -2.3466 | -2.9337 | -3.7479 | -4.3368 | -4.9991 | -5.805 | -6.6023 | -7.3906 | -8.0386 | -8.3213 | -8.7317 | -10.4979 | -11.3648 | -12.0183 | 0.60926 | 0.17778 | -0.37789 | -0.72323 | -1.0801 | -1.5057 | -1.9383 | -2.4055 | -2.7792 | -2.8778 | -3.1368 | -4.2167 | -4.733 | -5.3194 | -0.6222 | -1.1521 | -1.886 | -2.4155 | -3.0052 | -3.7144 | -4.4311 | -5.1449 | -5.7267 | -5.9515 | -6.331 | -7.9319 | -8.6989 | -9.2863
|  | GLENEAGLES | LW |  |  |  | 3.978 | -2.4184 | -3.0874 | -3.9399 | -4.4871 | -5.0697 | -5.8599 | -6.5998 | -7.3836 | -8.2139 | -8.6007 | -9.1235 | -10.7295 | -11.375 | -12.04 | 0.54798 | 0.044057 | -0.54148 | -0.84534 | -1.1385 | -1.5613 | -1.9598 | -2.4024 | -2.8991 | -3.0522 | -3.3728 | -4.3207 | -4.6185 | -4.9836 | -0.68427 | -1.2894 | -2.0568 | -2.5457 | -3.0594 | -3.7632 | -4.4328 | -5.14 | -5.8994 | -6.2208 | -6.7083 | -8.1864 | -8.7619 | -9.3737
|  | GLENEAGLES | ST |  |  |  | 3.978 | -2.2625 | -2.7451 | -3.3248 | -3.63 | -3.9195 | -4.2693 | -4.5939 | -4.9602 | -5.3166 | -5.7009 | -6.0433 | -7.6489 | -8.5841 | -9.2501 | 0.66122 | 0.304 | -0.13966 | -0.34897 | -0.52637 | -0.73852 | -0.95052 | -1.1923 | -1.4255 | -1.6808 | -1.9236 | -3.0505 | -3.676 | -4.2236 | -0.54296 | -0.97167 | -1.494 | -1.7662 | -2.018 | -2.3149 | -2.6045 | -2.9295 | -3.2467 | -3.593 | -3.9148 | -5.4013 | -6.252 | -6.8404
|  | GLENEAGLES | FS |  |  |  | 3.978 | -2.1048 | -2.4596 | -2.8563 | -3.046 | -3.2426 | -3.4748 | -3.7107 | -3.9913 | -4.3404 | -4.6789 | -4.9539 | -6.9912 | -8.2453 | -9.4128 | 0.75706 | 0.48716 | 0.17043 | 0.031818 | -0.10061 | -0.25521 | -0.42721 | -0.60449 | -0.83833 | -1.0612 | -1.2453 | -2.7317 | -3.7015 | -4.8909 | -0.40609 | -0.72055 | -1.0777 | -1.2457 | -1.415 | -1.6136 | -1.8234 | -2.0651 | -2.3744 | -2.6733 | -2.9196 | -4.7948 | -5.9325 | -6.9945
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.34295 | 0.33497 | 0.32627 | 0.31826 | 0.31246 | 0.30321 | 0.29037 | 0.28797 | 0.28499 | 0.28235 | 0.27991 | 0.2627 | 0.23981 | 0.21461 | 0.31491 | 0.30528 | 0.29467 | 0.28496 | 0.27836 | 0.26833 | 0.25356 | 0.25161 | 0.24915 | 0.24697 | 0.24498 | 0.22593 | 0.19791 | 0.1669 | 0.3336 | 0.32344 | 0.31243 | 0.30217 | 0.295 | 0.28398 | 0.26857 | 0.26626 | 0.26337 | 0.26082 | 0.25847 | 0.23848 | 0.21019 | 0.17896
|  | GLENETIVE | CT |  |  |  | 0 | 0.34299 | 0.34233 | 0.34174 | 0.33364 | 0.33063 | 0.32683 | 0.31925 | 0.31613 | 0.31361 | 0.31098 | 0.30855 | 0.29903 | 0.29252 | 0.28368 | 0.31491 | 0.31429 | 0.31372 | 0.3039 | 0.30108 | 0.29723 | 0.28901 | 0.28661 | 0.28418 | 0.28165 | 0.27926 | 0.26905 | 0.25755 | 0.24004 | 0.33363 | 0.33269 | 0.3317 | 0.32123 | 0.31787 | 0.31352 | 0.30458 | 0.30134 | 0.29867 | 0.29589 | 0.2933 | 0.28254 | 0.2747 | 0.26391
|  | GLENETIVE | LW |  |  |  | 0 | 0.34295 | 0.33497 | 0.32627 | 0.31826 | 0.31246 | 0.30321 | 0.29037 | 0.28797 | 0.28499 | 0.28235 | 0.27991 | 0.2627 | 0.23981 | 0.21461 | 0.31497 | 0.30528 | 0.29467 | 0.28496 | 0.27836 | 0.26833 | 0.25356 | 0.25161 | 0.24915 | 0.24697 | 0.24498 | 0.22593 | 0.19791 | 0.1669 | 0.3336 | 0.32344 | 0.31243 | 0.30217 | 0.295 | 0.28398 | 0.26857 | 0.26626 | 0.26337 | 0.26082 | 0.25847 | 0.23848 | 0.21019 | 0.17896
|  | GLENETIVE | ST |  |  |  | 0 | 0.34317 | 0.34285 | 0.33762 | 0.33399 | 0.33193 | 0.3306 | 0.32899 | 0.32687 | 0.32433 | 0.32167 | 0.31963 | 0.28956 | 0.2622 | 0.23894 | 0.31506 | 0.31475 | 0.30828 | 0.30378 | 0.30127 | 0.29971 | 0.29807 | 0.29633 | 0.29442 | 0.29244 | 0.29115 | 0.25801 | 0.22508 | 0.18953 | 0.3338 | 0.33351 | 0.32704 | 0.32236 | 0.31959 | 0.31769 | 0.31561 | 0.31333 | 0.31065 | 0.30785 | 0.30587 | 0.27127 | 0.23793 | 0.20901
|  | GLENETIVE | FS |  |  |  | 0 | 0.34329 | 0.34305 | 0.3412 | 0.33932 | 0.3374 | 0.33543 | 0.3326 | 0.33051 | 0.32703 | 0.32349 | 0.32228 | 0.31463 | 0.3079 | 0.30141 | 0.31511 | 0.31481 | 0.31246 | 0.31005 | 0.30759 | 0.30508 | 0.30143 | 0.29866 | 0.29474 | 0.29079 | 0.28985 | 0.28342 | 0.27291 | 0.25375 | 0.33391 | 0.33369 | 0.33145 | 0.32902 | 0.3265 | 0.32388 | 0.32016 | 0.31732 | 0.31322 | 0.30911 | 0.30794 | 0.30054 | 0.29407 | 0.28692
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0 | 0.052353 | 0.04065 | 0.028667 | 0.015652 | 0.0051544 | -0.011457 | -0.019551 | -0.016788 | -0.022883 | -0.024105 | -0.028174 | -0.043175 | -0.067004 | -0.094576 | -3.302 | -3.3151 | -3.3283 | -3.3417 | -3.3513 | -3.3675 | -3.366 | -3.3664 | -3.3692 | -3.3707 | -3.3728 | -3.3908 | -3.4185 | -3.4495 | 0.044125 | 0.030472 | 0.016069 | 0.0013447 | -0.0097032 | -0.027662 | -0.030665 | -0.03092 | -0.03504 | -0.037127 | -0.040183 | -0.0595 | -0.088102 | -0.11974
|  | GLENUIG | CT |  |  |  | 0 | 0.052353 | 0.047679 | 0.043084 | 0.029576 | 0.02026 | 0.010177 | 0.0070529 | 0.0091442 | 0.0047491 | 0.0036554 | -0.00036314 | -0.0088572 | -0.016328 | -0.026965 | -3.302 | -3.3061 | -3.3098 | -3.323 | -3.3303 | -3.3384 | -3.3301 | -3.3314 | -3.334 | -3.3358 | -3.3383 | -3.3474 | -3.3547 | -3.3652 | 0.044125 | 0.039258 | 0.03423 | 0.019434 | 0.010428 | 8.9344e-05 | 0.0035417 | 0.00261 | -0.00039239 | -0.0020727 | -0.0049802 | -0.0149 | -0.023001 | -0.034445
|  | GLENUIG | LW |  |  |  | 0 | 0.052392 | 0.04065 | 0.028667 | 0.015652 | 0.0051544 | -0.011457 | -0.019551 | -0.016788 | -0.022883 | -0.024105 | -0.028174 | -0.043175 | -0.067004 | -0.094576 | -3.302 | -3.3151 | -3.3283 | -3.3417 | -3.3513 | -3.3675 | -3.366 | -3.3664 | -3.3692 | -3.3707 | -3.3728 | -3.3908 | -3.4185 | -3.4495 | 0.044218 | 0.030472 | 0.016069 | 0.0013447 | -0.0097032 | -0.027662 | -0.030665 | -0.03092 | -0.03504 | -0.037127 | -0.040183 | -0.0595 | -0.088102 | -0.11974
|  | GLENUIG | ST |  |  |  | 0 | 0.05382 | 0.052133 | 0.045015 | 0.038982 | 0.033942 | 0.028901 | 0.02321 | 0.016881 | 0.0088657 | 0.014994 | 0.018783 | -0.011051 | -0.039152 | -0.062879 | -3.3007 | -3.302 | -3.3098 | -3.3162 | -3.3208 | -3.3249 | -3.3297 | -3.3353 | -3.3426 | -3.3267 | -3.3267 | -3.3587 | -3.3915 | -3.4203 | 0.045649 | 0.043798 | 0.035235 | 0.028164 | 0.022813 | 0.017863 | 0.012234 | 0.0058328 | -0.0023149 | 0.010045 | 0.0098893 | -0.026375 | -0.060921 | -0.090273
|  | GLENUIG | FS |  |  |  | 0 | 0.054251 | 0.05295 | 0.049843 | 0.046372 | 0.042757 | 0.038772 | 0.033538 | 0.028389 | 0.021372 | 0.014194 | 0.0089519 | 0.014888 | 0.0064109 | 0.00016462 | -3.3005 | -3.3015 | -3.3049 | -3.3086 | -3.3124 | -3.3166 | -3.3222 | -3.3273 | -3.3345 | -3.3418 | -3.3466 | -3.3314 | -3.3362 | -3.3429 | 0.046213 | 0.044816 | 0.041257 | 0.037333 | 0.033265 | 0.028827 | 0.022935 | 0.017236 | 0.0094631 | 0.0015296 | -0.0038583 | 0.0055059 | -0.0031205 | -0.011509
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 0.251 | 0.71281 | 0.58051 | 0.46345 | 0.35524 | 0.23268 | 0.10556 | -0.064575 | -0.16499 | -0.25535 | -0.31375 | -0.38993 | -0.59924 | -0.72869 | -0.86531 | 1.5053 | 1.3865 | 1.2961 | 1.2351 | 1.1757 | 1.1053 | 1.0112 | 0.95581 | 0.88673 | 0.8507 | 0.80087 | 0.6658 | 0.59993 | 0.47077 | 1.0372 | 0.90498 | 0.78252 | 0.68979 | 0.59645 | 0.48549 | 0.35261 | 0.2841 | 0.20686 | 0.15652 | 0.099755 | -0.068355 | -0.17641 | -0.27992
|  | GOLSPIE | CT |  |  |  | 0.251 | 0.71281 | 0.59959 | 0.47126 | 0.36247 | 0.23268 | 0.10778 | -0.064575 | -0.16499 | -0.23993 | -0.28055 | -0.3368 | -0.53856 | -0.64362 | -0.75657 | 1.5053 | 1.412 | 1.3229 | 1.2575 | 1.1869 | 1.1254 | 1.0329 | 0.96419 | 0.91187 | 0.88347 | 0.83946 | 0.68744 | 0.60245 | 0.47077 | 1.0372 | 0.92439 | 0.80766 | 0.70721 | 0.60516 | 0.50157 | 0.36995 | 0.29555 | 0.23979 | 0.20781 | 0.16991 | -0.003769 | -0.081382 | -0.16674
|  | GOLSPIE | LW |  |  |  | 0.251 | 0.72167 | 0.58051 | 0.46345 | 0.35524 | 0.24264 | 0.10556 | -0.063889 | -0.15262 | -0.25535 | -0.31375 | -0.38993 | -0.59924 | -0.72869 | -0.86531 | 1.5087 | 1.3865 | 1.2961 | 1.2351 | 1.1757 | 1.1053 | 1.0112 | 0.95581 | 0.88673 | 0.8507 | 0.80087 | 0.6658 | 0.59993 | 0.51294 | 1.044 | 0.90498 | 0.78252 | 0.68979 | 0.59645 | 0.48549 | 0.35261 | 0.2841 | 0.20686 | 0.15652 | 0.099755 | -0.068355 | -0.17641 | -0.27992
|  | GOLSPIE | ST |  |  |  | 0.251 | 0.73735 | 0.64879 | 0.55881 | 0.4829 | 0.43112 | 0.36786 | 0.28849 | 0.21179 | 0.14581 | 0.071172 | -0.011246 | -0.33144 | -0.45347 | -0.51825 | 1.5183 | 1.4391 | 1.3664 | 1.3211 | 1.2892 | 1.2528 | 1.2071 | 1.1597 | 1.1208 | 1.0749 | 1.0231 | 0.78702 | 0.6599 | 0.54032 | 1.0553 | 0.95983 | 0.86515 | 0.80208 | 0.74834 | 0.6906 | 0.62542 | 0.56298 | 0.50225 | 0.43862 | 0.36972 | 0.073789 | -0.06199 | -0.13467
|  | GOLSPIE | FS |  |  |  | 0.251 | 0.76855 | 0.70581 | 0.66347 | 0.629 | 0.6128 | 0.57864 | 0.53898 | 0.49061 | 0.42102 | 0.38039 | 0.31563 | -0.011008 | -0.33319 | -0.42579 | 1.5342 | 1.4752 | 1.4341 | 1.4106 | 1.3962 | 1.3713 | 1.3416 | 1.3081 | 1.2623 | 1.2319 | 1.1912 | 0.95158 | 0.68811 | 0.47182 | 1.0828 | 1.0147 | 0.96849 | 0.94315 | 0.92364 | 0.89632 | 0.8654 | 0.81975 | 0.76503 | 0.7199 | 0.66967 | 0.38507 | 0.11203 | -0.0097918
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 0.994 | 1.3085 | -0.54351 | -2.7334 | -4.8769 | -6.5672 | -8.9871 | -12.2053 | -13.6601 | -14.8257 | -15.8667 | -16.8236 | -21.6091 | -26.6855 | -32.5317 | 3.6648 | 1.56 | -0.70274 | -2.8336 | -4.47 | -6.9431 | -10.3324 | -11.3218 | -12.0727 | -12.7639 | -13.4255 | -17.9202 | -23.9885 | -31.0238 | 3.7907 | 1.6654 | -0.67713 | -3.1695 | -5.0728 | -7.8399 | -11.5638 | -12.9467 | -14.0312 | -15.0252 | -15.9423 | -21.1803 | -27.3931 | -34.5219
|  | GOODLYBURN | CT |  |  |  | 0.994 | 1.3169 | 0.99175 | 0.54633 | -1.5725 | -2.5076 | -3.6623 | -5.782 | -7.201 | -8.6146 | -9.3718 | -10.351 | -13.8972 | -16.4002 | -18.8866 | 3.6648 | 3.4647 | 3.3218 | 1.2029 | 0.48247 | -0.48768 | -2.5435 | -3.515 | -4.5895 | -5.136 | -5.9299 | -9.0057 | -11.653 | -15.0033 | 3.7907 | 3.561 | 3.3767 | 0.94416 | -0.010834 | -1.227 | -3.5863 | -4.9367 | -6.3287 | -7.081 | -8.0733 | -11.7178 | -14.4514 | -17.2882
|  | GOODLYBURN | LW |  |  |  | 0.994 | 1.3085 | -0.54351 | -2.7334 | -4.8769 | -6.5672 | -8.9871 | -12.2053 | -13.6601 | -14.8257 | -15.8667 | -16.8236 | -21.6091 | -26.6855 | -32.5317 | 3.6693 | 1.56 | -0.70274 | -2.8336 | -4.47 | -6.9431 | -10.3324 | -11.3218 | -12.0727 | -12.7639 | -13.4255 | -17.9202 | -23.9885 | -31.0238 | 3.7947 | 1.6654 | -0.67713 | -3.1695 | -5.0728 | -7.8399 | -11.5638 | -12.9467 | -14.0312 | -15.0252 | -15.9423 | -21.1803 | -27.3931 | -34.5219
|  | GOODLYBURN | ST |  |  |  | 0.994 | 1.4561 | 1.2929 | 0.21823 | -0.54427 | -1.07 | -1.3403 | -1.6763 | -2.4047 | -3.1837 | -3.7368 | -4.1464 | -9.8061 | -16.1612 | -22.4384 | 3.7061 | 3.5665 | 2.2703 | 1.3907 | 0.82561 | 0.58247 | 0.29685 | -0.41086 | -1.1593 | -1.7256 | -2.1456 | -8.6851 | -16.1639 | -23.5586 | 3.8444 | 3.7075 | 2.391 | 1.4865 | 0.89203 | 0.61244 | 0.2839 | -0.45019 | -1.2476 | -1.7735 | -2.1119 | -8.7313 | -16.1847 | -23.5263
|  | GOODLYBURN | FS |  |  |  | 0.994 | 1.4722 | 1.3916 | 0.98926 | 0.59314 | 0.1079 | -0.40261 | -1.1162 | -1.9075 | -2.8062 | -3.5256 | -3.8902 | -6.0768 | -8.3196 | -10.87 | 3.7113 | 3.6602 | 3.2572 | 2.8591 | 2.3687 | 1.8617 | 1.0905 | 0.32467 | -0.59751 | -1.3781 | -1.6915 | -3.4745 | -5.75 | -9.2867 | 3.8536 | 3.8088 | 3.4003 | 2.994 | 2.4929 | 1.9756 | 1.194 | 0.41353 | -0.57017 | -1.3803 | -1.7302 | -3.7799 | -5.8693 | -8.434
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0 | 4.6237 | 4.1674 | 3.7262 | 3.6755 | 3.5249 | 3.2833 | 2.7746 | 2.2336 | 1.9749 | 1.7692 | 1.5482 | 0.88815 | 0.53706 | 0.27159 | 4.949 | 4.5299 | 4.0951 | 4.0007 | 3.9096 | 3.7647 | 3.3757 | 2.9784 | 2.8116 | 2.6935 | 2.5577 | 2.1717 | 1.9085 | 1.5051 | 4.9014 | 4.4463 | 3.9418 | 3.7858 | 3.6271 | 3.3992 | 2.9242 | 2.4358 | 2.1794 | 1.9885 | 1.7809 | 1.1642 | 0.85591 | 0.59881
|  | GOURDIE | CT |  |  |  | 0 | 4.6237 | 4.2818 | 3.8955 | 3.8016 | 3.6 | 3.3561 | 2.8784 | 2.3541 | 2.0898 | 1.8687 | 1.7147 | 0.98705 | 0.53706 | 0.27159 | 4.949 | 4.6281 | 4.2444 | 4.1145 | 3.9881 | 3.8459 | 3.4947 | 3.1033 | 2.9249 | 2.7698 | 2.6665 | 2.2022 | 1.9085 | 1.6072 | 4.9014 | 4.5472 | 4.0974 | 3.9065 | 3.7073 | 3.4831 | 3.0413 | 2.5678 | 2.3223 | 2.1079 | 1.9624 | 1.2999 | 0.92866 | 0.70116
|  | GOURDIE | LW |  |  |  | 0 | 4.6247 | 4.1674 | 3.7262 | 3.6755 | 3.5249 | 3.2833 | 2.7746 | 2.2336 | 1.9749 | 1.7692 | 1.5482 | 0.88815 | 0.54693 | 0.27307 | 4.9527 | 4.5299 | 4.0951 | 4.0007 | 3.9096 | 3.7647 | 3.3757 | 2.9784 | 2.8116 | 2.6935 | 2.5577 | 2.1717 | 1.98 | 1.8144 | 4.9061 | 4.4463 | 3.9418 | 3.7858 | 3.6271 | 3.3992 | 2.9242 | 2.4358 | 2.1794 | 1.9885 | 1.7809 | 1.1642 | 0.85591 | 0.59881
|  | GOURDIE | ST |  |  |  | 0 | 4.6508 | 4.3282 | 3.9539 | 3.8864 | 3.8327 | 3.7769 | 3.4459 | 3.0721 | 2.9327 | 2.8296 | 2.7259 | 1.9908 | 1.4879 | 1.1248 | 4.9782 | 4.6821 | 4.3369 | 4.2572 | 4.186 | 4.1208 | 3.8415 | 3.5347 | 3.393 | 3.3015 | 3.1925 | 2.5878 | 2.2016 | 1.846 | 4.9454 | 4.6258 | 4.2527 | 4.1545 | 4.0635 | 3.9804 | 3.6783 | 3.3501 | 3.1834 | 3.0737 | 2.9396 | 2.1698 | 1.6975 | 1.3629
|  | GOURDIE | FS |  |  |  | 0 | 4.6571 | 4.4083 | 4.1464 | 4.1074 | 4.0796 | 4.0361 | 3.8147 | 3.5691 | 3.4636 | 3.3558 | 3.2515 | 2.3813 | 1.6895 | 1.0893 | 4.9864 | 4.7563 | 4.5152 | 4.461 | 4.4214 | 4.3618 | 4.1743 | 3.9506 | 3.8287 | 3.704 | 3.5837 | 2.8408 | 2.2216 | 1.5051 | 4.961 | 4.7144 | 4.4572 | 4.3928 | 4.3452 | 4.2753 | 4.0812 | 3.8374 | 3.696 | 3.551 | 3.41 | 2.5578 | 1.9139 | 1.3609
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.457 | 7.7869 | 7.6228 | 7.3823 | 7.0899 | 6.7736 | 6.447 | 6.0509 | 5.8956 | 5.8102 | 5.6111 | 5.3848 | 4.8326 | 4.5691 | 4.2129 | 9.8659 | 9.761 | 9.6525 | 9.5324 | 9.4176 | 9.2648 | 9.0727 | 8.9529 | 8.8225 | 8.6963 | 8.5795 | 8.1854 | 7.9984 | 7.7264 | 8.714 | 8.5775 | 8.3909 | 8.1455 | 7.8808 | 7.6104 | 7.2061 | 6.9512 | 6.7188 | 6.4693 | 6.247 | 5.7104 | 5.4537 | 5.0985
|  | GRANTOWN | CT |  |  |  | 0.457 | 7.7869 | 7.6228 | 7.3823 | 7.0899 | 6.7736 | 6.447 | 6.0509 | 5.8956 | 5.8102 | 5.7154 | 5.5993 | 5.1064 | 4.8953 | 4.6354 | 9.8669 | 9.7846 | 9.6953 | 9.561 | 9.436 | 9.3172 | 9.1474 | 9.0312 | 8.9561 | 8.8679 | 8.762 | 8.3584 | 8.1405 | 7.8086 | 8.714 | 8.5862 | 8.4019 | 8.1455 | 7.8808 | 7.6104 | 7.2097 | 6.959 | 6.8404 | 6.6549 | 6.4867 | 6.006 | 5.8115 | 5.5655
|  | GRANTOWN | LW |  |  |  | 0.457 | 7.8071 | 7.6376 | 7.3932 | 7.1261 | 6.8464 | 6.5178 | 6.135 | 5.9664 | 5.8114 | 5.6111 | 5.3848 | 4.8326 | 4.5691 | 4.2129 | 9.8659 | 9.761 | 9.6525 | 9.5324 | 9.4176 | 9.2648 | 9.0727 | 8.9529 | 8.8225 | 8.6963 | 8.5795 | 8.1854 | 7.9984 | 7.7264 | 8.722 | 8.5775 | 8.3909 | 8.1583 | 7.9203 | 7.6139 | 7.2061 | 6.9512 | 6.7188 | 6.4693 | 6.247 | 5.7104 | 5.4537 | 5.0985
|  | GRANTOWN | ST |  |  |  | 0.457 | 7.8338 | 7.7207 | 7.5709 | 7.4326 | 7.2945 | 7.1452 | 6.9952 | 6.8468 | 6.6961 | 6.5265 | 6.3473 | 5.5372 | 5.1758 | 4.9963 | 9.8885 | 9.8431 | 9.7686 | 9.7018 | 9.6365 | 9.5618 | 9.4815 | 9.3923 | 9.2953 | 9.1814 | 9.0577 | 8.4082 | 8.1291 | 7.9913 | 8.7515 | 8.6751 | 8.558 | 8.4332 | 8.3082 | 8.1734 | 8.0337 | 7.8946 | 7.7505 | 7.5869 | 7.4095 | 6.5563 | 6.2525 | 6.0727
|  | GRANTOWN | FS |  |  |  | 0.457 | 7.8855 | 7.8418 | 7.8022 | 7.7613 | 7.7081 | 7.6534 | 7.5844 | 7.4706 | 7.3391 | 7.222 | 7.0902 | 6.3828 | 5.6238 | 5.2357 | 9.9152 | 9.8815 | 9.8513 | 9.8184 | 9.7767 | 9.7377 | 9.684 | 9.6209 | 9.5409 | 9.4722 | 9.3936 | 8.9344 | 8.4516 | 7.9117 | 8.8015 | 8.7485 | 8.706 | 8.6598 | 8.6033 | 8.5502 | 8.4799 | 8.3828 | 8.2654 | 8.1621 | 8.0447 | 7.3506 | 6.5988 | 6.323
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 2.273 | 16.4032 | 15.3089 | 13.9796 | 12.4942 | 11.0265 | 9.3389 | 7.4825 | 5.8343 | 4.315 | 2.8242 | 1.953 | -0.47017 | -1.7151 | -2.5424 | 26.7379 | 25.5668 | 24.39 | 23.0868 | 21.8428 | 20.6819 | 19.4732 | 18.2006 | 16.7984 | 15.5495 | 15.0223 | 13.6986 | 13.3878 | 12.9123 | 16.7615 | 15.6609 | 14.415 | 13.0201 | 11.6476 | 10.1113 | 8.4155 | 6.8817 | 5.426 | 3.9966 | 3.2149 | 1.1468 | 0.51898 | -0.0019475
|  | GREMISTA | CT |  |  |  | 2.273 | 16.8808 | 15.9435 | 14.6621 | 12.9982 | 11.2152 | 9.3389 | 7.4825 | 5.8343 | 4.3283 | 2.9329 | 2.253 | -0.34667 | -1.7151 | -2.5424 | 27.3283 | 26.3617 | 25.2819 | 23.8366 | 22.3166 | 20.8614 | 19.5148 | 18.2006 | 16.9929 | 15.7676 | 15.3564 | 14.1933 | 13.5189 | 12.9123 | 17.2548 | 16.3149 | 15.1064 | 13.5044 | 11.8283 | 10.1113 | 8.4155 | 6.8817 | 5.4894 | 4.1575 | 3.5679 | 1.5236 | 0.54321 | -0.0019475
|  | GREMISTA | LW |  |  |  | 2.273 | 16.4032 | 15.3089 | 13.9796 | 12.4942 | 11.0265 | 9.4774 | 7.8513 | 6.0886 | 4.315 | 2.8242 | 1.953 | -0.47017 | -1.3297 | -2.0941 | 26.7379 | 25.5668 | 24.39 | 23.0868 | 21.8428 | 20.6819 | 19.4732 | 18.2198 | 16.7984 | 15.5495 | 15.0223 | 13.6986 | 13.3878 | 13.2007 | 16.7615 | 15.6609 | 14.415 | 13.0201 | 11.6476 | 10.2146 | 8.7012 | 7.0887 | 5.426 | 3.9966 | 3.2149 | 1.1468 | 0.51898 | 0.042579
|  | GREMISTA | ST |  |  |  | 2.273 | 17.0189 | 16.2122 | 15.3334 | 14.1842 | 12.9618 | 11.7517 | 10.7044 | 9.693 | 8.6611 | 7.4534 | 7.0048 | 4.6309 | 2.8341 | 1.2496 | 27.3791 | 26.4844 | 25.536 | 24.2717 | 22.919 | 21.6395 | 20.5514 | 19.5067 | 18.4489 | 17.1936 | 16.8615 | 14.8644 | 14.0547 | 13.7151 | 17.3728 | 16.5716 | 15.701 | 14.556 | 13.3253 | 12.1241 | 11.0685 | 10.0377 | 8.955 | 7.6921 | 7.1788 | 4.6258 | 3.3055 | 2.2834
|  | GREMISTA | FS |  |  |  | 2.273 | 17.6006 | 16.9322 | 16.2653 | 15.3402 | 14.3373 | 13.1801 | 12.4522 | 11.6254 | 10.7174 | 9.7086 | 8.9687 | 5.4401 | 3.1307 | 1.215 | 28.0831 | 27.3556 | 26.6531 | 25.641 | 24.5349 | 23.2771 | 22.5274 | 21.7585 | 20.9005 | 19.9289 | 19.2766 | 16.2424 | 14.4909 | 13.3175 | 17.9645 | 17.3069 | 16.654 | 15.7375 | 14.7375 | 13.5917 | 12.8713 | 12.0768 | 11.1873 | 10.1963 | 9.4605 | 5.8619 | 3.5125 | 1.6833
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 6.244 | 7.1501 | 6.5082 | 5.6124 | 4.6523 | 3.6037 | 2.3581 | 0.9412 | -0.47739 | -2.2941 | -3.9776 | -5.4145 | -9.2059 | -9.1233 | -10.6047 | 11.1275 | 10.7637 | 10.2487 | 9.6749 | 9.052 | 8.2266 | 7.2758 | 6.3033 | 5.0428 | 3.8714 | 2.8336 | 0.27085 | -0.63996 | -5.4243 | 10.6229 | 10.3653 | 9.5775 | 8.7204 | 7.7822 | 6.6274 | 5.3166 | 4.0079 | 2.3389 | 0.79339 | -0.57599 | -4.2366 | -4.1945 | -5.6662
|  | GREYFRIARS | CT |  |  |  | 6.244 | 7.1989 | 6.6202 | 5.8537 | 5.0203 | 4.0948 | 3.2642 | 2.176 | 0.71152 | -0.59982 | -1.9114 | -3.0257 | -7.1427 | -8.1855 | -9.2988 | 11.1275 | 10.7732 | 10.2723 | 9.6922 | 9.057 | 8.454 | 7.6599 | 6.6565 | 5.7805 | 4.8669 | 4.0467 | 0.93891 | -0.63996 | -3.3697 | 10.6251 | 10.4036 | 9.7897 | 9.0398 | 8.2019 | 7.4306 | 6.427 | 5.0914 | 3.9099 | 2.7196 | 1.697 | -2.1555 | -3.1022 | -4.1915
|  | GREYFRIARS | LW |  |  |  | 6.244 | 7.1501 | 6.5082 | 5.6124 | 4.6523 | 3.6037 | 2.3581 | 0.9412 | -0.47739 | -2.2941 | -3.9776 | -5.4145 | -9.2059 | -9.1233 | -10.6047 | 11.1357 | 10.7637 | 10.2487 | 9.6749 | 9.052 | 8.2266 | 7.2758 | 6.3033 | 5.0428 | 3.8714 | 2.8336 | 0.27085 | 0.1659 | -1.1372 | 10.6229 | 10.3653 | 9.5775 | 8.7204 | 7.7822 | 6.6274 | 5.3166 | 4.0079 | 2.3389 | 0.79339 | -0.57599 | -4.2366 | -4.1945 | -5.6662
|  | GREYFRIARS | ST |  |  |  | 6.244 | 7.2988 | 6.9304 | 6.5568 | 6.2448 | 5.8823 | 5.6002 | 5.2219 | 4.7712 | 4.1105 | 3.4219 | 2.7671 | -0.51634 | -1.7133 | -2.7144 | 11.1592 | 11.0324 | 10.7697 | 10.524 | 10.2334 | 9.9676 | 9.6248 | 9.2278 | 8.6774 | 8.0961 | 7.5167 | 4.2202 | 2.3472 | 0.02404 | 10.6593 | 10.5122 | 10.3464 | 10.1628 | 9.8379 | 9.576 | 9.2218 | 8.8051 | 8.2004 | 7.5695 | 6.9691 | 3.8692 | 2.7459 | 1.8618
|  | GREYFRIARS | FS |  |  |  | 6.244 | 7.3997 | 7.1563 | 6.8626 | 6.6193 | 6.3429 | 6.1032 | 5.8174 | 5.4288 | 4.8909 | 4.3601 | 3.8296 | -0.10379 | -3.6642 | -6.3123 | 11.1653 | 11.076 | 10.9098 | 10.7079 | 10.4739 | 10.236 | 9.9446 | 9.5762 | 9.0965 | 8.6136 | 8.1142 | 4.6311 | 0.16197 | -5.4243 | 10.6719 | 10.5537 | 10.4269 | 10.3334 | 10.2271 | 10.0113 | 9.7492 | 9.3933 | 8.9099 | 8.4276 | 7.9411 | 4.3916 | 1.1142 | -1.374
| GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309 623 | NO | YES | 0.466 | 22.7277 | 22.6753 | 22.6047 | 22.521 | 22.4239 | 22.3264 | 22.2011 | 22.1355 | 22.0713 | 22.0001 | 21.9432 | 21.7563 | 21.6584 | 21.5278 | 21.5677 | 21.5314 | 21.4922 | 21.4521 | 21.4068 | 21.3469 | 21.2673 | 21.211 | 21.1661 | 21.1099 | 21.0667 | 20.943 | 20.8896 | 20.8024 | 22.1364 | 22.0853 | 22.0225 | 21.947 | 21.8582 | 21.7673 | 21.6469 | 21.5764 | 21.5142 | 21.4452 | 21.3901 | 21.2119 | 21.1187 | 20.9904
|  | GRUDIE BRIDGE | CT |  |  |  | 0.466 | 22.7277 | 22.6753 | 22.6047 | 22.521 | 22.4239 | 22.3264 | 22.2011 | 22.1355 | 22.1028 | 22.0504 | 22.0117 | 21.8441 | 21.762 | 21.6639 | 21.5677 | 21.5343 | 21.5009 | 21.4604 | 21.4087 | 21.3629 | 21.2908 | 21.2324 | 21.211 | 21.1655 | 21.1304 | 21.002 | 20.9462 | 20.8476 | 22.1364 | 22.0853 | 22.0242 | 21.947 | 21.8582 | 21.7708 | 21.6537 | 21.5875 | 21.5551 | 21.5037 | 21.4653 | 21.3053 | 21.2314 | 21.1396
|  | GRUDIE BRIDGE | LW |  |  |  | 0.466 | 22.7368 | 22.6808 | 22.6084 | 22.5276 | 22.4385 | 22.3334 | 22.2059 | 22.136 | 22.0713 | 22.0001 | 21.9432 | 21.7563 | 21.6584 | 21.5278 | 21.5707 | 21.5314 | 21.4922 | 21.4521 | 21.4068 | 21.3469 | 21.2673 | 21.211 | 21.1661 | 21.1099 | 21.0667 | 20.943 | 20.8896 | 20.8024 | 22.1429 | 22.0875 | 22.0225 | 21.9476 | 21.8659 | 21.7673 | 21.6469 | 21.5764 | 21.5142 | 21.4452 | 21.3901 | 21.2119 | 21.1187 | 20.9904
|  | GRUDIE BRIDGE | ST |  |  |  | 0.466 | 22.741 | 22.7087 | 22.6587 | 22.6072 | 22.559 | 22.5049 | 22.4575 | 22.4073 | 22.3579 | 22.2993 | 22.2369 | 21.9755 | 21.8543 | 21.7869 | 21.5749 | 21.5615 | 21.5356 | 21.5076 | 21.4842 | 21.4529 | 21.4297 | 21.3974 | 21.3651 | 21.3227 | 21.278 | 21.0811 | 20.9822 | 20.8956 | 22.1486 | 22.12 | 22.0737 | 22.0263 | 21.9827 | 21.9334 | 21.8907 | 21.8431 | 21.7969 | 21.74 | 21.6799 | 21.4273 | 21.3094 | 21.2426
|  | GRUDIE BRIDGE | FS |  |  |  | 0.466 | 22.7624 | 22.7451 | 22.7283 | 22.7076 | 22.6902 | 22.6645 | 22.6347 | 22.6057 | 22.5582 | 22.519 | 22.4726 | 22.2287 | 21.9824 | 21.8829 | 21.583 | 21.5743 | 21.5625 | 21.5476 | 21.5353 | 21.516 | 21.4928 | 21.476 | 21.4423 | 21.417 | 21.3848 | 21.212 | 21.0297 | 20.8871 | 22.1658 | 22.1502 | 22.1339 | 22.1137 | 22.097 | 22.0718 | 22.0424 | 22.0173 | 21.9711 | 21.9354 | 21.8907 | 21.6598 | 21.4369 | 21.3461
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.403 | -0.055114 | -0.067355 | -0.089404 | -0.11692 | -0.14336 | -0.17736 | -0.22039 | -0.25622 | -0.29774 | -0.33506 | -0.36339 | -0.46949 | -0.53254 | -0.59876 | 0.11217 | 0.10177 | 0.086444 | 0.066978 | 0.050158 | 0.026413 | -0.0057494 | -0.024402 | -0.05054 | -0.074154 | -0.09209 | -0.15501 | -0.19413 | -0.23676 | -0.021904 | -0.034267 | -0.059186 | -0.086492 | -0.1118 | -0.14666 | -0.19116 | -0.22487 | -0.26546 | -0.30213 | -0.331 | -0.4286 | -0.4836 | -0.54149
|  | GUTCHER | CT |  |  |  | 0.403 | -0.051089 | -0.055524 | -0.075081 | -0.10673 | -0.13708 | -0.16805 | -0.21126 | -0.24428 | -0.27558 | -0.30494 | -0.32545 | -0.43227 | -0.5041 | -0.54975 | 0.11915 | 0.11584 | 0.10588 | 0.083698 | 0.06684 | 0.050933 | 0.024652 | 0.0068652 | -0.010489 | -0.027504 | -0.038868 | -0.091396 | -0.12135 | -0.15901 | -0.016721 | -0.022925 | -0.040569 | -0.072584 | -0.099835 | -0.12744 | -0.16721 | -0.1988 | -0.22768 | -0.2551 | -0.27487 | -0.36641 | -0.42768 | -0.46668
|  | GUTCHER | LW |  |  |  | 0.403 | -0.051083 | -0.064457 | -0.089404 | -0.11692 | -0.14336 | -0.17736 | -0.22039 | -0.25622 | -0.29774 | -0.33506 | -0.36339 | -0.46949 | -0.53254 | -0.59876 | 0.1188 | 0.10487 | 0.086444 | 0.066978 | 0.050158 | 0.026413 | -0.0057494 | -0.024402 | -0.05054 | -0.074154 | -0.09209 | -0.15501 | -0.19413 | -0.23676 | -0.017299 | -0.0342 | -0.059186 | -0.086492 | -0.1118 | -0.14666 | -0.19116 | -0.22487 | -0.26546 | -0.30213 | -0.331 | -0.4286 | -0.4836 | -0.54149
|  | GUTCHER | ST |  |  |  | 0.403 | -0.054202 | -0.047992 | -0.054291 | -0.061602 | -0.066663 | -0.071896 | -0.078855 | -0.087775 | -0.095984 | -0.10741 | -0.11364 | -0.23849 | -0.35388 | -0.44785 | 0.11217 | 0.12007 | 0.11276 | 0.1052 | 0.099876 | 0.09473 | 0.087993 | 0.079113 | 0.068821 | 0.055587 | 0.045506 | -0.055213 | -0.12099 | -0.16813 | -0.021798 | -0.014746 | -0.023295 | -0.032373 | -0.039477 | -0.046853 | -0.05623 | -0.068242 | -0.081301 | -0.097491 | -0.11 | -0.24376 | -0.33935 | -0.41183
|  | GUTCHER | FS |  |  |  | 0.403 | -0.055114 | -0.067355 | -0.05499 | -0.061826 | -0.068036 | -0.076532 | -0.08447 | -0.095672 | -0.11001 | -0.12165 | -0.13392 | -0.2059 | -0.27941 | -0.36215 | 0.11292 | 0.10177 | 0.11663 | 0.11135 | 0.1064 | 0.099526 | 0.092733 | 0.084752 | 0.07346 | 0.064528 | 0.055821 | -0.00027893 | -0.051829 | -0.096544 | -0.021904 | -0.034267 | -0.021143 | -0.028367 | -0.03541 | -0.044605 | -0.053971 | -0.065692 | -0.081327 | -0.094922 | -0.10839 | -0.19036 | -0.27009 | -0.34777
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0.153 | -0.050817 | -0.15182 | -0.28129 | -0.45214 | -0.62057 | -0.81834 | -1.0513 | -1.1719 | -1.2343 | -1.3464 | -1.4504 | -1.7764 | -1.9616 | -2.1245 | 0.57033 | 0.51514 | 0.4503 | 0.36757 | 0.28789 | 0.18727 | 0.063601 | -0.014589 | -0.059892 | -0.13606 | -0.20566 | -0.40154 | -0.49982 | -0.62221 | 0.4428 | 0.35735 | 0.24079 | 0.083187 | -0.068906 | -0.24855 | -0.46214 | -0.57606 | -0.64102 | -0.75271 | -0.85866 | -1.1699 | -1.3374 | -1.4932
|  | HALKIRK | CT |  |  |  | 0.153 | -0.050817 | -0.15182 | -0.28129 | -0.45214 | -0.62057 | -0.81834 | -1.0513 | -1.1719 | -1.2343 | -1.3162 | -1.3821 | -1.6499 | -1.7985 | -1.9364 | 0.57931 | 0.52571 | 0.46372 | 0.37113 | 0.28789 | 0.18727 | 0.063601 | -0.014589 | -0.051069 | -0.10832 | -0.15808 | -0.33648 | -0.44473 | -0.59012 | 0.44948 | 0.35735 | 0.24079 | 0.083187 | -0.068906 | -0.24855 | -0.46214 | -0.57606 | -0.63344 | -0.71158 | -0.77533 | -1.031 | -1.1597 | -1.2847
|  | HALKIRK | LW |  |  |  | 0.153 | -0.047816 | -0.14288 | -0.27413 | -0.43379 | -0.58156 | -0.78078 | -1.0002 | -1.1247 | -1.2307 | -1.3464 | -1.4504 | -1.7764 | -1.9616 | -2.1245 | 0.57033 | 0.51514 | 0.4503 | 0.36757 | 0.30147 | 0.19815 | 0.082375 | 0.0053401 | -0.059892 | -0.13606 | -0.20566 | -0.40154 | -0.49982 | -0.59489 | 0.4428 | 0.36137 | 0.2412 | 0.094397 | -0.038574 | -0.22186 | -0.42456 | -0.54163 | -0.64102 | -0.75271 | -0.85866 | -1.1699 | -1.3374 | -1.4932
|  | HALKIRK | ST |  |  |  | 0.153 | -0.020154 | -0.087548 | -0.18696 | -0.2816 | -0.38942 | -0.49267 | -0.60759 | -0.68981 | -0.79298 | -0.90343 | -1.0191 | -1.4891 | -1.7054 | -1.8127 | 0.59519 | 0.56407 | 0.5143 | 0.46839 | 0.41136 | 0.35844 | 0.29626 | 0.25407 | 0.19481 | 0.12944 | 0.059836 | -0.26194 | -0.43316 | -0.5731 | 0.4687 | 0.41752 | 0.32676 | 0.24123 | 0.14313 | 0.049882 | -0.054978 | -0.12939 | -0.22462 | -0.32705 | -0.43451 | -0.88038 | -1.0838 | -1.184
|  | HALKIRK | FS |  |  |  | 0.153 | 0.048415 | 0.0010908 | -0.027103 | -0.059176 | -0.095835 | -0.13169 | -0.174 | -0.25081 | -0.3191 | -0.40568 | -0.49076 | -0.92867 | -1.4215 | -1.6273 | 0.63559 | 0.60994 | 0.59228 | 0.5699 | 0.54443 | 0.51873 | 0.48735 | 0.44217 | 0.40331 | 0.34855 | 0.29519 | 0.0097803 | -0.34259 | -0.62221 | 0.49528 | 0.48546 | 0.4708 | 0.44083 | 0.40627 | 0.37262 | 0.3323 | 0.26173 | 0.19944 | 0.11902 | 0.04074 | -0.36486 | -0.81996 | -1.0068
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 1.831 | 15.4011 | 13.5985 | 11.7435 | 9.5895 | 8.1541 | 6.1514 | 3.6167 | 2.7933 | 1.9702 | 1.1783 | 0.76555 | -3.0833 | -7.3798 | -12.2664 | 15.8589 | 13.752 | 11.5692 | 9.4422 | 8.1707 | 6.2342 | 3.6044 | 3.1707 | 2.7142 | 2.2426 | 1.9059 | -1.4864 | -6.4116 | -11.833 | 17.1655 | 15.0779 | 12.9143 | 10.6428 | 9.061 | 6.7711 | 3.8078 | 2.9949 | 2.1644 | 1.3615 | 0.9865 | -3.2358 | -8.4104 | -14.3284
|  | HARBOUR | CT |  |  |  | 1.831 | 15.4658 | 14.9663 | 14.467 | 12.4438 | 11.5963 | 10.5466 | 8.8371 | 7.9641 | 7.1098 | 6.3303 | 5.8836 | 2.8969 | 0.83163 | -1.1859 | 15.9269 | 15.434 | 14.9639 | 12.7712 | 12.2058 | 11.4252 | 9.8111 | 9.3288 | 8.7931 | 8.2918 | 7.8953 | 6.1331 | 4.1253 | 1.5827 | 17.2334 | 16.7667 | 16.3316 | 14.1124 | 13.2638 | 12.1804 | 10.2728 | 9.4151 | 8.5485 | 7.7349 | 7.2977 | 4.2746 | 2.0996 | -0.19864
|  | HARBOUR | LW |  |  |  | 1.831 | 15.4011 | 13.5985 | 11.7435 | 9.5895 | 8.1541 | 6.1514 | 3.6167 | 2.7933 | 1.9702 | 1.1783 | 0.76555 | -3.0833 | -7.3798 | -12.2664 | 15.8589 | 13.752 | 11.5692 | 9.4422 | 8.1707 | 6.2342 | 3.6044 | 3.1707 | 2.7142 | 2.2426 | 1.9059 | -1.4864 | -6.4116 | -11.833 | 17.1655 | 15.0779 | 12.9143 | 10.6428 | 9.061 | 6.7711 | 3.8078 | 2.9949 | 2.1644 | 1.3615 | 0.9865 | -3.2358 | -8.4104 | -14.3284
|  | HARBOUR | ST |  |  |  | 1.831 | 15.5021 | 15.1209 | 13.9142 | 12.8686 | 12.3413 | 11.9885 | 11.619 | 11.1297 | 10.5213 | 9.9343 | 9.4127 | 3.7313 | -1.4727 | -6.1497 | 15.966 | 15.5707 | 14.1772 | 13.0213 | 12.4333 | 12.0736 | 11.6904 | 11.178 | 10.6058 | 10.0703 | 9.6482 | 3.7024 | -2.2028 | -7.3989 | 17.2648 | 16.874 | 15.4885 | 14.3426 | 13.7782 | 13.4522 | 13.1191 | 12.6674 | 12.1789 | 11.747 | 11.4279 | 5.038 | -1.0226 | -6.4579
|  | HARBOUR | FS |  |  |  | 1.831 | 15.5893 | 15.339 | 14.8316 | 14.2224 | 13.7908 | 13.3484 | 12.7181 | 12.2198 | 11.6102 | 10.9765 | 10.6386 | 8.2934 | 6.089 | 3.7151 | 16.0568 | 15.8036 | 15.2431 | 14.5949 | 14.1062 | 13.6052 | 12.8735 | 12.3106 | 11.6338 | 10.9611 | 10.6876 | 8.9833 | 7.5991 | 5.8114 | 17.3534 | 17.0999 | 16.5453 | 15.9021 | 15.4288 | 14.9497 | 14.2465 | 13.7213 | 13.0923 | 12.4047 | 12.0826 | 10.0632 | 8.5957 | 6.2179
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0.106 | 35.0962 | 35.0829 | 35.0504 | 35.0173 | 34.9854 | 34.9456 | 34.8954 | 34.869 | 34.8362 | 34.8143 | 34.7869 | 34.6835 | 34.6058 | 34.5273 | 32.3896 | 32.3788 | 32.3518 | 32.3261 | 32.3021 | 32.2699 | 32.2275 | 32.2112 | 32.1901 | 32.1729 | 32.153 | 32.0703 | 31.9983 | 31.9306 | 33.7442 | 33.7329 | 33.7017 | 33.6686 | 33.6368 | 33.5975 | 33.5436 | 33.5189 | 33.487 | 33.4662 | 33.4394 | 33.3354 | 33.2506 | 33.1619
|  | HARRIS GRID | CT |  |  |  | 0.106 | 35.1302 | 35.1202 | 35.1001 | 35.0631 | 35.0345 | 34.993 | 34.9355 | 34.9009 | 34.8749 | 34.8497 | 34.8368 | 34.753 | 34.6998 | 34.6596 | 32.4261 | 32.4234 | 32.4139 | 32.381 | 32.3621 | 32.3311 | 32.2855 | 32.2605 | 32.2444 | 32.2286 | 32.2187 | 32.1739 | 32.147 | 32.1204 | 33.7793 | 33.7754 | 33.7579 | 33.7172 | 33.692 | 33.654 | 33.5993 | 33.5668 | 33.5413 | 33.516 | 33.5032 | 33.4222 | 33.3717 | 33.3301
|  | HARRIS GRID | LW |  |  |  | 0.106 | 35.0962 | 35.0829 | 35.0504 | 35.0173 | 34.9854 | 34.9456 | 34.8954 | 34.869 | 34.8362 | 34.8143 | 34.7869 | 34.6835 | 34.6058 | 34.5273 | 32.3896 | 32.3788 | 32.3518 | 32.3261 | 32.3021 | 32.2699 | 32.2275 | 32.2112 | 32.1901 | 32.1729 | 32.153 | 32.0703 | 31.9983 | 31.9306 | 33.7442 | 33.7329 | 33.7017 | 33.6686 | 33.6368 | 33.5975 | 33.5436 | 33.5189 | 33.487 | 33.4662 | 33.4394 | 33.3354 | 33.2506 | 33.1619
|  | HARRIS GRID | ST |  |  |  | 0.106 | 35.141 | 35.1211 | 35.1101 | 35.0998 | 35.0851 | 35.0657 | 35.0425 | 35.0232 | 35.0087 | 34.9936 | 34.9746 | 34.831 | 34.7339 | 34.6678 | 32.4351 | 32.4158 | 32.4108 | 32.4015 | 32.3896 | 32.3729 | 32.3539 | 32.3344 | 32.3208 | 32.308 | 32.2939 | 32.1713 | 32.0807 | 32.0154 | 33.7891 | 33.7699 | 33.7651 | 33.753 | 33.738 | 33.7182 | 33.6955 | 33.6739 | 33.657 | 33.6411 | 33.6228 | 33.4749 | 33.369 | 33.2942
|  | HARRIS GRID | FS |  |  |  | 0.106 | 35.1737 | 35.1612 | 35.1444 | 35.1458 | 35.1336 | 35.1225 | 35.1036 | 35.0867 | 35.0722 | 35.058 | 35.0385 | 34.931 | 34.8437 | 34.7624 | 32.4694 | 32.4576 | 32.4413 | 32.4517 | 32.4383 | 32.4285 | 32.4098 | 32.3976 | 32.3854 | 32.3737 | 32.3581 | 32.2696 | 32.2086 | 32.1513 | 33.8224 | 33.8107 | 33.7944 | 33.8031 | 33.7889 | 33.7771 | 33.7566 | 33.741 | 33.7258 | 33.7114 | 33.6929 | 33.5852 | 33.5003 | 33.4217
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 1.298 | 19.2586 | 19.2405 | 19.2194 | 19.1988 | 19.183 | 19.1588 | 19.1275 | 19.1163 | 19.1177 | 19.1158 | 19.1086 | 19.0691 | 19.0195 | 18.9616 | 18.6871 | 18.6665 | 18.643 | 18.6205 | 18.6044 | 18.5786 | 18.5446 | 18.5358 | 18.5424 | 18.5417 | 18.5365 | 18.4979 | 18.4335 | 18.3081 | 18.6277 | 18.6069 | 18.5839 | 18.5622 | 18.5469 | 18.5225 | 18.4901 | 18.4829 | 18.4977 | 18.4971 | 18.4943 | 18.4614 | 18.404 | 18.34
|  | HARVEST AVENUE | CT |  |  |  | 1.298 | 19.2586 | 19.2539 | 19.2488 | 19.2282 | 19.2183 | 19.2057 | 19.1839 | 19.1728 | 19.1744 | 19.1654 | 19.1643 | 19.1339 | 19.1129 | 19.0898 | 18.6871 | 18.6821 | 18.6777 | 18.6543 | 18.645 | 18.6324 | 18.6092 | 18.5984 | 18.6019 | 18.5923 | 18.5885 | 18.5409 | 18.4852 | 18.3977 | 18.6277 | 18.6241 | 18.6214 | 18.6 | 18.5929 | 18.5827 | 18.5625 | 18.5551 | 18.5675 | 18.5624 | 18.5605 | 18.5416 | 18.5229 | 18.5016
|  | HARVEST AVENUE | LW |  |  |  | 1.298 | 19.2588 | 19.2405 | 19.2194 | 19.1988 | 19.183 | 19.1588 | 19.1275 | 19.1163 | 19.1177 | 19.1158 | 19.1086 | 19.0691 | 19.0195 | 18.9616 | 18.6878 | 18.6665 | 18.643 | 18.6205 | 18.6044 | 18.5786 | 18.5446 | 18.5358 | 18.5424 | 18.5417 | 18.5365 | 18.4979 | 18.4395 | 18.372 | 18.6277 | 18.6069 | 18.5839 | 18.5622 | 18.5469 | 18.5225 | 18.4901 | 18.4829 | 18.4977 | 18.4971 | 18.4943 | 18.4614 | 18.404 | 18.34
|  | HARVEST AVENUE | ST |  |  |  | 1.298 | 19.26 | 19.2575 | 19.2454 | 19.2361 | 19.2291 | 19.2241 | 19.2186 | 19.212 | 19.2042 | 19.1969 | 19.1908 | 19.1482 | 19.0894 | 19.0347 | 18.688 | 18.6849 | 18.6701 | 18.6589 | 18.6504 | 18.6443 | 18.6377 | 18.6294 | 18.6198 | 18.6106 | 18.6028 | 18.5356 | 18.4335 | 18.3081 | 18.6284 | 18.6264 | 18.6129 | 18.6031 | 18.5962 | 18.5921 | 18.5876 | 18.5817 | 18.5748 | 18.5688 | 18.5645 | 18.5311 | 18.4674 | 18.407
|  | HARVEST AVENUE | FS |  |  |  | 1.298 | 19.2604 | 19.2591 | 19.2551 | 19.2508 | 19.2456 | 19.2401 | 19.2318 | 19.2251 | 19.2167 | 19.2083 | 19.2036 | 19.1889 | 19.1776 | 19.1594 | 18.6881 | 18.686 | 18.6805 | 18.6746 | 18.6673 | 18.6595 | 18.6476 | 18.6374 | 18.6251 | 18.6126 | 18.6045 | 18.5662 | 18.4867 | 18.3364 | 18.6286 | 18.6278 | 18.6238 | 18.6196 | 18.6143 | 18.6087 | 18.5999 | 18.5937 | 18.5858 | 18.5779 | 18.5748 | 18.5802 | 18.5776 | 18.5654
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 0.362 | -0.018632 | -0.16845 | -0.41433 | -0.70039 | -1.0033 | -1.3391 | -1.7203 | -1.9116 | -2.0528 | -2.1557 | -2.2727 | -2.8335 | -3.1295 | -3.3699 | 0.65412 | 0.57139 | 0.46248 | 0.30121 | 0.16986 | 0.0243 | -0.17483 | -0.32858 | -0.43955 | -0.53892 | -0.63085 | -1.1953 | -1.5149 | -1.6356 | 0.15091 | 0.0098986 | -0.18525 | -0.44375 | -0.68216 | -0.9443 | -1.2743 | -1.4886 | -1.6437 | -1.7795 | -1.9029 | -2.667 | -3.1319 | -3.2836
|  | HASTIGROW | CT |  |  |  | 0.362 | -0.018632 | -0.16845 | -0.41433 | -0.70039 | -1.0033 | -1.3391 | -1.7203 | -1.9116 | -2.0528 | -2.1557 | -2.257 | -2.6679 | -2.8919 | -3.1015 | 0.65412 | 0.57139 | 0.46248 | 0.30121 | 0.16986 | 0.0243 | -0.17483 | -0.32858 | -0.43955 | -0.53892 | -0.63085 | -0.85112 | -0.89236 | -1.0678 | 0.15091 | 0.0098986 | -0.18525 | -0.44375 | -0.68216 | -0.9443 | -1.2743 | -1.4886 | -1.6437 | -1.7795 | -1.9006 | -2.2503 | -2.3656 | -2.463
|  | HASTIGROW | LW |  |  |  | 0.362 | -0.0029971 | -0.11647 | -0.34138 | -0.58219 | -0.84469 | -1.1748 | -1.5154 | -1.713 | -1.9349 | -2.0987 | -2.2727 | -2.8335 | -3.1295 | -3.3699 | 0.6618 | 0.58902 | 0.51233 | 0.42398 | 0.33272 | 0.19086 | 0.032839 | -0.11521 | -0.30151 | -0.46139 | -0.62395 | -1.0745 | -1.2115 | -1.2695 | 0.1705 | 0.048173 | -0.10723 | -0.28082 | -0.46682 | -0.7233 | -1.0012 | -1.2132 | -1.4692 | -1.6868 | -1.9029 | -2.5186 | -2.7435 | -2.861
|  | HASTIGROW | ST |  |  |  | 0.362 | 0.020437 | -0.064122 | -0.21531 | -0.37238 | -0.54001 | -0.70097 | -0.88459 | -1.0469 | -1.2375 | -1.4065 | -1.612 | -2.6225 | -3.0903 | -3.2499 | 0.67968 | 0.64415 | 0.59183 | 0.53243 | 0.4628 | 0.38607 | 0.29048 | 0.18328 | 0.040166 | -0.10586 | -0.28058 | -1.1953 | -1.5149 | -1.6083 | 0.19411 | 0.11747 | 0.0081235 | -0.11176 | -0.24505 | -0.38467 | -0.55044 | -0.72032 | -0.93557 | -1.1501 | -1.4037 | -2.667 | -3.1319 | -3.2836
|  | HASTIGROW | FS |  |  |  | 0.362 | 0.053243 | 0.016411 | -0.022663 | -0.071626 | -0.12367 | -0.18762 | -0.25601 | -0.35523 | -0.48101 | -0.62259 | -0.7692 | -1.6503 | -2.6074 | -3.2013 | 0.69556 | 0.67413 | 0.64747 | 0.61296 | 0.57612 | 0.52985 | 0.4798 | 0.41259 | 0.32741 | 0.23616 | 0.13676 | -0.51193 | -1.193 | -1.6356 | 0.23923 | 0.19304 | 0.14858 | 0.09333 | 0.035053 | -0.035242 | -0.10716 | -0.22102 | -0.35758 | -0.50147 | -0.65633 | -1.6142 | -2.6264 | -3.2256
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.59 | 4.3184 | 4.155 | 3.9298 | 3.6371 | 3.3311 | 2.9681 | 2.5284 | 2.0752 | 1.6903 | 1.3789 | 1.1072 | 0.34802 | -0.2171 | -0.63754 | 5.5414 | 5.4391 | 5.3288 | 5.1802 | 5.0288 | 4.8481 | 4.6239 | 4.3594 | 4.1121 | 3.9215 | 3.7502 | 3.3376 | 3.0377 | 2.6921 | 4.8869 | 4.7443 | 4.5285 | 4.2514 | 3.9588 | 3.6203 | 3.2232 | 2.8219 | 2.4618 | 2.1681 | 1.9107 | 1.2262 | 0.77478 | 0.41529
|  | HATTON | CT |  |  |  | 0.59 | 4.3184 | 4.155 | 3.9298 | 3.6371 | 3.3311 | 2.9681 | 2.5284 | 2.0752 | 1.7277 | 1.4603 | 1.2375 | 0.35405 | -0.2171 | -0.63754 | 5.5414 | 5.4391 | 5.3288 | 5.1802 | 5.0288 | 4.8481 | 4.6239 | 4.3594 | 4.1503 | 3.9806 | 3.8304 | 3.3376 | 3.0377 | 2.6921 | 4.8869 | 4.7443 | 4.5285 | 4.2514 | 3.9588 | 3.6203 | 3.2232 | 2.8219 | 2.5099 | 2.2591 | 2.0468 | 1.2554 | 0.77478 | 0.41529
|  | HATTON | LW |  |  |  | 0.59 | 4.3213 | 4.1644 | 3.9429 | 3.639 | 3.3672 | 2.9947 | 2.6194 | 2.1029 | 1.6903 | 1.3789 | 1.1072 | 0.34802 | 0.20724 | -0.19664 | 5.5419 | 5.4449 | 5.3425 | 5.1884 | 5.0644 | 4.8639 | 4.6839 | 4.3742 | 4.1121 | 3.9215 | 3.7502 | 3.3741 | 3.4898 | 3.3094 | 4.893 | 4.7577 | 4.5451 | 4.2623 | 3.9992 | 3.6523 | 3.3107 | 2.8438 | 2.4618 | 2.1681 | 1.9107 | 1.2262 | 1.1852 | 0.83579
|  | HATTON | ST |  |  |  | 0.59 | 4.3629 | 4.2705 | 4.151 | 4.0169 | 3.8603 | 3.7094 | 3.5527 | 3.3364 | 3.1033 | 2.9202 | 2.781 | 1.7743 | 1.1869 | 0.72587 | 5.5669 | 5.5171 | 5.4552 | 5.3857 | 5.2963 | 5.2086 | 5.1123 | 4.9636 | 4.8004 | 4.67 | 4.5793 | 3.8927 | 3.5373 | 3.1842 | 4.9286 | 4.8441 | 4.7339 | 4.6135 | 4.4771 | 4.3426 | 4.2024 | 3.996 | 3.7944 | 3.6347 | 3.5117 | 2.6199 | 2.0554 | 1.6032
|  | HATTON | FS |  |  |  | 0.59 | 4.4084 | 4.3416 | 4.2756 | 4.1781 | 4.0923 | 3.9958 | 3.9079 | 3.6995 | 3.5328 | 3.3731 | 3.2086 | 2.3468 | 1.4989 | 0.94792 | 5.5861 | 5.5475 | 5.5078 | 5.446 | 5.3956 | 5.3315 | 5.27 | 5.1284 | 5.0224 | 4.9145 | 4.8004 | 4.1999 | 3.5428 | 2.9073 | 4.9721 | 4.9123 | 4.8539 | 4.7721 | 4.7009 | 4.6197 | 4.543 | 4.352 | 4.2009 | 4.0576 | 3.9097 | 3.1248 | 2.3283 | 1.773
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | YES | 4.185 | 8.2022 | 7.7259 | 7.0376 | 6.1271 | 5.2955 | 4.085 | 2.7137 | 1.3011 | -0.32359 | -1.8031 | -3.1707 | -6.4418 | -6.642 | -7.8308 | 9.5022 | 9.1641 | 8.7448 | 8.2189 | 7.6661 | 7.0458 | 6.198 | 5.2944 | 4.189 | 3.1789 | 2.2372 | 0.27822 | -0.4581 | -3.8488 | 9.2027 | 8.7478 | 8.0888 | 7.2731 | 6.5368 | 5.4197 | 4.1565 | 2.8412 | 1.2991 | -0.10599 | -1.4078 | -4.3406 | -4.5495 | -5.7546
|  | HAUDAGAIN | CT |  |  |  | 4.185 | 8.2568 | 7.7972 | 7.1616 | 6.3837 | 5.5385 | 4.6392 | 3.4902 | 2.0008 | 0.79324 | -0.39577 | -1.483 | -5.1039 | -6.313 | -7.2672 | 9.5095 | 9.1655 | 8.7448 | 8.2189 | 7.6661 | 7.088 | 6.3356 | 5.3923 | 4.6362 | 3.8441 | 3.0995 | 0.74106 | -0.4581 | -2.2833 | 9.2506 | 8.8124 | 8.2054 | 7.4538 | 6.6704 | 5.8433 | 4.7801 | 3.4125 | 2.3114 | 1.2061 | 0.19122 | -2.9219 | -3.9082 | -4.8114
|  | HAUDAGAIN | LW |  |  |  | 4.185 | 8.2022 | 7.7259 | 7.0376 | 6.1271 | 5.2955 | 4.085 | 2.7137 | 1.3011 | -0.32359 | -1.8031 | -3.1707 | -6.4418 | -6.642 | -7.8308 | 9.5022 | 9.1641 | 8.7602 | 8.2462 | 7.7949 | 7.0458 | 6.198 | 5.2944 | 4.189 | 3.1789 | 2.2372 | 0.27822 | 0.095226 | -0.85143 | 9.2027 | 8.7478 | 8.0888 | 7.2731 | 6.5368 | 5.4197 | 4.1565 | 2.8412 | 1.2991 | -0.10599 | -1.4078 | -4.3406 | -4.5495 | -5.7546
|  | HAUDAGAIN | ST |  |  |  | 4.185 | 8.3654 | 8.1298 | 7.878 | 7.605 | 7.3323 | 6.9998 | 6.6361 | 6.1643 | 5.5473 | 4.9499 | 4.2206 | 0.7837 | -0.88494 | -2.2529 | 9.6012 | 9.4376 | 9.2461 | 9.035 | 8.8056 | 8.5243 | 8.216 | 7.8224 | 7.309 | 6.8056 | 6.1962 | 3.1742 | 1.4977 | -0.30865 | 9.3573 | 9.1398 | 8.9029 | 8.6447 | 8.3783 | 8.0528 | 7.6973 | 7.2363 | 6.6322 | 6.0383 | 5.3226 | 1.9226 | 0.40019 | -0.7254
|  | HAUDAGAIN | FS |  |  |  | 4.185 | 8.4957 | 8.342 | 8.1381 | 7.8936 | 7.6842 | 7.4252 | 7.1138 | 6.7649 | 6.2957 | 5.8225 | 5.3034 | 1.2323 | -2.4445 | -5.334 | 9.6607 | 9.5374 | 9.3841 | 9.1958 | 9.0216 | 8.8013 | 8.5258 | 8.229 | 7.8293 | 7.4226 | 6.9778 | 3.8682 | 0.30168 | -3.8488 | 9.4781 | 9.3388 | 9.149 | 8.9204 | 8.717 | 8.4661 | 8.1639 | 7.8263 | 7.3704 | 6.9086 | 6.4037 | 2.6277 | -0.60368 | -3.1137
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 0.79 | 15.4836 | 15.0625 | 14.5217 | 13.8215 | 13.0827 | 12.0754 | 10.7969 | 9.5109 | 7.8517 | 6.3369 | 5.1088 | 1.9648 | 1.8956 | 1.0877 | 17.1536 | 16.8071 | 16.4171 | 15.8743 | 15.339 | 14.7573 | 13.9512 | 13.0441 | 12.1139 | 11.1056 | 10.2494 | 8.1644 | 6.8476 | 2.1518 | 15.5426 | 15.1464 | 14.6229 | 13.9443 | 13.22 | 12.2338 | 11.006 | 9.7935 | 8.2371 | 6.8181 | 5.6391 | 2.6481 | 2.5585 | 1.7384
|  | HAYTON | CT |  |  |  | 0.79 | 15.5189 | 15.0868 | 14.5519 | 13.8215 | 13.0827 | 12.2786 | 11.1849 | 9.8532 | 8.6248 | 7.401 | 6.4501 | 3.1819 | 2.3751 | 1.6984 | 17.1536 | 16.8071 | 16.4171 | 15.8743 | 15.339 | 14.7573 | 13.9512 | 13.0441 | 12.2439 | 11.4169 | 10.7226 | 8.214 | 6.9399 | 4.8572 | 15.5772 | 15.1657 | 14.6577 | 13.9443 | 13.22 | 12.4327 | 11.3592 | 10.0877 | 8.9557 | 7.8214 | 6.9166 | 3.8758 | 3.1509 | 2.4979
|  | HAYTON | LW |  |  |  | 0.79 | 15.4836 | 15.0625 | 14.5217 | 13.8319 | 13.1034 | 12.0754 | 10.7969 | 9.5109 | 7.8517 | 6.3369 | 5.1088 | 1.9648 | 1.8956 | 1.0877 | 17.1583 | 16.8411 | 16.5012 | 16.059 | 15.599 | 14.91 | 14.0584 | 13.2195 | 12.1139 | 11.1056 | 10.2494 | 8.1644 | 8.0299 | 7.3274 | 15.5426 | 15.1464 | 14.6229 | 13.9561 | 13.2451 | 12.2338 | 11.006 | 9.7935 | 8.2371 | 6.8181 | 5.6391 | 2.6481 | 2.5585 | 1.7384
|  | HAYTON | ST |  |  |  | 0.79 | 15.6458 | 15.4769 | 15.2665 | 15.0004 | 14.6998 | 14.3213 | 13.8567 | 13.3471 | 12.5804 | 11.768 | 10.9766 | 5.6447 | 3.8262 | 3.3813 | 17.2509 | 17.1092 | 16.9277 | 16.7016 | 16.444 | 16.122 | 15.7278 | 15.296 | 14.6758 | 14.0134 | 13.3354 | 9.4568 | 7.5744 | 5.4249 | 15.693 | 15.5357 | 15.3376 | 15.086 | 14.7959 | 14.4295 | 13.9785 | 13.4849 | 12.7524 | 11.9744 | 11.0837 | 5.8202 | 4.0519 | 3.6188
|  | HAYTON | FS |  |  |  | 0.79 | 15.7476 | 15.6281 | 15.465 | 15.2672 | 15.0243 | 14.7665 | 14.45 | 14.056 | 13.5234 | 13.0225 | 12.5124 | 8.693 | 5.1815 | 2.9923 | 17.3017 | 17.1844 | 17.0407 | 16.8663 | 16.6528 | 16.4164 | 16.1149 | 15.7509 | 15.2787 | 14.8266 | 14.3493 | 10.9686 | 6.8476 | 2.1518 | 15.7921 | 15.6822 | 15.5287 | 15.3401 | 15.1078 | 14.8611 | 14.5558 | 14.1821 | 13.6831 | 13.2083 | 12.709 | 9.0253 | 5.7112 | 3.6751
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 0.035 | 0.32311 | 0.27381 | 0.18288 | 0.10533 | 0.0084565 | -0.08612 | -0.21086 | -0.26417 | -0.33913 | -0.39918 | -0.45599 | -0.62283 | -0.71881 | -0.83231 | 0.70717 | 0.6771 | 0.59773 | 0.5601 | 0.52035 | 0.46722 | 0.38875 | 0.35559 | 0.29346 | 0.24736 | 0.20005 | 0.089295 | 0.038821 | -0.036207 | 0.46446 | 0.4185 | 0.33009 | 0.26552 | 0.18322 | 0.099036 | -0.019758 | -0.068966 | -0.15276 | -0.21547 | -0.27853 | -0.43581 | -0.51316 | -0.61544
|  | HELMSDALE | CT |  |  |  | 0.035 | 0.32311 | 0.27381 | 0.18288 | 0.10533 | 0.0084565 | -0.08612 | -0.21086 | -0.26417 | -0.31525 | -0.3611 | -0.40309 | -0.55765 | -0.63654 | -0.72366 | 0.70717 | 0.67835 | 0.61662 | 0.57341 | 0.52583 | 0.48223 | 0.40937 | 0.3735 | 0.33194 | 0.29367 | 0.25249 | 0.13574 | 0.084206 | -0.0071288 | 0.46446 | 0.4185 | 0.33449 | 0.26927 | 0.18322 | 0.10673 | -0.0078321 | -0.058539 | -0.11426 | -0.16391 | -0.21504 | -0.36802 | -0.42572 | -0.49564
|  | HELMSDALE | LW |  |  |  | 0.035 | 0.33179 | 0.28151 | 0.18327 | 0.10698 | 0.020291 | -0.083635 | -0.21021 | -0.26409 | -0.33913 | -0.39918 | -0.45599 | -0.62283 | -0.71881 | -0.83231 | 0.70861 | 0.6771 | 0.59773 | 0.5601 | 0.52035 | 0.46722 | 0.38875 | 0.35559 | 0.29346 | 0.24736 | 0.20005 | 0.089295 | 0.038821 | -0.036207 | 0.47226 | 0.42302 | 0.33009 | 0.26552 | 0.19105 | 0.099036 | -0.019758 | -0.068966 | -0.15276 | -0.21547 | -0.27853 | -0.43581 | -0.51316 | -0.61544
|  | HELMSDALE | ST |  |  |  | 0.035 | 0.33955 | 0.31038 | 0.236 | 0.18655 | 0.13686 | 0.085493 | 0.039591 | -0.012063 | -0.061355 | -0.12027 | -0.16446 | -0.41683 | -0.5236 | -0.58004 | 0.71137 | 0.70081 | 0.63724 | 0.61014 | 0.58417 | 0.55806 | 0.53818 | 0.51304 | 0.4852 | 0.44311 | 0.42087 | 0.21501 | 0.12241 | 0.040113 | 0.4833 | 0.4535 | 0.39555 | 0.35308 | 0.30575 | 0.25497 | 0.22039 | 0.1699 | 0.12404 | 0.064078 | 0.028625 | -0.23639 | -0.33551 | -0.39241
|  | HELMSDALE | FS |  |  |  | 0.035 | 0.35772 | 0.34091 | 0.30722 | 0.29067 | 0.27501 | 0.25093 | 0.22136 | 0.19548 | 0.14606 | 0.11002 | 0.062901 | -0.1654 | -0.4016 | -0.48505 | 0.71125 | 0.70956 | 0.67356 | 0.66638 | 0.65784 | 0.64416 | 0.62019 | 0.60523 | 0.57067 | 0.54697 | 0.51533 | 0.35642 | 0.16863 | 0.031812 | 0.49625 | 0.48074 | 0.45178 | 0.43249 | 0.41719 | 0.39344 | 0.36412 | 0.33955 | 0.2927 | 0.25826 | 0.21388 | -0.002221 | -0.22362 | -0.29311
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 4.025 | 5.8732 | 5.0008 | 4.2413 | 3.3675 | 2.4137 | 1.1974 | 0.12327 | -1.3502 | -2.747 | -4.0978 | -5.3223 | -8.8523 | -11.0667 | -12.8523 | 8.3543 | 7.5055 | 7.4045 | 7.2594 | 6.7839 | 6.1313 | 5.6614 | 4.8414 | 4.1059 | 3.3566 | 2.6719 | 0.78976 | -0.71057 | -2.449 | 8.1102 | 7.2989 | 6.614 | 5.8187 | 4.9596 | 3.815 | 2.8993 | 1.5253 | 0.12293 | -1.1783 | -2.3608 | -5.5829 | -7.1739 | -8.7404
|  | HILTON | CT |  |  |  | 4.025 | 6.145 | 5.3698 | 4.5775 | 3.6922 | 2.5633 | 1.2901 | 0.12327 | -1.3502 | -2.541 | -3.6313 | -4.5714 | -8.5362 | -11.0667 | -12.8523 | 8.7363 | 8.0325 | 7.9009 | 7.5319 | 6.918 | 6.2264 | 5.6614 | 4.8414 | 4.1975 | 3.5806 | 3.0242 | 0.78976 | -0.71057 | -2.449 | 8.3454 | 7.6177 | 6.8966 | 6.0936 | 5.0629 | 3.9146 | 2.8993 | 1.5253 | 0.42408 | -0.61372 | -1.5224 | -5.089 | -7.1739 | -8.7404
|  | HILTON | LW |  |  |  | 4.025 | 5.8732 | 5.0008 | 4.2413 | 3.3675 | 2.4137 | 1.1974 | 0.20836 | -1.243 | -2.747 | -4.0978 | -5.3223 | -8.8523 | -10.2997 | -11.9628 | 8.3543 | 7.5055 | 7.4045 | 7.2594 | 6.7839 | 6.1313 | 5.6917 | 4.9399 | 4.1059 | 3.3566 | 2.6719 | 0.89014 | 0.30918 | -0.56464 | 8.1102 | 7.2989 | 6.614 | 5.8187 | 4.9596 | 3.815 | 2.9283 | 1.5731 | 0.12293 | -1.1783 | -2.3608 | -5.5829 | -6.7781 | -8.3135
|  | HILTON | ST |  |  |  | 4.025 | 6.2964 | 5.7139 | 5.5447 | 5.3865 | 5.141 | 4.8575 | 4.4904 | 4.1153 | 4.0137 | 3.6263 | 3.2045 | -0.039189 | -2.3939 | -4.479 | 8.762 | 8.108 | 8.0144 | 7.9397 | 7.7909 | 7.577 | 7.3257 | 7.1257 | 7.0671 | 6.8704 | 6.5575 | 4.3758 | 2.7861 | 1.0106 | 8.4973 | 7.9727 | 7.7963 | 7.6314 | 7.3759 | 7.0829 | 6.702 | 6.3044 | 6.1873 | 5.8075 | 5.393 | 2.3263 | 0.21793 | -1.6123
|  | HILTON | FS |  |  |  | 4.025 | 6.6191 | 6.1598 | 5.9656 | 5.7523 | 5.5035 | 5.2049 | 4.9362 | 4.5207 | 4.0809 | 3.6165 | 3.4178 | 0.29012 | -2.784 | -5.5689 | 9.1762 | 8.6646 | 8.584 | 8.4752 | 8.351 | 8.1815 | 8.0293 | 7.7426 | 7.4121 | 7.0578 | 6.9078 | 4.5466 | 1.8999 | -1.3023 | 8.7796 | 8.3659 | 8.1784 | 7.9767 | 7.733 | 7.4399 | 7.1706 | 6.7707 | 6.3335 | 5.873 | 5.7066 | 2.7419 | -0.090406 | -2.5674
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.381 | 13.4518 | 12.7974 | 12.2624 | 11.7145 | 11.0828 | 10.3162 | 9.42 | 8.5215 | 7.5503 | 6.9745 | 6.2214 | 4.067 | 3.2758 | 2.4273 | 15.8046 | 15.421 | 15.1468 | 14.8642 | 14.5407 | 14.119 | 13.6087 | 13.0946 | 12.5018 | 12.2064 | 11.6726 | 10.3265 | 9.7547 | 8.7401 | 15.3115 | 14.785 | 14.3078 | 13.8075 | 13.2341 | 12.5257 | 11.6915 | 10.8562 | 9.8566 | 9.3001 | 8.5094 | 6.4154 | 5.9655 | 5.1372
|  | HUME STREET | CT |  |  |  | 0.381 | 13.4821 | 12.8797 | 12.4236 | 11.9215 | 11.3079 | 10.6803 | 9.8675 | 8.8887 | 8.0923 | 7.6343 | 6.8944 | 4.4082 | 3.2758 | 2.4273 | 15.8103 | 15.4505 | 15.1908 | 14.9038 | 14.5528 | 14.2078 | 13.7284 | 13.1637 | 12.7102 | 12.4958 | 12.0579 | 10.4807 | 9.7547 | 8.7401 | 15.3328 | 14.8417 | 14.4268 | 13.9635 | 13.3985 | 12.8239 | 12.0675 | 11.1531 | 10.3741 | 9.9697 | 9.2419 | 6.8965 | 5.9655 | 5.1372
|  | HUME STREET | LW |  |  |  | 0.381 | 13.4518 | 12.7974 | 12.2624 | 11.7145 | 11.0828 | 10.3162 | 9.42 | 8.5215 | 7.5503 | 6.9745 | 6.2214 | 4.067 | 3.6836 | 2.8654 | 15.8046 | 15.421 | 15.1468 | 14.8642 | 14.5407 | 14.119 | 13.6087 | 13.0946 | 12.5018 | 12.2064 | 11.6726 | 10.3265 | 10.1327 | 9.5482 | 15.3115 | 14.785 | 14.3078 | 13.8075 | 13.2341 | 12.5257 | 11.6915 | 10.8562 | 9.8566 | 9.3001 | 8.5094 | 6.4154 | 6.0654 | 5.2717
|  | HUME STREET | ST |  |  |  | 0.381 | 13.5416 | 13.0679 | 12.9296 | 12.8128 | 12.6596 | 12.503 | 12.3024 | 12.0488 | 11.7548 | 11.4152 | 10.9708 | 8.5566 | 7.1409 | 6.2539 | 15.8572 | 15.5921 | 15.4875 | 15.3936 | 15.2717 | 15.1442 | 14.9777 | 14.775 | 14.5378 | 14.2621 | 13.919 | 11.9651 | 11.027 | 10.4796 | 15.3917 | 15.0256 | 14.8986 | 14.787 | 14.6414 | 14.4918 | 14.296 | 14.0506 | 13.7648 | 13.4071 | 12.929 | 10.3689 | 9.0384 | 8.2325
|  | HUME STREET | FS |  |  |  | 0.381 | 13.6663 | 13.3432 | 13.2371 | 13.1357 | 13.0066 | 12.8564 | 12.7145 | 12.4728 | 12.183 | 11.8895 | 11.5502 | 9.3539 | 7.0628 | 5.2227 | 15.9124 | 15.7144 | 15.6354 | 15.5561 | 15.4547 | 15.3327 | 15.2096 | 15.0289 | 14.8063 | 14.5794 | 14.3294 | 12.7546 | 10.8421 | 8.7651 | 15.4972 | 15.2551 | 15.1594 | 15.0648 | 14.9447 | 14.8035 | 14.6692 | 14.442 | 14.1673 | 13.888 | 13.5822 | 11.4484 | 9.2523 | 7.3452
| KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0.722 | 7.5944 | 7.4257 | 7.0897 | 6.6644 | 6.2445 | 5.6934 | 5.061 | 4.3891 | 3.5641 | 3.0839 | 2.6498 | 1.7286 | 1.2227 | 0.68587 | 9.2807 | 9.1755 | 9.0033 | 8.7833 | 8.5657 | 8.2912 | 7.9031 | 7.4699 | 6.9006 | 6.6218 | 6.3674 | 5.9443 | 5.5472 | 5.0153 | 8.5832 | 8.4497 | 8.2773 | 8.0219 | 7.7459 | 7.4056 | 6.8572 | 6.2425 | 5.4705 | 4.9907 | 4.5553 | 3.7689 | 3.3988 | 2.9018
|  | HUNTLY | CT |  |  |  | 0.722 | 7.5944 | 7.4257 | 7.1099 | 6.6879 | 6.2488 | 5.7439 | 5.1369 | 4.4838 | 3.803 | 3.3591 | 2.9841 | 1.9143 | 1.2227 | 0.68587 | 9.2807 | 9.1773 | 9.015 | 8.7851 | 8.5657 | 8.3084 | 7.9473 | 7.5235 | 7.0566 | 6.7799 | 6.5403 | 5.9889 | 5.5472 | 5.0153 | 8.5869 | 8.4603 | 8.2838 | 8.0219 | 7.7459 | 7.4085 | 6.9408 | 6.3442 | 5.7157 | 5.2796 | 4.9015 | 4.0049 | 3.3988 | 2.922
|  | HUNTLY | LW |  |  |  | 0.722 | 7.5976 | 7.4282 | 7.0897 | 6.6644 | 6.2445 | 5.6934 | 5.061 | 4.3891 | 3.5641 | 3.0839 | 2.6498 | 1.7286 | 1.2985 | 0.79269 | 9.2843 | 9.1755 | 9.0033 | 8.7833 | 8.5843 | 8.2912 | 7.9031 | 7.4699 | 6.9006 | 6.6218 | 6.3674 | 5.9443 | 5.7167 | 5.4087 | 8.5832 | 8.4497 | 8.2773 | 8.0579 | 7.7981 | 7.4056 | 6.8572 | 6.2425 | 5.4705 | 4.9907 | 4.5553 | 3.7689 | 3.4 | 2.9018
|  | HUNTLY | ST |  |  |  | 0.722 | 7.6646 | 7.569 | 7.4343 | 7.2818 | 7.111 | 6.9277 | 6.7094 | 6.3983 | 5.9361 | 5.7088 | 5.4578 | 4.4001 | 3.6048 | 2.8071 | 9.3192 | 9.2651 | 9.1838 | 9.094 | 8.991 | 8.8774 | 8.7077 | 8.4542 | 8.0769 | 7.9072 | 7.7197 | 6.954 | 6.3835 | 5.7606 | 8.6289 | 8.5716 | 8.4811 | 8.3762 | 8.255 | 8.1171 | 7.9009 | 7.5918 | 7.1215 | 6.8509 | 6.5425 | 5.0932 | 4.3966 | 3.9371
|  | HUNTLY | FS |  |  |  | 0.722 | 7.7224 | 7.6562 | 7.5737 | 7.4608 | 7.358 | 7.2388 | 7.0762 | 6.8122 | 6.4792 | 6.2464 | 5.9982 | 4.5236 | 3.4123 | 2.3932 | 9.3451 | 9.305 | 9.2529 | 9.1796 | 9.1135 | 9.0326 | 8.8948 | 8.6948 | 8.4361 | 8.2694 | 8.0893 | 7.0395 | 6.1867 | 5.1088 | 8.6541 | 8.6156 | 8.5588 | 8.4837 | 8.4056 | 8.3143 | 8.1639 | 7.9504 | 7.6469 | 7.4556 | 7.2439 | 5.7982 | 4.6163 | 3.6598
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 0.491 | 1.2811 | 1.2634 | 1.2468 | 1.2295 | 1.1825 | 1.129 | 1.0582 | 1.0211 | 0.96971 | 0.92349 | 0.89735 | 0.761 | 0.67508 | 0.57923 | 1.4603 | 1.4428 | 1.4255 | 1.4084 | 1.3879 | 1.3562 | 1.3087 | 1.2862 | 1.2492 | 1.2159 | 1.201 | 1.0835 | 1.0133 | 0.93334 | 1.4164 | 1.3863 | 1.3468 | 1.3068 | 1.2642 | 1.2192 | 1.1508 | 1.1168 | 1.0629 | 1.0156 | 1.0005 | 0.82242 | 0.73933 | 0.63311
|  | INCHBARE | CT |  |  |  | 0.491 | 1.282 | 1.2717 | 1.2613 | 1.2393 | 1.1893 | 1.1458 | 1.0798 | 1.0431 | 1.0062 | 0.96975 | 0.95106 | 0.81546 | 0.73966 | 0.69009 | 1.461 | 1.4525 | 1.4437 | 1.4249 | 1.4025 | 1.3823 | 1.3416 | 1.3176 | 1.2916 | 1.2637 | 1.2512 | 1.158 | 1.1078 | 1.0627 | 1.4164 | 1.3912 | 1.3601 | 1.3219 | 1.2757 | 1.2445 | 1.1824 | 1.1469 | 1.1097 | 1.0701 | 1.0589 | 0.94368 | 0.89007 | 0.84997
|  | INCHBARE | LW |  |  |  | 0.491 | 1.2811 | 1.2634 | 1.2468 | 1.2295 | 1.1825 | 1.129 | 1.0582 | 1.0211 | 0.96971 | 0.92349 | 0.89735 | 0.761 | 0.67508 | 0.60667 | 1.4603 | 1.4428 | 1.4255 | 1.4084 | 1.3879 | 1.3562 | 1.3087 | 1.2862 | 1.2492 | 1.2159 | 1.201 | 1.0835 | 1.0199 | 0.98358 | 1.4184 | 1.3863 | 1.3468 | 1.3068 | 1.2642 | 1.2192 | 1.1508 | 1.1168 | 1.0629 | 1.0156 | 1.0005 | 0.82242 | 0.73933 | 0.68972
|  | INCHBARE | ST |  |  |  | 0.491 | 1.2834 | 1.2815 | 1.2719 | 1.2628 | 1.2535 | 1.2348 | 1.2048 | 1.184 | 1.1497 | 1.1131 | 1.0823 | 0.8522 | 0.72462 | 0.69575 | 1.4619 | 1.4605 | 1.4506 | 1.4418 | 1.4334 | 1.4261 | 1.4114 | 1.4 | 1.3759 | 1.3498 | 1.3301 | 1.1258 | 1.0133 | 0.97767 | 1.4165 | 1.4108 | 1.3872 | 1.3646 | 1.3412 | 1.3214 | 1.2929 | 1.2777 | 1.2435 | 1.2073 | 1.1816 | 0.88472 | 0.74646 | 0.70028
|  | INCHBARE | FS |  |  |  | 0.491 | 1.2848 | 1.2837 | 1.2786 | 1.2729 | 1.2654 | 1.2579 | 1.2496 | 1.2393 | 1.2241 | 1.2125 | 1.1909 | 1.0262 | 0.81899 | 0.57923 | 1.4629 | 1.4622 | 1.4574 | 1.452 | 1.445 | 1.4379 | 1.4299 | 1.4203 | 1.4063 | 1.3958 | 1.3813 | 1.267 | 1.1139 | 0.93334 | 1.4248 | 1.423 | 1.4129 | 1.4022 | 1.3868 | 1.3731 | 1.3614 | 1.3375 | 1.3076 | 1.2939 | 1.2672 | 1.1052 | 0.86255 | 0.63311
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0.208 | 1.5311 | 1.4967 | 1.4154 | 1.3261 | 1.226 | 1.1106 | 0.96908 | 0.81513 | 0.64948 | 0.53235 | 0.40416 | 0.035584 | -0.1969 | -0.36817 | 1.768 | 1.7379 | 1.6923 | 1.6489 | 1.5862 | 1.5371 | 1.4538 | 1.3583 | 1.2452 | 1.1799 | 1.0942 | 0.90187 | 0.80991 | 0.67594 | 1.859 | 1.8194 | 1.7457 | 1.6666 | 1.5741 | 1.4751 | 1.3421 | 1.1912 | 1.0193 | 0.91497 | 0.78529 | 0.45834 | 0.29301 | 0.14292
|  | INNELLAN | CT |  |  |  | 0.208 | 1.5324 | 1.4971 | 1.4206 | 1.3403 | 1.2352 | 1.1411 | 1.0094 | 0.85634 | 0.73114 | 0.63735 | 0.53504 | 0.07763 | -0.1969 | -0.36817 | 1.768 | 1.7379 | 1.6923 | 1.6489 | 1.5862 | 1.5409 | 1.464 | 1.3678 | 1.2918 | 1.2425 | 1.1728 | 0.93283 | 0.80991 | 0.67594 | 1.8601 | 1.8194 | 1.7457 | 1.675 | 1.5741 | 1.4972 | 1.3746 | 1.2238 | 1.1036 | 1.0233 | 0.91898 | 0.51886 | 0.29301 | 0.14292
|  | INNELLAN | LW |  |  |  | 0.208 | 1.5311 | 1.4967 | 1.4154 | 1.3261 | 1.226 | 1.1106 | 0.96908 | 0.81513 | 0.64948 | 0.53235 | 0.40416 | 0.035584 | -0.11944 | -0.28758 | 1.7682 | 1.7404 | 1.6975 | 1.6513 | 1.5997 | 1.5371 | 1.4538 | 1.3583 | 1.2452 | 1.1799 | 1.0942 | 0.90187 | 0.85136 | 0.76663 | 1.859 | 1.8201 | 1.7458 | 1.6666 | 1.5776 | 1.4751 | 1.3421 | 1.1912 | 1.0193 | 0.91497 | 0.78529 | 0.45834 | 0.33101 | 0.17747
|  | INNELLAN | ST |  |  |  | 0.208 | 1.5416 | 1.5215 | 1.5027 | 1.4755 | 1.457 | 1.4338 | 1.3995 | 1.3575 | 1.3235 | 1.2723 | 1.219 | 0.86718 | 0.67769 | 0.47855 | 1.7781 | 1.7643 | 1.749 | 1.7252 | 1.7106 | 1.69 | 1.6584 | 1.6201 | 1.5899 | 1.5416 | 1.4948 | 1.2422 | 1.1112 | 0.9872 | 1.8733 | 1.853 | 1.832 | 1.7986 | 1.7814 | 1.7551 | 1.7128 | 1.6611 | 1.6232 | 1.5592 | 1.4994 | 1.1608 | 0.98906 | 0.84934
|  | INNELLAN | FS |  |  |  | 0.208 | 1.5548 | 1.5426 | 1.5262 | 1.5034 | 1.4884 | 1.4637 | 1.4358 | 1.4028 | 1.3547 | 1.3227 | 1.274 | 0.93573 | 0.58298 | 0.27099 | 1.7833 | 1.7731 | 1.7604 | 1.7409 | 1.7297 | 1.7079 | 1.6822 | 1.6583 | 1.6192 | 1.5964 | 1.5562 | 1.3012 | 1.0509 | 0.80243 | 1.8841 | 1.8707 | 1.8534 | 1.8265 | 1.8138 | 1.7848 | 1.7516 | 1.7199 | 1.6667 | 1.6382 | 1.5845 | 1.2412 | 0.93492 | 0.68982
| KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0.769 | -1.0941 | -1.4068 | 5.4254 | 4.9314 | 4.3788 | 3.791 | 2.9538 | 2.4356 | 2.0397 | 1.7612 | 1.7788 | 0.97834 | 0.48448 | -0.00015309 | 1.9073 | 1.7403 | 8.4282 | 8.201 | 7.932 | 7.651 | 7.1679 | 6.778 | 6.4488 | 6.2575 | 6.3115 | 5.8451 | 5.587 | 5.0223 | 1.3224 | 1.0496 | 7.9586 | 7.5645 | 7.0905 | 6.5621 | 5.8011 | 5.313 | 4.9319 | 4.6757 | 4.6992 | 3.9621 | 3.5315 | 3.1064
|  | INSCH | CT |  |  |  | 0.769 | -1.0941 | -1.4068 | 5.4254 | 4.9314 | 4.3788 | 3.791 | 2.9538 | 2.4356 | 2.0397 | 1.7612 | 1.8768 | 1.1712 | 0.74395 | 0.30008 | 1.9073 | 1.7403 | 8.4282 | 8.201 | 7.932 | 7.651 | 7.1679 | 6.778 | 6.4777 | 6.2575 | 6.3659 | 5.8809 | 5.587 | 5.1615 | 1.3224 | 1.0496 | 7.9586 | 7.5645 | 7.0905 | 6.5621 | 5.8011 | 5.313 | 4.9409 | 4.6757 | 4.7993 | 4.1529 | 3.7802 | 3.3925
|  | INSCH | LW |  |  |  | 0.769 | -1.046 | -1.327 | 5.5246 | 5.0522 | 4.5508 | 3.9929 | 3.1068 | 2.5609 | 2.0405 | 2.0365 | 1.7788 | 0.97834 | 0.48448 | -0.00015309 | 1.9246 | 1.7745 | 8.4838 | 8.2752 | 8.049 | 7.7803 | 7.2428 | 6.8418 | 6.4488 | 6.4958 | 6.3115 | 5.8451 | 5.6442 | 5.416 | 1.3557 | 1.1079 | 8.0381 | 7.6592 | 7.2497 | 6.7519 | 5.9403 | 5.4257 | 4.9319 | 4.9432 | 4.6992 | 3.9621 | 3.5315 | 3.1064
|  | INSCH | ST |  |  |  | 0.769 | -1.005 | -1.2268 | 5.7406 | 5.44 | 5.1324 | 4.8396 | 4.3215 | 3.8568 | 3.4363 | 3.0785 | 2.7189 | 1.6537 | 1.0779 | 0.75664 | 1.9553 | 1.8538 | 8.6132 | 8.4782 | 8.3335 | 8.201 | 7.8674 | 7.5533 | 7.2729 | 7.0462 | 6.818 | 6.1347 | 5.7254 | 5.3649 | 1.4026 | 1.2253 | 8.2522 | 8.0139 | 7.7624 | 7.521 | 7.0467 | 6.6169 | 6.2296 | 5.8989 | 5.5664 | 4.5931 | 4.0773 | 3.8021
|  | INSCH | FS |  |  |  | 0.769 | -0.85717 | -1.0065 | 6.1653 | 6.0614 | 5.9508 | 5.835 | 5.5844 | 5.2782 | 4.9409 | 4.6552 | 4.3927 | 2.8904 | 1.8028 | 1.1991 | 2.0094 | 1.9319 | 8.7713 | 8.7095 | 8.6401 | 8.5618 | 8.3638 | 8.1697 | 7.9426 | 7.7588 | 7.5918 | 6.5584 | 5.8225 | 5.0223 | 1.513 | 1.388 | 8.572 | 8.4815 | 8.3805 | 8.2686 | 8.0402 | 7.7884 | 7.4888 | 7.2314 | 7.0046 | 5.6202 | 4.721 | 4.1779
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 2.8 | 20.9632 | 20.2728 | 19.5603 | 18.5537 | 17.8474 | 17.5636 | 17.3148 | 16.8929 | 16.3648 | 15.7909 | 15.2252 | 13.4034 | 12.9212 | 12.8641 | 22.099 | 21.3672 | 20.6059 | 19.5547 | 18.7822 | 18.5344 | 18.3194 | 17.9177 | 17.6244 | 17.3372 | 17.0461 | 15.9125 | 15.6748 | 15.6103 | 21.8674 | 21.1601 | 20.4067 | 19.3363 | 18.544 | 18.1739 | 17.8605 | 17.33 | 16.8884 | 16.4552 | 16.0147 | 14.1849 | 13.7785 | 13.7271
|  | INVERALMOND | CT |  |  |  | 2.8 | 21.154 | 20.5883 | 19.9345 | 18.8621 | 18.0966 | 17.735 | 17.3977 | 16.961 | 16.5256 | 16.1001 | 15.6913 | 13.6257 | 12.9212 | 12.8641 | 22.3099 | 21.7163 | 21.0307 | 19.9208 | 19.0827 | 18.7321 | 18.4138 | 17.984 | 17.6896 | 17.4364 | 17.1826 | 16.0841 | 15.7278 | 15.6103 | 22.0618 | 21.4793 | 20.7906 | 19.6686 | 18.8224 | 18.3616 | 17.9507 | 17.4033 | 16.9805 | 16.6001 | 16.2164 | 14.3707 | 13.7785 | 13.7271
|  | INVERALMOND | LW |  |  |  | 2.8 | 20.9632 | 20.2728 | 19.5603 | 18.5537 | 17.8474 | 17.5636 | 17.3148 | 16.8929 | 16.3648 | 15.7909 | 15.2252 | 13.4034 | 12.9321 | 12.8839 | 22.099 | 21.3672 | 20.6059 | 19.5547 | 18.7822 | 18.5344 | 18.3194 | 17.9177 | 17.6244 | 17.3372 | 17.0461 | 15.9125 | 15.6748 | 15.6274 | 21.8674 | 21.1601 | 20.4067 | 19.3363 | 18.544 | 18.1739 | 17.8605 | 17.33 | 16.8884 | 16.4552 | 16.0147 | 14.1849 | 13.7795 | 13.7275
|  | INVERALMOND | ST |  |  |  | 2.8 | 21.1708 | 20.6436 | 20.0312 | 19.0452 | 18.3233 | 18.0015 | 17.7328 | 17.3464 | 17.0255 | 16.7267 | 16.4004 | 14.2715 | 13.4915 | 13.3911 | 22.32 | 21.754 | 21.106 | 20.0783 | 19.3089 | 19.0456 | 18.8251 | 18.4993 | 18.2707 | 18.0711 | 17.8542 | 16.7287 | 16.3064 | 16.1537 | 22.0752 | 21.5313 | 20.9028 | 19.9025 | 19.1686 | 18.854 | 18.5974 | 18.2242 | 17.9245 | 17.6488 | 17.3483 | 15.8058 | 15.2889 | 15.2073
|  | INVERALMOND | FS |  |  |  | 2.8 | 21.3838 | 20.9675 | 20.5166 | 19.7695 | 19.1467 | 18.8837 | 18.6469 | 18.32 | 17.9911 | 17.6712 | 17.3236 | 15.5587 | 14.4838 | 13.6705 | 22.5565 | 22.121 | 21.6546 | 20.8859 | 20.2263 | 20.004 | 19.8043 | 19.5297 | 19.2703 | 19.0239 | 18.7544 | 17.4077 | 16.731 | 16.2675 | 22.2983 | 21.8844 | 21.4371 | 20.6936 | 20.0736 | 19.8267 | 19.6058 | 19.3007 | 18.9989 | 18.7072 | 18.3912 | 16.7951 | 15.9887 | 15.5082
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0.021 | 2.0905 | 2.0743 | 2.084 | 2.0754 | 2.0575 | 2.0335 | 2.0006 | 1.9758 | 1.9496 | 1.9236 | 1.8946 | 1.8255 | 1.8099 | 1.7721 | 2.1084 | 2.0908 | 2.0996 | 2.0899 | 2.0798 | 2.0692 | 2.0554 | 2.0473 | 2.0404 | 2.0354 | 2.026 | 2 | 1.9904 | 1.9777 | 2.2342 | 2.2149 | 2.2195 | 2.1988 | 2.1777 | 2.1561 | 2.1293 | 2.1171 | 2.0967 | 2.0709 | 2.0421 | 1.9741 | 1.9597 | 1.9231
|  | INVERARAY | CT |  |  |  | 0.021 | 2.0905 | 2.0743 | 2.0896 | 2.0825 | 2.0575 | 2.0335 | 2.0006 | 1.9758 | 1.9554 | 1.9398 | 1.9202 | 1.8624 | 1.8465 | 1.8192 | 2.1084 | 2.0908 | 2.1015 | 2.0904 | 2.0798 | 2.0692 | 2.0554 | 2.0473 | 2.0404 | 2.0354 | 2.029 | 2.0065 | 1.9945 | 1.9792 | 2.2342 | 2.2149 | 2.2195 | 2.1988 | 2.1777 | 2.1561 | 2.1293 | 2.1171 | 2.1036 | 2.088 | 2.0684 | 2.011 | 1.9961 | 1.9699
|  | INVERARAY | LW |  |  |  | 0.021 | 2.0912 | 2.077 | 2.0888 | 2.0871 | 2.0728 | 2.0448 | 2.012 | 1.983 | 1.9496 | 1.9236 | 1.8946 | 1.8255 | 1.8099 | 1.7721 | 2.1097 | 2.0942 | 2.1017 | 2.0956 | 2.0875 | 2.0766 | 2.0642 | 2.0547 | 2.044 | 2.0355 | 2.026 | 2 | 1.9904 | 1.9788 | 2.2357 | 2.2187 | 2.2215 | 2.2077 | 2.1909 | 2.1698 | 2.1457 | 2.1297 | 2.0967 | 2.0709 | 2.0421 | 1.9741 | 1.9597 | 1.9231
|  | INVERARAY | ST |  |  |  | 0.021 | 2.0958 | 2.0906 | 2.084 | 2.0754 | 2.0891 | 2.0889 | 2.0858 | 2.0825 | 2.0653 | 2.0502 | 2.0315 | 1.9459 | 1.9259 | 1.9282 | 2.114 | 2.1073 | 2.0996 | 2.0899 | 2.1019 | 2.1004 | 2.0965 | 2.0923 | 2.0851 | 2.0791 | 2.0717 | 2.0361 | 2.0234 | 2.0185 | 2.24 | 2.2318 | 2.2239 | 2.214 | 2.2225 | 2.2188 | 2.212 | 2.205 | 2.194 | 2.1845 | 2.173 | 2.0897 | 2.0699 | 2.0719
|  | INVERARAY | FS |  |  |  | 0.021 | 2.0967 | 2.0925 | 2.0875 | 2.0812 | 2.0743 | 2.0896 | 2.09 | 2.0882 | 2.084 | 2.0812 | 2.0774 | 2.0015 | 1.9207 | 1.8772 | 2.1161 | 2.111 | 2.1061 | 2.0999 | 2.0932 | 2.1082 | 2.1085 | 2.1052 | 2.0997 | 2.0959 | 2.0916 | 2.0582 | 2.015 | 1.9777 | 2.2433 | 2.2374 | 2.2333 | 2.228 | 2.2221 | 2.2367 | 2.2383 | 2.2329 | 2.2247 | 2.2185 | 2.2116 | 2.1438 | 2.0656 | 2.0234
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 0.29857 | 0.2808 | 0.24643 | 0.17995 | 0.11897 | 0.060529 | -0.026071 | -0.066284 | -0.10142 | -0.13508 | -0.19487 | -0.41577 | -0.4969 | -0.54039 | 0.446 | 0.42517 | 0.39469 | 0.33299 | 0.29262 | 0.25022 | 0.18305 | 0.13799 | 0.10261 | 0.066609 | 0.0092373 | -0.16193 | -0.22648 | -0.26213 | 0.4289 | 0.3993 | 0.35622 | 0.29446 | 0.23819 | 0.1872 | 0.10496 | 0.065239 | 0.029497 | -0.006187 | -0.044593 | -0.25847 | -0.34118 | -0.38856
|  | INVERARITY | CT |  |  |  | 0 | 0.29857 | 0.28146 | 0.24643 | 0.17995 | 0.11897 | 0.060529 | -0.026071 | -0.066284 | -0.10142 | -0.13508 | -0.16325 | -0.25938 | -0.29229 | -0.33907 | 0.44606 | 0.42695 | 0.39469 | 0.33299 | 0.29262 | 0.25022 | 0.18305 | 0.13799 | 0.10261 | 0.06826 | 0.039587 | -0.026165 | -0.039097 | -0.055095 | 0.4289 | 0.3993 | 0.35622 | 0.29446 | 0.23819 | 0.1872 | 0.10496 | 0.065239 | 0.029497 | -0.006187 | -0.037032 | -0.11177 | -0.15251 | -0.19498
|  | INVERARITY | LW |  |  |  | 0 | 0.29901 | 0.2808 | 0.25395 | 0.20521 | 0.15318 | 0.09414 | 0.018317 | -0.02099 | -0.073087 | -0.12149 | -0.19487 | -0.41577 | -0.4969 | -0.54039 | 0.446 | 0.42517 | 0.39737 | 0.36674 | 0.33531 | 0.29066 | 0.23231 | 0.18648 | 0.12576 | 0.066609 | 0.0092373 | -0.16193 | -0.22648 | -0.26213 | 0.43151 | 0.40203 | 0.35933 | 0.31441 | 0.26705 | 0.213 | 0.14013 | 0.10264 | 0.049855 | 0.0010446 | -0.044593 | -0.25847 | -0.34118 | -0.38856
|  | INVERARITY | ST |  |  |  | 0 | 0.30223 | 0.2995 | 0.28803 | 0.25857 | 0.2286 | 0.19971 | 0.16515 | 0.13083 | 0.099785 | 0.058527 | 0.021441 | -0.29287 | -0.43483 | -0.47922 | 0.44677 | 0.44409 | 0.42654 | 0.40947 | 0.39253 | 0.3769 | 0.35641 | 0.32792 | 0.29324 | 0.25169 | 0.20728 | -0.060859 | -0.17028 | -0.20544 | 0.4335 | 0.42323 | 0.39593 | 0.3693 | 0.34235 | 0.31713 | 0.28518 | 0.2523 | 0.22421 | 0.18415 | 0.14999 | -0.13447 | -0.2761 | -0.32363
|  | INVERARITY | FS |  |  |  | 0 | 0.30393 | 0.30161 | 0.29565 | 0.28943 | 0.28266 | 0.2741 | 0.26448 | 0.24938 | 0.21956 | 0.19769 | 0.16858 | -0.0074573 | -0.27489 | -0.44557 | 0.45124 | 0.4479 | 0.43935 | 0.43137 | 0.42346 | 0.41262 | 0.40221 | 0.38428 | 0.36123 | 0.33949 | 0.3149 | 0.14487 | -0.042961 | -0.17027 | 0.44354 | 0.43595 | 0.42488 | 0.41421 | 0.40343 | 0.38988 | 0.37684 | 0.35265 | 0.3233 | 0.30379 | 0.27591 | 0.10818 | -0.11258 | -0.27598
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 0.486 | 1.3361 | 1.3003 | 1.2564 | 1.1921 | 1.0846 | 0.97109 | 0.8128 | 0.67794 | 0.58724 | 0.49954 | 0.29704 | -0.75939 | -1.1109 | -1.2456 | 1.4217 | 1.3667 | 1.3164 | 1.2476 | 1.1758 | 1.1001 | 0.98886 | 0.88446 | 0.81393 | 0.72502 | 0.56685 | -0.25421 | -0.52939 | -0.63693 | 1.4325 | 1.3915 | 1.3329 | 1.2558 | 1.1658 | 1.0588 | 0.90812 | 0.77843 | 0.69108 | 0.60672 | 0.40987 | -0.60738 | -0.9495 | -1.0835
|  | INVERARNIE | CT |  |  |  | 0.486 | 1.3361 | 1.3003 | 1.2564 | 1.1921 | 1.0846 | 0.97109 | 0.8128 | 0.67794 | 0.58724 | 0.49954 | 0.41714 | 0.23555 | 0.20201 | 0.16876 | 1.4217 | 1.3667 | 1.3164 | 1.2476 | 1.1758 | 1.1001 | 0.98886 | 0.88446 | 0.81393 | 0.74504 | 0.67926 | 0.54177 | 0.52329 | 0.502 | 1.4325 | 1.3915 | 1.3329 | 1.2558 | 1.1658 | 1.0588 | 0.90812 | 0.77843 | 0.69108 | 0.60672 | 0.52698 | 0.3522 | 0.32064 | 0.28821
|  | INVERARNIE | LW |  |  |  | 0.486 | 1.3394 | 1.3021 | 1.2581 | 1.2049 | 1.1499 | 1.0353 | 0.8965 | 0.78382 | 0.65284 | 0.53852 | 0.43806 | 0.23915 | 0.18879 | 0.13874 | 1.4238 | 1.3715 | 1.3253 | 1.2674 | 1.22 | 1.1319 | 1.0318 | 0.94649 | 0.84629 | 0.75849 | 0.68106 | 0.52978 | 0.49096 | 0.44879 | 1.4382 | 1.3943 | 1.3341 | 1.2638 | 1.2013 | 1.1112 | 0.97826 | 0.87037 | 0.74499 | 0.63529 | 0.53886 | 0.34636 | 0.294 | 0.2406
|  | INVERARNIE | ST |  |  |  | 0.486 | 1.3441 | 1.3214 | 1.2905 | 1.2547 | 1.202 | 1.1063 | 0.98994 | 0.86195 | 0.68772 | 0.50435 | 0.29704 | -0.75939 | -1.1109 | -1.2456 | 1.4268 | 1.4001 | 1.3579 | 1.3073 | 1.2477 | 1.1786 | 1.0932 | 0.99716 | 0.86465 | 0.72502 | 0.56685 | -0.25421 | -0.52939 | -0.63693 | 1.4431 | 1.4152 | 1.3748 | 1.3304 | 1.2612 | 1.1805 | 1.0727 | 0.95057 | 0.78375 | 0.60826 | 0.40987 | -0.60738 | -0.9495 | -1.0835
|  | INVERARNIE | FS |  |  |  | 0.486 | 1.3562 | 1.3432 | 1.3277 | 1.3097 | 1.2885 | 1.2654 | 1.1974 | 1.1106 | 1.0027 | 0.88753 | 0.76198 | -0.040606 | -0.75813 | -1.2142 | 1.4303 | 1.4245 | 1.3995 | 1.3672 | 1.3284 | 1.2834 | 1.2279 | 1.163 | 1.0813 | 0.99379 | 0.89924 | 0.28967 | -0.24881 | -0.59816 | 1.4601 | 1.4438 | 1.4264 | 1.4014 | 1.3569 | 1.305 | 1.2414 | 1.1666 | 1.072 | 0.9697 | 0.84979 | 0.082519 | -0.60161 | -1.0383
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 0.641 | 3.3821 | 3.2304 | 2.9858 | 2.7009 | 2.3875 | 2.081 | 1.6878 | 1.3983 | 0.85267 | 0.56165 | 0.301 | -0.45615 | -0.95946 | -1.3738 | 4.1573 | 4.0674 | 3.9505 | 3.808 | 3.65 | 3.5092 | 3.3061 | 3.1484 | 2.7435 | 2.5455 | 2.3668 | 1.9671 | 1.7034 | 1.3618 | 3.8199 | 3.6773 | 3.4636 | 3.2116 | 2.9279 | 2.6548 | 2.2943 | 2.0272 | 1.504 | 1.2213 | 0.96744 | 0.27076 | -0.12086 | -0.48268
|  | INVERBERVIE | CT |  |  |  | 0.641 | 3.3821 | 3.2304 | 2.9858 | 2.7009 | 2.3875 | 2.081 | 1.6878 | 1.3983 | 0.9226 | 0.66142 | 0.43398 | -0.40956 | -0.95946 | -1.3738 | 4.1573 | 4.0674 | 3.9505 | 3.808 | 3.65 | 3.5092 | 3.3061 | 3.1484 | 2.8032 | 2.6344 | 2.4697 | 1.9801 | 1.7034 | 1.3618 | 3.8199 | 3.6773 | 3.4636 | 3.2116 | 2.9279 | 2.6548 | 2.2943 | 2.0272 | 1.5846 | 1.3335 | 1.1133 | 0.34292 | -0.12086 | -0.48268
|  | INVERBERVIE | LW |  |  |  | 0.641 | 3.396 | 3.2553 | 3.0093 | 2.7263 | 2.4441 | 2.126 | 1.7498 | 1.4599 | 0.85267 | 0.56165 | 0.301 | -0.45615 | -0.86459 | -1.2508 | 4.1625 | 4.0798 | 3.9696 | 3.8318 | 3.7004 | 3.5444 | 3.3476 | 3.1912 | 2.7435 | 2.5455 | 2.3668 | 1.9671 | 1.8331 | 1.6503 | 3.8323 | 3.7003 | 3.4883 | 3.2379 | 2.9861 | 2.6953 | 2.3465 | 2.0793 | 1.504 | 1.2213 | 0.96744 | 0.27076 | -0.073295 | -0.42069
|  | INVERBERVIE | ST |  |  |  | 0.641 | 3.4359 | 3.3462 | 3.2029 | 3.0495 | 2.9254 | 2.7876 | 2.6388 | 2.5227 | 2.1469 | 1.9649 | 1.7775 | 0.84468 | 0.244 | -0.25098 | 4.1856 | 4.1402 | 4.0706 | 3.989 | 3.928 | 3.8533 | 3.768 | 3.6992 | 3.3969 | 3.2679 | 3.1352 | 2.4723 | 2.1343 | 1.8226 | 3.8699 | 3.7906 | 3.6676 | 3.5331 | 3.4233 | 3.2969 | 3.158 | 3.0479 | 2.6929 | 2.5149 | 2.331 | 1.4499 | 0.91594 | 0.50027
|  | INVERBERVIE | FS |  |  |  | 0.641 | 3.495 | 3.4399 | 3.3549 | 3.2656 | 3.1862 | 3.1185 | 3.037 | 2.9052 | 2.6178 | 2.4918 | 2.3239 | 1.4118 | 0.50192 | -0.12568 | 4.2096 | 4.1786 | 4.129 | 4.0769 | 4.0275 | 3.9878 | 3.9332 | 3.8543 | 3.6345 | 3.5559 | 3.4423 | 2.8014 | 2.1191 | 1.5259 | 3.9193 | 3.8696 | 3.7944 | 3.7177 | 3.6439 | 3.5827 | 3.5055 | 3.384 | 3.1168 | 2.9993 | 2.841 | 1.9843 | 1.1438 | 0.59764
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | YES | 0.008 | 0.049078 | 0.047075 | 0.025493 | 0.012555 | -0.0053821 | -0.026442 | -0.054315 | -0.061931 | -0.078272 | -0.092079 | -0.10421 | -0.12155 | -0.14984 | -0.18457 | 0.19135 | 0.18216 | 0.16364 | 0.15269 | 0.13904 | 0.12203 | 0.098328 | 0.092775 | 0.080029 | 0.069171 | 0.059525 | 0.041541 | 0.0114 | -0.02566 | 0.06724 | 0.055041 | 0.032156 | 0.018157 | -0.00013585 | -0.022093 | -0.0516 | -0.059022 | -0.075186 | -0.088866 | -0.10091 | -0.12113 | -0.15421 | -0.1948
|  | INVERBROOM | CT |  |  |  | 0.008 | 0.049078 | 0.052856 | 0.041797 | 0.019042 | 0.0054729 | -0.008515 | -0.032384 | -0.040606 | -0.050743 | -0.062 | -0.07217 | -0.083848 | -0.095598 | -0.11224 | 0.19135 | 0.19051 | 0.18442 | 0.16594 | 0.15771 | 0.14909 | 0.13137 | 0.12449 | 0.11584 | 0.10604 | 0.096866 | 0.082948 | 0.069969 | 0.049259 | 0.06724 | 0.062802 | 0.052575 | 0.028917 | 0.015949 | 0.0024446 | -0.021648 | -0.029982 | -0.040288 | -0.051772 | -0.062241 | -0.07545 | -0.088033 | -0.1063
|  | INVERBROOM | LW |  |  |  | 0.008 | 0.049605 | 0.047075 | 0.025493 | 0.012555 | -0.0053821 | -0.026442 | -0.054315 | -0.061931 | -0.078272 | -0.092079 | -0.10421 | -0.12155 | -0.14984 | -0.18457 | 0.1915 | 0.18216 | 0.16364 | 0.15269 | 0.13904 | 0.12203 | 0.098328 | 0.092775 | 0.080029 | 0.069171 | 0.059525 | 0.041541 | 0.0114 | -0.02566 | 0.067787 | 0.055041 | 0.032156 | 0.018157 | -0.00013585 | -0.022093 | -0.0516 | -0.059022 | -0.075186 | -0.088866 | -0.10091 | -0.12113 | -0.15421 | -0.1948
|  | INVERBROOM | ST |  |  |  | 0.008 | 0.056019 | 0.047445 | 0.031583 | 0.029898 | 0.030224 | 0.024091 | 0.018646 | 0.0074791 | 0.00037518 | -0.0090474 | -0.021377 | -0.082887 | -0.10103 | -0.12539 | 0.19777 | 0.19038 | 0.17502 | 0.17014 | 0.17082 | 0.16665 | 0.16303 | 0.15458 | 0.14938 | 0.14231 | 0.13323 | 0.076149 | 0.048135 | 0.013453 | 0.074277 | 0.065579 | 0.048575 | 0.038378 | 0.03863 | 0.032653 | 0.027362 | 0.016311 | 0.009307 | -7.6367e-06 | -0.012016 | -0.077535 | -0.10141 | -0.1313
|  | INVERBROOM | FS |  |  |  | 0.008 | 0.058773 | 0.052309 | 0.043855 | 0.047448 | 0.049695 | 0.041951 | 0.037592 | 0.03316 | 0.021652 | 0.015803 | 0.0069422 | -0.028279 | -0.067633 | -0.07972 | 0.19939 | 0.19354 | 0.18495 | 0.18322 | 0.18445 | 0.17763 | 0.17312 | 0.16951 | 0.1598 | 0.15465 | 0.14814 | 0.12142 | 0.089013 | 0.067873 | 0.076652 | 0.07032 | 0.061462 | 0.056232 | 0.058133 | 0.050077 | 0.045189 | 0.040608 | 0.028768 | 0.022568 | 0.013984 | -0.019914 | -0.057587 | -0.069839
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 0.61665 | 0.61072 | 0.58895 | 0.56514 | 0.54323 | 0.51427 | 0.47444 | 0.45361 | 0.44282 | 0.42407 | 0.40755 | 0.37207 | 0.33774 | 0.29639 | 0.94935 | 0.94455 | 0.92751 | 0.90949 | 0.89448 | 0.87315 | 0.8411 | 0.8241 | 0.8172 | 0.8017 | 0.78792 | 0.7595 | 0.72761 | 0.68824 | 0.70173 | 0.6994 | 0.67863 | 0.65434 | 0.63268 | 0.6035 | 0.5628 | 0.54245 | 0.53204 | 0.51361 | 0.49734 | 0.46041 | 0.42217 | 0.37605
|  | INVERGARRY | CT |  |  |  | 0 | 0.61665 | 0.61535 | 0.59915 | 0.57472 | 0.55065 | 0.52871 | 0.49215 | 0.47096 | 0.469 | 0.4543 | 0.4412 | 0.4138 | 0.39611 | 0.3732 | 0.94935 | 0.95222 | 0.94363 | 0.92596 | 0.91095 | 0.89878 | 0.87251 | 0.85392 | 0.85353 | 0.84 | 0.82735 | 0.8039 | 0.79038 | 0.76979 | 0.70173 | 0.7079 | 0.69308 | 0.66835 | 0.64559 | 0.6249 | 0.58898 | 0.5679 | 0.56586 | 0.55103 | 0.53765 | 0.5097 | 0.49204 | 0.46847
|  | INVERGARRY | LW |  |  |  | 0 | 0.61793 | 0.61072 | 0.58895 | 0.56514 | 0.54323 | 0.51427 | 0.47444 | 0.45361 | 0.44282 | 0.42407 | 0.40755 | 0.37207 | 0.33774 | 0.29639 | 0.94983 | 0.94455 | 0.92751 | 0.90949 | 0.89448 | 0.87315 | 0.8411 | 0.8241 | 0.8172 | 0.8017 | 0.78792 | 0.7595 | 0.72761 | 0.68824 | 0.70267 | 0.70121 | 0.67863 | 0.65434 | 0.63268 | 0.6035 | 0.5628 | 0.54245 | 0.53204 | 0.51361 | 0.49734 | 0.46041 | 0.42217 | 0.37605
|  | INVERGARRY | ST |  |  |  | 0 | 0.62923 | 0.6142 | 0.61295 | 0.60098 | 0.59185 | 0.58269 | 0.56882 | 0.5568 | 0.54562 | 0.52878 | 0.51152 | 0.44545 | 0.40578 | 0.37957 | 0.96077 | 0.94845 | 0.94974 | 0.94044 | 0.93439 | 0.92867 | 0.91843 | 0.90943 | 0.90161 | 0.88825 | 0.87478 | 0.81597 | 0.77433 | 0.74144 | 0.7136 | 0.6994 | 0.70457 | 0.69241 | 0.6835 | 0.67478 | 0.66136 | 0.64969 | 0.63885 | 0.62238 | 0.60569 | 0.53647 | 0.4917 | 0.46028
|  | INVERGARRY | FS |  |  |  | 0 | 0.63375 | 0.6223 | 0.61828 | 0.61809 | 0.61289 | 0.60822 | 0.60201 | 0.58988 | 0.57748 | 0.56266 | 0.55608 | 0.49964 | 0.45103 | 0.43109 | 0.96312 | 0.95332 | 0.95057 | 0.95088 | 0.94643 | 0.94252 | 0.93695 | 0.92725 | 0.91705 | 0.9046 | 0.90097 | 0.85983 | 0.82582 | 0.80598 | 0.71767 | 0.7068 | 0.7097 | 0.70929 | 0.70388 | 0.69901 | 0.69239 | 0.68037 | 0.66786 | 0.65295 | 0.64686 | 0.59301 | 0.54755 | 0.52823
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 3.324 | -1.0992 | -1.2966 | -1.5601 | -1.8928 | -2.2511 | -2.7773 | -3.4133 | -4.0913 | -4.7885 | -5.7007 | -6.5007 | -8.632 | -9.1432 | -9.6002 | 4.0334 | 3.9034 | 3.7875 | 3.6297 | 3.4036 | 3.1125 | 2.7358 | 2.2771 | 1.7825 | 1.1312 | 0.49726 | -1.1845 | -1.6639 | -1.8564 | 4.7423 | 4.5533 | 4.3163 | 4.0093 | 3.6693 | 3.2029 | 2.6164 | 1.9814 | 1.3222 | 0.47323 | -0.28199 | -2.2785 | -2.7381 | -3.1643
|  | INVERGORDON | CT |  |  |  | 3.324 | -0.91469 | -1.1495 | -1.4281 | -1.8104 | -2.2511 | -2.7773 | -3.4133 | -4.0913 | -4.7452 | -5.5814 | -6.2907 | -8.2957 | -8.9479 | -9.4818 | 4.2306 | 4.0654 | 3.9057 | 3.6503 | 3.4036 | 3.1125 | 2.7358 | 2.2771 | 1.7844 | 1.161 | 0.59521 | -0.79523 | -1.1597 | -1.6184 | 4.9066 | 4.6819 | 4.427 | 4.0743 | 3.6693 | 3.2029 | 2.6164 | 1.9814 | 1.3709 | 0.59347 | -0.075783 | -1.9427 | -2.5155 | -2.9945
|  | INVERGORDON | LW |  |  |  | 3.324 | -1.0992 | -1.2966 | -1.5601 | -1.8928 | -2.2399 | -2.7159 | -3.2631 | -3.9395 | -4.7885 | -5.7007 | -6.5007 | -8.632 | -9.1432 | -9.6002 | 4.0334 | 3.9034 | 3.7875 | 3.6297 | 3.4492 | 3.1855 | 2.8614 | 2.4043 | 1.7825 | 1.1312 | 0.49726 | -1.1845 | -1.3758 | -1.5082 | 4.7423 | 4.5533 | 4.3163 | 4.0093 | 3.6906 | 3.2586 | 2.7546 | 2.1219 | 1.3222 | 0.47323 | -0.28199 | -2.2785 | -2.7381 | -3.1643
|  | INVERGORDON | ST |  |  |  | 3.324 | -0.84358 | -0.97338 | -1.1034 | -1.2452 | -1.4302 | -1.7054 | -1.9748 | -2.3383 | -2.8422 | -3.5198 | -4.1751 | -6.8658 | -7.7748 | -8.4152 | 4.2703 | 4.188 | 4.1166 | 4.0291 | 3.8924 | 3.6952 | 3.4877 | 3.1537 | 2.6479 | 2.0007 | 1.3438 | -1.08 | -1.6639 | -1.8564 | 4.9747 | 4.8591 | 4.7372 | 4.605 | 4.4354 | 4.1858 | 3.9378 | 3.5936 | 3.1188 | 2.4824 | 1.858 | -0.93441 | -1.8104 | -2.2339
|  | INVERGORDON | FS |  |  |  | 3.324 | -0.57294 | -0.67195 | -0.75984 | -0.87587 | -1.0224 | -1.1844 | -1.3631 | -1.6263 | -2.0013 | -2.4184 | -2.9052 | -5.3705 | -7.1384 | -8.2122 | 4.5032 | 4.4385 | 4.385 | 4.3027 | 4.1952 | 4.0803 | 3.9448 | 3.7473 | 3.4349 | 3.0699 | 2.6315 | 0.42396 | -1.0298 | -1.8065 | 5.2107 | 5.1196 | 5.0391 | 4.932 | 4.7962 | 4.6518 | 4.4854 | 4.2438 | 3.8939 | 3.521 | 3.0619 | 0.7371 | -1.0465 | -2.1487
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 6.265 | -1.277 | -1.497 | -1.9057 | -2.4546 | -3.0476 | -3.7077 | -4.4482 | -4.7709 | -5.0382 | -5.2899 | -5.5651 | -6.2569 | -6.745 | -7.2546 | 1.2925 | 1.1501 | 0.99324 | 0.77775 | 0.59029 | 0.34836 | -0.047316 | -0.29067 | -0.5042 | -0.7648 | -1.0177 | -1.4369 | -1.7942 | -2.4571 | -1.1372 | -1.3758 | -1.7848 | -2.2583 | -2.7566 | -3.317 | -3.9472 | -4.2056 | -4.4186 | -4.6561 | -4.9483 | -5.5718 | -6.0195 | -6.4717
|  | INVERLOCHY | CT |  |  |  | 6.265 | -1.2707 | -1.4938 | -1.9057 | -2.4546 | -3.0476 | -3.7077 | -4.4482 | -4.7709 | -5.0382 | -5.2899 | -5.4837 | -5.9946 | -6.4218 | -6.8482 | 1.3017 | 1.1609 | 0.99324 | 0.77775 | 0.59029 | 0.34836 | -0.047316 | -0.29067 | -0.5042 | -0.72631 | -0.92278 | -1.3264 | -1.6632 | -2.1188 | -1.1372 | -1.3758 | -1.7848 | -2.2583 | -2.7566 | -3.317 | -3.9472 | -4.2056 | -4.4186 | -4.6561 | -4.8637 | -5.3315 | -5.7131 | -6.0914
|  | INVERLOCHY | LW |  |  |  | 6.265 | -1.277 | -1.497 | -1.8457 | -2.3291 | -2.8262 | -3.4465 | -4.1186 | -4.4602 | -4.8693 | -5.2377 | -5.5651 | -6.2569 | -6.745 | -7.2546 | 1.2925 | 1.1501 | 1.0076 | 0.85685 | 0.71125 | 0.4684 | 0.096296 | -0.14544 | -0.46968 | -0.7648 | -1.0177 | -1.4369 | -1.6898 | -1.9925 | -1.1302 | -1.3584 | -1.7247 | -2.1356 | -2.5558 | -3.0784 | -3.6461 | -3.9201 | -4.2718 | -4.6448 | -4.9483 | -5.5718 | -6.0195 | -6.4717
|  | INVERLOCHY | ST |  |  |  | 6.265 | -1.2251 | -1.3897 | -1.5508 | -1.7598 | -2.0399 | -2.3276 | -2.6153 | -2.8814 | -3.1989 | -3.5292 | -3.8342 | -5.2436 | -5.7871 | -5.9474 | 1.3411 | 1.2605 | 1.1645 | 1.0768 | 0.96989 | 0.85122 | 0.72018 | 0.57745 | 0.38222 | 0.16829 | -0.055627 | -1.3338 | -1.7942 | -1.8879 | -1.067 | -1.2176 | -1.4507 | -1.6608 | -1.8935 | -2.1334 | -2.3748 | -2.5933 | -2.8585 | -3.1357 | -3.406 | -5.1474 | -5.7943 | -5.96
|  | INVERLOCHY | FS |  |  |  | 6.265 | -1.1177 | -1.2297 | -1.2928 | -1.3504 | -1.4135 | -1.4908 | -1.5651 | -1.7279 | -1.952 | -2.1926 | -2.4383 | -3.7265 | -5.2363 | -6.0921 | 1.3833 | 1.3254 | 1.27 | 1.214 | 1.151 | 1.0759 | 0.99552 | 0.89512 | 0.77808 | 0.6488 | 0.50955 | -0.39085 | -1.4545 | -2.4571 | -0.97365 | -1.0714 | -1.1538 | -1.2387 | -1.3282 | -1.4357 | -1.55 | -1.7201 | -1.9071 | -2.1123 | -2.3308 | -3.6625 | -5.1674 | -6.2203
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0 | 4.9351 | 4.909 | 4.8702 | 4.8304 | 4.7771 | 4.7358 | 4.6681 | 4.6327 | 4.5976 | 4.5471 | 4.5247 | 4.4379 | 4.4177 | 4.3679 | 5.7302 | 5.7124 | 5.6893 | 5.6665 | 5.6335 | 5.6115 | 5.5695 | 5.5417 | 5.507 | 5.4661 | 5.4498 | 5.3841 | 5.376 | 5.3305 | 5.0868 | 5.0618 | 5.0257 | 4.9888 | 4.9389 | 4.9011 | 4.8374 | 4.8025 | 4.765 | 4.7149 | 4.6926 | 4.6071 | 4.589 | 4.5412
|  | INVERNEIL | CT |  |  |  | 0 | 4.9351 | 4.909 | 4.8702 | 4.8304 | 4.7771 | 4.7358 | 4.6681 | 4.6327 | 4.6005 | 4.5657 | 4.5349 | 4.4869 | 4.4679 | 4.4299 | 5.7302 | 5.7124 | 5.6893 | 5.6665 | 5.6335 | 5.6115 | 5.5695 | 5.5417 | 5.5144 | 5.4836 | 5.455 | 5.4073 | 5.3836 | 5.3305 | 5.0868 | 5.0618 | 5.0257 | 4.9888 | 4.9389 | 4.9011 | 4.8374 | 4.8025 | 4.7704 | 4.7356 | 4.7045 | 4.6562 | 4.6389 | 4.603
|  | INVERNEIL | LW |  |  |  | 0 | 4.938 | 4.9146 | 4.8825 | 4.8467 | 4.8055 | 4.7586 | 4.6932 | 4.6554 | 4.5976 | 4.5471 | 4.5247 | 4.4379 | 4.4177 | 4.3679 | 5.7318 | 5.716 | 5.6974 | 5.6765 | 5.6519 | 5.6248 | 5.5822 | 5.5536 | 5.507 | 5.4661 | 5.4498 | 5.3841 | 5.376 | 5.3423 | 5.0894 | 5.0669 | 5.0371 | 5.0038 | 4.9654 | 4.9214 | 4.8593 | 4.8222 | 4.765 | 4.7149 | 4.6926 | 4.6071 | 4.589 | 4.5412
|  | INVERNEIL | ST |  |  |  | 0 | 4.9379 | 4.9317 | 4.9188 | 4.904 | 4.8868 | 4.8709 | 4.847 | 4.8196 | 4.7991 | 4.7657 | 4.7403 | 4.6192 | 4.598 | 4.6053 | 5.7313 | 5.7289 | 5.7205 | 5.7106 | 5.6986 | 5.6874 | 5.67 | 5.6498 | 5.635 | 5.6098 | 5.5906 | 5.4844 | 5.4495 | 5.4221 | 5.0892 | 5.0839 | 5.0718 | 5.0578 | 5.0415 | 5.0263 | 5.0032 | 4.9766 | 4.957 | 4.9244 | 4.8998 | 4.7797 | 4.7583 | 4.7646
|  | INVERNEIL | FS |  |  |  | 0 | 4.9453 | 4.9395 | 4.9341 | 4.9292 | 4.924 | 4.9158 | 4.9092 | 4.8901 | 4.8662 | 4.8547 | 4.8306 | 4.7073 | 4.6119 | 4.5759 | 5.7348 | 5.7314 | 5.7262 | 5.7212 | 5.7159 | 5.708 | 5.7011 | 5.6863 | 5.6671 | 5.6584 | 5.6393 | 5.5318 | 5.4346 | 5.3473 | 5.0959 | 5.0907 | 5.0853 | 5.0803 | 5.075 | 5.0667 | 5.0601 | 5.0416 | 5.0184 | 5.0075 | 4.984 | 4.8633 | 4.7717 | 4.7368
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 2.939 | 3.4068 | 3.1915 | 2.7783 | 2.2488 | 1.6392 | 1.0153 | 0.19957 | -0.61565 | -1.0918 | -1.8283 | -2.5014 | -4.5419 | -5.5262 | -6.3785 | 5.2617 | 5.1143 | 4.9039 | 4.6211 | 4.3006 | 3.9935 | 3.5549 | 3.0929 | 2.9171 | 2.5006 | 2.1169 | 1.0642 | 0.41063 | -0.38681 | 4.3509 | 4.1467 | 3.772 | 3.2869 | 2.7302 | 2.1664 | 1.4178 | 0.66411 | 0.22983 | -0.45313 | -1.0774 | -2.9315 | -3.7463 | -4.5107
|  | INVERNESS | CT |  |  |  | 2.939 | 3.4082 | 3.1915 | 2.7783 | 2.2488 | 1.6392 | 1.0153 | 0.19957 | -0.61565 | -0.96438 | -1.5481 | -2.0503 | -4.2622 | -5.5262 | -6.3785 | 5.2617 | 5.1143 | 4.9039 | 4.6211 | 4.3006 | 3.9935 | 3.5549 | 3.0929 | 2.9768 | 2.6422 | 2.3421 | 1.1303 | 0.41063 | -0.38681 | 4.3514 | 4.1467 | 3.772 | 3.2869 | 2.7302 | 2.1664 | 1.4178 | 0.66411 | 0.36698 | -0.17203 | -0.63851 | -2.6383 | -3.7463 | -4.5107
|  | INVERNESS | LW |  |  |  | 2.939 | 3.4068 | 3.1922 | 2.7842 | 2.2766 | 1.741 | 1.0824 | 0.29646 | -0.54532 | -1.0918 | -1.8283 | -2.5014 | -4.5419 | -5.2586 | -6.1418 | 5.2657 | 5.1221 | 4.9246 | 4.6645 | 4.4002 | 4.0538 | 3.6212 | 3.1605 | 2.9171 | 2.5006 | 2.1169 | 1.0642 | 0.7545 | 0.27986 | 4.3509 | 4.1467 | 3.7769 | 3.3128 | 2.826 | 2.2215 | 1.4944 | 0.7178 | 0.22983 | -0.45313 | -1.0774 | -2.9315 | -3.5636 | -4.3727
|  | INVERNESS | ST |  |  |  | 2.939 | 3.512 | 3.4134 | 3.317 | 3.1963 | 3.0581 | 2.9273 | 2.7487 | 2.5419 | 2.3265 | 2.0592 | 1.7682 | 0.1877 | -1.0935 | -2.2939 | 5.3216 | 5.2569 | 5.1884 | 5.1001 | 4.9977 | 4.9015 | 4.7658 | 4.6063 | 4.4385 | 4.2275 | 3.9952 | 2.9161 | 2.0773 | 1.2044 | 4.4482 | 4.3575 | 4.2664 | 4.1515 | 4.0199 | 3.8963 | 3.725 | 3.5258 | 3.3179 | 3.0584 | 2.7751 | 1.3251 | 0.15072 | -0.90591
|  | INVERNESS | FS |  |  |  | 2.939 | 3.5319 | 3.4499 | 3.3425 | 3.243 | 3.124 | 2.9863 | 2.8622 | 2.6351 | 2.3728 | 2.1472 | 1.8747 | 0.34647 | -1.5389 | -3.1841 | 5.3317 | 5.2764 | 5.2035 | 5.1359 | 5.0517 | 4.9513 | 4.8567 | 4.7032 | 4.5185 | 4.3629 | 4.1685 | 3.1276 | 1.6606 | 0.063434 | 4.4659 | 4.3907 | 4.2905 | 4.1983 | 4.0871 | 3.9573 | 3.841 | 3.6302 | 3.384 | 3.1744 | 2.9184 | 1.5109 | -0.21433 | -1.6878
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 2.227 | 10.6965 | 9.9102 | 8.658 | 7.0943 | 5.2842 | 3.6227 | 1.2785 | -0.89214 | -2.7262 | -4.6677 | -6.4774 | -11.2145 | -12.6606 | -13.9594 | 16.0131 | 15.5226 | 14.8372 | 13.9656 | 12.986 | 12.1759 | 10.7416 | 9.3601 | 8.2203 | 7.1127 | 6.0019 | 2.4908 | 0.56871 | 0.14298 | 14.0453 | 13.3365 | 12.2245 | 10.8227 | 9.2118 | 7.7828 | 5.6459 | 3.6527 | 1.9972 | 0.20054 | -1.4715 | -5.7973 | -6.9815 | -8.1392
|  | INVERURIE | CT |  |  |  | 2.227 | 10.7311 | 9.9148 | 8.658 | 7.0943 | 5.2842 | 3.6227 | 1.2785 | -0.89214 | -2.6997 | -4.375 | -5.8657 | -10.8173 | -12.6606 | -13.9594 | 16.0255 | 15.5226 | 14.8372 | 13.9656 | 12.986 | 12.1759 | 10.7416 | 9.3601 | 8.2203 | 7.1617 | 6.2138 | 3.3332 | 2.2307 | 1.0049 | 14.0669 | 13.3365 | 12.2245 | 10.8227 | 9.2118 | 7.7828 | 5.6459 | 3.6527 | 2.0025 | 0.46336 | -0.90447 | -5.3681 | -6.9815 | -8.1392
|  | INVERURIE | LW |  |  |  | 2.227 | 10.6965 | 9.9102 | 8.7416 | 7.3019 | 5.678 | 4.0033 | 1.7384 | -0.46724 | -2.7262 | -4.6677 | -6.4774 | -11.2145 | -12.2016 | -13.4688 | 16.0131 | 15.544 | 14.9488 | 14.1969 | 13.3659 | 12.5333 | 11.1166 | 9.7314 | 8.2979 | 7.1127 | 6.0019 | 3.2278 | 2.7752 | 2.034 | 14.0453 | 13.3523 | 12.3353 | 11.0648 | 9.6413 | 8.187 | 6.1157 | 4.0902 | 1.9972 | 0.20054 | -1.4715 | -5.7973 | -6.6695 | -7.8201
|  | INVERURIE | ST |  |  |  | 2.227 | 10.9614 | 10.4994 | 9.9467 | 9.3244 | 8.606 | 7.7254 | 6.6454 | 5.4933 | 4.579 | 3.2922 | 1.5171 | -6.6855 | -9.2042 | -10.0405 | 16.1559 | 15.8875 | 15.5662 | 15.189 | 14.7506 | 14.2051 | 13.3818 | 12.4945 | 11.6129 | 10.2937 | 8.8818 | 2.4908 | 0.56871 | 0.14298 | 14.2812 | 13.8911 | 13.4222 | 12.8824 | 12.2673 | 11.506 | 10.5144 | 9.446 | 8.5205 | 7.0448 | 5.3357 | -2.5693 | -4.9899 | -5.5506
|  | INVERURIE | FS |  |  |  | 2.227 | 11.1208 | 10.7755 | 10.3593 | 9.934 | 9.3918 | 8.8426 | 8.1051 | 7.2079 | 6.1994 | 5.5586 | 4.5507 | -0.99097 | -5.848 | -9.022 | 16.2396 | 16.0327 | 15.7787 | 15.5189 | 15.1808 | 14.8325 | 14.2685 | 13.6226 | 12.8981 | 12.4525 | 11.7368 | 7.3213 | 3.4745 | 1.2226 | 14.4142 | 14.1256 | 13.7712 | 13.4088 | 12.9474 | 12.4805 | 11.8136 | 10.9999 | 10.0814 | 9.5277 | 8.6138 | 3.3883 | -1.4619 | -4.502
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0.065 | 2.4885 | 2.4778 | 2.4485 | 2.4156 | 2.3815 | 2.3362 | 2.2861 | 2.2545 | 2.228 | 2.1971 | 2.169 | 2.0857 | 2.0387 | 1.9738 | 2.3464 | 2.3398 | 2.3194 | 2.2972 | 2.2758 | 2.2449 | 2.2096 | 2.1862 | 2.1673 | 2.1435 | 2.1217 | 2.0589 | 2.0218 | 1.9663 | 2.3514 | 2.3349 | 2.307 | 2.276 | 2.2442 | 2.2009 | 2.1536 | 2.1215 | 2.0991 | 2.0682 | 2.0401 | 1.9613 | 1.9159 | 1.8518
|  | KALNAKIL | CT |  |  |  | 0.065 | 2.4885 | 2.4806 | 2.4578 | 2.4244 | 2.3907 | 2.3526 | 2.3082 | 2.2768 | 2.2529 | 2.2402 | 2.2199 | 2.1502 | 2.1191 | 2.078 | 2.3464 | 2.347 | 2.3352 | 2.3129 | 2.2936 | 2.2714 | 2.2436 | 2.2195 | 2.2008 | 2.1915 | 2.1741 | 2.1203 | 2.0988 | 2.0639 | 2.3514 | 2.3403 | 2.3207 | 2.2899 | 2.2597 | 2.2248 | 2.1846 | 2.152 | 2.1272 | 2.1187 | 2.0971 | 2.0301 | 2.0043 | 1.9681
|  | KALNAKIL | LW |  |  |  | 0.065 | 2.491 | 2.4778 | 2.4485 | 2.4156 | 2.3815 | 2.3362 | 2.2861 | 2.2545 | 2.228 | 2.1971 | 2.169 | 2.0857 | 2.0387 | 1.9738 | 2.3473 | 2.3398 | 2.3194 | 2.2972 | 2.2758 | 2.2449 | 2.2096 | 2.1862 | 2.1673 | 2.1435 | 2.1217 | 2.0589 | 2.0218 | 1.9663 | 2.3533 | 2.3349 | 2.307 | 2.276 | 2.2442 | 2.2009 | 2.1536 | 2.1215 | 2.0991 | 2.0682 | 2.0401 | 1.9613 | 1.9159 | 1.8518
|  | KALNAKIL | ST |  |  |  | 0.065 | 2.5023 | 2.4838 | 2.4762 | 2.458 | 2.4381 | 2.422 | 2.4044 | 2.3858 | 2.3617 | 2.3428 | 2.3183 | 2.2067 | 2.1511 | 2.1179 | 2.358 | 2.345 | 2.3441 | 2.3325 | 2.3198 | 2.3109 | 2.3008 | 2.2887 | 2.2717 | 2.2593 | 2.2422 | 2.1504 | 2.0981 | 2.0593 | 2.3643 | 2.3478 | 2.337 | 2.3202 | 2.301 | 2.2874 | 2.2724 | 2.2552 | 2.231 | 2.2143 | 2.19 | 2.08 | 2.024 | 1.9891
|  | KALNAKIL | FS |  |  |  | 0.065 | 2.5099 | 2.4964 | 2.493 | 2.49 | 2.4828 | 2.4758 | 2.4637 | 2.4505 | 2.4328 | 2.4133 | 2.4004 | 2.3138 | 2.2234 | 2.1854 | 2.3612 | 2.3511 | 2.3502 | 2.3482 | 2.3424 | 2.3366 | 2.3261 | 2.3175 | 2.3047 | 2.2901 | 2.2823 | 2.2222 | 2.1592 | 2.1213 | 2.3702 | 2.358 | 2.3481 | 2.3468 | 2.3399 | 2.3334 | 2.3202 | 2.3087 | 2.2917 | 2.272 | 2.2615 | 2.1821 | 2.0995 | 2.068
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0 | 2.3119 | 2.2652 | 2.2051 | 2.1282 | 2.0543 | 1.965 | 1.8627 | 1.7856 | 1.7512 | 1.6718 | 1.5979 | 1.437 | 1.3981 | 1.2997 | 2.4205 | 2.3896 | 2.3548 | 2.3088 | 2.2669 | 2.2146 | 2.1535 | 2.0949 | 2.0644 | 2.0022 | 1.9452 | 1.8264 | 1.8064 | 1.7392 | 2.3785 | 2.3339 | 2.2782 | 2.2065 | 2.1383 | 2.0552 | 1.9597 | 1.8837 | 1.8485 | 1.7676 | 1.6944 | 1.5368 | 1.5018 | 1.407
|  | KAMES | CT |  |  |  | 0 | 2.3119 | 2.2652 | 2.2051 | 2.1282 | 2.0543 | 1.965 | 1.8627 | 1.7856 | 1.7512 | 1.6939 | 1.6432 | 1.5072 | 1.4682 | 1.3939 | 2.4205 | 2.3896 | 2.3548 | 2.3088 | 2.2669 | 2.2146 | 2.1535 | 2.0949 | 2.0674 | 2.0213 | 1.9789 | 1.8636 | 1.8246 | 1.7447 | 2.3785 | 2.3339 | 2.2782 | 2.2065 | 2.1383 | 2.0552 | 1.9597 | 1.8837 | 1.8497 | 1.7926 | 1.7416 | 1.6069 | 1.5713 | 1.5008
|  | KAMES | LW |  |  |  | 0 | 2.3179 | 2.2766 | 2.2266 | 2.1582 | 2.1015 | 2.0058 | 1.9074 | 1.828 | 1.7536 | 1.6718 | 1.5979 | 1.437 | 1.3981 | 1.2997 | 2.424 | 2.3969 | 2.3691 | 2.3285 | 2.2984 | 2.2392 | 2.1787 | 2.1203 | 2.0644 | 2.0022 | 1.9452 | 1.8264 | 1.8064 | 1.7392 | 2.384 | 2.3445 | 2.2984 | 2.2345 | 2.1825 | 2.0922 | 1.9996 | 1.9216 | 1.8485 | 1.7676 | 1.6944 | 1.5368 | 1.5018 | 1.407
|  | KAMES | ST |  |  |  | 0 | 2.3254 | 2.3052 | 2.2812 | 2.2526 | 2.2254 | 2.1891 | 2.1475 | 2.1167 | 2.0629 | 2.0187 | 1.9595 | 1.7398 | 1.6987 | 1.7043 | 2.4295 | 2.418 | 2.4033 | 2.3849 | 2.3673 | 2.3427 | 2.3138 | 2.2931 | 2.2545 | 2.2227 | 2.1795 | 1.9996 | 1.9487 | 1.9167 | 2.3914 | 2.3728 | 2.3504 | 2.3236 | 2.2981 | 2.2634 | 2.2234 | 2.1942 | 2.1421 | 2.0994 | 2.0419 | 1.8252 | 1.7847 | 1.7889
|  | KAMES | FS |  |  |  | 0 | 2.3381 | 2.3211 | 2.3117 | 2.3005 | 2.2866 | 2.2741 | 2.2532 | 2.22 | 2.1934 | 2.1546 | 2.1126 | 1.9094 | 1.7047 | 1.6242 | 2.4353 | 2.4244 | 2.4165 | 2.4072 | 2.3957 | 2.3849 | 2.3674 | 2.3435 | 2.3246 | 2.2962 | 2.265 | 2.1052 | 1.9309 | 1.8072 | 2.4027 | 2.3867 | 2.3776 | 2.3665 | 2.3529 | 2.3406 | 2.3199 | 2.288 | 2.2628 | 2.2255 | 2.1849 | 1.988 | 1.7918 | 1.7145
| KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 2.213 | 4.3529 | 4.1759 | 3.6717 | 3.2631 | 2.6582 | 2.1731 | 1.4954 | 0.9399 | 0.36532 | -0.14924 | -0.61438 | -1.6147 | -2.4005 | -3.0705 | 5.7826 | 5.6734 | 5.3475 | 5.177 | 4.7676 | 4.575 | 4.1754 | 3.9291 | 3.6469 | 3.3906 | 3.155 | 2.7083 | 2.442 | 1.8557 | 4.1879 | 4.0747 | 3.7621 | 3.41 | 2.8563 | 2.4119 | 1.786 | 1.2704 | 0.72413 | 0.23508 | -0.21184 | -1.0695 | -1.6708 | -2.2682
|  | KEITH | CT |  |  |  | 2.213 | 4.3529 | 4.1781 | 3.7178 | 3.2939 | 2.6582 | 2.1896 | 1.5376 | 0.95811 | 0.47893 | 0.036251 | -0.34969 | -1.5085 | -2.4005 | -3.0705 | 5.7868 | 5.6883 | 5.3936 | 5.177 | 4.7676 | 4.575 | 4.211 | 3.9496 | 3.7443 | 3.5462 | 3.3775 | 2.956 | 2.442 | 1.8557 | 4.1928 | 4.088 | 3.7939 | 3.4353 | 2.8563 | 2.4324 | 1.8368 | 1.2983 | 0.85632 | 0.43831 | 0.071061 | -0.91214 | -1.6708 | -2.2682
|  | KEITH | LW |  |  |  | 2.213 | 4.3541 | 4.1759 | 3.6717 | 3.2631 | 2.666 | 2.1731 | 1.4954 | 0.9399 | 0.36532 | -0.14924 | -0.61438 | -1.6147 | -2.1994 | -2.6871 | 5.7826 | 5.6734 | 5.3475 | 5.1815 | 4.8047 | 4.5846 | 4.1754 | 3.9291 | 3.6469 | 3.3906 | 3.155 | 2.7083 | 2.5109 | 2.3597 | 4.1879 | 4.0747 | 3.7621 | 3.41 | 2.8702 | 2.4119 | 1.786 | 1.2704 | 0.72413 | 0.23508 | -0.21184 | -1.0695 | -1.5797 | -2.0464
|  | KEITH | ST |  |  |  | 2.213 | 4.4053 | 4.2948 | 4.0322 | 3.8879 | 3.5217 | 3.3729 | 3.1215 | 2.9488 | 2.7493 | 2.5773 | 2.3694 | 1.2087 | 0.18053 | -0.73345 | 5.8135 | 5.7642 | 5.5356 | 5.4458 | 5.1195 | 5.0207 | 4.7968 | 4.6632 | 4.4998 | 4.3411 | 4.1613 | 3.2476 | 2.7981 | 2.5366 | 4.2215 | 4.1739 | 3.9707 | 3.8824 | 3.5643 | 3.4501 | 3.1961 | 3.0241 | 2.8141 | 2.6093 | 2.3759 | 1.124 | 0.40942 | -0.26851
|  | KEITH | FS |  |  |  | 2.213 | 4.4715 | 4.3983 | 4.214 | 4.1047 | 3.8241 | 3.7048 | 3.4922 | 3.3108 | 3.1274 | 2.9277 | 2.721 | 1.4742 | 0.52187 | -0.48958 | 5.8353 | 5.8021 | 5.6424 | 5.5824 | 5.3285 | 5.2476 | 5.0692 | 4.9639 | 4.8395 | 4.711 | 4.5775 | 3.7459 | 3.1349 | 2.2709 | 4.2396 | 4.2065 | 4.0651 | 4.006 | 3.7573 | 3.6758 | 3.4992 | 3.3834 | 3.2188 | 3.0439 | 2.8385 | 1.6341 | 0.79448 | -0.0492
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0.262 | 10.4385 | 10.3148 | 10.0956 | 9.8285 | 9.5101 | 9.192 | 8.7333 | 8.2858 | 7.8085 | 7.4812 | 7.1871 | 6.3917 | 5.7974 | 5.3801 | 11.1536 | 11.0763 | 10.9715 | 10.8406 | 10.681 | 10.5352 | 10.2764 | 10.0077 | 9.6962 | 9.5151 | 9.3517 | 8.8877 | 8.5487 | 8.1722 | 10.917 | 10.8074 | 10.6115 | 10.3724 | 10.0871 | 9.8049 | 9.3876 | 8.9783 | 8.5422 | 8.248 | 7.9839 | 7.2625 | 6.7202 | 6.3453
|  | KEMNAY | CT |  |  |  | 0.262 | 10.4385 | 10.3148 | 10.0956 | 9.8285 | 9.5101 | 9.192 | 8.7333 | 8.2858 | 7.863 | 7.5635 | 7.3101 | 6.3917 | 5.7974 | 5.3801 | 11.1536 | 11.0763 | 10.9715 | 10.8406 | 10.681 | 10.5352 | 10.2764 | 10.0077 | 9.7339 | 9.5556 | 9.4007 | 8.8877 | 8.5487 | 8.1722 | 10.917 | 10.8074 | 10.6115 | 10.3724 | 10.0871 | 9.8049 | 9.3876 | 8.9783 | 8.5904 | 8.3205 | 8.0931 | 7.2625 | 6.7202 | 6.3453
|  | KEMNAY | LW |  |  |  | 0.262 | 10.4477 | 10.3316 | 10.1172 | 9.85 | 9.5641 | 9.2375 | 8.7873 | 8.3186 | 7.8085 | 7.4812 | 7.1871 | 6.4125 | 6.0359 | 5.6788 | 11.1594 | 11.0891 | 10.9925 | 10.864 | 10.7295 | 10.5716 | 10.3081 | 10.0296 | 9.6962 | 9.5151 | 9.3517 | 8.973 | 8.8268 | 8.6583 | 10.9254 | 10.823 | 10.6317 | 10.3938 | 10.138 | 9.8492 | 9.4382 | 9.0087 | 8.5422 | 8.248 | 7.9839 | 7.283 | 6.9422 | 6.6258
|  | KEMNAY | ST |  |  |  | 0.262 | 10.4793 | 10.4118 | 10.323 | 10.2197 | 10.129 | 10.0178 | 9.8413 | 9.643 | 9.3878 | 9.2332 | 9.0787 | 8.1552 | 7.47 | 6.914 | 11.1766 | 11.1395 | 11.0912 | 11.031 | 10.9804 | 10.9137 | 10.7834 | 10.6305 | 10.4246 | 10.3094 | 10.1945 | 9.5974 | 9.1932 | 8.7809 | 10.9534 | 10.8942 | 10.8174 | 10.7277 | 10.6495 | 10.5538 | 10.392 | 10.2139 | 9.9793 | 9.841 | 9.7035 | 8.8707 | 8.2476 | 7.7433
|  | KEMNAY | FS |  |  |  | 0.262 | 10.5116 | 10.4642 | 10.3985 | 10.3359 | 10.2628 | 10.2029 | 10.0864 | 9.9045 | 9.6921 | 9.5694 | 9.4115 | 8.5414 | 7.6957 | 7.0316 | 11.1898 | 11.1613 | 11.1205 | 11.0817 | 11.034 | 10.996 | 10.9041 | 10.7725 | 10.6108 | 10.5275 | 10.4144 | 9.7895 | 9.1135 | 8.4099 | 10.9827 | 10.9416 | 10.8851 | 10.8315 | 10.7686 | 10.7176 | 10.6116 | 10.4477 | 10.2532 | 10.1457 | 10.0041 | 9.2168 | 8.4516 | 7.8459
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 0.40823 | 0.39555 | 0.39023 | 0.3795 | 0.3681 | 0.35244 | 0.33726 | 0.32646 | 0.32303 | 0.3127 | 0.30181 | 0.28014 | 0.27414 | 0.26431 | 0.40644 | 0.40213 | 0.39773 | 0.39342 | 0.38698 | 0.37779 | 0.36902 | 0.36125 | 0.35849 | 0.35092 | 0.34311 | 0.32793 | 0.32187 | 0.30881 | 0.35888 | 0.34666 | 0.34211 | 0.33227 | 0.32185 | 0.30723 | 0.2932 | 0.28259 | 0.27925 | 0.26859 | 0.25784 | 0.23684 | 0.2315 | 0.22224
|  | KENMORE | CT |  |  |  | 0 | 0.40823 | 0.39555 | 0.39023 | 0.3795 | 0.3681 | 0.35244 | 0.33726 | 0.32646 | 0.32303 | 0.31351 | 0.30487 | 0.2833 | 0.27771 | 0.26973 | 0.40644 | 0.40213 | 0.39955 | 0.39342 | 0.38698 | 0.37779 | 0.36902 | 0.36125 | 0.35849 | 0.35149 | 0.34497 | 0.32793 | 0.32187 | 0.31145 | 0.35888 | 0.34666 | 0.34211 | 0.33227 | 0.32185 | 0.30723 | 0.2932 | 0.28259 | 0.27925 | 0.26979 | 0.26113 | 0.23997 | 0.23497 | 0.22756
|  | KENMORE | LW |  |  |  | 0 | 0.40944 | 0.39824 | 0.39446 | 0.38421 | 0.37157 | 0.35898 | 0.34479 | 0.33428 | 0.32498 | 0.3127 | 0.30181 | 0.28014 | 0.27414 | 0.26431 | 0.40724 | 0.4038 | 0.40229 | 0.39653 | 0.38925 | 0.38192 | 0.37365 | 0.3663 | 0.35963 | 0.35092 | 0.34311 | 0.32804 | 0.32503 | 0.31901 | 0.35999 | 0.34919 | 0.3461 | 0.33664 | 0.32487 | 0.31321 | 0.30002 | 0.28977 | 0.28068 | 0.26859 | 0.25784 | 0.23684 | 0.2315 | 0.22224
|  | KENMORE | ST |  |  |  | 0 | 0.41461 | 0.40684 | 0.39694 | 0.39177 | 0.3913 | 0.38216 | 0.37638 | 0.37167 | 0.36489 | 0.35415 | 0.34533 | 0.30381 | 0.29295 | 0.29106 | 0.41228 | 0.40588 | 0.39773 | 0.4005 | 0.4006 | 0.39481 | 0.39125 | 0.38818 | 0.38369 | 0.37645 | 0.37032 | 0.33957 | 0.32915 | 0.32224 | 0.36515 | 0.35769 | 0.34821 | 0.34351 | 0.34344 | 0.33473 | 0.32936 | 0.32499 | 0.31856 | 0.30818 | 0.29973 | 0.25939 | 0.2491 | 0.24743
|  | KENMORE | FS |  |  |  | 0 | 0.41728 | 0.41148 | 0.40566 | 0.39839 | 0.39798 | 0.40136 | 0.39578 | 0.39205 | 0.38821 | 0.38016 | 0.37613 | 0.33866 | 0.30052 | 0.29016 | 0.41381 | 0.40879 | 0.40324 | 0.39625 | 0.40275 | 0.40482 | 0.40078 | 0.39827 | 0.39555 | 0.39 | 0.38716 | 0.35936 | 0.32813 | 0.30881 | 0.36757 | 0.36196 | 0.35622 | 0.34903 | 0.34878 | 0.35222 | 0.34673 | 0.34328 | 0.33973 | 0.33197 | 0.32822 | 0.29217 | 0.25577 | 0.24604
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 0.22 | 2.7776 | 2.7406 | 2.6311 | 2.4351 | 2.17 | 1.8776 | 1.5633 | 1.2908 | 0.98201 | 0.73794 | 0.48205 | -0.36599 | -0.89401 | -1.4346 | 4.3323 | 4.267 | 4.1701 | 4.0796 | 3.954 | 3.8185 | 3.6766 | 3.5097 | 3.3164 | 3.1839 | 3.0272 | 2.6231 | 2.3702 | 2.0174 | 4.1711 | 4.0724 | 3.9033 | 3.7376 | 3.5171 | 3.2743 | 3.019 | 2.7598 | 2.4554 | 2.2471 | 2.007 | 1.3211 | 0.94682 | 0.53405
|  | KEPCULLOCH | CT |  |  |  | 0.22 | 2.7811 | 2.7446 | 2.6311 | 2.4351 | 2.17 | 1.8776 | 1.5633 | 1.2908 | 1.0561 | 0.82981 | 0.66755 | -0.21954 | -0.85045 | -1.3736 | 4.3323 | 4.267 | 4.1701 | 4.0796 | 3.954 | 3.8185 | 3.6766 | 3.5097 | 3.3726 | 3.2273 | 3.1382 | 2.6816 | 2.3702 | 2.0174 | 4.1711 | 4.0724 | 3.9033 | 3.7376 | 3.5171 | 3.2743 | 3.019 | 2.7598 | 2.5441 | 2.3248 | 2.1902 | 1.4611 | 1.0133 | 0.62627
|  | KEPCULLOCH | LW |  |  |  | 0.22 | 2.7776 | 2.7406 | 2.6482 | 2.453 | 2.2108 | 1.9005 | 1.5896 | 1.2997 | 0.98201 | 0.73794 | 0.48205 | -0.36599 | -0.89401 | -1.4346 | 4.3341 | 4.2735 | 4.1853 | 4.094 | 3.9902 | 3.8314 | 3.6857 | 3.5173 | 3.3164 | 3.1839 | 3.0272 | 2.6231 | 2.424 | 2.1674 | 4.1742 | 4.0809 | 3.9208 | 3.7517 | 3.5599 | 3.2885 | 3.0319 | 2.7631 | 2.4554 | 2.2471 | 2.007 | 1.3211 | 0.94682 | 0.53405
|  | KEPCULLOCH | ST |  |  |  | 0.22 | 2.7901 | 2.7702 | 2.7489 | 2.7203 | 2.6251 | 2.5297 | 2.411 | 2.293 | 2.1409 | 2.0253 | 1.8656 | 1.055 | 0.56847 | 0.15472 | 4.356 | 4.3193 | 4.28 | 4.2315 | 4.1692 | 4.1164 | 4.0423 | 3.9657 | 3.8623 | 3.7875 | 3.6769 | 3.1365 | 2.8476 | 2.5811 | 4.2076 | 4.1476 | 4.0836 | 4.006 | 3.9101 | 3.8284 | 3.7187 | 3.6101 | 3.4649 | 3.3597 | 3.2069 | 2.4742 | 2.0802 | 1.7717
|  | KEPCULLOCH | FS |  |  |  | 0.22 | 2.7938 | 2.7776 | 2.7606 | 2.7352 | 2.7088 | 2.6754 | 2.6348 | 2.5286 | 2.4113 | 2.2875 | 2.1562 | 1.4177 | 0.70306 | 0.14767 | 4.3671 | 4.3388 | 4.3116 | 4.2699 | 4.233 | 4.1824 | 4.1443 | 4.0768 | 4.0005 | 3.9184 | 3.8299 | 3.3311 | 2.8264 | 2.3546 | 4.2317 | 4.1884 | 4.1496 | 4.0904 | 4.038 | 3.9677 | 3.9175 | 3.8198 | 3.713 | 3.5974 | 3.4741 | 2.79 | 2.1632 | 1.7502
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.28585 | 0.28037 | 0.27411 | 0.26609 | 0.25618 | 0.24634 | 0.24511 | 0.24667 | 0.24031 | 0.23635 | 0.22876 | 0.21551 | 0.21088 | 0.20936 | 0.27532 | 0.27047 | 0.26557 | 0.26014 | 0.25322 | 0.24639 | 0.25043 | 0.25108 | 0.24544 | 0.24353 | 0.23901 | 0.23305 | 0.22938 | 0.22513 | 0.26195 | 0.25659 | 0.25062 | 0.24398 | 0.2357 | 0.22745 | 0.22316 | 0.22476 | 0.21825 | 0.21499 | 0.20897 | 0.20004 | 0.19562 | 0.19428
|  | KERRERA | CT |  |  |  | 0 | 0.28585 | 0.28037 | 0.27411 | 0.26609 | 0.25618 | 0.24634 | 0.24511 | 0.24667 | 0.24171 | 0.24015 | 0.23554 | 0.22927 | 0.2267 | 0.22224 | 0.27532 | 0.27047 | 0.26557 | 0.26014 | 0.25322 | 0.24639 | 0.25043 | 0.25108 | 0.24739 | 0.24595 | 0.24241 | 0.23653 | 0.2335 | 0.22775 | 0.26195 | 0.25659 | 0.25062 | 0.24398 | 0.2357 | 0.22745 | 0.22316 | 0.22476 | 0.21983 | 0.21828 | 0.21366 | 0.20753 | 0.20521 | 0.20101
|  | KERRERA | LW |  |  |  | 0 | 0.28617 | 0.28116 | 0.27593 | 0.26893 | 0.26148 | 0.24943 | 0.24769 | 0.24879 | 0.24031 | 0.23635 | 0.22876 | 0.21551 | 0.21364 | 0.21159 | 0.27553 | 0.27111 | 0.2671 | 0.26173 | 0.25693 | 0.24836 | 0.25189 | 0.25231 | 0.24617 | 0.24353 | 0.23901 | 0.23305 | 0.23234 | 0.22864 | 0.26224 | 0.25734 | 0.25236 | 0.24589 | 0.23989 | 0.22988 | 0.22545 | 0.22663 | 0.21825 | 0.21499 | 0.20897 | 0.20004 | 0.1984 | 0.19439
|  | KERRERA | ST |  |  |  | 0 | 0.28754 | 0.28527 | 0.28238 | 0.27891 | 0.27507 | 0.26987 | 0.26334 | 0.25575 | 0.24581 | 0.25089 | 0.25327 | 0.221 | 0.21088 | 0.20936 | 0.2768 | 0.27498 | 0.27266 | 0.26978 | 0.26655 | 0.26268 | 0.25811 | 0.25267 | 0.24544 | 0.25258 | 0.25438 | 0.23662 | 0.22938 | 0.22872 | 0.2636 | 0.26144 | 0.25868 | 0.25534 | 0.25164 | 0.24728 | 0.24219 | 0.23629 | 0.22796 | 0.22819 | 0.23137 | 0.20521 | 0.19562 | 0.19428
|  | KERRERA | FS |  |  |  | 0 | 0.28835 | 0.28668 | 0.28502 | 0.28297 | 0.28074 | 0.27812 | 0.275 | 0.27023 | 0.26373 | 0.25703 | 0.24962 | 0.24502 | 0.22283 | 0.21032 | 0.27725 | 0.27583 | 0.27427 | 0.27233 | 0.27022 | 0.26771 | 0.2647 | 0.26086 | 0.25591 | 0.25078 | 0.24511 | 0.24779 | 0.23554 | 0.22513 | 0.26434 | 0.26273 | 0.2611 | 0.25907 | 0.25688 | 0.25429 | 0.25121 | 0.24712 | 0.24189 | 0.23624 | 0.22901 | 0.22583 | 0.20693 | 0.19505
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | YES | 0.157 | 0.7061 | 0.65603 | 0.57513 | 0.4714 | 0.36903 | 0.25506 | 0.12937 | 0.082206 | 0.042267 | -0.046036 | -0.08469 | -0.28826 | -0.38328 | -0.52165 | 0.94812 | 0.91009 | 0.862 | 0.79936 | 0.73832 | 0.66516 | 0.58325 | 0.52069 | 0.45011 | 0.38387 | 0.35111 | 0.20915 | 0.14599 | 0.04714 | 0.73205 | 0.67046 | 0.59448 | 0.48018 | 0.36739 | 0.23869 | 0.097878 | 0.021455 | -0.06377 | -0.15103 | -0.19526 | -0.39504 | -0.49857 | -0.6402
|  | KERRY FALLS | CT |  |  |  | 0.157 | 0.7061 | 0.65603 | 0.57513 | 0.4714 | 0.36903 | 0.25506 | 0.12937 | 0.082206 | 0.047493 | -0.0010094 | -0.061479 | -0.19116 | -0.26878 | -0.37106 | 0.94812 | 0.9104 | 0.86583 | 0.79936 | 0.73832 | 0.66739 | 0.58931 | 0.53361 | 0.48656 | 0.43529 | 0.38835 | 0.27454 | 0.20691 | 0.10088 | 0.73205 | 0.67046 | 0.59448 | 0.48018 | 0.36739 | 0.23869 | 0.097878 | 0.021455 | -0.03824 | -0.1003 | -0.15397 | -0.29166 | -0.37364 | -0.47795
|  | KERRY FALLS | LW |  |  |  | 0.157 | 0.7149 | 0.66291 | 0.583 | 0.48964 | 0.39835 | 0.28156 | 0.1584 | 0.10198 | 0.042267 | -0.046036 | -0.08469 | -0.28826 | -0.38328 | -0.52165 | 0.9528 | 0.91009 | 0.862 | 0.79983 | 0.74753 | 0.66516 | 0.58325 | 0.52069 | 0.45011 | 0.38387 | 0.35111 | 0.20915 | 0.14599 | 0.04714 | 0.73941 | 0.67478 | 0.59991 | 0.49453 | 0.39787 | 0.25803 | 0.11744 | 0.030643 | -0.06377 | -0.15103 | -0.19526 | -0.39504 | -0.49857 | -0.6402
|  | KERRY FALLS | ST |  |  |  | 0.157 | 0.72321 | 0.68973 | 0.6392 | 0.58984 | 0.54251 | 0.48994 | 0.43849 | 0.38799 | 0.33048 | 0.27954 | 0.21929 | -0.03801 | -0.162 | -0.22871 | 0.96074 | 0.93997 | 0.9072 | 0.87691 | 0.85013 | 0.81536 | 0.78351 | 0.74549 | 0.69908 | 0.66388 | 0.61166 | 0.37733 | 0.26482 | 0.17859 | 0.75301 | 0.71858 | 0.66892 | 0.61929 | 0.5715 | 0.51193 | 0.45629 | 0.39483 | 0.32175 | 0.26641 | 0.19085 | -0.11517 | -0.24237 | -0.30431
|  | KERRY FALLS | FS |  |  |  | 0.157 | 0.7446 | 0.72497 | 0.70862 | 0.69224 | 0.6731 | 0.65672 | 0.63422 | 0.59385 | 0.55333 | 0.50829 | 0.46374 | 0.23264 | -0.0040661 | -0.12049 | 0.96899 | 0.95709 | 0.94286 | 0.92933 | 0.91135 | 0.8986 | 0.87592 | 0.8441 | 0.8136 | 0.77396 | 0.7342 | 0.52679 | 0.32203 | 0.16275 | 0.76793 | 0.74928 | 0.72927 | 0.71037 | 0.68454 | 0.66789 | 0.63626 | 0.5887 | 0.54434 | 0.48861 | 0.43219 | 0.15302 | -0.10292 | -0.21483
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.038 | 0.061475 | 0.040894 | 0.010541 | -0.024721 | -0.06165 | -0.10541 | -0.14814 | -0.18051 | -0.20392 | -0.22679 | -0.25747 | -0.32281 | -0.3395 | -0.37746 | 0.4892 | 0.47797 | 0.46138 | 0.44169 | 0.42158 | 0.39613 | 0.37483 | 0.34882 | 0.32956 | 0.30742 | 0.28329 | 0.2379 | 0.23132 | 0.20915 | 0.31276 | 0.29798 | 0.26684 | 0.23056 | 0.19262 | 0.14873 | 0.10435 | 0.079217 | 0.061502 | 0.049309 | 0.024206 | -0.03946 | -0.055946 | -0.09243
|  | KILCHRENAN | CT |  |  |  | 0.038 | 0.062127 | 0.040894 | 0.010541 | -0.024721 | -0.06165 | -0.10541 | -0.14814 | -0.18051 | -0.20392 | -0.21797 | -0.23928 | -0.29832 | -0.3151 | -0.34454 | 0.49252 | 0.47797 | 0.46138 | 0.44169 | 0.42158 | 0.39613 | 0.37483 | 0.34882 | 0.32956 | 0.31856 | 0.29987 | 0.25319 | 0.24283 | 0.22093 | 0.31742 | 0.29798 | 0.26684 | 0.23056 | 0.19262 | 0.14873 | 0.10435 | 0.079217 | 0.061502 | 0.051581 | 0.036653 | -0.014983 | -0.031464 | -0.060106
|  | KILCHRENAN | LW |  |  |  | 0.038 | 0.064277 | 0.04532 | 0.020196 | -0.0121 | -0.039774 | -0.086634 | -0.12681 | -0.16102 | -0.1923 | -0.22679 | -0.25747 | -0.32281 | -0.3395 | -0.37746 | 0.49333 | 0.48027 | 0.46691 | 0.44798 | 0.43427 | 0.40448 | 0.38358 | 0.3573 | 0.3343 | 0.30742 | 0.28329 | 0.2379 | 0.23132 | 0.20915 | 0.32002 | 0.3028 | 0.27686 | 0.24451 | 0.21509 | 0.17051 | 0.12988 | 0.10202 | 0.076745 | 0.049309 | 0.024206 | -0.03946 | -0.055946 | -0.09243
|  | KILCHRENAN | ST |  |  |  | 0.038 | 0.061475 | 0.058103 | 0.044359 | 0.030731 | 0.016554 | -0.0007744 | -0.02266 | -0.038618 | -0.06584 | -0.081243 | -0.1094 | -0.21747 | -0.24385 | -0.24622 | 0.4892 | 0.49095 | 0.48275 | 0.47471 | 0.46657 | 0.45553 | 0.44038 | 0.43031 | 0.41018 | 0.40238 | 0.38198 | 0.30093 | 0.28108 | 0.27485 | 0.31276 | 0.31274 | 0.29904 | 0.28521 | 0.27109 | 0.25428 | 0.2342 | 0.2192 | 0.19565 | 0.18064 | 0.15622 | 0.061419 | 0.034906 | 0.031488
|  | KILCHRENAN | FS |  |  |  | 0.038 | 0.068516 | 0.059291 | 0.05824 | 0.055549 | 0.04525 | 0.038266 | 0.028433 | 0.011103 | -0.0028812 | -0.02287 | -0.04442 | -0.13702 | -0.23813 | -0.27223 | 0.49289 | 0.4873 | 0.48786 | 0.48696 | 0.47886 | 0.47425 | 0.46694 | 0.45461 | 0.44575 | 0.43128 | 0.41549 | 0.35416 | 0.28217 | 0.24448 | 0.32062 | 0.31721 | 0.31525 | 0.31216 | 0.30347 | 0.29727 | 0.28859 | 0.27296 | 0.25974 | 0.24203 | 0.22311 | 0.13859 | 0.043088 | 0.0096949
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.403 | -1.6244 | -1.7125 | -1.8712 | -2.0777 | -2.3052 | -2.5693 | -2.8652 | -3.1042 | -3.3915 | -3.6614 | -3.9183 | -4.8456 | -5.5449 | -6.2249 | -0.70004 | -0.75915 | -0.83916 | -0.94234 | -1.047 | -1.1692 | -1.3192 | -1.4396 | -1.5835 | -1.733 | -1.8737 | -2.2955 | -2.6861 | -3.1405 | -0.85222 | -0.9335 | -1.063 | -1.2319 | -1.4134 | -1.6395 | -1.8978 | -2.104 | -2.3468 | -2.5832 | -2.8069 | -3.5763 | -4.1389 | -4.6898
|  | KILLEARN | CT |  |  |  | 0.403 | -1.6197 | -1.7079 | -1.8712 | -2.0777 | -2.3052 | -2.5693 | -2.8652 | -3.1042 | -3.3305 | -3.547 | -3.7502 | -4.6985 | -5.4547 | -6.1025 | -0.69912 | -0.75915 | -0.83916 | -0.94234 | -1.047 | -1.1692 | -1.3192 | -1.4396 | -1.5615 | -1.6864 | -1.806 | -2.2955 | -2.6861 | -3.1405 | -0.84839 | -0.93065 | -1.063 | -1.2319 | -1.4134 | -1.6395 | -1.8978 | -2.104 | -2.2997 | -2.4879 | -2.6638 | -3.462 | -4.0812 | -4.6091
|  | KILLEARN | LW |  |  |  | 0.403 | -1.6244 | -1.7125 | -1.8673 | -2.0673 | -2.2752 | -2.5448 | -2.8297 | -3.0964 | -3.3915 | -3.6614 | -3.9183 | -4.8456 | -5.5449 | -6.2249 | -0.70004 | -0.75677 | -0.82798 | -0.9271 | -1.0136 | -1.1464 | -1.2927 | -1.4178 | -1.5835 | -1.733 | -1.8737 | -2.2762 | -2.5562 | -2.8436 | -0.85222 | -0.9335 | -1.057 | -1.2223 | -1.3804 | -1.6103 | -1.8583 | -2.0875 | -2.3468 | -2.5832 | -2.8069 | -3.5763 | -4.1389 | -4.6898
|  | KILLEARN | ST |  |  |  | 0.403 | -1.5937 | -1.6478 | -1.727 | -1.8085 | -1.9029 | -2.0132 | -2.1196 | -2.2145 | -2.3324 | -2.4554 | -2.5617 | -3.3368 | -3.9275 | -4.4594 | -0.6835 | -0.71575 | -0.76436 | -0.81072 | -0.86605 | -0.93484 | -1.0054 | -1.0643 | -1.1464 | -1.236 | -1.3041 | -1.841 | -2.2112 | -2.6127 | -0.82391 | -0.86865 | -0.93634 | -1.0018 | -1.0791 | -1.1735 | -1.2682 | -1.3475 | -1.4547 | -1.5701 | -1.6584 | -2.353 | -2.8094 | -3.2011
|  | KILLEARN | FS |  |  |  | 0.403 | -1.5828 | -1.6304 | -1.6884 | -1.7521 | -1.8326 | -1.9107 | -1.9931 | -2.0967 | -2.1899 | -2.2977 | -2.406 | -3.028 | -3.6901 | -4.2582 | -0.67806 | -0.70977 | -0.74579 | -0.78402 | -0.83588 | -0.88441 | -0.94232 | -1.0125 | -1.0729 | -1.1494 | -1.2251 | -1.6773 | -2.2535 | -2.8908 | -0.81479 | -0.85582 | -0.90364 | -0.95423 | -1.0218 | -1.0854 | -1.1572 | -1.2464 | -1.3223 | -1.4174 | -1.5109 | -2.0459 | -2.605 | -3.0299
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0.023 | 1.7794 | 1.7526 | 1.7166 | 1.6667 | 1.6221 | 1.5591 | 1.4606 | 1.3824 | 1.3172 | 1.2399 | 1.1692 | 0.9711 | 0.84232 | 0.69477 | 2.0886 | 2.0637 | 2.0348 | 1.9962 | 1.9623 | 1.9211 | 1.8658 | 1.8165 | 1.7682 | 1.7124 | 1.6608 | 1.5189 | 1.4356 | 1.3323 | 1.9614 | 1.9337 | 1.8992 | 1.8456 | 1.7947 | 1.7063 | 1.6119 | 1.5371 | 1.4754 | 1.4014 | 1.3336 | 1.1468 | 1.0261 | 0.88466
|  | KILLIN TOWN | CT |  |  |  | 0.023 | 1.7794 | 1.7529 | 1.7195 | 1.6667 | 1.6221 | 1.5608 | 1.4647 | 1.386 | 1.3503 | 1.2894 | 1.2339 | 1.0599 | 0.95564 | 0.83931 | 2.0886 | 2.0662 | 2.0407 | 1.9962 | 1.9623 | 1.9211 | 1.8658 | 1.8247 | 1.7996 | 1.7549 | 1.7133 | 1.5859 | 1.5115 | 1.4083 | 1.9614 | 1.9338 | 1.9007 | 1.8456 | 1.7947 | 1.7152 | 1.6248 | 1.5491 | 1.516 | 1.4574 | 1.4037 | 1.2406 | 1.1473 | 1.0407
|  | KILLIN TOWN | LW |  |  |  | 0.023 | 1.7825 | 1.7526 | 1.7166 | 1.6716 | 1.632 | 1.5591 | 1.4606 | 1.3824 | 1.3172 | 1.2399 | 1.1692 | 0.9711 | 0.84232 | 0.69477 | 2.0909 | 2.0637 | 2.0348 | 1.9998 | 1.9711 | 1.9241 | 1.8702 | 1.8165 | 1.7682 | 1.7124 | 1.6608 | 1.5189 | 1.4356 | 1.3323 | 1.9648 | 1.9337 | 1.8992 | 1.8519 | 1.8 | 1.7063 | 1.6119 | 1.5371 | 1.4754 | 1.4014 | 1.3336 | 1.1468 | 1.0261 | 0.88466
|  | KILLIN TOWN | ST |  |  |  | 0.023 | 1.7843 | 1.7697 | 1.7497 | 1.7283 | 1.7078 | 1.6834 | 1.6625 | 1.6339 | 1.5956 | 1.5513 | 1.4915 | 1.2586 | 1.1244 | 1.0513 | 2.0939 | 2.0838 | 2.0631 | 2.0415 | 2.0204 | 1.9954 | 1.971 | 1.9403 | 1.901 | 1.8623 | 1.8174 | 1.5814 | 1.4718 | 1.41 | 1.969 | 1.9563 | 1.9314 | 1.905 | 1.8785 | 1.8477 | 1.8168 | 1.7796 | 1.7323 | 1.6858 | 1.6315 | 1.3463 | 1.2166 | 1.1453
|  | KILLIN TOWN | FS |  |  |  | 0.023 | 1.7933 | 1.7826 | 1.7763 | 1.7687 | 1.7589 | 1.7491 | 1.7352 | 1.7133 | 1.693 | 1.6668 | 1.6459 | 1.4519 | 1.2448 | 1.1141 | 2.0989 | 2.0918 | 2.0816 | 2.0697 | 2.0559 | 2.0413 | 2.0224 | 1.9999 | 1.9757 | 1.9472 | 1.9217 | 1.7545 | 1.5879 | 1.4792 | 1.9754 | 1.9668 | 1.9543 | 1.94 | 1.9233 | 1.9056 | 1.8833 | 1.8564 | 1.8269 | 1.7928 | 1.762 | 1.5571 | 1.3519 | 1.2181
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0 | -1.3827 | -1.4184 | -1.4831 | -1.5426 | -1.6238 | -1.6874 | -1.7804 | -1.8162 | -1.8557 | -1.8987 | -1.9483 | -2.0494 | -2.0785 | -2.1348 | -1.0794 | -1.0951 | -1.1249 | -1.1542 | -1.1912 | -1.2214 | -1.2629 | -1.2778 | -1.2928 | -1.3078 | -1.3277 | -1.3985 | -1.4107 | -1.4429 | -1.3162 | -1.3347 | -1.3587 | -1.3735 | -1.4042 | -1.4488 | -1.5207 | -1.5359 | -1.5513 | -1.5853 | -1.6254 | -1.7052 | -1.7349 | -1.7851
|  | KILMELFORD | CT |  |  |  | 0 | -1.3827 | -1.4184 | -1.4831 | -1.5426 | -1.6238 | -1.6874 | -1.7804 | -1.8162 | -1.8557 | -1.8976 | -1.9273 | -2.0168 | -2.0437 | -2.0891 | -1.0794 | -1.0951 | -1.1249 | -1.1542 | -1.1912 | -1.2214 | -1.2629 | -1.2778 | -1.2928 | -1.3078 | -1.3185 | -1.3826 | -1.4027 | -1.4409 | -1.3158 | -1.3347 | -1.3587 | -1.3735 | -1.4042 | -1.4488 | -1.5207 | -1.5359 | -1.5513 | -1.5664 | -1.5948 | -1.6774 | -1.7054 | -1.7489
|  | KILMELFORD | LW |  |  |  | 0 | -1.38 | -1.4127 | -1.4689 | -1.5246 | -1.591 | -1.6588 | -1.7454 | -1.7815 | -1.8483 | -1.8987 | -1.9483 | -2.0494 | -2.0785 | -2.1348 | -1.078 | -1.0921 | -1.1174 | -1.1431 | -1.1734 | -1.2035 | -1.2411 | -1.2564 | -1.282 | -1.3021 | -1.3277 | -1.3985 | -1.4107 | -1.4429 | -1.3162 | -1.334 | -1.3551 | -1.3724 | -1.3951 | -1.4243 | -1.4777 | -1.4962 | -1.5465 | -1.5853 | -1.6254 | -1.7052 | -1.7349 | -1.7851
|  | KILMELFORD | ST |  |  |  | 0 | -1.3703 | -1.3931 | -1.4172 | -1.4446 | -1.4788 | -1.5105 | -1.5312 | -1.5686 | -1.6025 | -1.6482 | -1.6755 | -1.8577 | -1.8939 | -1.8925 | -1.0743 | -1.0847 | -1.0958 | -1.1084 | -1.1235 | -1.1373 | -1.147 | -1.1632 | -1.1784 | -1.198 | -1.2122 | -1.3108 | -1.3359 | -1.3469 | -1.3087 | -1.3175 | -1.3264 | -1.3382 | -1.3553 | -1.3741 | -1.3833 | -1.4073 | -1.4293 | -1.4607 | -1.4776 | -1.6239 | -1.6506 | -1.6556
|  | KILMELFORD | FS |  |  |  | 0 | -1.3628 | -1.3752 | -1.3883 | -1.4049 | -1.4185 | -1.4351 | -1.4552 | -1.4711 | -1.5055 | -1.5286 | -1.5635 | -1.7282 | -1.8854 | -1.9371 | -1.0702 | -1.0761 | -1.0816 | -1.0886 | -1.0946 | -1.1014 | -1.1097 | -1.1178 | -1.133 | -1.1439 | -1.1594 | -1.2402 | -1.3362 | -1.4143 | -1.3097 | -1.3138 | -1.322 | -1.3333 | -1.3419 | -1.3553 | -1.3712 | -1.3777 | -1.3995 | -1.413 | -1.4358 | -1.5485 | -1.6391 | -1.6571
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.023 | -0.73252 | -0.77946 | -0.84892 | -0.91595 | -1.0069 | -1.0902 | -1.2095 | -1.2724 | -1.3489 | -1.4312 | -1.5104 | -1.686 | -1.7336 | -1.8329 | -0.010667 | -0.040128 | -0.081251 | -0.12011 | -0.17397 | -0.22156 | -0.29324 | -0.33829 | -0.39312 | -0.45069 | -0.50743 | -0.62912 | -0.65356 | -0.71914 | -0.57612 | -0.62047 | -0.68518 | -0.74677 | -0.83156 | -0.9082 | -1.02 | -1.0811 | -1.1593 | -1.2401 | -1.3183 | -1.4887 | -1.531 | -1.6257
|  | KILNINVER | CT |  |  |  | 0.023 | -0.73252 | -0.77946 | -0.84892 | -0.91595 | -1.0069 | -1.0902 | -1.2095 | -1.2724 | -1.3329 | -1.3902 | -1.446 | -1.6042 | -1.6522 | -1.7297 | -0.010667 | -0.040128 | -0.081251 | -0.12011 | -0.17397 | -0.22156 | -0.29324 | -0.33829 | -0.38138 | -0.42281 | -0.46485 | -0.58765 | -0.63411 | -0.71914 | -0.57612 | -0.62047 | -0.68518 | -0.74677 | -0.83156 | -0.9082 | -1.02 | -1.0811 | -1.1403 | -1.197 | -1.2526 | -1.4071 | -1.4503 | -1.5231
|  | KILNINVER | LW |  |  |  | 0.023 | -0.72659 | -0.76863 | -0.83038 | -0.8935 | -0.96832 | -1.0627 | -1.1812 | -1.2471 | -1.3489 | -1.4312 | -1.5104 | -1.686 | -1.7336 | -1.8329 | -0.0073243 | -0.033426 | -0.068772 | -0.10439 | -0.14723 | -0.20342 | -0.2757 | -0.32173 | -0.39312 | -0.45069 | -0.50743 | -0.62912 | -0.65356 | -0.71772 | -0.57088 | -0.61069 | -0.66796 | -0.72605 | -0.79532 | -0.8836 | -0.99547 | -1.0594 | -1.1593 | -1.2401 | -1.3183 | -1.4887 | -1.531 | -1.6257
|  | KILNINVER | ST |  |  |  | 0.023 | -0.71461 | -0.74248 | -0.77349 | -0.8035 | -0.84336 | -0.88801 | -0.92303 | -0.97332 | -1.0227 | -1.0849 | -1.1299 | -1.3884 | -1.4462 | -1.4476 | 0.00082146 | -0.015379 | -0.0338 | -0.051971 | -0.076969 | -0.10551 | -0.12779 | -0.16104 | -0.19424 | -0.23641 | -0.2681 | -0.46331 | -0.52572 | -0.56656 | -0.55904 | -0.58479 | -0.6134 | -0.64102 | -0.67847 | -0.72075 | -0.75343 | -0.80157 | -0.84882 | -0.90877 | -0.95157 | -1.2048 | -1.2607 | -1.2619
|  | KILNINVER | FS |  |  |  | 0.023 | -0.70266 | -0.71786 | -0.72969 | -0.74533 | -0.75814 | -0.779 | -0.80347 | -0.82822 | -0.87221 | -0.90579 | -0.95198 | -1.1867 | -1.4149 | -1.4967 | 0.0058052 | -0.0033919 | -0.012366 | -0.024258 | -0.034419 | -0.05026 | -0.069133 | -0.086028 | -0.11651 | -0.13999 | -0.17237 | -0.3483 | -0.53615 | -0.67072 | -0.54875 | -0.56269 | -0.57414 | -0.58938 | -0.60181 | -0.62232 | -0.6464 | -0.66938 | -0.71151 | -0.74327 | -0.78759 | -1.0138 | -1.2308 | -1.3085
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 0.259 | 3.6325 | 3.5567 | 3.4627 | 3.3485 | 3.2151 | 3.0726 | 2.9209 | 2.8426 | 2.7547 | 2.7028 | 2.6316 | 2.4326 | 2.3194 | 2.1888 | 4.4644 | 4.4199 | 4.3806 | 4.3267 | 4.2664 | 4.1814 | 4.1048 | 4.0448 | 3.9632 | 3.9267 | 3.8686 | 3.7403 | 3.6838 | 3.6019 | 4.1664 | 4.0966 | 4.0178 | 3.9184 | 3.8015 | 3.6773 | 3.5449 | 3.4631 | 3.3604 | 3.3101 | 3.2374 | 3.0487 | 2.9472 | 2.8223
|  | KILTARLITY | CT |  |  |  | 0.259 | 3.6325 | 3.5567 | 3.4627 | 3.3485 | 3.2151 | 3.0726 | 2.9209 | 2.8426 | 2.7805 | 2.7178 | 2.7002 | 2.5173 | 2.4222 | 2.3197 | 4.4644 | 4.4235 | 4.3892 | 4.3338 | 4.2664 | 4.1964 | 4.1258 | 4.0638 | 4.0124 | 3.9554 | 3.9375 | 3.7991 | 3.7401 | 3.6507 | 4.1664 | 4.0966 | 4.0178 | 3.9184 | 3.8015 | 3.6773 | 3.5468 | 3.467 | 3.4034 | 3.3369 | 3.318 | 3.1415 | 3.0611 | 2.969
|  | KILTARLITY | LW |  |  |  | 0.259 | 3.6442 | 3.5686 | 3.4733 | 3.3621 | 3.2427 | 3.0887 | 2.9376 | 2.8553 | 2.7547 | 2.7028 | 2.6316 | 2.4326 | 2.3194 | 2.1888 | 4.4669 | 4.4199 | 4.3806 | 4.3267 | 4.2691 | 4.1814 | 4.1048 | 4.0448 | 3.9632 | 3.9267 | 3.8686 | 3.7403 | 3.6838 | 3.6019 | 4.1753 | 4.1028 | 4.0203 | 3.9223 | 3.8184 | 3.6783 | 3.5449 | 3.4631 | 3.3604 | 3.3101 | 3.2374 | 3.0487 | 2.9472 | 2.8223
|  | KILTARLITY | ST |  |  |  | 0.259 | 3.6543 | 3.6084 | 3.5415 | 3.4681 | 3.4058 | 3.3306 | 3.261 | 3.1897 | 3.1268 | 3.0468 | 2.9708 | 2.6394 | 2.4915 | 2.4107 | 4.4755 | 4.4582 | 4.4293 | 4.3945 | 4.3693 | 4.3296 | 4.2956 | 4.251 | 4.2173 | 4.1644 | 4.1159 | 3.8705 | 3.7618 | 3.6782 | 4.186 | 4.1475 | 4.0894 | 4.0242 | 3.9721 | 3.9056 | 3.8453 | 3.7791 | 3.7233 | 3.6478 | 3.5761 | 3.2542 | 3.1167 | 3.0428
|  | KILTARLITY | FS |  |  |  | 0.259 | 3.6858 | 3.655 | 3.63 | 3.6066 | 3.5769 | 3.5565 | 3.5224 | 3.475 | 3.4122 | 3.3486 | 3.3044 | 2.9765 | 2.6828 | 2.5692 | 4.4844 | 4.4706 | 4.4546 | 4.4402 | 4.4197 | 4.4092 | 4.3847 | 4.3599 | 4.3174 | 4.2741 | 4.2535 | 4.0273 | 3.8334 | 3.7002 | 4.2113 | 4.1846 | 4.1608 | 4.1385 | 4.1094 | 4.091 | 4.0571 | 4.0149 | 3.9558 | 3.8958 | 3.8587 | 3.5503 | 3.2918 | 3.1944
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 2.551 | 2.6575 | 2.4696 | 1.9249 | 0.84343 | -0.27738 | -1.1138 | -2.0507 | -2.7666 | -3.549 | -3.9546 | -4.5614 | -6.2057 | -6.6474 | -7.1827 | 8.7709 | 8.5535 | 7.9674 | 7.2339 | 6.3197 | 5.6854 | 4.981 | 4.5954 | 4.1642 | 3.977 | 3.5974 | 2.5359 | 1.7264 | -0.49281 | -1.329 | -1.4975 | -2.0539 | -2.7392 | -3.7307 | -4.3296 | -5.0408 | -5.4956 | -6.0556 | -6.4213 | -6.9031 | -8.2618 | -8.622 | -9.0636
|  | KINCORTH | CT |  |  |  | 2.551 | 2.6585 | 2.4798 | 1.9741 | 1.0427 | -0.086135 | -0.83252 | -1.6665 | -2.4665 | -3.1541 | -3.4867 | -4.0084 | -5.8149 | -6.6474 | -7.1827 | 8.7709 | 8.5552 | 8.0255 | 7.2726 | 6.3254 | 5.7272 | 5.0991 | 4.6374 | 4.2552 | 4.086 | 3.7834 | 2.5359 | 1.7264 | 0.57086 | -1.3284 | -1.485 | -1.9931 | -2.7392 | -3.7307 | -4.3296 | -4.9771 | -5.4786 | -5.8764 | -6.1241 | -6.4606 | -7.9143 | -8.622 | -9.0636
|  | KINCORTH | LW |  |  |  | 2.551 | 2.6575 | 2.4696 | 1.9249 | 0.84343 | -0.27738 | -1.1138 | -2.0507 | -2.7666 | -3.549 | -3.9546 | -4.5614 | -6.2057 | -6.4708 | -6.8537 | 8.776 | 8.5535 | 7.9674 | 7.2339 | 6.3197 | 5.6854 | 4.981 | 4.5954 | 4.1642 | 3.977 | 3.5974 | 2.5983 | 2.4278 | 2.0675 | -1.329 | -1.4975 | -2.0539 | -2.7257 | -3.662 | -4.3145 | -5.0408 | -5.4956 | -6.0556 | -6.4213 | -6.9031 | -8.2618 | -8.5248 | -8.8627
|  | KINCORTH | ST |  |  |  | 2.551 | 2.6916 | 2.5928 | 2.1448 | 1.524 | 0.70994 | 0.29219 | -0.077924 | -0.31212 | -0.62639 | -0.95911 | -1.3306 | -3.1785 | -3.9186 | -4.626 | 8.8297 | 8.7118 | 8.2933 | 7.7155 | 6.8402 | 6.3598 | 5.9496 | 5.7798 | 5.5392 | 5.2784 | 4.9889 | 3.5285 | 2.8437 | 1.5253 | -1.296 | -1.3827 | -1.8182 | -2.4248 | -3.2568 | -3.6832 | -4.0626 | -4.2588 | -4.4835 | -4.7358 | -5.085 | -6.893 | -7.6924 | -8.1306
|  | KINCORTH | FS |  |  |  | 2.551 | 2.6978 | 2.6205 | 2.2994 | 1.8538 | 1.1732 | 0.73544 | 0.45132 | 0.30025 | 0.079192 | -0.17342 | -0.42716 | -2.2944 | -3.8385 | -5.2948 | 8.8323 | 8.7417 | 8.4381 | 8.0114 | 7.287 | 6.7603 | 6.4277 | 6.2617 | 6.0017 | 5.747 | 5.518 | 3.8847 | 2.0917 | -0.49281 | -1.2903 | -1.3575 | -1.6651 | -2.0955 | -2.7897 | -3.2329 | -3.5223 | -3.6768 | -3.8999 | -4.0994 | -4.2969 | -5.9422 | -7.296 | -8.3883
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0.059 | -0.0053194 | -0.015488 | -0.025981 | -0.036469 | -0.044485 | -0.057191 | -0.074221 | -0.081485 | -0.090627 | -0.098865 | -0.10642 | -0.13247 | -0.15544 | -0.18083 | -3.3597 | -3.3711 | -3.383 | -3.3945 | -3.4029 | -3.4162 | -3.4343 | -3.4397 | -3.4467 | -3.4529 | -3.4586 | -3.4835 | -3.5111 | -3.542 | -0.013357 | -0.025475 | -0.038176 | -0.050693 | -0.060147 | -0.074942 | -0.094823 | -0.10185 | -0.1107 | -0.11868 | -0.12599 | -0.15455 | -0.18291 | -0.21433
|  | KINGAIRLOCH | CT |  |  |  | 0.059 | -0.0051454 | -0.008013 | -0.01094 | -0.022269 | -0.02774 | -0.033901 | -0.044959 | -0.052865 | -0.059063 | -0.065595 | -0.071711 | -0.089271 | -0.09591 | -0.10492 | -3.3596 | -3.3618 | -3.364 | -3.3761 | -3.3811 | -3.387 | -3.3982 | -3.4047 | -3.4098 | -3.4154 | -3.4206 | -3.4365 | -3.4437 | -3.4541 | -0.013207 | -0.016201 | -0.019294 | -0.032667 | -0.038761 | -0.045769 | -0.058467 | -0.066364 | -0.072601 | -0.07918 | -0.085364 | -0.10394 | -0.11189 | -0.12285
|  | KINGAIRLOCH | LW |  |  |  | 0.059 | -0.0053194 | -0.015488 | -0.025981 | -0.036469 | -0.044485 | -0.057191 | -0.074221 | -0.081485 | -0.090627 | -0.098865 | -0.10642 | -0.13247 | -0.15544 | -0.18083 | -3.3597 | -3.3711 | -3.383 | -3.3945 | -3.4029 | -3.4162 | -3.4343 | -3.4397 | -3.4467 | -3.4529 | -3.4586 | -3.4835 | -3.5111 | -3.542 | -0.013357 | -0.025475 | -0.038176 | -0.050693 | -0.060147 | -0.074942 | -0.094823 | -0.10185 | -0.1107 | -0.11868 | -0.12599 | -0.15455 | -0.18291 | -0.21433
|  | KINGAIRLOCH | ST |  |  |  | 0.059 | -0.0043409 | -0.0054286 | -0.011803 | -0.016905 | -0.020724 | -0.02421 | -0.028248 | -0.032926 | -0.038915 | -0.045587 | -0.052279 | -0.10626 | -0.1396 | -0.1633 | -3.3589 | -3.3597 | -3.3669 | -3.3723 | -3.3759 | -3.3789 | -3.3824 | -3.3864 | -3.3915 | -3.3969 | -3.4018 | -3.452 | -3.4885 | -3.5172 | -0.012366 | -0.013547 | -0.021281 | -0.027339 | -0.031713 | -0.035555 | -0.039957 | -0.044987 | -0.051348 | -0.058131 | -0.064597 | -0.12235 | -0.16142 | -0.19074
|  | KINGAIRLOCH | FS |  |  |  | 0.059 | -0.0040915 | -0.0049279 | -0.0075476 | -0.010393 | -0.013424 | -0.016725 | -0.021158 | -0.025223 | -0.030866 | -0.036615 | -0.040318 | -0.066256 | -0.088983 | -0.10228 | -3.3588 | -3.3594 | -3.3623 | -3.3652 | -3.3684 | -3.3717 | -3.3764 | -3.3803 | -3.3859 | -3.3915 | -3.3945 | -3.4147 | -3.4311 | -3.4417 | -0.012048 | -0.012941 | -0.016006 | -0.0193 | -0.022781 | -0.026536 | -0.031632 | -0.036212 | -0.042585 | -0.049066 | -0.052894 | -0.078791 | -0.1007 | -0.11435
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.58 | 1.0208 | 0.7437 | 8.3479 | 7.8386 | 7.2774 | 6.7566 | 6.2649 | 5.7209 | 5.2407 | 4.7852 | 4.572 | 4.0524 | 3.525 | 3.1134 | 2.3825 | 2.2187 | 9.2972 | 9.0503 | 8.7784 | 8.4971 | 8.2466 | 7.8754 | 7.5169 | 7.1831 | 7.1059 | 7.0232 | 6.7163 | 6.3447 | 2.0019 | 1.773 | 9.0722 | 8.6544 | 8.1671 | 7.7103 | 7.2582 | 6.7579 | 6.3164 | 5.8889 | 5.6993 | 5.2611 | 4.7989 | 4.4371
|  | KINGSEAT | CT |  |  |  | 1.58 | 1.0208 | 0.7437 | 8.3479 | 7.8535 | 7.286 | 6.7651 | 6.2649 | 5.7209 | 5.2837 | 4.8467 | 4.572 | 4.0524 | 3.525 | 3.1134 | 2.3837 | 2.2257 | 9.3041 | 9.0792 | 8.7968 | 8.54 | 8.2873 | 7.9258 | 7.6271 | 7.3004 | 7.1059 | 7.0232 | 6.7163 | 6.3447 | 2.0019 | 1.773 | 9.0722 | 8.6544 | 8.1671 | 7.7103 | 7.2582 | 6.7579 | 6.3568 | 5.9505 | 5.6993 | 5.2611 | 4.7989 | 4.4371
|  | KINGSEAT | LW |  |  |  | 1.58 | 1.0282 | 0.74944 | 8.3552 | 7.8386 | 7.2774 | 6.7566 | 6.2938 | 5.7379 | 5.2407 | 4.7852 | 4.8324 | 4.0768 | 3.6702 | 3.2633 | 2.3825 | 2.2187 | 9.2972 | 9.0503 | 8.7784 | 8.4971 | 8.2466 | 7.8754 | 7.5169 | 7.1831 | 7.4152 | 7.063 | 6.9146 | 6.7267 | 2.012 | 1.7837 | 9.0879 | 8.6565 | 8.1819 | 7.7223 | 7.3003 | 6.7831 | 6.3164 | 5.8889 | 5.9538 | 5.2677 | 4.9122 | 4.5531
|  | KINGSEAT | ST |  |  |  | 1.58 | 1.0785 | 0.87331 | 8.6419 | 8.3684 | 8.0849 | 7.8499 | 7.6449 | 7.2914 | 6.9592 | 6.6413 | 6.4111 | 5.6445 | 5.0029 | 4.4629 | 2.4133 | 2.306 | 9.4536 | 9.3118 | 9.1575 | 9.0195 | 8.9042 | 8.6503 | 8.402 | 8.1726 | 8.0005 | 7.6326 | 7.2523 | 6.8413 | 2.0563 | 1.8933 | 9.3406 | 9.1209 | 8.8896 | 8.6893 | 8.5038 | 8.1785 | 7.8707 | 7.5758 | 7.3646 | 6.6721 | 6.1001 | 5.6272
|  | KINGSEAT | FS |  |  |  | 1.58 | 1.1267 | 0.97963 | 8.87 | 8.7116 | 8.5348 | 8.4049 | 8.2512 | 8.002 | 7.7209 | 7.4336 | 7.1886 | 6.093 | 5.4172 | 4.7622 | 2.4357 | 2.3472 | 9.5503 | 9.4551 | 9.3428 | 9.26 | 9.1506 | 8.9904 | 8.7956 | 8.5936 | 8.4234 | 7.6557 | 7.2569 | 6.543 | 2.1025 | 1.9858 | 9.5353 | 9.4105 | 9.271 | 9.1634 | 9.027 | 8.7969 | 8.5452 | 8.2854 | 8.0674 | 7.0603 | 6.4654 | 5.8813
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 0.267 | 1.7746 | 1.5937 | 1.3274 | 1.0371 | 0.69992 | 0.32904 | -0.071104 | -0.36702 | -0.61344 | -0.83384 | -1.0655 | -1.6422 | -1.8699 | -2.197 | 3.743 | 3.6297 | 3.4772 | 3.2951 | 3.0984 | 2.8833 | 2.6403 | 2.4306 | 2.2318 | 2.0561 | 1.878 | 1.4298 | 1.2733 | 1.0259 | 2.8125 | 2.6659 | 2.4407 | 2.16 | 1.8712 | 1.5547 | 1.1953 | 0.97872 | 0.80873 | 0.5973 | 0.37081 | -0.18747 | -0.47714 | -0.77527
|  | KINGUSSIE | CT |  |  |  | 0.267 | 1.7746 | 1.5937 | 1.3274 | 1.0371 | 0.69992 | 0.32904 | -0.071104 | -0.36702 | -0.5772 | -0.73294 | -0.89921 | -1.4009 | -1.5814 | -1.8146 | 3.743 | 3.6304 | 3.4772 | 3.2951 | 3.0984 | 2.8833 | 2.6403 | 2.4306 | 2.2769 | 2.145 | 2.0099 | 1.598 | 1.4276 | 1.1539 | 2.8125 | 2.6659 | 2.4407 | 2.16 | 1.8712 | 1.5547 | 1.1953 | 0.97872 | 0.82702 | 0.69712 | 0.55363 | 0.068139 | -0.096281 | -0.33641
|  | KINGUSSIE | LW |  |  |  | 0.267 | 1.7867 | 1.6061 | 1.3529 | 1.083 | 0.79623 | 0.40224 | 0.015399 | -0.28646 | -0.61344 | -0.83384 | -1.0655 | -1.6422 | -1.8699 | -2.197 | 3.7494 | 3.6297 | 3.4798 | 3.3192 | 3.1546 | 2.914 | 2.6724 | 2.4667 | 2.2318 | 2.0561 | 1.878 | 1.4298 | 1.2733 | 1.0259 | 2.8285 | 2.681 | 2.4683 | 2.2313 | 1.9824 | 1.6602 | 1.3215 | 1.0997 | 0.80873 | 0.5973 | 0.37081 | -0.18747 | -0.42029 | -0.77527
|  | KINGUSSIE | ST |  |  |  | 0.267 | 1.8303 | 1.7115 | 1.5707 | 1.4182 | 1.2473 | 1.0866 | 0.89885 | 0.70674 | 0.48094 | 0.29322 | 0.062589 | -0.97656 | -1.4995 | -1.7106 | 3.7782 | 3.7113 | 3.6233 | 3.5291 | 3.423 | 3.3203 | 3.1979 | 3.0671 | 2.9074 | 2.7699 | 2.5997 | 1.7498 | 1.3837 | 1.14 | 2.8572 | 2.7631 | 2.6309 | 2.4933 | 2.3451 | 2.1923 | 2.0244 | 1.8502 | 1.6462 | 1.4478 | 1.2238 | 0.031533 | -0.47714 | -0.68643
|  | KINGUSSIE | FS |  |  |  | 0.267 | 1.8978 | 1.8171 | 1.7612 | 1.6823 | 1.609 | 1.5156 | 1.4413 | 1.2917 | 1.1349 | 0.96685 | 0.84028 | -0.069683 | -0.86266 | -1.4415 | 3.8108 | 3.7631 | 3.7211 | 3.6643 | 3.6096 | 3.5405 | 3.4777 | 3.375 | 3.2619 | 3.141 | 3.0472 | 2.3396 | 1.6276 | 1.0726 | 2.9158 | 2.8563 | 2.8063 | 2.7459 | 2.6839 | 2.6111 | 2.5383 | 2.4135 | 2.2737 | 2.1285 | 1.9969 | 1.1052 | 0.1717 | -0.40298
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.04 | -0.61939 | -0.66218 | -0.72439 | -0.80261 | -0.87824 | -0.96837 | -1.0715 | -1.1452 | -1.2005 | -1.2573 | -1.3284 | -1.4853 | -1.5276 | -1.6209 | -0.1049 | -0.13193 | -0.16574 | -0.2104 | -0.25105 | -0.30154 | -0.36047 | -0.41753 | -0.4699 | -0.5131 | -0.56886 | -0.68316 | -0.70189 | -0.76377 | -0.43238 | -0.47281 | -0.53012 | -0.60277 | -0.67233 | -0.75584 | -0.85172 | -0.92419 | -0.98241 | -1.0381 | -1.1084 | -1.2611 | -1.299 | -1.3882
|  | KINLOCH | CT |  |  |  | 0.04 | -0.61939 | -0.66218 | -0.72439 | -0.80261 | -0.87824 | -0.96837 | -1.0715 | -1.1452 | -1.1993 | -1.2326 | -1.2807 | -1.4141 | -1.4555 | -1.5269 | -0.1049 | -0.13193 | -0.16574 | -0.2104 | -0.25105 | -0.30154 | -0.36047 | -0.41753 | -0.46045 | -0.48814 | -0.52936 | -0.63872 | -0.67132 | -0.73794 | -0.43238 | -0.47281 | -0.53012 | -0.60277 | -0.67233 | -0.75584 | -0.85172 | -0.92419 | -0.97767 | -1.0108 | -1.059 | -1.1901 | -1.2276 | -1.2949
|  | KINLOCH | LW |  |  |  | 0.04 | -0.61339 | -0.65109 | -0.7037 | -0.77396 | -0.83331 | -0.93003 | -1.0295 | -1.1064 | -1.2005 | -1.2573 | -1.3284 | -1.4853 | -1.5276 | -1.6209 | -0.10202 | -0.12577 | -0.15316 | -0.19317 | -0.22284 | -0.28118 | -0.3402 | -0.39763 | -0.4699 | -0.5131 | -0.56886 | -0.68316 | -0.70189 | -0.76377 | -0.427 | -0.46267 | -0.5109 | -0.57626 | -0.63033 | -0.72125 | -0.8145 | -0.88975 | -0.98241 | -1.0381 | -1.1084 | -1.2611 | -1.299 | -1.3882
|  | KINLOCH | ST |  |  |  | 0.04 | -0.60204 | -0.62854 | -0.65298 | -0.6863 | -0.71834 | -0.75932 | -0.80552 | -0.83966 | -0.89617 | -0.94362 | -1.0055 | -1.2456 | -1.3028 | -1.3101 | -0.093314 | -0.10845 | -0.12069 | -0.14012 | -0.15859 | -0.1844 | -0.21445 | -0.23607 | -0.27575 | -0.30821 | -0.35242 | -0.53755 | -0.58821 | -0.61451 | -0.41576 | -0.44033 | -0.46248 | -0.49346 | -0.52318 | -0.56184 | -0.60569 | -0.63782 | -0.69222 | -0.73757 | -0.79733 | -1.0312 | -1.0857 | -1.0923
|  | KINLOCH | FS |  |  |  | 0.04 | -0.58778 | -0.60562 | -0.61717 | -0.63064 | -0.64662 | -0.66131 | -0.68423 | -0.71962 | -0.74868 | -0.78951 | -0.83364 | -1.0525 | -1.2715 | -1.359 | -0.087206 | -0.098125 | -0.10636 | -0.11621 | -0.12817 | -0.13923 | -0.15719 | -0.18128 | -0.2004 | -0.22902 | -0.2604 | -0.42103 | -0.58936 | -0.6951 | -0.40302 | -0.4197 | -0.43075 | -0.44369 | -0.45915 | -0.47335 | -0.49573 | -0.52939 | -0.55671 | -0.59575 | -0.63808 | -0.84809 | -1.0562 | -1.1394
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | 0.021862 | 0.010655 | -0.0021684 | -0.01696 | -0.028631 | -0.047428 | -0.076142 | -0.085814 | -0.10938 | -0.12979 | -0.13957 | -0.17951 | -0.20377 | -0.23673 | 0.40613 | 0.39146 | 0.37095 | 0.34845 | 0.32877 | 0.301 | 0.2617 | 0.24957 | 0.22362 | 0.2007 | 0.18887 | 0.13147 | 0.094127 | 0.044041 | 0.024385 | 0.0066276 | -0.022327 | -0.054577 | -0.084618 | -0.12454 | -0.17828 | -0.19461 | -0.22789 | -0.25756 | -0.27206 | -0.34341 | -0.38968 | -0.4503
|  | KINLOCH RANNOCH | CT |  |  |  | 0 | 0.021862 | 0.020743 | 0.013737 | -0.0040987 | -0.016909 | -0.026411 | -0.050482 | -0.062234 | -0.077984 | -0.096395 | -0.10586 | -0.14352 | -0.15078 | -0.16416 | 0.40613 | 0.40157 | 0.3877 | 0.35965 | 0.33833 | 0.31922 | 0.28397 | 0.27061 | 0.25378 | 0.235 | 0.2262 | 0.17826 | 0.15818 | 0.12382 | 0.024385 | 0.016118 | -0.0078926 | -0.047978 | -0.082113 | -0.11399 | -0.16543 | -0.18195 | -0.20222 | -0.22443 | -0.23355 | -0.28827 | -0.30886 | -0.34169
|  | KINLOCH RANNOCH | LW |  |  |  | 0 | 0.022275 | 0.010655 | -0.0021684 | -0.01696 | -0.028631 | -0.047428 | -0.076142 | -0.085814 | -0.10938 | -0.12979 | -0.13957 | -0.17951 | -0.20377 | -0.23673 | 0.40739 | 0.39146 | 0.37095 | 0.34845 | 0.32877 | 0.301 | 0.2617 | 0.24957 | 0.22362 | 0.2007 | 0.18887 | 0.13147 | 0.094127 | 0.044041 | 0.02656 | 0.0066276 | -0.022327 | -0.054577 | -0.084618 | -0.12454 | -0.17828 | -0.19461 | -0.22789 | -0.25756 | -0.27206 | -0.34341 | -0.38968 | -0.4503
|  | KINLOCH RANNOCH | ST |  |  |  | 0 | 0.024804 | 0.021689 | 0.01737 | 0.0092001 | 0.0042278 | -0.0014603 | -0.0096374 | -0.02155 | -0.031283 | -0.046791 | -0.052059 | -0.13471 | -0.17099 | -0.19522 | 0.40827 | 0.40461 | 0.39577 | 0.38417 | 0.37558 | 0.3667 | 0.35535 | 0.34074 | 0.32808 | 0.30938 | 0.30031 | 0.1966 | 0.13931 | 0.094938 | 0.031696 | 0.02114 | 0.0088375 | -0.0073569 | -0.020279 | -0.033796 | -0.050263 | -0.070262 | -0.08782 | -0.1128 | -0.12602 | -0.25158 | -0.31253 | -0.35029
|  | KINLOCH RANNOCH | FS |  |  |  | 0 | 0.026472 | 0.01632 | 0.023941 | 0.01885 | 0.015182 | 0.0072665 | 0.0013664 | -0.0061602 | -0.018638 | -0.026014 | -0.036524 | -0.091413 | -0.12917 | -0.14245 | 0.41163 | 0.39976 | 0.40761 | 0.4015 | 0.39635 | 0.38717 | 0.3796 | 0.36942 | 0.35383 | 0.34337 | 0.33019 | 0.25829 | 0.19061 | 0.13723 | 0.037428 | 0.023824 | 0.027865 | 0.020418 | 0.014188 | 0.0030454 | -0.0056787 | -0.019203 | -0.039104 | -0.052633 | -0.070194 | -0.16324 | -0.24435 | -0.28724
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | YES | 0.323 | 0.020666 | 0.011683 | -0.020514 | -0.056432 | -0.089794 | -0.13877 | -0.19126 | -0.2307 | -0.26535 | -0.30415 | -0.33872 | -0.42552 | -0.47081 | -0.53843 | 0.64421 | 0.62712 | 0.60296 | 0.57385 | 0.55323 | 0.51223 | 0.47533 | 0.44563 | 0.41836 | 0.38739 | 0.35926 | 0.29009 | 0.25349 | 0.19712 | 0.12668 | 0.10044 | 0.066317 | 0.02362 | -0.012784 | -0.070811 | -0.12802 | -0.1643 | -0.19833 | -0.23448 | -0.26682 | -0.35557 | -0.40761 | -0.48013
|  | KINLOCHEWE | CT |  |  |  | 0.323 | 0.031822 | 0.01467 | -0.011734 | -0.051886 | -0.087349 | -0.1299 | -0.17879 | -0.21754 | -0.23364 | -0.26236 | -0.28793 | -0.36132 | -0.38933 | -0.4309 | 0.64965 | 0.63376 | 0.61943 | 0.58778 | 0.56504 | 0.53547 | 0.50528 | 0.47466 | 0.46086 | 0.43662 | 0.41357 | 0.34966 | 0.32613 | 0.28603 | 0.12767 | 0.10541 | 0.079039 | 0.032141 | -0.0080629 | -0.056113 | -0.10831 | -0.14355 | -0.16056 | -0.18668 | -0.20971 | -0.28241 | -0.31355 | -0.35815
|  | KINLOCHEWE | LW |  |  |  | 0.323 | 0.034395 | 0.011683 | -0.020514 | -0.056432 | -0.089794 | -0.13877 | -0.19126 | -0.2307 | -0.26535 | -0.30415 | -0.33872 | -0.42552 | -0.47081 | -0.53843 | 0.65065 | 0.62712 | 0.60296 | 0.57385 | 0.55323 | 0.51223 | 0.47533 | 0.44563 | 0.41836 | 0.38739 | 0.35926 | 0.29009 | 0.25349 | 0.19712 | 0.12975 | 0.10044 | 0.066317 | 0.02362 | -0.012784 | -0.070811 | -0.12802 | -0.1643 | -0.19833 | -0.23448 | -0.26682 | -0.35557 | -0.40761 | -0.48013
|  | KINLOCHEWE | ST |  |  |  | 0.323 | 0.020666 | 0.027007 | 0.0079568 | -0.0096671 | -0.026104 | -0.04335 | -0.060597 | -0.0791 | -0.10063 | -0.11809 | -0.14702 | -0.28476 | -0.33851 | -0.36656 | 0.64421 | 0.64774 | 0.63262 | 0.61971 | 0.60872 | 0.59554 | 0.58393 | 0.56579 | 0.5427 | 0.53202 | 0.50945 | 0.39076 | 0.33419 | 0.29239 | 0.12668 | 0.12362 | 0.10346 | 0.08424 | 0.066235 | 0.045982 | 0.026908 | 0.0028753 | -0.026313 | -0.044766 | -0.073873 | -0.21128 | -0.27322 | -0.30913
|  | KINLOCHEWE | FS |  |  |  | 0.323 | 0.029277 | 0.038272 | 0.031685 | 0.025062 | 0.016768 | 0.0095874 | 0.00029305 | -0.015111 | -0.030704 | -0.048527 | -0.071736 | -0.16968 | -0.28187 | -0.31951 | 0.64904 | 0.65348 | 0.64658 | 0.64 | 0.62941 | 0.62252 | 0.61158 | 0.59602 | 0.58277 | 0.56369 | 0.54622 | 0.4723 | 0.38584 | 0.33472 | 0.13391 | 0.13411 | 0.12579 | 0.1178 | 0.10547 | 0.096584 | 0.083614 | 0.063561 | 0.046127 | 0.022214 | -0.00028405 | -0.096719 | -0.20367 | -0.24452
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0.028 | 1.933 | 1.89 | 1.8022 | 1.7378 | 1.6648 | 1.5794 | 1.4697 | 1.4261 | 1.3689 | 1.3125 | 1.2563 | 1.1148 | 1.0439 | 0.9436 | 2.4723 | 2.4475 | 2.3673 | 2.3319 | 2.2951 | 2.2473 | 2.1755 | 2.1447 | 2.0893 | 2.0473 | 2.0049 | 1.9015 | 1.8507 | 1.7743 | 2.2184 | 2.1939 | 2.1302 | 2.0785 | 2.0214 | 1.9474 | 1.8459 | 1.8158 | 1.7833 | 1.7487 | 1.7149 | 1.6043 | 1.5234 | 1.4208
|  | KINLOCHLEVEN | CT |  |  |  | 0.028 | 1.933 | 1.89 | 1.8026 | 1.7378 | 1.6648 | 1.5794 | 1.4697 | 1.4261 | 1.3795 | 1.3368 | 1.2941 | 1.1743 | 1.1216 | 1.0498 | 2.4723 | 2.4497 | 2.3826 | 2.3405 | 2.3005 | 2.2533 | 2.1842 | 2.1507 | 2.1137 | 2.0786 | 2.0415 | 1.9328 | 1.8757 | 1.7819 | 2.2212 | 2.1989 | 2.1409 | 2.0806 | 2.0214 | 1.9474 | 1.8459 | 1.8158 | 1.7871 | 1.764 | 1.7429 | 1.6657 | 1.6096 | 1.5379
|  | KINLOCHLEVEN | LW |  |  |  | 0.028 | 1.9342 | 1.8929 | 1.8022 | 1.7437 | 1.6774 | 1.5945 | 1.4874 | 1.4438 | 1.3689 | 1.3125 | 1.2563 | 1.1148 | 1.0439 | 0.9436 | 2.4734 | 2.4475 | 2.3673 | 2.3319 | 2.2951 | 2.2473 | 2.1755 | 2.1447 | 2.0893 | 2.0473 | 2.0049 | 1.9015 | 1.8507 | 1.7743 | 2.2184 | 2.1939 | 2.1302 | 2.0785 | 2.0245 | 1.9599 | 1.8627 | 1.8305 | 1.7833 | 1.7487 | 1.7149 | 1.6043 | 1.5234 | 1.4208
|  | KINLOCHLEVEN | ST |  |  |  | 0.028 | 1.9448 | 1.9214 | 1.8716 | 1.8418 | 1.8075 | 1.7826 | 1.7452 | 1.7144 | 1.666 | 1.6153 | 1.5861 | 1.3659 | 1.2984 | 1.2733 | 2.4779 | 2.4656 | 2.412 | 2.3913 | 2.3706 | 2.3547 | 2.3347 | 2.3162 | 2.2809 | 2.2436 | 2.2224 | 2.0298 | 1.9403 | 1.8602 | 2.2261 | 2.2174 | 2.1818 | 2.1539 | 2.1265 | 2.103 | 2.0763 | 2.0532 | 2.0229 | 1.9914 | 1.9674 | 1.8227 | 1.7516 | 1.7066
|  | KINLOCHLEVEN | FS |  |  |  | 0.028 | 1.9574 | 1.9414 | 1.9135 | 1.899 | 1.888 | 1.8694 | 1.8579 | 1.8258 | 1.7857 | 1.7579 | 1.7203 | 1.5356 | 1.3502 | 1.2923 | 2.4842 | 2.4755 | 2.4422 | 2.4322 | 2.4239 | 2.4121 | 2.3995 | 2.3746 | 2.3426 | 2.3199 | 2.2909 | 2.1349 | 1.9582 | 1.8189 | 2.2286 | 2.222 | 2.2011 | 2.1893 | 2.1819 | 2.1675 | 2.1611 | 2.1431 | 2.1185 | 2.1061 | 2.0826 | 1.9598 | 1.8343 | 1.7764
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 0 | 0.93927 | 0.92808 | 0.91673 | 0.90471 | 0.89523 | 0.88006 | 0.87147 | 0.87422 | 0.86865 | 0.86771 | 0.86401 | 0.84916 | 0.8251 | 0.79798 | -2.4106 | -2.4233 | -2.4361 | -2.449 | -2.4582 | -2.4735 | -2.472 | -2.4716 | -2.4734 | -2.474 | -2.4753 | -2.4916 | -2.5193 | -2.5501 | 0.9358 | 0.92266 | 0.90901 | 0.8952 | 0.88507 | 0.86832 | 0.86475 | 0.86619 | 0.86239 | 0.8618 | 0.85781 | 0.84086 | 0.81166 | 0.77866
|  | KINLOCHMOIDART | CT |  |  |  | 0 | 0.93927 | 0.93524 | 0.93166 | 0.92 | 0.91234 | 0.90388 | 0.90036 | 0.90206 | 0.89777 | 0.89313 | 0.8927 | 0.87937 | 0.87157 | 0.86116 | -2.4105 | -2.4142 | -2.4172 | -2.4297 | -2.4362 | -2.4436 | -2.436 | -2.4367 | -2.4388 | -2.4409 | -2.442 | -2.451 | -2.4583 | -2.4687 | 0.9358 | 0.93159 | 0.92776 | 0.91441 | 0.90688 | 0.89808 | 0.90091 | 0.90103 | 0.89824 | 0.89333 | 0.89313 | 0.87832 | 0.86949 | 0.85742
|  | KINLOCHMOIDART | LW |  |  |  | 0 | 0.93928 | 0.92808 | 0.91673 | 0.90471 | 0.89523 | 0.88006 | 0.87147 | 0.87422 | 0.86865 | 0.86771 | 0.86401 | 0.84916 | 0.8251 | 0.79798 | -2.4106 | -2.4233 | -2.4361 | -2.449 | -2.4582 | -2.4735 | -2.472 | -2.4716 | -2.4734 | -2.474 | -2.4753 | -2.4916 | -2.5193 | -2.5501 | 0.93586 | 0.92266 | 0.90901 | 0.8952 | 0.88507 | 0.86832 | 0.86475 | 0.86619 | 0.86239 | 0.8618 | 0.85781 | 0.84086 | 0.81166 | 0.77866
|  | KINLOCHMOIDART | ST |  |  |  | 0 | 0.94058 | 0.93913 | 0.93235 | 0.92664 | 0.92184 | 0.91737 | 0.91238 | 0.90691 | 0.90017 | 0.90431 | 0.89927 | 0.87635 | 0.84825 | 0.82418 | -2.4094 | -2.4105 | -2.4181 | -2.424 | -2.4282 | -2.4318 | -2.4359 | -2.4408 | -2.4469 | -2.4322 | -2.4337 | -2.4606 | -2.4924 | -2.5211 | 0.93715 | 0.93555 | 0.92732 | 0.92068 | 0.91585 | 0.9115 | 0.90646 | 0.9009 | 0.89407 | 0.90564 | 0.90005 | 0.87357 | 0.83961 | 0.81008
|  | KINLOCHMOIDART | FS |  |  |  | 0 | 0.94094 | 0.93981 | 0.93692 | 0.93373 | 0.93043 | 0.92682 | 0.9221 | 0.9176 | 0.91147 | 0.90512 | 0.90067 | 0.90302 | 0.89477 | 0.88873 | -2.4092 | -2.4102 | -2.4133 | -2.4168 | -2.4204 | -2.4242 | -2.4294 | -2.434 | -2.4404 | -2.4469 | -2.4507 | -2.4354 | -2.4379 | -2.4431 | 0.93765 | 0.93643 | 0.93307 | 0.92941 | 0.92564 | 0.92157 | 0.91618 | 0.91112 | 0.90424 | 0.89728 | 0.89304 | 0.90347 | 0.89648 | 0.89005
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.109 | 11.63 | 11.5076 | 11.3183 | 11.057 | 10.8166 | 10.5441 | 10.195 | 9.9329 | 9.708 | 9.4914 | 9.2413 | 8.4888 | 7.8415 | 7.5395 | 12.5292 | 12.4549 | 12.3724 | 12.1745 | 12.0168 | 11.8468 | 11.594 | 11.3564 | 11.1721 | 10.957 | 10.6986 | 9.766 | 9.2026 | 9.0273 | 11.932 | 11.8143 | 11.6429 | 11.3988 | 11.1813 | 10.9328 | 10.6058 | 10.357 | 10.1436 | 9.924 | 9.6335 | 8.7394 | 8.0465 | 7.8397
|  | KINLOSS | CT |  |  |  | 0.109 | 11.63 | 11.5076 | 11.3183 | 11.057 | 10.8166 | 10.5441 | 10.195 | 9.9329 | 9.708 | 9.4914 | 9.2994 | 8.7509 | 8.4453 | 8.209 | 12.5292 | 12.4647 | 12.3822 | 12.1745 | 12.0168 | 11.8468 | 11.594 | 11.3564 | 11.1721 | 10.9826 | 10.8142 | 10.4297 | 10.3948 | 10.3392 | 11.932 | 11.8143 | 11.6429 | 11.3988 | 11.1813 | 10.9328 | 10.6058 | 10.357 | 10.1436 | 9.9341 | 9.7503 | 9.2283 | 8.9806 | 8.7699
|  | KINLOSS | LW |  |  |  | 0.109 | 11.6377 | 11.517 | 11.3477 | 11.1401 | 10.9472 | 10.6709 | 10.3575 | 10.1013 | 9.7889 | 9.5037 | 9.2413 | 8.4888 | 8.2552 | 8.0603 | 12.5305 | 12.4549 | 12.3724 | 12.2623 | 12.1811 | 11.9879 | 11.7522 | 11.527 | 11.2301 | 10.957 | 10.6986 | 10.0485 | 9.9084 | 9.7761 | 11.939 | 11.8192 | 11.6628 | 11.4691 | 11.2957 | 11.0359 | 10.7372 | 10.4955 | 10.1944 | 9.924 | 9.6335 | 8.8099 | 8.5815 | 8.3891
|  | KINLOSS | ST |  |  |  | 0.109 | 11.671 | 11.6099 | 11.5298 | 11.4358 | 11.3412 | 11.2275 | 11.1166 | 10.9792 | 10.8052 | 10.6141 | 10.4194 | 8.5986 | 7.8415 | 7.5395 | 12.5502 | 12.5215 | 12.4802 | 12.4247 | 12.3754 | 12.2774 | 12.1492 | 11.987 | 11.7705 | 11.5314 | 11.2688 | 9.766 | 9.2026 | 9.0273 | 11.9712 | 11.9153 | 11.839 | 11.749 | 11.6601 | 11.5519 | 11.4469 | 11.3125 | 11.1451 | 10.9309 | 10.6117 | 8.7394 | 8.0465 | 7.8397
|  | KINLOSS | FS |  |  |  | 0.109 | 11.6985 | 11.6584 | 11.6076 | 11.5594 | 11.497 | 11.4355 | 11.3576 | 11.2669 | 11.1412 | 11.0156 | 10.8779 | 9.9396 | 8.7118 | 7.8594 | 12.5577 | 12.5388 | 12.5074 | 12.4829 | 12.4445 | 12.4088 | 12.3504 | 12.2629 | 12.1411 | 12.0151 | 11.8753 | 10.928 | 9.9654 | 9.3216 | 11.9949 | 11.9583 | 11.9097 | 11.864 | 11.8037 | 11.7449 | 11.6678 | 11.583 | 11.4628 | 11.3434 | 11.2134 | 10.1832 | 8.9741 | 8.1733
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 1.195 | 1.2079 | 1.0421 | 0.78479 | 0.47542 | 0.1226 | -0.23307 | -0.66723 | -0.87701 | -1.0174 | -1.2508 | -1.464 | -2.2066 | -2.7376 | -3.2603 | 3.4712 | 3.3735 | 3.2629 | 3.1212 | 2.9523 | 2.7979 | 2.5792 | 2.4211 | 2.3249 | 2.1141 | 1.9561 | 1.5486 | 1.257 | 0.92398 | 2.5415 | 2.4015 | 2.2154 | 1.9564 | 1.6726 | 1.3836 | 1.0247 | 0.82192 | 0.68117 | 0.46392 | 0.26206 | -0.39707 | -0.86596 | -1.0561
|  | KIPPEN | CT |  |  |  | 1.195 | 1.2079 | 1.0421 | 0.78479 | 0.47542 | 0.1226 | -0.23307 | -0.66723 | -0.87701 | -1.0174 | -1.2343 | -1.3709 | -1.9888 | -2.4776 | -2.9639 | 3.4712 | 3.3735 | 3.2629 | 3.1212 | 2.9523 | 2.7979 | 2.5792 | 2.4211 | 2.3249 | 2.1474 | 2.0231 | 1.6025 | 1.3113 | 0.92398 | 2.5415 | 2.4015 | 2.2154 | 1.9564 | 1.6726 | 1.3836 | 1.0247 | 0.82192 | 0.68117 | 0.4752 | 0.35048 | -0.11341 | -0.42257 | -0.71588
|  | KIPPEN | LW |  |  |  | 1.195 | 1.2321 | 1.0835 | 0.8536 | 0.57317 | 0.26433 | -0.089775 | -0.49581 | -0.72953 | -0.96321 | -1.2508 | -1.464 | -2.2066 | -2.7376 | -3.2603 | 3.4784 | 3.3902 | 3.2994 | 3.1709 | 3.0353 | 2.8724 | 2.6645 | 2.499 | 2.3345 | 2.1141 | 1.9561 | 1.5486 | 1.3337 | 1.0891 | 2.5533 | 2.4299 | 2.2787 | 2.0658 | 1.8268 | 1.534 | 1.1987 | 0.98171 | 0.74418 | 0.46392 | 0.26206 | -0.33709 | -0.68449 | -0.98165
|  | KIPPEN | ST |  |  |  | 1.195 | 1.2528 | 1.1441 | 0.99333 | 0.83849 | 0.66551 | 0.49966 | 0.31762 | 0.13902 | -0.040098 | -0.30524 | -0.52429 | -1.5513 | -2.0591 | -2.274 | 3.4967 | 3.4491 | 3.3788 | 3.3046 | 3.2144 | 3.1346 | 3.0357 | 2.9252 | 2.8209 | 2.6373 | 2.49 | 1.6066 | 1.257 | 1.121 | 2.5777 | 2.5014 | 2.3923 | 2.2725 | 2.125 | 1.9714 | 1.7992 | 1.6222 | 1.4229 | 1.1288 | 0.8665 | -0.39707 | -0.86596 | -1.0561
|  | KIPPEN | FS |  |  |  | 1.195 | 1.3171 | 1.2446 | 1.1928 | 1.1318 | 1.0579 | 0.97628 | 0.90929 | 0.77811 | 0.62538 | 0.44167 | 0.30712 | -0.56209 | -1.5291 | -2.1402 | 3.5126 | 3.4747 | 3.4428 | 3.4026 | 3.3505 | 3.2911 | 3.2445 | 3.1641 | 3.0621 | 2.934 | 2.8544 | 2.2385 | 1.5318 | 0.93014 | 2.6158 | 2.5668 | 2.5176 | 2.4582 | 2.3872 | 2.3059 | 2.226 | 2.1055 | 1.9562 | 1.7729 | 1.6207 | 0.60891 | -0.37598 | -0.94558
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 5.991 | 7.1418 | 3.8655 | 1.1362 | -1.73 | -4.2207 | -7.929 | -11.2165 | -11.8571 | -12.9121 | -14.0284 | -14.9463 | -20.1703 | -25.7983 | -31.0879 | 14.4424 | 11.105 | 8.5995 | 5.9 | 3.7348 | 0.20852 | -2.8773 | -3.2153 | -4.0155 | -4.9217 | -5.6503 | -10.4985 | -16.4009 | -22.1217 | 10.2144 | 6.8378 | 4.2422 | 1.5837 | -0.53468 | -4.0107 | -7.6574 | -8.246 | -9.3288 | -10.4785 | -11.4336 | -17.008 | -23.3099 | -29.5498
|  | KIRKWALL | CT |  |  |  | 5.991 | 7.3662 | 5.5595 | 4.2637 | 1.4132 | -0.50972 | -3.4423 | -6.0454 | -6.8327 | -7.9345 | -9.0771 | -10.0032 | -14.2315 | -17.2446 | -19.6529 | 14.8132 | 13.3413 | 12.4525 | 9.7524 | 8.2914 | 5.7972 | 3.6104 | 3.0927 | 2.1516 | 1.1179 | 0.25778 | -3.3857 | -6.1646 | -8.6807 | 10.5416 | 8.9893 | 8.0981 | 5.3861 | 3.9511 | 1.5197 | -1.2083 | -1.9352 | -3.0682 | -4.2573 | -5.251 | -9.5824 | -12.669 | -15.2918
|  | KIRKWALL | LW |  |  |  | 5.991 | 7.1418 | 3.8655 | 1.1362 | -1.73 | -4.2207 | -7.929 | -11.2165 | -11.8571 | -12.9121 | -14.0284 | -14.9463 | -20.1703 | -25.7983 | -31.0879 | 14.4424 | 11.105 | 8.5995 | 5.9 | 3.7348 | 0.20852 | -2.8773 | -3.2153 | -4.0155 | -4.9217 | -5.6503 | -10.4985 | -16.4009 | -22.1217 | 10.2144 | 6.8378 | 4.2422 | 1.5837 | -0.53468 | -4.0107 | -7.6574 | -8.246 | -9.3288 | -10.4785 | -11.4336 | -17.008 | -23.3099 | -29.5498
|  | KIRKWALL | ST |  |  |  | 5.991 | 7.5439 | 5.8795 | 3.8771 | 1.9611 | 0.26688 | -1.985 | -3.1698 | -4.1198 | -5.3175 | -6.6243 | -7.6647 | -14.7899 | -21.1525 | -26.0898 | 14.8571 | 13.4699 | 11.6961 | 9.9972 | 8.5677 | 6.5426 | 5.6768 | 4.9712 | 3.9904 | 2.905 | 2.1339 | -4.9612 | -11.5495 | -17.0885 | 10.6319 | 9.2028 | 7.3936 | 5.7305 | 4.3248 | 2.3917 | 1.5209 | 0.7062 | -0.4751 | -1.7726 | -2.7769 | -10.6755 | -17.7776 | -23.4185
|  | KIRKWALL | FS |  |  |  | 5.991 | 8.2488 | 7.0754 | 6.2452 | 5.2375 | 4.109 | 2.1579 | 1.2172 | 0.27335 | -0.86847 | -2.0718 | -2.9499 | -7.5951 | -11.7989 | -13.9609 | 15.2664 | 14.2492 | 13.4531 | 12.4782 | 11.3568 | 9.2708 | 8.3485 | 7.6821 | 6.6963 | 5.6336 | 4.9766 | 1.3016 | -1.6809 | -4.0686 | 11.1122 | 10.0803 | 9.2885 | 8.3144 | 7.201 | 5.2366 | 4.253 | 3.4646 | 2.4383 | 1.3512 | 0.66548 | -3.1893 | -6.9477 | -9.1584
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0.631 | -0.6017 | -0.61054 | -0.63193 | -0.65385 | -0.67259 | -0.7016 | -0.73312 | -0.74893 | -0.76811 | -0.77301 | -0.7859 | -0.82692 | -0.85969 | -0.89996 | -0.42466 | -0.43177 | -0.44848 | -0.4649 | -0.47699 | -0.49854 | -0.52309 | -0.53582 | -0.55181 | -0.55509 | -0.56599 | -0.60175 | -0.63338 | -0.6731 | -0.54261 | -0.55873 | -0.58055 | -0.60243 | -0.61938 | -0.64879 | -0.68044 | -0.69824 | -0.72032 | -0.72193 | -0.73614 | -0.77844 | -0.81361 | -0.85697
|  | KISHORNHILL | CT |  |  |  | 0.631 | -0.6017 | -0.60529 | -0.62121 | -0.64429 | -0.66442 | -0.6873 | -0.71534 | -0.73077 | -0.74196 | -0.75402 | -0.75282 | -0.78267 | -0.79855 | -0.8202 | -0.42464 | -0.42357 | -0.4317 | -0.44818 | -0.45934 | -0.47257 | -0.49107 | -0.50474 | -0.51513 | -0.52675 | -0.52679 | -0.55548 | -0.56979 | -0.59228 | -0.54261 | -0.5513 | -0.56553 | -0.58759 | -0.60548 | -0.62624 | -0.65264 | -0.67082 | -0.68418 | -0.69907 | -0.69499 | -0.7274 | -0.74189 | -0.76251
|  | KISHORNHILL | LW |  |  |  | 0.631 | -0.60097 | -0.61054 | -0.63193 | -0.65385 | -0.67259 | -0.7016 | -0.73312 | -0.74893 | -0.76811 | -0.77301 | -0.7859 | -0.82692 | -0.85969 | -0.89996 | -0.42466 | -0.43177 | -0.44848 | -0.4649 | -0.47699 | -0.49854 | -0.52309 | -0.53582 | -0.55181 | -0.55509 | -0.56599 | -0.60175 | -0.63338 | -0.6731 | -0.54214 | -0.55873 | -0.58055 | -0.60243 | -0.61938 | -0.64879 | -0.68044 | -0.69824 | -0.72032 | -0.72193 | -0.73614 | -0.77844 | -0.81361 | -0.85697
|  | KISHORNHILL | ST |  |  |  | 0.631 | -0.59184 | -0.60386 | -0.61305 | -0.61979 | -0.6289 | -0.63691 | -0.64934 | -0.65782 | -0.67005 | -0.67943 | -0.69314 | -0.76014 | -0.79924 | -0.82593 | -0.41582 | -0.42525 | -0.43099 | -0.43548 | -0.44158 | -0.44642 | -0.45522 | -0.46089 | -0.46986 | -0.47644 | -0.48659 | -0.54771 | -0.59022 | -0.62549 | -0.53319 | -0.5442 | -0.56029 | -0.56545 | -0.57407 | -0.58113 | -0.59424 | -0.60197 | -0.61442 | -0.62304 | -0.63762 | -0.70837 | -0.75135 | -0.78217
|  | KISHORNHILL | FS |  |  |  | 0.631 | -0.58803 | -0.59719 | -0.60829 | -0.60024 | -0.60774 | -0.61246 | -0.61754 | -0.62817 | -0.63707 | -0.64753 | -0.65788 | -0.70754 | -0.74619 | -0.76521 | -0.41407 | -0.4217 | -0.43242 | -0.42292 | -0.42967 | -0.43389 | -0.43879 | -0.44723 | -0.45433 | -0.46279 | -0.4704 | -0.50739 | -0.53547 | -0.55937 | -0.53015 | -0.53869 | -0.54974 | -0.54671 | -0.55569 | -0.56054 | -0.56569 | -0.57733 | -0.58595 | -0.59661 | -0.60762 | -0.65777 | -0.68989 | -0.70604
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0.041 | 4.7538 | 5.9199 | 5.8975 | 5.8215 | 5.7233 | 5.6094 | 5.4846 | 5.3895 | 5.2944 | 5.1957 | 5.1065 | 4.9217 | 4.83 | 4.6905 | 4.8275 | 6.4771 | 6.4252 | 6.3761 | 6.3198 | 6.2468 | 6.1658 | 6.0976 | 6.0187 | 5.945 | 5.8777 | 5.7464 | 5.684 | 5.5808 | 4.3198 | 5.9614 | 5.8874 | 5.7981 | 5.7033 | 5.5956 | 5.4742 | 5.4144 | 5.3603 | 5.3007 | 5.2479 | 5.098 | 4.9931 | 4.8742
|  | KYLE | CT |  |  |  | 0.041 | 4.7544 | 5.9269 | 5.9146 | 5.8215 | 5.7233 | 5.6094 | 5.4846 | 5.3895 | 5.3254 | 5.251 | 5.1846 | 5.0249 | 4.9494 | 4.8485 | 4.8275 | 6.4778 | 6.4391 | 6.3769 | 6.3198 | 6.2529 | 6.1777 | 6.1065 | 6.0574 | 5.998 | 5.9426 | 5.8047 | 5.7266 | 5.6005 | 4.3198 | 5.9614 | 5.8925 | 5.7981 | 5.7033 | 5.5956 | 5.4742 | 5.4144 | 5.3751 | 5.3336 | 5.3001 | 5.1853 | 5.1049 | 5.0153
|  | KYLE | LW |  |  |  | 0.041 | 4.7538 | 5.9199 | 5.8975 | 5.8336 | 5.7516 | 5.6233 | 5.4968 | 5.4017 | 5.2944 | 5.1957 | 5.1065 | 4.9217 | 4.83 | 4.6905 | 4.8293 | 6.4771 | 6.4252 | 6.3761 | 6.3289 | 6.2468 | 6.1658 | 6.0976 | 6.0187 | 5.945 | 5.8777 | 5.7464 | 5.684 | 5.5808 | 4.3277 | 5.9658 | 5.8874 | 5.806 | 5.7215 | 5.6079 | 5.4878 | 5.4257 | 5.3603 | 5.3007 | 5.2479 | 5.098 | 4.9931 | 4.8742
|  | KYLE | ST |  |  |  | 0.041 | 4.7586 | 5.9434 | 5.9305 | 5.9188 | 5.9049 | 5.8678 | 5.8114 | 5.7636 | 5.6922 | 5.6406 | 5.5656 | 5.2313 | 5.168 | 5.1401 | 4.8352 | 6.5122 | 6.4831 | 6.4559 | 6.4236 | 6.3991 | 6.3608 | 6.3278 | 6.2766 | 6.2399 | 6.1854 | 5.904 | 5.8134 | 5.7183 | 4.3331 | 5.9944 | 5.9541 | 5.9151 | 5.8735 | 5.837 | 5.7914 | 5.7511 | 5.6984 | 5.6544 | 5.5995 | 5.3697 | 5.2954 | 5.2645
|  | KYLE | FS |  |  |  | 0.041 | 4.7605 | 5.9451 | 5.9392 | 5.9316 | 5.9214 | 5.9094 | 5.9004 | 5.8858 | 5.8697 | 5.8291 | 5.7741 | 5.4983 | 5.2454 | 5.1286 | 4.8374 | 6.5218 | 6.5113 | 6.4971 | 6.4778 | 6.4552 | 6.4388 | 6.4054 | 6.3722 | 6.3312 | 6.2899 | 6.0672 | 5.8348 | 5.6238 | 4.3545 | 6.0251 | 6.0167 | 6.0058 | 5.9916 | 5.9753 | 5.963 | 5.9268 | 5.89 | 5.8483 | 5.8075 | 5.6053 | 5.3863 | 5.2785
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 0.078 | -0.47392 | -0.55604 | -0.65023 | -0.781 | -0.90671 | -1.059 | -1.2284 | -1.324 | -1.3981 | -1.493 | -1.5523 | -1.8264 | -1.9649 | -2.0993 | 0.036528 | -0.01365 | -0.058664 | -0.12389 | -0.18321 | -0.26302 | -0.34305 | -0.41402 | -0.49379 | -0.56979 | -0.60439 | -0.76685 | -0.83641 | -0.92366 | -0.15083 | -0.2255 | -0.29931 | -0.40981 | -0.51325 | -0.6387 | -0.77018 | -0.86351 | -0.96279 | -1.0622 | -1.1049 | -1.3485 | -1.4724 | -1.6009
|  | LAIRG | CT |  |  |  | 0.078 | -0.47392 | -0.55604 | -0.65023 | -0.781 | -0.90671 | -1.059 | -1.2284 | -1.324 | -1.3981 | -1.4744 | -1.5061 | -1.7252 | -1.8293 | -1.9349 | 0.04195 | -0.0074578 | -0.050039 | -0.12124 | -0.18321 | -0.26061 | -0.34305 | -0.41402 | -0.47033 | -0.53152 | -0.55485 | -0.70713 | -0.77566 | -0.88638 | -0.15083 | -0.2255 | -0.29931 | -0.40981 | -0.51325 | -0.6387 | -0.77018 | -0.86351 | -0.93749 | -1.0147 | -1.0388 | -1.2434 | -1.3313 | -1.4261
|  | LAIRG | LW |  |  |  | 0.078 | -0.47369 | -0.54913 | -0.64153 | -0.75897 | -0.87124 | -1.0251 | -1.1811 | -1.2739 | -1.3892 | -1.493 | -1.5523 | -1.8264 | -1.9649 | -2.0993 | 0.036528 | -0.01365 | -0.058664 | -0.12389 | -0.17508 | -0.26302 | -0.34302 | -0.40753 | -0.49379 | -0.56979 | -0.60439 | -0.76685 | -0.83641 | -0.92366 | -0.14996 | -0.22282 | -0.29916 | -0.40417 | -0.49375 | -0.63181 | -0.7598 | -0.84908 | -0.96279 | -1.0622 | -1.1049 | -1.3485 | -1.4724 | -1.6009
|  | LAIRG | ST |  |  |  | 0.078 | -0.44745 | -0.49922 | -0.56482 | -0.63797 | -0.70439 | -0.78635 | -0.86476 | -0.94273 | -1.0284 | -1.0981 | -1.184 | -1.5762 | -1.7461 | -1.8242 | 0.058124 | 0.032152 | 0.00052095 | -0.038814 | -0.067599 | -0.11163 | -0.15103 | -0.1998 | -0.25725 | -0.29366 | -0.3468 | -0.62096 | -0.7517 | -0.85393 | -0.12608 | -0.16995 | -0.22425 | -0.28918 | -0.33995 | -0.40963 | -0.4725 | -0.54337 | -0.62546 | -0.67938 | -0.75509 | -1.1057 | -1.2633 | -1.335
|  | LAIRG | FS |  |  |  | 0.078 | -0.4037 | -0.43621 | -0.46255 | -0.4861 | -0.51928 | -0.54241 | -0.5807 | -0.63145 | -0.69693 | -0.7632 | -0.81557 | -1.1955 | -1.553 | -1.7225 | 0.078903 | 0.061282 | 0.04265 | 0.02671 | 0.0017195 | -0.012079 | -0.042199 | -0.070968 | -0.1146 | -0.1589 | -0.18526 | -0.44224 | -0.68501 | -0.89676 | -0.09288 | -0.12139 | -0.14624 | -0.16813 | -0.20028 | -0.21797 | -0.25516 | -0.29773 | -0.35882 | -0.4208 | -0.45865 | -0.79808 | -1.0869 | -1.2354
| MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0.13 | 0.89879 | 0.79367 | 0.65511 | 0.48338 | 0.30627 | 0.10266 | -0.13231 | -0.2476 | -0.33759 | -0.44344 | -0.53658 | -0.84186 | -1.0336 | -1.2248 | 1.5806 | 1.5262 | 1.4577 | 1.3767 | 1.2945 | 1.1962 | 1.0737 | 0.99771 | 0.93341 | 0.86092 | 0.79592 | 0.61909 | 0.5276 | 0.41692 | 1.2364 | 1.1401 | 1.0295 | 0.88578 | 0.74911 | 0.58129 | 0.37644 | 0.23752 | 0.13043 | 0.0013783 | -0.11344 | -0.39929 | -0.53645 | -0.71926
|  | LATHERON | CT |  |  |  | 0.13 | 0.89879 | 0.79367 | 0.65511 | 0.48338 | 0.30627 | 0.10266 | -0.13231 | -0.2476 | -0.31475 | -0.39339 | -0.45643 | -0.74585 | -0.91823 | -1.0815 | 1.5806 | 1.5262 | 1.4632 | 1.3767 | 1.2972 | 1.2015 | 1.0844 | 1.0065 | 0.96993 | 0.91203 | 0.86093 | 0.67214 | 0.56422 | 0.42064 | 1.2364 | 1.1401 | 1.0295 | 0.88578 | 0.74911 | 0.58129 | 0.37644 | 0.23752 | 0.18148 | 0.079416 | -0.010233 | -0.29757 | -0.41363 | -0.5506
|  | LATHERON | LW |  |  |  | 0.13 | 0.91723 | 0.82114 | 0.66907 | 0.50457 | 0.32545 | 0.12201 | -0.11307 | -0.23182 | -0.33759 | -0.44344 | -0.53658 | -0.84186 | -1.0336 | -1.2248 | 1.5865 | 1.5329 | 1.4577 | 1.3786 | 1.2945 | 1.1962 | 1.0737 | 0.99771 | 0.93341 | 0.86092 | 0.79592 | 0.61909 | 0.5276 | 0.41692 | 1.2458 | 1.1581 | 1.031 | 0.89703 | 0.75254 | 0.58637 | 0.37781 | 0.24006 | 0.13043 | 0.0013783 | -0.11344 | -0.39929 | -0.53645 | -0.71926
|  | LATHERON | ST |  |  |  | 0.13 | 0.9301 | 0.85189 | 0.74413 | 0.63809 | 0.5256 | 0.41725 | 0.29844 | 0.20821 | 0.098209 | -0.0089847 | -0.12352 | -0.58822 | -0.81824 | -0.94669 | 1.5972 | 1.5609 | 1.5099 | 1.4618 | 1.4076 | 1.3573 | 1.2974 | 1.2535 | 1.1903 | 1.1289 | 1.0611 | 0.7564 | 0.59415 | 0.45999 | 1.2669 | 1.2034 | 1.1181 | 1.037 | 0.9431 | 0.85673 | 0.75277 | 0.68057 | 0.57259 | 0.47123 | 0.35308 | -0.12193 | -0.31127 | -0.42788
|  | LATHERON | FS |  |  |  | 0.13 | 0.98572 | 0.93677 | 0.90478 | 0.86676 | 0.83555 | 0.79515 | 0.7586 | 0.67664 | 0.59967 | 0.51224 | 0.42916 | -0.025937 | -0.52324 | -0.71338 | 1.6182 | 1.5936 | 1.5745 | 1.5496 | 1.5318 | 1.5047 | 1.4799 | 1.4337 | 1.3924 | 1.3405 | 1.2927 | 1.0157 | 0.68989 | 0.46034 | 1.3048 | 1.2625 | 1.2318 | 1.1903 | 1.1639 | 1.1198 | 1.0832 | 1.0077 | 0.94502 | 0.86166 | 0.78597 | 0.35319 | -0.094136 | -0.23487
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 3.202 | 6.005 | 5.841 | 5.4818 | 5.0696 | 4.5899 | 4.0796 | 3.3494 | 2.6259 | 1.6754 | 1.0766 | 0.77966 | -0.056401 | -0.61159 | -1.0908 | 7.0351 | 6.9313 | 6.7497 | 6.5455 | 6.2998 | 6.0427 | 5.609 | 5.0892 | 4.3659 | 3.9634 | 3.7449 | 3.3919 | 3.0498 | 2.6306 | 6.8629 | 6.7036 | 6.3925 | 6.0285 | 5.6025 | 5.1488 | 4.4947 | 3.8292 | 2.9293 | 2.3688 | 2.1128 | 1.3734 | 0.91809 | 0.49459
|  | LAURENCEKIRK | CT |  |  |  | 3.202 | 6.005 | 5.841 | 5.4818 | 5.0696 | 4.5899 | 4.0796 | 3.3494 | 2.6259 | 1.8149 | 1.2261 | 0.77966 | 0.029317 | -0.61159 | -1.0908 | 7.0351 | 6.9313 | 6.7497 | 6.5455 | 6.2998 | 6.0427 | 5.609 | 5.1105 | 4.511 | 4.0895 | 3.7449 | 3.4102 | 3.0498 | 2.6306 | 6.8629 | 6.7036 | 6.3925 | 6.0285 | 5.6025 | 5.1488 | 4.4947 | 3.8292 | 3.0843 | 2.5398 | 2.1128 | 1.481 | 0.91809 | 0.49459
|  | LAURENCEKIRK | LW |  |  |  | 3.202 | 6.0209 | 5.8674 | 5.5162 | 5.1182 | 4.676 | 4.1583 | 3.4222 | 2.6464 | 1.6754 | 1.0766 | 0.88662 | -0.056401 | -0.5534 | -1.0266 | 7.0404 | 6.9394 | 6.7654 | 6.5732 | 6.3588 | 6.0777 | 5.6187 | 5.0892 | 4.3659 | 3.9634 | 3.8882 | 3.3919 | 3.1733 | 2.93 | 6.8748 | 6.7219 | 6.4188 | 6.07 | 5.6819 | 5.2111 | 4.5455 | 3.834 | 2.9293 | 2.3688 | 2.2371 | 1.3734 | 0.93483 | 0.50869
|  | LAURENCEKIRK | ST |  |  |  | 3.202 | 6.0599 | 5.9618 | 5.7677 | 5.5797 | 5.3743 | 5.1634 | 4.8029 | 4.3249 | 3.6544 | 3.2091 | 2.7925 | 1.8096 | 1.0607 | 0.47171 | 7.0682 | 7.0196 | 6.9122 | 6.8114 | 6.6962 | 6.5697 | 6.3139 | 5.9385 | 5.3939 | 5.0552 | 4.7234 | 4.0862 | 3.6137 | 3.16 | 6.9151 | 6.8282 | 6.6583 | 6.496 | 6.3156 | 6.1263 | 5.7982 | 5.3602 | 4.7385 | 4.3324 | 3.9346 | 3.0278 | 2.3354 | 1.8031
|  | LAURENCEKIRK | FS |  |  |  | 3.202 | 6.1278 | 6.0575 | 5.9621 | 5.8637 | 5.7489 | 5.6407 | 5.4107 | 5.0808 | 4.5964 | 4.2454 | 3.8928 | 2.4371 | 1.5201 | 0.74177 | 7.0951 | 7.0542 | 6.9935 | 6.9304 | 6.8513 | 6.775 | 6.5892 | 6.3521 | 5.9699 | 5.7073 | 5.4334 | 4.3538 | 3.6779 | 2.8753 | 6.9714 | 6.9074 | 6.822 | 6.7341 | 6.6271 | 6.525 | 6.3114 | 6.0282 | 5.5843 | 5.262 | 4.9322 | 3.5817 | 2.7821 | 2.0999
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0.065 | -0.81171 | -0.87584 | -0.98938 | -1.1089 | -1.2351 | -1.3858 | -1.5813 | -1.7648 | -1.9153 | -2.0897 | -2.2477 | -2.736 | -2.9938 | -3.2496 | -0.16422 | -0.21026 | -0.28328 | -0.3579 | -0.43345 | -0.52602 | -0.64626 | -0.7486 | -0.8398 | -0.93927 | -1.0301 | -1.2935 | -1.4349 | -1.5909 | -0.3906 | -0.45342 | -0.57322 | -0.6997 | -0.83283 | -0.98951 | -1.1865 | -1.3575 | -1.5141 | -1.6764 | -1.8236 | -2.2762 | -2.518 | -2.768
|  | LAXAY | CT |  |  |  | 0.065 | -0.81171 | -0.87332 | -0.96968 | -1.1089 | -1.2321 | -1.3858 | -1.5813 | -1.7648 | -1.889 | -2.0293 | -2.1518 | -2.6746 | -2.9938 | -3.1906 | -0.16422 | -0.20168 | -0.25621 | -0.34696 | -0.41767 | -0.50737 | -0.62643 | -0.72967 | -0.79269 | -0.87528 | -0.95023 | -1.2329 | -1.4072 | -1.5768 | -0.3906 | -0.44806 | -0.54791 | -0.69438 | -0.82551 | -0.98574 | -1.1865 | -1.3563 | -1.4695 | -1.6003 | -1.7152 | -2.1918 | -2.4775 | -2.6586
|  | LAXAY | LW |  |  |  | 0.065 | -0.80692 | -0.87584 | -0.98938 | -1.1088 | -1.2351 | -1.3838 | -1.5723 | -1.7527 | -1.9153 | -2.0897 | -2.2477 | -2.736 | -2.9907 | -3.2496 | -0.16072 | -0.21026 | -0.28328 | -0.3579 | -0.43345 | -0.52602 | -0.64626 | -0.7486 | -0.8398 | -0.93927 | -1.0301 | -1.2935 | -1.4349 | -1.5909 | -0.385 | -0.45342 | -0.57322 | -0.6997 | -0.83283 | -0.98951 | -1.1829 | -1.3575 | -1.5141 | -1.6764 | -1.8236 | -2.2762 | -2.518 | -2.768
|  | LAXAY | ST |  |  |  | 0.065 | -0.78024 | -0.81671 | -0.86723 | -0.91336 | -0.97039 | -1.0194 | -1.0853 | -1.1314 | -1.2125 | -1.2895 | -1.379 | -1.9241 | -2.2761 | -2.5494 | -0.14597 | -0.16819 | -0.20392 | -0.23533 | -0.27204 | -0.30229 | -0.34329 | -0.37416 | -0.42671 | -0.4774 | -0.53496 | -0.90342 | -1.1607 | -1.3925 | -0.36135 | -0.39658 | -0.44949 | -0.49782 | -0.55315 | -0.60124 | -0.66244 | -0.70743 | -0.77896 | -0.8481 | -0.92583 | -1.4462 | -1.824 | -2.1208
|  | LAXAY | FS |  |  |  | 0.065 | -0.76891 | -0.7965 | -0.82493 | -0.8633 | -0.88918 | -0.93093 | -0.96776 | -1.0316 | -1.0845 | -1.1569 | -1.2235 | -1.6504 | -2.1143 | -2.499 | -0.14031 | -0.1573 | -0.17633 | -0.20162 | -0.2205 | -0.24893 | -0.27676 | -0.31876 | -0.35573 | -0.40435 | -0.44785 | -0.73413 | -1.088 | -1.4304 | -0.34951 | -0.37588 | -0.40414 | -0.43985 | -0.46708 | -0.50604 | -0.54245 | -0.60423 | -0.65901 | -0.7281 | -0.79168 | -1.2029 | -1.6692 | -2.0341
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0.276 | -2.3391 | -2.436 | -2.611 | -2.8207 | -3.0538 | -3.29 | -3.6037 | -3.8654 | -4.1159 | -4.362 | -4.5829 | -5.2406 | -5.6265 | -5.9327 | -1.1363 | -1.2081 | -1.2979 | -1.4101 | -1.5194 | -1.6533 | -1.8291 | -1.9801 | -2.1297 | -2.2856 | -2.4267 | -2.7838 | -2.9952 | -3.2878 | -1.5274 | -1.627 | -1.7866 | -1.9809 | -2.1835 | -2.4128 | -2.7026 | -2.9586 | -3.1919 | -3.4281 | -3.6404 | -4.2467 | -4.5359 | -4.8184
|  | LEOCH | CT |  |  |  | 0.276 | -2.3391 | -2.4339 | -2.5979 | -2.8135 | -3.0538 | -3.29 | -3.6037 | -3.8654 | -4.0496 | -4.2465 | -4.4167 | -5.1625 | -5.6265 | -5.9327 | -1.1363 | -1.1994 | -1.2774 | -1.395 | -1.5194 | -1.631 | -1.8017 | -1.9555 | -2.0519 | -2.182 | -2.3015 | -2.7335 | -2.9952 | -3.2878 | -1.5274 | -1.6199 | -1.7655 | -1.9643 | -2.1835 | -2.3951 | -2.6864 | -2.9353 | -3.0998 | -3.289 | -3.4548 | -4.1316 | -4.5288 | -4.8013
|  | LEOCH | LW |  |  |  | 0.276 | -2.3327 | -2.436 | -2.611 | -2.8207 | -3.039 | -3.289 | -3.594 | -3.8654 | -4.1159 | -4.362 | -4.5829 | -5.2406 | -5.5595 | -5.8555 | -1.1325 | -1.2081 | -1.2979 | -1.4101 | -1.5193 | -1.6533 | -1.8291 | -1.9801 | -2.1297 | -2.2856 | -2.4267 | -2.7838 | -2.9419 | -3.119 | -1.522 | -1.627 | -1.7866 | -1.9809 | -2.1791 | -2.4128 | -2.7026 | -2.9586 | -3.1919 | -3.4281 | -3.6404 | -4.2467 | -4.5359 | -4.8184
|  | LEOCH | ST |  |  |  | 0.276 | -2.3053 | -2.3549 | -2.4295 | -2.4979 | -2.5738 | -2.6361 | -2.7149 | -2.8011 | -2.8771 | -2.9801 | -3.0902 | -3.8012 | -4.3149 | -4.7663 | -1.1163 | -1.1445 | -1.1954 | -1.2403 | -1.2912 | -1.3297 | -1.3838 | -1.4477 | -1.5056 | -1.589 | -1.6833 | -2.2373 | -2.5872 | -2.9347 | -1.4948 | -1.54 | -1.6128 | -1.6786 | -1.7523 | -1.811 | -1.8886 | -1.9753 | -2.0538 | -2.1598 | -2.273 | -2.9667 | -3.4402 | -3.8381
|  | LEOCH | FS |  |  |  | 0.276 | -2.2847 | -2.3234 | -2.3605 | -2.402 | -2.4511 | -2.4897 | -2.5457 | -2.6316 | -2.7341 | -2.8381 | -2.9129 | -3.5203 | -4.2295 | -4.7961 | -1.1103 | -1.135 | -1.161 | -1.1912 | -1.2288 | -1.2575 | -1.3043 | -1.3627 | -1.4372 | -1.5133 | -1.5647 | -2.0149 | -2.5923 | -3.171 | -1.4781 | -1.5138 | -1.5496 | -1.5899 | -1.6388 | -1.6762 | -1.7332 | -1.815 | -1.915 | -2.0167 | -2.0885 | -2.6641 | -3.3212 | -3.8175
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.363 | -0.045397 | -0.11998 | -0.23706 | -0.36853 | -0.50414 | -0.67242 | -0.85372 | -0.9417 | -1.044 | -1.1084 | -1.1858 | -1.459 | -1.6561 | -1.847 | 0.53 | 0.47097 | 0.40019 | 0.32302 | 0.24925 | 0.1458 | 0.036726 | -0.018068 | -0.084716 | -0.1236 | -0.17515 | -0.35096 | -0.48823 | -0.63367 | 0.33004 | 0.25279 | 0.14623 | 0.029021 | -0.088112 | -0.24264 | -0.41442 | -0.5049 | -0.60951 | -0.68999 | -0.77485 | -1.0491 | -1.2258 | -1.3857
|  | LETHEN | CT |  |  |  | 0.363 | -0.045397 | -0.11998 | -0.22026 | -0.36127 | -0.49834 | -0.65056 | -0.82636 | -0.91113 | -0.98211 | -1.0499 | -1.0779 | -1.3049 | -1.4435 | -1.5772 | 0.53 | 0.48579 | 0.43946 | 0.35539 | 0.28346 | 0.20312 | 0.10722 | 0.050569 | 0.0023523 | -0.04707 | -0.068567 | -0.22451 | -0.33002 | -0.4694 | 0.33004 | 0.26337 | 0.17854 | 0.044968 | -0.070859 | -0.19874 | -0.35371 | -0.43806 | -0.50593 | -0.56997 | -0.60715 | -0.80493 | -0.9294 | -1.0549
|  | LETHEN | LW |  |  |  | 0.363 | -0.031281 | -0.11767 | -0.23706 | -0.36853 | -0.50414 | -0.67242 | -0.85372 | -0.9417 | -1.044 | -1.1084 | -1.1858 | -1.459 | -1.6561 | -1.847 | 0.53601 | 0.47097 | 0.40019 | 0.32302 | 0.24925 | 0.1458 | 0.036726 | -0.018068 | -0.084716 | -0.1236 | -0.17515 | -0.35096 | -0.48823 | -0.63367 | 0.33892 | 0.25279 | 0.14623 | 0.029021 | -0.088112 | -0.24264 | -0.41442 | -0.5049 | -0.60951 | -0.68999 | -0.77485 | -1.0491 | -1.2258 | -1.3857
|  | LETHEN | ST |  |  |  | 0.363 | -0.024198 | -0.075301 | -0.16141 | -0.24736 | -0.32534 | -0.40799 | -0.48845 | -0.56532 | -0.64068 | -0.72502 | -0.80923 | -1.2354 | -1.4806 | -1.6404 | 0.54191 | 0.51749 | 0.46718 | 0.41736 | 0.37845 | 0.33415 | 0.2931 | 0.24628 | 0.20409 | 0.15062 | 0.1002 | -0.20746 | -0.4168 | -0.60107 | 0.34911 | 0.30842 | 0.23331 | 0.15903 | 0.091249 | 0.018939 | -0.05405 | -0.1282 | -0.20666 | -0.29431 | -0.3832 | -0.86399 | -1.1224 | -1.2763
|  | LETHEN | FS |  |  |  | 0.363 | -0.0021029 | -0.018301 | -0.046171 | -0.073567 | -0.10536 | -0.13295 | -0.17081 | -0.22754 | -0.29494 | -0.36358 | -0.41718 | -0.78829 | -1.1555 | -1.3293 | 0.55616 | 0.5394 | 0.5194 | 0.50006 | 0.47533 | 0.45644 | 0.42406 | 0.39006 | 0.34364 | 0.29633 | 0.26809 | 0.029484 | -0.22593 | -0.45458 | 0.37414 | 0.34972 | 0.32362 | 0.29688 | 0.26533 | 0.23611 | 0.19586 | 0.14348 | 0.078508 | 0.012371 | -0.04098 | -0.39936 | -0.75654 | -0.95027
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | YES | 0 | 0.11032 | 0.10276 | 0.094429 | 0.086803 | 0.081609 | 0.073761 | 0.062551 | 0.061882 | 0.061041 | 0.060261 | 0.059528 | 0.045739 | 0.023577 | -0.0010096 | 0.10752 | 0.098127 | 0.087761 | 0.078359 | 0.072006 | 0.062431 | 0.048699 | 0.048176 | 0.047517 | 0.046906 | 0.046334 | 0.029849 | 0.002228 | -0.02844 | 0.10722 | 0.097989 | 0.087749 | 0.078323 | 0.071936 | 0.062304 | 0.048503 | 0.047904 | 0.047148 | 0.046447 | 0.045791 | 0.029055 | 0.0013996 | -0.029296
|  | LETTEREWE | CT |  |  |  | 0 | 0.11036 | 0.11016 | 0.10994 | 0.10218 | 0.10022 | 0.097448 | 0.091308 | 0.089904 | 0.088637 | 0.087371 | 0.086161 | 0.07945 | 0.073624 | 0.06537 | 0.10755 | 0.10736 | 0.10715 | 0.097646 | 0.095345 | 0.092035 | 0.084561 | 0.083081 | 0.081709 | 0.080337 | 0.079008 | 0.071101 | 0.063895 | 0.053639 | 0.10723 | 0.10719 | 0.10714 | 0.097595 | 0.095256 | 0.091909 | 0.084386 | 0.082839 | 0.081415 | 0.079992 | 0.078618 | 0.070597 | 0.063378 | 0.053113
|  | LETTEREWE | LW |  |  |  | 0 | 0.11032 | 0.10276 | 0.094429 | 0.086803 | 0.081609 | 0.073761 | 0.062551 | 0.061882 | 0.061041 | 0.060261 | 0.059528 | 0.045739 | 0.023577 | -0.0010096 | 0.10752 | 0.098127 | 0.087761 | 0.078359 | 0.072006 | 0.062431 | 0.048699 | 0.048176 | 0.047517 | 0.046906 | 0.046334 | 0.029849 | 0.002228 | -0.02844 | 0.10722 | 0.097989 | 0.087749 | 0.078323 | 0.071936 | 0.062304 | 0.048503 | 0.047904 | 0.047148 | 0.046447 | 0.045791 | 0.029055 | 0.0013996 | -0.029296
|  | LETTEREWE | ST |  |  |  | 0 | 0.11041 | 0.11033 | 0.10533 | 0.10194 | 0.10015 | 0.099083 | 0.097963 | 0.096775 | 0.095462 | 0.094106 | 0.093497 | 0.070688 | 0.045249 | 0.022333 | 0.1076 | 0.10753 | 0.10131 | 0.097103 | 0.094907 | 0.093693 | 0.092433 | 0.091121 | 0.08971 | 0.088266 | 0.087787 | 0.060771 | 0.029416 | 0.00079888 | 0.10724 | 0.10721 | 0.10106 | 0.096956 | 0.094883 | 0.093661 | 0.092367 | 0.091013 | 0.089545 | 0.088039 | 0.087491 | 0.060092 | 0.028575 | -4.8242e-05
|  | LETTEREWE | FS |  |  |  | 0 | 0.11042 | 0.11036 | 0.10866 | 0.10694 | 0.1052 | 0.10344 | 0.10081 | 0.098959 | 0.096222 | 0.093478 | 0.093145 | 0.090943 | 0.088933 | 0.084437 | 0.10762 | 0.10756 | 0.10545 | 0.10332 | 0.10118 | 0.099011 | 0.095802 | 0.093591 | 0.090303 | 0.087009 | 0.086748 | 0.085015 | 0.083434 | 0.078385 | 0.10725 | 0.10723 | 0.10517 | 0.10311 | 0.10104 | 0.098977 | 0.095782 | 0.093546 | 0.090226 | 0.086898 | 0.086599 | 0.084615 | 0.082806 | 0.077556
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0.293 | 4.5767 | 4.4026 | 4.1738 | 4.0217 | 3.8581 | 3.6515 | 3.4167 | 3.2401 | 3.0205 | 2.8263 | 2.6909 | 2.2423 | 1.9303 | 1.6934 | 5.3375 | 5.2306 | 5.1092 | 5.0264 | 4.9406 | 4.8223 | 4.681 | 4.5918 | 4.4632 | 4.3496 | 4.2783 | 4.0356 | 3.829 | 3.5834 | 5.1038 | 4.9622 | 4.7621 | 4.6179 | 4.4635 | 4.2705 | 4.0518 | 3.89 | 3.6983 | 3.5281 | 3.4066 | 2.9861 | 2.6855 | 2.4557
|  | LHANBRYDE | CT |  |  |  | 0.293 | 4.5804 | 4.4246 | 4.2164 | 4.0724 | 3.8947 | 3.7043 | 3.462 | 3.2682 | 3.0942 | 2.9269 | 2.756 | 2.2599 | 1.9303 | 1.6934 | 5.3383 | 5.2489 | 5.1457 | 5.065 | 4.9704 | 4.8725 | 4.7347 | 4.6328 | 4.5334 | 4.4312 | 4.3267 | 4.0399 | 3.829 | 3.5834 | 5.105 | 4.9817 | 4.8049 | 4.6661 | 4.5037 | 4.3258 | 4.1028 | 3.9276 | 3.7708 | 3.6234 | 3.4758 | 3.0123 | 2.6855 | 2.4557
|  | LHANBRYDE | LW |  |  |  | 0.293 | 4.5767 | 4.4026 | 4.1738 | 4.0217 | 3.8581 | 3.6515 | 3.4167 | 3.2401 | 3.0205 | 2.8263 | 2.6909 | 2.2423 | 1.9952 | 1.764 | 5.3375 | 5.2306 | 5.1092 | 5.0264 | 4.9406 | 4.8223 | 4.681 | 4.5918 | 4.4632 | 4.3496 | 4.2783 | 4.0356 | 3.9012 | 3.7528 | 5.1038 | 4.9622 | 4.7621 | 4.6179 | 4.4635 | 4.2705 | 4.0518 | 3.89 | 3.6983 | 3.5281 | 3.4066 | 2.9861 | 2.7334 | 2.5045
|  | LHANBRYDE | ST |  |  |  | 0.293 | 4.6073 | 4.4901 | 4.3607 | 4.297 | 4.2397 | 4.1672 | 4.111 | 4.0302 | 3.9508 | 3.8623 | 3.7916 | 3.219 | 2.8175 | 2.4922 | 5.3555 | 5.2932 | 5.219 | 5.1757 | 5.1392 | 5.0923 | 5.0572 | 5.0009 | 4.9427 | 4.877 | 4.829 | 4.4101 | 4.1334 | 3.839 | 5.1276 | 5.0357 | 4.9302 | 4.8725 | 4.8213 | 4.7596 | 4.7114 | 4.6441 | 4.5767 | 4.4897 | 4.4229 | 3.8714 | 3.5262 | 3.2051
|  | LHANBRYDE | FS |  |  |  | 0.293 | 4.6442 | 4.5634 | 4.4738 | 4.444 | 4.3963 | 4.3556 | 4.2918 | 4.23 | 4.1421 | 4.0684 | 3.9752 | 3.4958 | 3.0387 | 2.6834 | 5.3708 | 5.326 | 5.2721 | 5.251 | 5.2166 | 5.1871 | 5.1385 | 5.0979 | 5.0354 | 4.9818 | 4.9174 | 4.5696 | 4.1818 | 3.7463 | 5.1602 | 5.1001 | 5.0318 | 5.0054 | 4.965 | 4.9304 | 4.8773 | 4.8228 | 4.7471 | 4.6808 | 4.5979 | 4.1333 | 3.7379 | 3.4271
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0 | -0.66754 | -0.67537 | -0.68408 | -0.69212 | -0.69768 | -0.70609 | -0.71792 | -0.719 | -0.72037 | -0.72156 | -0.72263 | -0.73659 | -0.75886 | -0.78394 | -0.38118 | -0.39078 | -0.40136 | -0.41106 | -0.41764 | -0.42765 | -0.44188 | -0.44286 | -0.44411 | -0.4452 | -0.44617 | -0.46293 | -0.49057 | -0.52158 | -0.45946 | -0.46915 | -0.47994 | -0.48988 | -0.49672 | -0.50702 | -0.52158 | -0.52268 | -0.52408 | -0.52529 | -0.52637 | -0.54343 | -0.57124 | -0.6024
|  | LIDDESDALE | CT |  |  |  | 0 | -0.66754 | -0.66807 | -0.66872 | -0.6768 | -0.6793 | -0.68262 | -0.68951 | -0.69137 | -0.69295 | -0.69463 | -0.69625 | -0.70366 | -0.70961 | -0.7182 | -0.38118 | -0.38162 | -0.38208 | -0.39177 | -0.39445 | -0.39813 | -0.40618 | -0.40817 | -0.40992 | -0.41177 | -0.41358 | -0.42227 | -0.42952 | -0.43999 | -0.45946 | -0.46001 | -0.46073 | -0.47072 | -0.47369 | -0.47769 | -0.48609 | -0.48817 | -0.48996 | -0.49185 | -0.49368 | -0.50252 | -0.50992 | -0.52054
|  | LIDDESDALE | LW |  |  |  | 0 | -0.66752 | -0.67537 | -0.68408 | -0.69212 | -0.69768 | -0.70609 | -0.71792 | -0.719 | -0.72037 | -0.72156 | -0.72263 | -0.73659 | -0.75886 | -0.78394 | -0.38118 | -0.39078 | -0.40136 | -0.41106 | -0.41764 | -0.42765 | -0.44188 | -0.44286 | -0.44411 | -0.4452 | -0.44617 | -0.46293 | -0.49057 | -0.52158 | -0.45944 | -0.46915 | -0.47994 | -0.48988 | -0.49672 | -0.50702 | -0.52158 | -0.52268 | -0.52408 | -0.52529 | -0.52637 | -0.54343 | -0.57124 | -0.6024
|  | LIDDESDALE | ST |  |  |  | 0 | -0.66738 | -0.6676 | -0.67279 | -0.67641 | -0.67843 | -0.67969 | -0.68103 | -0.68242 | -0.68398 | -0.68558 | -0.68644 | -0.71018 | -0.73554 | -0.75857 | -0.38104 | -0.3812 | -0.38753 | -0.39187 | -0.3942 | -0.39557 | -0.397 | -0.3985 | -0.40016 | -0.40186 | -0.4026 | -0.43075 | -0.462 | -0.49064 | -0.45929 | -0.45953 | -0.46598 | -0.47044 | -0.4729 | -0.47441 | -0.47599 | -0.47762 | -0.47943 | -0.48129 | -0.4822 | -0.51111 | -0.5427 | -0.57149
|  | LIDDESDALE | FS |  |  |  | 0 | -0.66729 | -0.66746 | -0.66926 | -0.67109 | -0.67294 | -0.67484 | -0.67759 | -0.67962 | -0.68256 | -0.68553 | -0.68608 | -0.68946 | -0.69233 | -0.69628 | -0.38101 | -0.38113 | -0.38331 | -0.38552 | -0.38775 | -0.39002 | -0.39334 | -0.39571 | -0.3992 | -0.40269 | -0.40317 | -0.40609 | -0.40848 | -0.41302 | -0.45919 | -0.45937 | -0.46158 | -0.46384 | -0.46611 | -0.46843 | -0.4718 | -0.47427 | -0.47786 | -0.48146 | -0.48205 | -0.48564 | -0.48872 | -0.49361
| KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0.099 | -0.34497 | -0.42276 | -0.53756 | -0.66887 | -0.80811 | -0.96511 | -1.1484 | -1.2501 | -1.3345 | -1.426 | -1.5073 | -1.761 | -1.9548 | -2.1454 | 0.19569 | 0.14682 | 0.088688 | 0.026458 | -0.03341 | -0.11218 | -0.21051 | -0.27581 | -0.34195 | -0.41122 | -0.47507 | -0.64389 | -0.74075 | -0.83418 | 0.0095574 | -0.06044 | -0.17296 | -0.29457 | -0.42183 | -0.56738 | -0.74025 | -0.83492 | -0.91264 | -0.99865 | -1.0753 | -1.3163 | -1.4976 | -1.6816
|  | LIMEHILLOCKS | CT |  |  |  | 0.099 | -0.34497 | -0.42276 | -0.52935 | -0.65919 | -0.8004 | -0.93813 | -1.1143 | -1.2147 | -1.2957 | -1.3444 | -1.406 | -1.6493 | -1.794 | -1.9393 | 0.19569 | 0.16116 | 0.11804 | 0.047074 | -0.010481 | -0.064709 | -0.14527 | -0.20678 | -0.25663 | -0.29336 | -0.33558 | -0.48995 | -0.60659 | -0.76945 | 0.0095574 | -0.06044 | -0.15576 | -0.27644 | -0.40393 | -0.52727 | -0.68998 | -0.78353 | -0.85921 | -0.90402 | -0.96272 | -1.1873 | -1.3174 | -1.4488
|  | LIMEHILLOCKS | LW |  |  |  | 0.099 | -0.33173 | -0.41477 | -0.53756 | -0.66887 | -0.80811 | -0.96511 | -1.1484 | -1.2501 | -1.3345 | -1.426 | -1.5073 | -1.761 | -1.9548 | -2.1454 | 0.19665 | 0.14682 | 0.088688 | 0.026458 | -0.03341 | -0.11218 | -0.21051 | -0.27581 | -0.34195 | -0.41122 | -0.47507 | -0.64389 | -0.74075 | -0.83418 | 0.021397 | -0.058026 | -0.17296 | -0.29457 | -0.42183 | -0.56738 | -0.74025 | -0.83492 | -0.91264 | -0.99865 | -1.0753 | -1.3163 | -1.4976 | -1.6816
|  | LIMEHILLOCKS | ST |  |  |  | 0.099 | -0.32141 | -0.3786 | -0.46633 | -0.55808 | -0.63885 | -0.72162 | -0.81159 | -0.89422 | -0.96899 | -1.0538 | -1.1449 | -1.534 | -1.7482 | -1.8907 | 0.20608 | 0.18644 | 0.14847 | 0.10975 | 0.075978 | 0.040287 | -0.0010148 | -0.045977 | -0.093001 | -0.14689 | -0.20583 | -0.52593 | -0.68118 | -0.81548 | 0.031133 | -0.019412 | -0.10003 | -0.18383 | -0.25599 | -0.32962 | -0.41112 | -0.48695 | -0.55486 | -0.63284 | -0.71654 | -1.0878 | -1.2958 | -1.4352
|  | LIMEHILLOCKS | FS |  |  |  | 0.099 | -0.28216 | -0.31768 | -0.34687 | -0.38192 | -0.41031 | -0.4473 | -0.4811 | -0.54661 | -0.61932 | -0.67666 | -0.74552 | -1.0878 | -1.4655 | -1.6351 | 0.21573 | 0.20303 | 0.18772 | 0.16891 | 0.1514 | 0.12885 | 0.10372 | 0.071417 | 0.031837 | -0.00083376 | -0.037758 | -0.24854 | -0.51663 | -0.78981 | 0.065406 | 0.034248 | 0.0077377 | -0.024553 | -0.050302 | -0.084837 | -0.11707 | -0.17713 | -0.2444 | -0.2965 | -0.35901 | -0.67045 | -1.0137 | -1.1671
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0.059 | 9.725 | 9.7056 | 9.674 | 9.6403 | 9.6104 | 9.569 | 9.513 | 9.4732 | 9.4437 | 9.405 | 9.3788 | 9.2591 | 9.1777 | 9.1001 | 9.2783 | 9.2635 | 9.2357 | 9.2082 | 9.1858 | 9.153 | 9.1086 | 9.0868 | 9.0663 | 9.0414 | 9.0198 | 8.9189 | 8.84 | 8.7714 | 9.3404 | 9.3227 | 9.293 | 9.2628 | 9.237 | 9.1995 | 9.1498 | 9.1213 | 9.0921 | 9.0592 | 9.0319 | 8.9072 | 8.8141 | 8.7317
|  | LOCH CARNAN | CT |  |  |  | 0.059 | 9.725 | 9.7177 | 9.6956 | 9.6503 | 9.6157 | 9.5821 | 9.5248 | 9.4973 | 9.4661 | 9.4352 | 9.418 | 9.3306 | 9.279 | 9.2365 | 9.285 | 9.2782 | 9.2635 | 9.2213 | 9.2003 | 9.1756 | 9.1323 | 9.1143 | 9.096 | 9.0785 | 9.0663 | 9.0216 | 8.9894 | 8.9447 | 9.3454 | 9.3351 | 9.3154 | 9.2647 | 9.2379 | 9.2062 | 9.1531 | 9.1292 | 9.1065 | 9.085 | 9.0705 | 9.0028 | 8.952 | 8.9138
|  | LOCH CARNAN | LW |  |  |  | 0.059 | 9.7279 | 9.7056 | 9.674 | 9.6403 | 9.6104 | 9.569 | 9.513 | 9.4732 | 9.4437 | 9.405 | 9.3788 | 9.2591 | 9.1777 | 9.1001 | 9.2863 | 9.2635 | 9.2357 | 9.2082 | 9.1858 | 9.153 | 9.1086 | 9.0868 | 9.0663 | 9.0414 | 9.0198 | 8.9189 | 8.84 | 8.7714 | 9.3475 | 9.3227 | 9.293 | 9.2628 | 9.237 | 9.1995 | 9.1498 | 9.1213 | 9.0921 | 9.0592 | 9.0319 | 8.9072 | 8.8141 | 8.7317
|  | LOCH CARNAN | ST |  |  |  | 0.059 | 9.7335 | 9.7266 | 9.714 | 9.6994 | 9.6884 | 9.6785 | 9.6657 | 9.6484 | 9.6333 | 9.6123 | 9.5904 | 9.448 | 9.3361 | 9.2521 | 9.2783 | 9.2852 | 9.2707 | 9.2585 | 9.2493 | 9.2418 | 9.2322 | 9.2194 | 9.2054 | 9.1891 | 9.1724 | 9.0402 | 8.944 | 8.8765 | 9.3404 | 9.3464 | 9.3309 | 9.3173 | 9.3063 | 9.2968 | 9.2852 | 9.27 | 9.2526 | 9.2326 | 9.2113 | 9.0537 | 8.9471 | 8.8772
|  | LOCH CARNAN | FS |  |  |  | 0.059 | 9.7349 | 9.7232 | 9.7269 | 9.719 | 9.7072 | 9.6995 | 9.6884 | 9.6749 | 9.656 | 9.6426 | 9.6268 | 9.5379 | 9.4445 | 9.3681 | 9.2796 | 9.2691 | 9.2835 | 9.2779 | 9.2702 | 9.2635 | 9.2531 | 9.2439 | 9.2313 | 9.2198 | 9.2106 | 9.1491 | 9.0735 | 9.0043 | 9.342 | 9.3311 | 9.3448 | 9.3385 | 9.3299 | 9.3221 | 9.3104 | 9.2995 | 9.2849 | 9.2714 | 9.2598 | 9.1802 | 9.0797 | 8.9967
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | YES | 0 | 0.58813 | 0.58079 | 0.57262 | 0.56528 | 0.56038 | 0.55303 | 0.54242 | 0.54242 | 0.54242 | 0.54242 | 0.54242 | 0.53018 | 0.50813 | 0.48364 | 0.54367 | 0.53449 | 0.52428 | 0.5151 | 0.50897 | 0.49979 | 0.48653 | 0.48653 | 0.48653 | 0.48653 | 0.48653 | 0.47122 | 0.44367 | 0.41306 | 0.56595 | 0.55676 | 0.54656 | 0.53737 | 0.53125 | 0.52207 | 0.5088 | 0.5088 | 0.5088 | 0.5088 | 0.5088 | 0.4935 | 0.46595 | 0.43533
|  | LOCH GLASCARNOCH | CT |  |  |  | 0 | 0.58813 | 0.58813 | 0.58813 | 0.58079 | 0.57915 | 0.57671 | 0.57099 | 0.57018 | 0.56936 | 0.56854 | 0.56773 | 0.56201 | 0.5563 | 0.54813 | 0.54367 | 0.54367 | 0.54367 | 0.53449 | 0.53244 | 0.52938 | 0.52224 | 0.52122 | 0.5202 | 0.51918 | 0.51816 | 0.51102 | 0.50387 | 0.49367 | 0.56595 | 0.56595 | 0.56595 | 0.55676 | 0.55472 | 0.55166 | 0.54452 | 0.5435 | 0.54248 | 0.54146 | 0.54044 | 0.53329 | 0.52615 | 0.51595
|  | LOCH GLASCARNOCH | LW |  |  |  | 0 | 0.58813 | 0.58079 | 0.57262 | 0.56528 | 0.56038 | 0.55303 | 0.54242 | 0.54242 | 0.54242 | 0.54242 | 0.54242 | 0.53018 | 0.50813 | 0.48364 | 0.54367 | 0.53449 | 0.52428 | 0.5151 | 0.50897 | 0.49979 | 0.48653 | 0.48653 | 0.48653 | 0.48653 | 0.48653 | 0.47122 | 0.44367 | 0.41306 | 0.56595 | 0.55676 | 0.54656 | 0.53737 | 0.53125 | 0.52207 | 0.5088 | 0.5088 | 0.5088 | 0.5088 | 0.5088 | 0.4935 | 0.46595 | 0.43533
|  | LOCH GLASCARNOCH | ST |  |  |  | 0 | 0.58813 | 0.58813 | 0.58324 | 0.57997 | 0.57834 | 0.57752 | 0.57671 | 0.57589 | 0.57507 | 0.57426 | 0.57426 | 0.55467 | 0.53018 | 0.50732 | 0.54367 | 0.54367 | 0.53755 | 0.53346 | 0.53142 | 0.5304 | 0.52938 | 0.52836 | 0.52734 | 0.52632 | 0.52632 | 0.50183 | 0.47122 | 0.44265 | 0.56595 | 0.56595 | 0.55982 | 0.55574 | 0.5537 | 0.55268 | 0.55166 | 0.55064 | 0.54962 | 0.5486 | 0.5486 | 0.52411 | 0.4935 | 0.46493
|  | LOCH GLASCARNOCH | FS |  |  |  | 0 | 0.58813 | 0.58813 | 0.5865 | 0.58487 | 0.58324 | 0.5816 | 0.57915 | 0.57752 | 0.57507 | 0.57262 | 0.57262 | 0.57262 | 0.57262 | 0.56936 | 0.54367 | 0.54367 | 0.54163 | 0.53959 | 0.53755 | 0.53551 | 0.53244 | 0.5304 | 0.52734 | 0.52428 | 0.52428 | 0.52428 | 0.52428 | 0.5202 | 0.56595 | 0.56595 | 0.56391 | 0.56186 | 0.55982 | 0.55778 | 0.55472 | 0.55268 | 0.54962 | 0.54656 | 0.54656 | 0.54656 | 0.54656 | 0.54248
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 0.02 | 0.0069599 | 0.00098728 | -0.020948 | -0.05476 | -0.093894 | -0.14051 | -0.19681 | -0.2163 | -0.25432 | -0.27869 | -0.30878 | -0.39977 | -0.45453 | -0.52123 | 0.30765 | 0.30707 | 0.2924 | 0.2769 | 0.26043 | 0.2282 | 0.18462 | 0.17108 | 0.14651 | 0.1323 | 0.1139 | 0.053974 | 0.011667 | -0.04139 | 0.22915 | 0.21757 | 0.18851 | 0.15514 | 0.11839 | 0.073933 | 0.01934 | 0.0014366 | -0.022921 | -0.039736 | -0.058082 | -0.12573 | -0.17854 | -0.2299
|  | LOCHALINE | CT |  |  |  | 0.02 | 0.018515 | 0.0061693 | -0.0088597 | -0.047525 | -0.084033 | -0.12559 | -0.17674 | -0.1955 | -0.22259 | -0.24069 | -0.26421 | -0.34911 | -0.38794 | -0.43191 | 0.32193 | 0.31624 | 0.31075 | 0.29425 | 0.27909 | 0.25235 | 0.21498 | 0.20022 | 0.1833 | 0.17204 | 0.15659 | 0.10131 | 0.073479 | 0.035482 | 0.23894 | 0.22324 | 0.20311 | 0.1671 | 0.13391 | 0.095832 | 0.047757 | 0.030617 | 0.014305 | 0.0031219 | -0.0088919 | -0.063841 | -0.095578 | -0.12579
|  | LOCHALINE | LW |  |  |  | 0.02 | 0.019712 | 0.00098728 | -0.020948 | -0.05476 | -0.093894 | -0.14051 | -0.19681 | -0.2163 | -0.25432 | -0.27869 | -0.30878 | -0.39977 | -0.45453 | -0.52123 | 0.32174 | 0.30707 | 0.2924 | 0.2769 | 0.26043 | 0.2282 | 0.18462 | 0.17108 | 0.14651 | 0.1323 | 0.1139 | 0.053974 | 0.011667 | -0.04139 | 0.241 | 0.21757 | 0.18851 | 0.15514 | 0.11839 | 0.073933 | 0.01934 | 0.0014366 | -0.022921 | -0.039736 | -0.058082 | -0.12573 | -0.17854 | -0.2299
|  | LOCHALINE | ST |  |  |  | 0.02 | 0.0069599 | 0.012016 | -0.00063733 | -0.017843 | -0.041239 | -0.066124 | -0.091086 | -0.11142 | -0.13615 | -0.16165 | -0.18243 | -0.3186 | -0.39432 | -0.44161 | 0.30765 | 0.31909 | 0.31189 | 0.30431 | 0.29842 | 0.29185 | 0.27677 | 0.26443 | 0.24589 | 0.22658 | 0.21575 | 0.11425 | 0.051918 | 0.0026136 | 0.22915 | 0.2301 | 0.21285 | 0.19399 | 0.17256 | 0.14989 | 0.12716 | 0.10851 | 0.085519 | 0.061783 | 0.042978 | -0.079484 | -0.15325 | -0.20308
|  | LOCHALINE | FS |  |  |  | 0.02 | 0.01298 | 0.019612 | 0.015344 | 0.0092718 | 0.0033376 | -0.0031714 | -0.012295 | -0.023232 | -0.035507 | -0.053963 | -0.072533 | -0.17164 | -0.29476 | -0.34111 | 0.31002 | 0.32097 | 0.31815 | 0.31389 | 0.30972 | 0.30518 | 0.29818 | 0.29195 | 0.28412 | 0.27509 | 0.26683 | 0.20066 | 0.12328 | 0.075505 | 0.23727 | 0.24106 | 0.23562 | 0.22803 | 0.22075 | 0.21279 | 0.20175 | 0.1878 | 0.17256 | 0.15518 | 0.14001 | 0.054027 | -0.040975 | -0.084015
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | YES | 0.064 | -0.14429 | -0.19676 | -0.25176 | -0.30882 | -0.37242 | -0.44199 | -0.52912 | -0.57547 | -0.65206 | -0.71157 | -0.76997 | -0.91466 | -0.98444 | -1.081 | 0.24575 | 0.1977 | 0.15762 | 0.12 | 0.079105 | 0.02602 | -0.04429 | -0.07553 | -0.12785 | -0.1681 | -0.20875 | -0.311 | -0.36247 | -0.4363 | 0.031483 | -0.027436 | -0.091529 | -0.1547 | -0.22757 | -0.31063 | -0.41896 | -0.46432 | -0.53453 | -0.58862 | -0.64207 | -0.7844 | -0.86233 | -0.96344
|  | LOCHCARRON | CT |  |  |  | 0.064 | -0.14429 | -0.19298 | -0.24516 | -0.30662 | -0.37242 | -0.43972 | -0.52586 | -0.5689 | -0.61701 | -0.66687 | -0.70372 | -0.83471 | -0.88803 | -0.95565 | 0.24575 | 0.20636 | 0.17115 | 0.1324 | 0.086491 | 0.04564 | -0.019881 | -0.052983 | -0.087209 | -0.12327 | -0.15048 | -0.25097 | -0.29856 | -0.37062 | 0.031483 | -0.023249 | -0.083914 | -0.14928 | -0.22757 | -0.30171 | -0.40757 | -0.4524 | -0.49675 | -0.54167 | -0.57365 | -0.69828 | -0.75532 | -0.82541
|  | LOCHCARRON | LW |  |  |  | 0.064 | -0.13831 | -0.19676 | -0.25176 | -0.30882 | -0.36997 | -0.44199 | -0.52912 | -0.57547 | -0.65206 | -0.71157 | -0.76997 | -0.91466 | -0.98444 | -1.081 | 0.24872 | 0.1977 | 0.15762 | 0.12 | 0.079105 | 0.02602 | -0.04429 | -0.07553 | -0.12785 | -0.1681 | -0.20875 | -0.311 | -0.36247 | -0.4363 | 0.037548 | -0.027436 | -0.091529 | -0.1547 | -0.22454 | -0.31063 | -0.41896 | -0.46432 | -0.53453 | -0.58862 | -0.64207 | -0.7844 | -0.86233 | -0.96344
|  | LOCHCARRON | ST |  |  |  | 0.064 | -0.13271 | -0.17243 | -0.20692 | -0.24061 | -0.27187 | -0.30662 | -0.33922 | -0.37339 | -0.40726 | -0.44495 | -0.48787 | -0.70355 | -0.78736 | -0.82415 | 0.25538 | 0.22577 | 0.20222 | 0.17826 | 0.15854 | 0.13248 | 0.11251 | 0.083063 | 0.055396 | 0.020512 | -0.016266 | -0.1822 | -0.26613 | -0.33099 | 0.046537 | 0.0054923 | -0.031665 | -0.069897 | -0.10332 | -0.14473 | -0.17836 | -0.22174 | -0.26284 | -0.31293 | -0.36544 | -0.57686 | -0.66823 | -0.71493
|  | LOCHCARRON | FS |  |  |  | 0.064 | -0.11889 | -0.14533 | -0.15628 | -0.16852 | -0.17939 | -0.19417 | -0.21025 | -0.23377 | -0.26405 | -0.29028 | -0.31851 | -0.5063 | -0.70029 | -0.77356 | 0.25997 | 0.24034 | 0.2302 | 0.21758 | 0.20749 | 0.19118 | 0.17214 | 0.15625 | 0.12788 | 0.10659 | 0.080534 | -0.062726 | -0.21322 | -0.32223 | 0.058827 | 0.032827 | 0.019641 | 0.0034822 | -0.0095427 | -0.029977 | -0.053259 | -0.077461 | -0.11676 | -0.14731 | -0.18436 | -0.37718 | -0.56638 | -0.64404
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.035 | 0.030916 | 0.017748 | -0.013567 | -0.049062 | -0.084616 | -0.12797 | -0.28041 | -0.39807 | -0.50633 | -0.5256 | -0.54629 | -0.61428 | -0.66272 | -0.71661 | 0.28798 | 0.27581 | 0.25412 | 0.22888 | 0.20574 | 0.17538 | 0.052415 | -0.04322 | -0.13634 | -0.15462 | -0.1775 | -0.24101 | -0.27827 | -0.33027 | 0.15031 | 0.14009 | 0.11701 | 0.091105 | 0.067655 | 0.034155 | -0.10917 | -0.23173 | -0.34522 | -0.36978 | -0.39471 | -0.50631 | -0.58744 | -0.63053
|  | LOCHDONHEAD | CT |  |  |  | 0.035 | 0.033417 | 0.018879 | -0.0069137 | -0.04543 | -0.080535 | -0.12144 | -0.25332 | -0.36102 | -0.45896 | -0.49074 | -0.51521 | -0.57233 | -0.60158 | -0.63652 | 0.28798 | 0.28156 | 0.26732 | 0.24036 | 0.22024 | 0.19492 | 0.092751 | 0.0037475 | -0.078968 | -0.10799 | -0.13545 | -0.19616 | -0.21981 | -0.25931 | 0.15802 | 0.14526 | 0.12802 | 0.09647 | 0.072339 | 0.04488 | -0.076027 | -0.19015 | -0.29121 | -0.3277 | -0.35577 | -0.40679 | -0.42224 | -0.44165
|  | LOCHDONHEAD | LW |  |  |  | 0.035 | 0.036908 | 0.017748 | -0.013567 | -0.049062 | -0.084616 | -0.12797 | -0.28041 | -0.39807 | -0.50633 | -0.5256 | -0.54629 | -0.61428 | -0.66272 | -0.71661 | 0.28955 | 0.27581 | 0.25412 | 0.22888 | 0.20574 | 0.17538 | 0.052415 | -0.04322 | -0.13634 | -0.15462 | -0.1775 | -0.24101 | -0.27827 | -0.33027 | 0.15943 | 0.14009 | 0.11701 | 0.091105 | 0.067655 | 0.034155 | -0.10917 | -0.23173 | -0.34522 | -0.36978 | -0.39471 | -0.46494 | -0.5051 | -0.54465
|  | LOCHDONHEAD | ST |  |  |  | 0.035 | 0.030916 | 0.027288 | 0.012209 | -0.005853 | -0.024872 | -0.041878 | -0.1398 | -0.24513 | -0.3477 | -0.39058 | -0.41907 | -0.53699 | -0.59115 | -0.62024 | 0.28998 | 0.28628 | 0.27916 | 0.26699 | 0.25315 | 0.24273 | 0.16514 | 0.081717 | -0.00085358 | -0.036734 | -0.055923 | -0.19336 | -0.26248 | -0.30101 | 0.15031 | 0.15484 | 0.14099 | 0.12524 | 0.10858 | 0.092038 | -0.0080058 | -0.11834 | -0.22789 | -0.2775 | -0.31681 | -0.50631 | -0.58744 | -0.63053
|  | LOCHDONHEAD | FS |  |  |  | 0.035 | 0.040264 | 0.040864 | 0.037019 | 0.030405 | 0.024178 | 0.017289 | -0.043249 | -0.1127 | -0.1811 | -0.21844 | -0.25785 | -0.42582 | -0.52874 | -0.57489 | 0.2938 | 0.29219 | 0.28966 | 0.28285 | 0.27691 | 0.2701 | 0.21733 | 0.1613 | 0.10743 | 0.075859 | 0.043308 | -0.097377 | -0.1805 | -0.23816 | 0.15507 | 0.16185 | 0.15542 | 0.14666 | 0.13736 | 0.12676 | 0.061375 | -0.0094972 | -0.081704 | -0.12153 | -0.16379 | -0.36421 | -0.48772 | -0.5612
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.142 | -1.2409 | -1.2696 | -1.3168 | -1.365 | -1.4189 | -1.4835 | -1.5614 | -1.5963 | -1.6845 | -1.7559 | -1.8279 | -2.0361 | -2.1708 | -2.3217 | -0.72347 | -0.74891 | -0.78195 | -0.81522 | -0.85 | -0.89623 | -0.9534 | -0.98242 | -1.0246 | -1.0604 | -1.0948 | -1.2023 | -1.2839 | -1.3863 | -1.0258 | -1.0545 | -1.0934 | -1.1337 | -1.1761 | -1.2375 | -1.3581 | -1.411 | -1.5001 | -1.5682 | -1.637 | -1.8326 | -1.9583 | -2.1022
|  | LOCHEARNHEAD | CT |  |  |  | 0.142 | -1.2409 | -1.2679 | -1.3093 | -1.3588 | -1.4148 | -1.4704 | -1.544 | -1.5777 | -1.6383 | -1.6937 | -1.7508 | -1.9501 | -2.063 | -2.1832 | -0.72347 | -0.74176 | -0.76724 | -0.80348 | -0.83815 | -0.87225 | -0.92053 | -0.94813 | -0.97508 | -1.0004 | -1.0245 | -1.143 | -1.2225 | -1.33 | -1.0258 | -1.0487 | -1.0806 | -1.1248 | -1.1678 | -1.2209 | -1.3351 | -1.3873 | -1.4466 | -1.4997 | -1.5549 | -1.7413 | -1.8422 | -1.952
|  | LOCHEARNHEAD | LW |  |  |  | 0.142 | -1.2376 | -1.2696 | -1.3168 | -1.365 | -1.4189 | -1.4835 | -1.5614 | -1.5963 | -1.6845 | -1.7559 | -1.8279 | -2.0361 | -2.1708 | -2.3217 | -0.72262 | -0.74891 | -0.78195 | -0.81522 | -0.85 | -0.89623 | -0.9534 | -0.98242 | -1.0246 | -1.0604 | -1.0948 | -1.2023 | -1.2839 | -1.3863 | -1.0242 | -1.0545 | -1.0934 | -1.1337 | -1.1761 | -1.2375 | -1.3581 | -1.411 | -1.5001 | -1.5682 | -1.637 | -1.8326 | -1.9583 | -2.1022
|  | LOCHEARNHEAD | ST |  |  |  | 0.142 | -1.2329 | -1.2524 | -1.2798 | -1.308 | -1.3384 | -1.3703 | -1.3965 | -1.4283 | -1.4595 | -1.4964 | -1.5256 | -1.7891 | -1.9173 | -1.9974 | -0.71723 | -0.72802 | -0.7481 | -0.76806 | -0.78923 | -0.81169 | -0.83128 | -0.8558 | -0.88264 | -0.9134 | -0.93841 | -1.1109 | -1.1986 | -1.2735 | -1.0178 | -1.0313 | -1.0557 | -1.0803 | -1.1064 | -1.1341 | -1.1592 | -1.1888 | -1.2207 | -1.2763 | -1.3141 | -1.5962 | -1.7203 | -1.7983
|  | LOCHEARNHEAD | FS |  |  |  | 0.142 | -1.2226 | -1.2337 | -1.2437 | -1.256 | -1.2676 | -1.2829 | -1.2999 | -1.3191 | -1.3481 | -1.372 | -1.3991 | -1.5427 | -1.7804 | -1.8798 | -0.7131 | -0.7195 | -0.72878 | -0.73974 | -0.75043 | -0.76407 | -0.77979 | -0.79458 | -0.81746 | -0.83778 | -0.85889 | -0.97431 | -1.1098 | -1.2498 | -1.012 | -1.0202 | -1.0312 | -1.0441 | -1.057 | -1.0729 | -1.091 | -1.1096 | -1.1366 | -1.1604 | -1.1859 | -1.3631 | -1.5829 | -1.6733
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.997 | 15.6011 | 15.4576 | 15.1176 | 14.7429 | 14.3037 | 13.7388 | 13.1357 | 12.4984 | 11.8301 | 11.1363 | 10.4676 | 8.761 | 8.7308 | 8.1616 | 16.4684 | 16.3441 | 16.1653 | 15.9441 | 15.6714 | 15.4078 | 15.0408 | 14.5996 | 14.1826 | 13.706 | 13.2535 | 12.0309 | 11.1443 | 8.3767 | 16.3297 | 16.1577 | 15.8356 | 15.4745 | 15.0572 | 14.4803 | 13.8606 | 13.1853 | 12.4471 | 11.7494 | 11.1073 | 9.4905 | 9.4585 | 8.8935
|  | LOCHEE | CT |  |  |  | 0.997 | 15.6272 | 15.4774 | 15.1979 | 14.8505 | 14.4242 | 14.0051 | 13.4649 | 12.8149 | 12.3123 | 11.8032 | 11.307 | 9.3894 | 8.8143 | 8.2798 | 16.4684 | 16.3441 | 16.1653 | 15.9441 | 15.6714 | 15.4078 | 15.0408 | 14.5996 | 14.2675 | 13.8953 | 13.5306 | 12.0309 | 11.1443 | 9.6631 | 16.3501 | 16.1646 | 15.8833 | 15.531 | 15.0987 | 14.6869 | 14.1271 | 13.45 | 12.9406 | 12.3977 | 11.9104 | 10.1247 | 9.6102 | 9.0999
|  | LOCHEE | LW |  |  |  | 0.997 | 15.6011 | 15.4576 | 15.1176 | 14.7429 | 14.3037 | 13.7388 | 13.1357 | 12.4984 | 11.8301 | 11.1363 | 10.4676 | 8.761 | 8.7308 | 8.1616 | 16.4696 | 16.3697 | 16.1865 | 15.9885 | 15.752 | 15.4291 | 15.056 | 14.6425 | 14.1826 | 13.706 | 13.2535 | 12.1749 | 12.1365 | 11.6797 | 16.3297 | 16.1577 | 15.8356 | 15.4745 | 15.0572 | 14.4803 | 13.8606 | 13.1853 | 12.4471 | 11.7494 | 11.1073 | 9.4905 | 9.4585 | 8.8935
|  | LOCHEE | ST |  |  |  | 0.997 | 15.6765 | 15.6149 | 15.5662 | 15.5123 | 15.4176 | 15.3378 | 15.2444 | 15.1134 | 14.9637 | 14.7822 | 14.5796 | 13.1864 | 12.6692 | 12.1326 | 16.503 | 16.4471 | 16.3825 | 16.3108 | 16.2034 | 16.1061 | 15.9967 | 15.8606 | 15.6835 | 15.4734 | 15.2382 | 13.8436 | 12.8793 | 11.5375 | 16.4111 | 16.3407 | 16.2742 | 16.1969 | 16.0752 | 15.9634 | 15.8284 | 15.6533 | 15.4523 | 15.2102 | 14.9404 | 13.621 | 13.0997 | 12.6029
|  | LOCHEE | FS |  |  |  | 0.997 | 15.71 | 15.6706 | 15.6102 | 15.5401 | 15.4516 | 15.3538 | 15.2748 | 15.1282 | 14.9574 | 14.7803 | 14.6176 | 13.0818 | 11.4534 | 10.3361 | 16.5147 | 16.4669 | 16.4007 | 16.323 | 16.2267 | 16.1179 | 16.0119 | 15.8577 | 15.6771 | 15.4795 | 15.2807 | 13.695 | 11.4264 | 8.3767 | 16.4403 | 16.3915 | 16.3227 | 16.2385 | 16.1375 | 16.0203 | 15.9189 | 15.7557 | 15.5616 | 15.358 | 15.1721 | 13.553 | 12.0219 | 10.994
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 1.307 | 14.7437 | 14.5526 | 14.1947 | 13.7702 | 13.3253 | 12.8808 | 12.3576 | 12.1213 | 11.904 | 11.6624 | 11.4696 | 10.9242 | 10.7628 | 10.4573 | 17.0008 | 16.8905 | 16.7259 | 16.5214 | 16.3132 | 16.1032 | 15.8427 | 15.6293 | 15.4195 | 15.1738 | 15.0636 | 14.7594 | 14.5962 | 14.198 | 16.6234 | 16.5328 | 16.3845 | 16.1624 | 15.8802 | 15.4801 | 15.0054 | 14.7651 | 14.4895 | 14.1447 | 13.8902 | 13.3521 | 13.2058 | 12.9141
|  | LOCHGILPHEAD | CT |  |  |  | 1.307 | 14.7437 | 14.5526 | 14.1947 | 13.7702 | 13.3253 | 12.8808 | 12.3576 | 12.1213 | 11.904 | 11.6624 | 11.555 | 11.1285 | 10.9873 | 10.7457 | 17.0008 | 16.8905 | 16.7259 | 16.5214 | 16.3132 | 16.1032 | 15.8427 | 15.6293 | 15.4195 | 15.1738 | 15.0695 | 14.7784 | 14.5962 | 14.2849 | 16.6234 | 16.5328 | 16.3845 | 16.1624 | 15.8802 | 15.4801 | 15.0054 | 14.7651 | 14.4895 | 14.1747 | 13.9912 | 13.5583 | 13.4287 | 13.2016
|  | LOCHGILPHEAD | LW |  |  |  | 1.307 | 14.7708 | 14.5963 | 14.2996 | 13.9458 | 13.5665 | 13.1797 | 12.7309 | 12.4439 | 12.096 | 11.7245 | 11.4696 | 10.9242 | 10.7628 | 10.4573 | 17.0134 | 16.9139 | 16.7794 | 16.6113 | 16.4334 | 16.2432 | 16.0116 | 15.7701 | 15.4737 | 15.1984 | 15.0636 | 14.7594 | 14.6671 | 14.5091 | 16.6257 | 16.5419 | 16.4349 | 16.2585 | 16.047 | 15.7119 | 15.2906 | 14.9682 | 14.5352 | 14.1447 | 13.8902 | 13.3521 | 13.2058 | 12.9141
|  | LOCHGILPHEAD | ST |  |  |  | 1.307 | 14.7972 | 14.6756 | 14.5499 | 14.4098 | 14.2768 | 14.1555 | 14.0159 | 13.7802 | 13.4874 | 13.1537 | 12.969 | 11.9996 | 11.8026 | 11.826 | 17.0308 | 16.9691 | 16.9028 | 16.8246 | 16.7514 | 16.6794 | 16.5928 | 16.4106 | 16.1801 | 15.9102 | 15.7819 | 15.158 | 14.9276 | 14.7504 | 16.6478 | 16.6175 | 16.5748 | 16.5096 | 16.4489 | 16.3919 | 16.3197 | 16.1412 | 15.8593 | 15.5244 | 15.3324 | 14.3652 | 14.0643 | 13.9963
|  | LOCHGILPHEAD | FS |  |  |  | 1.307 | 14.8617 | 14.7826 | 14.7402 | 14.6998 | 14.6289 | 14.5917 | 14.5245 | 14.3411 | 14.1602 | 13.9409 | 13.7538 | 12.7929 | 11.9017 | 11.5554 | 17.0561 | 17.0123 | 16.9773 | 16.9433 | 16.9001 | 16.8736 | 16.8311 | 16.6905 | 16.5424 | 16.3728 | 16.2481 | 15.5675 | 14.8329 | 14.198 | 16.6556 | 16.6325 | 16.5987 | 16.5708 | 16.5299 | 16.5117 | 16.4745 | 16.3647 | 16.2705 | 16.1375 | 16.041 | 15.1204 | 14.2643 | 13.8231
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0 | -1.1838 | -1.1921 | -1.1787 | -1.1824 | -1.1878 | -1.1905 | -1.1978 | -1.2017 | -1.2068 | -1.22 | -1.2287 | -1.2661 | -1.2786 | -1.2982 | -0.27849 | -0.28632 | -0.28254 | -0.29261 | -0.30508 | -0.31568 | -0.33134 | -0.33538 | -0.34109 | -0.34705 | -0.34813 | -0.36289 | -0.37226 | -0.38521 | -0.98637 | -0.9936 | -0.99923 | -1.0153 | -1.0345 | -1.0519 | -1.079 | -1.0862 | -1.0943 | -1.102 | -1.103 | -1.1251 | -1.1405 | -1.1569
|  | LOCHGOILHEAD | CT |  |  |  | 0 | -1.1753 | -1.1759 | -1.1787 | -1.1824 | -1.1878 | -1.1905 | -1.1978 | -1.2017 | -1.2068 | -1.2197 | -1.2247 | -1.2621 | -1.2746 | -1.2915 | -0.27088 | -0.27393 | -0.28254 | -0.29261 | -0.30508 | -0.31568 | -0.33134 | -0.33538 | -0.34109 | -0.34705 | -0.34813 | -0.36289 | -0.37226 | -0.38521 | -0.98035 | -0.98551 | -0.99923 | -1.0153 | -1.0345 | -1.0519 | -1.079 | -1.0862 | -1.0943 | -1.102 | -1.103 | -1.1234 | -1.138 | -1.1542
|  | LOCHGOILHEAD | LW |  |  |  | 0 | -1.175 | -1.1767 | -1.1786 | -1.1814 | -1.184 | -1.1882 | -1.1952 | -1.1982 | -1.2066 | -1.22 | -1.2287 | -1.2661 | -1.2786 | -1.2982 | -0.26968 | -0.27344 | -0.28064 | -0.28913 | -0.29809 | -0.30898 | -0.32308 | -0.32717 | -0.3363 | -0.34403 | -0.34662 | -0.36077 | -0.36746 | -0.37524 | -0.9786 | -0.98449 | -0.9962 | -1.0099 | -1.0245 | -1.0416 | -1.063 | -1.0711 | -1.0847 | -1.0961 | -1.1006 | -1.1251 | -1.1405 | -1.1569
|  | LOCHGOILHEAD | ST |  |  |  | 0 | -1.1838 | -1.1751 | -1.175 | -1.1768 | -1.1781 | -1.1798 | -1.1825 | -1.1867 | -1.1899 | -1.1954 | -1.1971 | -1.2198 | -1.2299 | -1.2334 | -0.27849 | -0.27223 | -0.27493 | -0.27949 | -0.28358 | -0.28793 | -0.29331 | -0.29969 | -0.30487 | -0.31239 | -0.31577 | -0.34314 | -0.35391 | -0.36136 | -0.98637 | -0.98316 | -0.98743 | -0.9939 | -0.99975 | -1.0059 | -1.0134 | -1.0219 | -1.0288 | -1.0385 | -1.0435 | -1.082 | -1.0964 | -1.1009
|  | LOCHGOILHEAD | FS |  |  |  | 0 | -1.1823 | -1.1921 | -1.1736 | -1.1748 | -1.1756 | -1.178 | -1.179 | -1.1811 | -1.1849 | -1.1865 | -1.1904 | -1.209 | -1.2226 | -1.2388 | -0.27519 | -0.28632 | -0.26847 | -0.27015 | -0.27138 | -0.27421 | -0.27577 | -0.27998 | -0.28578 | -0.28941 | -0.29532 | -0.32404 | -0.35349 | -0.37361 | -0.9814 | -0.9936 | -0.97631 | -0.97785 | -0.97881 | -0.98162 | -0.9829 | -0.98844 | -0.99571 | -1.0003 | -1.0076 | -1.0418 | -1.0837 | -1.1001
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | YES | 0.207 | -1.0279 | -1.0744 | -1.1484 | -1.2308 | -1.3185 | -1.4181 | -1.5823 | -1.6593 | -1.7153 | -1.7919 | -1.8692 | -2.1005 | -2.1929 | -2.3387 | -0.73541 | -0.75913 | -0.78384 | -0.81179 | -0.83857 | -0.87042 | -0.93238 | -0.96369 | -1.0184 | -1.0871 | -1.1559 | -1.3201 | -1.3746 | -1.4781 | -1.112 | -1.1548 | -1.2152 | -1.2821 | -1.3615 | -1.4698 | -1.6169 | -1.6912 | -1.7838 | -1.8684 | -1.952 | -2.1585 | -2.2378 | -2.3703
|  | LOCHINVER | CT |  |  |  | 0.207 | -0.95533 | -1.0114 | -1.0879 | -1.1837 | -1.2936 | -1.4181 | -1.5823 | -1.6593 | -1.7153 | -1.7672 | -1.8136 | -1.9746 | -2.0466 | -2.1514 | -0.65144 | -0.67957 | -0.69787 | -0.72942 | -0.7682 | -0.83279 | -0.923 | -0.96369 | -0.98748 | -1.0308 | -1.0831 | -1.2305 | -1.2792 | -1.3768 | -1.0339 | -1.084 | -1.1447 | -1.2255 | -1.3348 | -1.4541 | -1.6169 | -1.6912 | -1.754 | -1.8124 | -1.871 | -2.0405 | -2.0966 | -2.1857
|  | LOCHINVER | LW |  |  |  | 0.207 | -1.0279 | -1.0744 | -1.1484 | -1.2308 | -1.3185 | -1.4139 | -1.5428 | -1.6125 | -1.7103 | -1.7919 | -1.8692 | -2.1005 | -2.1929 | -2.3387 | -0.73541 | -0.75913 | -0.78384 | -0.81179 | -0.83857 | -0.87042 | -0.93238 | -0.95872 | -1.0184 | -1.0871 | -1.1559 | -1.3201 | -1.3746 | -1.4781 | -1.112 | -1.1548 | -1.2152 | -1.2821 | -1.3615 | -1.4698 | -1.6107 | -1.6768 | -1.7838 | -1.8684 | -1.952 | -2.1585 | -2.2378 | -2.3703
|  | LOCHINVER | ST |  |  |  | 0.207 | -0.93993 | -0.98119 | -1.02 | -1.0607 | -1.1164 | -1.185 | -1.2496 | -1.3056 | -1.3504 | -1.4015 | -1.4482 | -1.726 | -1.833 | -1.867 | -0.64689 | -0.66749 | -0.68099 | -0.69521 | -0.72369 | -0.76456 | -0.80179 | -0.83142 | -0.84934 | -0.87537 | -0.9 | -1.0899 | -1.1854 | -1.2524 | -1.0206 | -1.0556 | -1.0883 | -1.1225 | -1.1723 | -1.2358 | -1.2951 | -1.3479 | -1.4005 | -1.467 | -1.5135 | -1.8202 | -1.9239 | -1.9677
|  | LOCHINVER | FS |  |  |  | 0.207 | -0.84043 | -0.867 | -0.88623 | -0.91015 | -0.94127 | -0.97354 | -1.0107 | -1.0468 | -1.0872 | -1.1291 | -1.189 | -1.4703 | -1.7616 | -1.8828 | -0.55851 | -0.57315 | -0.58596 | -0.60318 | -0.62812 | -0.6531 | -0.68289 | -0.69892 | -0.71689 | -0.73869 | -0.77617 | -0.94938 | -1.1444 | -1.3 | -0.92401 | -0.94694 | -0.96597 | -0.99 | -1.0214 | -1.0544 | -1.0928 | -1.1242 | -1.165 | -1.2104 | -1.2788 | -1.5896 | -1.8458 | -1.9426
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 2.02 | 5.5388 | 4.5353 | 3.2238 | 2.5409 | 1.7946 | 0.8936 | -0.29774 | -1.508 | -2.4802 | -3.3149 | -4.0777 | -6.2113 | -7.051 | -7.9181 | 6.7672 | 5.8671 | 4.946 | 4.7787 | 4.596 | 4.3087 | 3.7053 | 3.0374 | 2.4578 | 2.0788 | 1.7215 | 0.76932 | 0.078937 | -0.85635 | 7.2174 | 6.3249 | 5.4051 | 4.9628 | 4.3139 | 3.5463 | 2.5004 | 1.4154 | 0.52565 | -0.27292 | -1.0184 | -3.0446 | -3.6289 | -4.4322
|  | LOCHSIDE | CT |  |  |  | 2.02 | 5.831 | 4.9896 | 3.813 | 3.0515 | 2.2091 | 1.1904 | -0.079827 | -1.3813 | -2.1981 | -2.9572 | -3.6002 | -5.8848 | -7.051 | -7.9181 | 7.0413 | 6.306 | 5.4721 | 5.1564 | 4.8067 | 4.3975 | 3.7053 | 3.0374 | 2.5598 | 2.2355 | 1.9689 | 0.82999 | 0.078937 | -0.85635 | 7.4907 | 6.7579 | 5.9193 | 5.4349 | 4.6925 | 3.8095 | 2.6891 | 1.5265 | 0.77786 | 0.10798 | -0.51102 | -2.6292 | -3.6289 | -4.4322
|  | LOCHSIDE | LW |  |  |  | 2.02 | 5.5388 | 4.5353 | 3.2238 | 2.5409 | 1.7946 | 0.8936 | -0.29774 | -1.508 | -2.4802 | -3.3149 | -4.0777 | -6.2113 | -6.7505 | -7.4281 | 6.7672 | 5.8671 | 4.946 | 4.7787 | 4.596 | 4.3087 | 3.7077 | 3.0865 | 2.4578 | 2.0788 | 1.7215 | 0.76932 | 0.5141 | -0.0060904 | 7.2174 | 6.3249 | 5.4051 | 4.9628 | 4.3139 | 3.5463 | 2.5004 | 1.4154 | 0.52565 | -0.27292 | -1.0184 | -3.0446 | -3.5254 | -4.2197
|  | LOCHSIDE | ST |  |  |  | 2.02 | 5.918 | 5.1909 | 4.373 | 4.0937 | 3.7729 | 3.4061 | 2.836 | 2.3015 | 1.6928 | 1.3351 | 0.9674 | -0.80413 | -2.1388 | -3.4193 | 7.0713 | 6.3921 | 5.6129 | 5.4273 | 5.2141 | 4.9557 | 4.4772 | 3.9718 | 3.4022 | 3.0793 | 2.7421 | 1.2089 | 0.63811 | 0.44291 | 7.5281 | 6.8649 | 6.0966 | 5.8872 | 5.6459 | 5.3588 | 4.8541 | 4.3874 | 3.8736 | 3.5778 | 3.2717 | 1.7725 | 0.56525 | -0.53496
|  | LOCHSIDE | FS |  |  |  | 2.02 | 6.2818 | 5.7348 | 5.1126 | 4.8806 | 4.6254 | 4.3363 | 3.8964 | 3.4389 | 2.8989 | 2.5256 | 2.063 | -0.51726 | -2.6122 | -4.4195 | 7.378 | 6.8532 | 6.2819 | 6.1406 | 5.9883 | 5.8084 | 5.4586 | 5.1334 | 4.7642 | 4.507 | 4.1749 | 2.2646 | 1.0324 | -0.61501 | 7.8365 | 7.3271 | 6.7657 | 6.6078 | 6.4348 | 6.2337 | 5.8634 | 5.5347 | 5.156 | 4.9288 | 4.59 | 2.2187 | 0.22477 | -1.4109
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 0.023 | 3.9454 | 3.9166 | 3.8693 | 3.8193 | 3.7662 | 3.7066 | 3.6376 | 3.6003 | 3.5592 | 3.5363 | 3.5067 | 3.4119 | 3.346 | 3.2804 | 3.5878 | 3.5657 | 3.5368 | 3.5078 | 3.4787 | 3.4455 | 3.404 | 3.3784 | 3.348 | 3.3356 | 3.3141 | 3.2528 | 3.2097 | 3.161 | 3.945 | 3.9259 | 3.8812 | 3.8341 | 3.7855 | 3.7297 | 3.6642 | 3.6313 | 3.5953 | 3.5735 | 3.5472 | 3.4572 | 3.389 | 3.3209
|  | LOGIE PERT | CT |  |  |  | 0.023 | 3.9454 | 3.9166 | 3.8796 | 3.8265 | 3.7794 | 3.7225 | 3.6588 | 3.6213 | 3.5923 | 3.5764 | 3.5545 | 3.4656 | 3.4164 | 3.3683 | 3.5878 | 3.5723 | 3.5545 | 3.5219 | 3.4997 | 3.4697 | 3.4348 | 3.4074 | 3.3862 | 3.3769 | 3.3582 | 3.2951 | 3.2592 | 3.2096 | 3.9456 | 3.9286 | 3.8957 | 3.846 | 3.8034 | 3.7525 | 3.6937 | 3.6606 | 3.6349 | 3.6195 | 3.6002 | 3.5195 | 3.4723 | 3.4252
|  | LOGIE PERT | LW |  |  |  | 0.023 | 3.9508 | 3.9167 | 3.8693 | 3.8193 | 3.7662 | 3.7066 | 3.6376 | 3.6003 | 3.5592 | 3.5363 | 3.5067 | 3.4119 | 3.346 | 3.2804 | 3.5899 | 3.5657 | 3.5368 | 3.5078 | 3.4787 | 3.4455 | 3.404 | 3.3784 | 3.348 | 3.3356 | 3.3141 | 3.2528 | 3.2097 | 3.161 | 3.945 | 3.9259 | 3.8812 | 3.8341 | 3.7855 | 3.7297 | 3.6642 | 3.6313 | 3.5953 | 3.5735 | 3.5472 | 3.4572 | 3.389 | 3.3209
|  | LOGIE PERT | ST |  |  |  | 0.023 | 3.9556 | 3.9335 | 3.9002 | 3.8677 | 3.8351 | 3.8048 | 3.7694 | 3.744 | 3.709 | 3.6796 | 3.6439 | 3.4855 | 3.3995 | 3.3455 | 3.5941 | 3.5832 | 3.5642 | 3.5466 | 3.5292 | 3.5143 | 3.4943 | 3.4817 | 3.4591 | 3.4422 | 3.4193 | 3.3017 | 3.229 | 3.1657 | 3.9487 | 3.9433 | 3.9121 | 3.8822 | 3.853 | 3.8254 | 3.7941 | 3.7707 | 3.7394 | 3.7122 | 3.6804 | 3.5292 | 3.4416 | 3.3852
|  | LOGIE PERT | FS |  |  |  | 0.023 | 3.9656 | 3.9565 | 3.9459 | 3.9348 | 3.9226 | 3.9083 | 3.8963 | 3.8705 | 3.8479 | 3.8198 | 3.7928 | 3.6527 | 3.5178 | 3.458 | 3.5946 | 3.5922 | 3.5847 | 3.5767 | 3.5675 | 3.5561 | 3.5467 | 3.5297 | 3.5164 | 3.497 | 3.4794 | 3.3846 | 3.2926 | 3.2135 | 3.9469 | 3.9466 | 3.9419 | 3.9366 | 3.9306 | 3.9189 | 3.907 | 3.8837 | 3.8625 | 3.8368 | 3.8131 | 3.6881 | 3.5656 | 3.5085
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 1.11 | 18.4842 | 17.5851 | 16.3625 | 15.2656 | 13.7947 | 12.5356 | 11.1587 | 10.2828 | 9.6432 | 8.8726 | 8.0013 | 5.9449 | 4.8183 | 3.955 | 19.8761 | 19.0753 | 18.0807 | 17.2557 | 16.1212 | 15.2066 | 14.2144 | 13.6733 | 13.4146 | 13.0049 | 12.4713 | 10.9879 | 9.9731 | 7.923 | 19.8686 | 18.9903 | 17.7913 | 16.7405 | 15.3442 | 14.1613 | 12.8711 | 12.0993 | 11.5248 | 10.8446 | 10.0639 | 8.216 | 7.2658 | 6.5158
|  | LONGHAUGH | CT |  |  |  | 1.11 | 18.6771 | 17.9182 | 16.8375 | 15.6519 | 14.0658 | 12.7599 | 11.4033 | 10.3665 | 9.8236 | 9.1304 | 8.3844 | 6.103 | 4.8183 | 3.955 | 20.0507 | 19.3758 | 18.4858 | 17.5494 | 16.2844 | 15.2916 | 14.3019 | 13.6733 | 13.4146 | 13.0049 | 12.5045 | 10.9879 | 9.9731 | 8.6567 | 20.0646 | 19.3303 | 18.27 | 17.1323 | 15.6233 | 14.3843 | 13.115 | 12.1893 | 11.6927 | 11.0797 | 10.4124 | 8.3902 | 7.2658 | 6.5158
|  | LONGHAUGH | LW |  |  |  | 1.11 | 18.4842 | 17.5851 | 16.3625 | 15.2656 | 13.7947 | 12.5356 | 11.1587 | 10.2828 | 9.6432 | 8.8726 | 8.0013 | 5.9449 | 5.286 | 4.6462 | 19.8761 | 19.0753 | 18.0807 | 17.2557 | 16.1212 | 15.2066 | 14.2144 | 13.7444 | 13.4448 | 13.0175 | 12.4713 | 11.3097 | 11.0212 | 10.6434 | 19.8686 | 18.9903 | 17.7913 | 16.7405 | 15.3442 | 14.1613 | 12.8711 | 12.0993 | 11.5248 | 10.8446 | 10.0639 | 8.216 | 7.62 | 7.0582
|  | LONGHAUGH | ST |  |  |  | 1.11 | 18.7548 | 18.1019 | 17.3303 | 16.5535 | 15.4253 | 14.6047 | 13.8718 | 13.551 | 13.2591 | 12.9627 | 12.494 | 10.5805 | 9.185 | 7.9165 | 20.1024 | 19.5066 | 18.7572 | 18.021 | 16.9703 | 16.1906 | 15.4811 | 15.1975 | 14.9518 | 14.6991 | 14.2872 | 12.7389 | 11.5475 | 10.1188 | 20.1314 | 19.4903 | 18.7043 | 17.9319 | 16.827 | 16.0082 | 15.2885 | 14.9885 | 14.7239 | 14.4567 | 14.029 | 12.2599 | 10.9469 | 9.7908
|  | LONGHAUGH | FS |  |  |  | 1.11 | 19.0346 | 18.5455 | 17.9464 | 17.3531 | 16.3902 | 15.5314 | 14.9888 | 14.6561 | 14.2552 | 13.9052 | 13.4129 | 10.9383 | 8.864 | 7.079 | 20.3322 | 19.8702 | 19.299 | 18.7425 | 17.8483 | 17.0359 | 16.5129 | 16.2225 | 15.8655 | 15.5527 | 15.1126 | 12.9322 | 10.7247 | 7.923 | 20.4054 | 19.9234 | 19.3203 | 18.7322 | 17.7907 | 16.942 | 16.4047 | 16.0959 | 15.7214 | 15.3987 | 14.9406 | 12.6388 | 10.7901 | 9.2086
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | YES | 3.1 | 9.4326 | 8.9257 | 8.2653 | 7.2078 | 6.2792 | 5.3111 | 4.0363 | 2.7316 | 1.7933 | 0.88122 | 0.18777 | -3.0131 | -5.0661 | -5.3966 | 13.5777 | 13.0622 | 12.5038 | 11.7319 | 11.0916 | 10.4227 | 9.511 | 8.6054 | 7.9451 | 7.2703 | 6.7331 | 3.3454 | 1.733 | 0.37552 | 10.1842 | 9.6983 | 9.0101 | 8.0497 | 7.2671 | 6.4523 | 5.321 | 4.1782 | 3.2985 | 2.4412 | 1.7832 | -1.8733 | -3.857 | -4.1759
|  | LONGMAN DRIVE | CT |  |  |  | 3.1 | 9.4599 | 8.9387 | 8.2653 | 7.2078 | 6.2792 | 5.3111 | 4.0363 | 2.7316 | 1.7933 | 0.88122 | 0.18777 | -1.5204 | -1.7026 | -1.8285 | 13.5912 | 13.0622 | 12.5038 | 11.7319 | 11.0916 | 10.4227 | 9.511 | 8.6054 | 7.9451 | 7.2703 | 6.7331 | 5.2423 | 4.6635 | 3.7025 | 10.2064 | 9.6983 | 9.0101 | 8.0497 | 7.2671 | 6.4523 | 5.321 | 4.1782 | 3.2985 | 2.4412 | 1.7832 | 0.17067 | 0.011333 | -0.10204
|  | LONGMAN DRIVE | LW |  |  |  | 3.1 | 9.4326 | 8.9257 | 8.4365 | 7.7617 | 7.1062 | 6.1344 | 5.0454 | 3.8355 | 2.4838 | 1.2551 | 0.25784 | -2.2851 | -2.6405 | -2.8754 | 13.5777 | 13.0792 | 12.6874 | 12.2085 | 11.7895 | 11.1293 | 10.376 | 9.5574 | 8.5808 | 7.6139 | 6.7766 | 4.6652 | 4.3729 | 4.2109 | 10.1842 | 9.7114 | 9.2636 | 8.6937 | 8.186 | 7.368 | 6.3851 | 5.2544 | 3.9727 | 2.8087 | 1.8542 | -0.58171 | -0.92005 | -1.1457
|  | LONGMAN DRIVE | ST |  |  |  | 3.1 | 9.5659 | 9.2586 | 8.9236 | 8.5532 | 8.1092 | 7.5062 | 6.8128 | 6.0009 | 5.0237 | 3.9842 | 2.8795 | -3.0131 | -5.0661 | -5.3966 | 13.7134 | 13.4317 | 13.1222 | 12.7608 | 12.3851 | 11.9276 | 11.3993 | 10.7914 | 10.041 | 9.224 | 8.2655 | 3.3454 | 1.733 | 0.87938 | 10.3102 | 10.0305 | 9.7317 | 9.3675 | 8.9028 | 8.3361 | 7.6762 | 6.9126 | 5.9578 | 4.936 | 3.8242 | -1.8733 | -3.857 | -4.1759
|  | LONGMAN DRIVE | FS |  |  |  | 3.1 | 9.6498 | 9.4142 | 9.1749 | 8.9035 | 8.6323 | 8.3101 | 7.9178 | 7.4483 | 6.8785 | 6.2967 | 5.6861 | 1.8404 | -1.7069 | -3.7922 | 13.7878 | 13.5745 | 13.3612 | 13.1073 | 12.8474 | 12.5537 | 12.215 | 11.8404 | 11.3835 | 10.9152 | 10.4177 | 7.1023 | 3.5655 | 0.37552 | 10.3867 | 10.174 | 9.9626 | 9.7174 | 9.4675 | 9.1155 | 8.7128 | 8.2713 | 7.7249 | 7.1645 | 6.5681 | 2.7843 | -0.60109 | -2.6092
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0.575 | 7.3306 | 7.174 | 6.8424 | 6.446 | 6.0454 | 5.5332 | 4.9776 | 4.3181 | 3.6295 | 3.0085 | 2.4413 | 1.0919 | 0.094818 | -0.65248 | 8.5159 | 8.402 | 8.2283 | 7.9954 | 7.7702 | 7.5077 | 7.1949 | 6.8116 | 6.4432 | 6.0756 | 5.7374 | 5.0678 | 4.3923 | 3.6007 | 7.8481 | 7.69 | 7.3876 | 7.0229 | 6.6525 | 6.1802 | 5.66 | 5.0457 | 4.3884 | 3.7961 | 3.2545 | 2.0739 | 1.3174 | 0.65183
|  | LOSSIEMOUTH | CT |  |  |  | 0.575 | 7.3334 | 7.1814 | 6.8658 | 6.4638 | 6.0454 | 5.5599 | 5.0001 | 4.3269 | 3.7618 | 3.2282 | 2.7562 | 1.2004 | 0.094818 | -0.65248 | 8.5159 | 8.402 | 8.2283 | 7.9954 | 7.7702 | 7.5077 | 7.1949 | 6.8116 | 6.495 | 6.1746 | 5.8795 | 5.0678 | 4.3923 | 3.6007 | 7.8484 | 7.697 | 7.4085 | 7.0354 | 6.6525 | 6.2091 | 5.6929 | 5.0652 | 4.5432 | 4.04 | 3.5912 | 2.2531 | 1.3174 | 0.65183
|  | LOSSIEMOUTH | LW |  |  |  | 0.575 | 7.3306 | 7.174 | 6.8424 | 6.446 | 6.0592 | 5.5332 | 4.9776 | 4.3181 | 3.6295 | 3.0085 | 2.4413 | 1.0919 | 0.42571 | -0.17621 | 8.5207 | 8.4037 | 8.2292 | 8.0152 | 7.8255 | 7.5264 | 7.213 | 6.8513 | 6.4432 | 6.0756 | 5.7374 | 5.1206 | 4.8224 | 4.455 | 7.8481 | 7.69 | 7.3876 | 7.0229 | 6.6746 | 6.1802 | 5.66 | 5.0457 | 4.3884 | 3.7961 | 3.2545 | 2.0739 | 1.4933 | 0.91179
|  | LOSSIEMOUTH | ST |  |  |  | 0.575 | 7.3796 | 7.296 | 7.2034 | 7.1079 | 6.9901 | 6.8633 | 6.7464 | 6.5767 | 6.3635 | 6.1697 | 5.9294 | 4.4269 | 3.1864 | 2.1455 | 8.5511 | 8.4941 | 8.4209 | 8.3458 | 8.2516 | 8.1489 | 8.0494 | 7.908 | 7.727 | 7.5653 | 7.359 | 6.2427 | 5.3917 | 4.5099 | 7.8971 | 7.8192 | 7.7285 | 7.6353 | 7.5189 | 7.3926 | 7.2723 | 7.0996 | 6.8794 | 6.6849 | 6.437 | 4.9805 | 3.8929 | 2.9954
|  | LOSSIEMOUTH | FS |  |  |  | 0.575 | 7.4292 | 7.3748 | 7.2954 | 7.1984 | 7.1097 | 7.0029 | 6.8831 | 6.7072 | 6.5335 | 6.3319 | 6.12 | 4.7174 | 3.5044 | 2.1777 | 8.5725 | 8.5295 | 8.4719 | 8.3982 | 8.3309 | 8.2449 | 8.1398 | 8.0048 | 7.8666 | 7.7048 | 7.534 | 6.4119 | 5.2734 | 3.6886 | 7.9393 | 7.8879 | 7.8136 | 7.7208 | 7.6376 | 7.5339 | 7.4142 | 7.2463 | 7.078 | 6.8813 | 6.6744 | 5.3235 | 4.2321 | 3.0558
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0.127 | -0.037871 | -0.074347 | -0.12867 | -0.20445 | -0.28064 | -0.35197 | -0.45301 | -0.49234 | -0.53117 | -0.56676 | -0.61224 | -0.75278 | -0.82749 | -0.91444 | 0.11441 | 0.086404 | 0.052517 | 0.017391 | -0.019453 | -0.061651 | -0.12609 | -0.16 | -0.21383 | -0.24019 | -0.28088 | -0.3855 | -0.43202 | -0.49964 | 0.0098981 | -0.026546 | -0.078346 | -0.13351 | -0.20095 | -0.25635 | -0.34933 | -0.39393 | -0.46194 | -0.49524 | -0.54562 | -0.67911 | -0.7424 | -0.82824
|  | LOWER OLLACH | CT |  |  |  | 0.127 | -0.037871 | -0.074347 | -0.12794 | -0.20445 | -0.28064 | -0.35197 | -0.45301 | -0.49234 | -0.52645 | -0.56067 | -0.57161 | -0.6674 | -0.7159 | -0.7768 | 0.11441 | 0.091635 | 0.067627 | 0.02283 | -0.019453 | -0.050054 | -0.11003 | -0.14428 | -0.17657 | -0.2121 | -0.22301 | -0.30784 | -0.3386 | -0.39077 | 0.0098981 | -0.024427 | -0.066592 | -0.13351 | -0.20095 | -0.25461 | -0.34511 | -0.38797 | -0.42751 | -0.46981 | -0.48049 | -0.58286 | -0.62066 | -0.67423
|  | LOWER OLLACH | LW |  |  |  | 0.127 | -0.032384 | -0.071294 | -0.12867 | -0.19003 | -0.25586 | -0.3318 | -0.42904 | -0.47164 | -0.53117 | -0.56676 | -0.61224 | -0.75278 | -0.82749 | -0.91444 | 0.11575 | 0.086404 | 0.052517 | 0.017391 | -0.018949 | -0.061651 | -0.12609 | -0.16 | -0.21383 | -0.24019 | -0.28088 | -0.3855 | -0.43202 | -0.49964 | 0.013174 | -0.026546 | -0.078346 | -0.13273 | -0.19076 | -0.25635 | -0.34933 | -0.39393 | -0.46194 | -0.49524 | -0.54562 | -0.67911 | -0.7424 | -0.82824
|  | LOWER OLLACH | ST |  |  |  | 0.127 | -0.031475 | -0.0481 | -0.081069 | -0.11384 | -0.14777 | -0.18016 | -0.21967 | -0.24891 | -0.29173 | -0.3365 | -0.37414 | -0.57357 | -0.66283 | -0.70623 | 0.11521 | 0.11136 | 0.092575 | 0.074249 | 0.055244 | 0.038274 | 0.013414 | -0.0022358 | -0.033582 | -0.066798 | -0.09141 | -0.25254 | -0.32678 | -0.37572 | 0.01264 | 0.002612 | -0.026286 | -0.05487 | -0.084793 | -0.11211 | -0.14927 | -0.17281 | -0.21586 | -0.26105 | -0.29556 | -0.49502 | -0.57807 | -0.6192
|  | LOWER OLLACH | FS |  |  |  | 0.127 | -0.016216 | -0.02512 | -0.036297 | -0.048386 | -0.062301 | -0.079268 | -0.093818 | -0.12298 | -0.15716 | -0.18164 | -0.21412 | -0.38714 | -0.55746 | -0.63932 | 0.12101 | 0.1199 | 0.11151 | 0.10205 | 0.090798 | 0.075967 | 0.06392 | 0.043347 | 0.017204 | 0.0036489 | -0.01971 | -0.14614 | -0.25844 | -0.33627 | 0.024508 | 0.020231 | 0.0091495 | -0.0030421 | -0.017475 | -0.036294 | -0.05088 | -0.079607 | -0.11477 | -0.13375 | -0.16586 | -0.33352 | -0.47692 | -0.54136
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20911 | 0.20782 | 0.20649 | 0.20499 | 0.20312 | 0.20125 | 0.19842 | 0.19562 | 0.19198 | 0.18806 | 0.18456 | 0.17953 | 0.1792 | 0.17885 | 0.036266 | 0.034863 | 0.033609 | 0.032031 | 0.030167 | 0.028177 | 0.025165 | 0.021902 | 0.017728 | 0.014136 | 0.010929 | 0.006574 | 0.0064502 | 0.0062836 | 0.21361 | 0.21213 | 0.21075 | 0.20902 | 0.20701 | 0.20492 | 0.2017 | 0.19827 | 0.19385 | 0.18998 | 0.18654 | 0.18162 | 0.18134 | 0.18102
|  | LUBNAIG | CT |  |  |  | 0 | 0.20914 | 0.20784 | 0.20649 | 0.20499 | 0.20312 | 0.20128 | 0.19868 | 0.19598 | 0.19401 | 0.19175 | 0.18942 | 0.18475 | 0.18445 | 0.18411 | 0.036349 | 0.034955 | 0.033609 | 0.032031 | 0.030167 | 0.028371 | 0.025769 | 0.022659 | 0.020355 | 0.017757 | 0.015388 | 0.011122 | 0.011005 | 0.010856 | 0.2137 | 0.21222 | 0.21075 | 0.20902 | 0.20701 | 0.20506 | 0.20228 | 0.19897 | 0.19652 | 0.19379 | 0.19133 | 0.18672 | 0.18646 | 0.18615
|  | LUBNAIG | LW |  |  |  | 0 | 0.20911 | 0.20782 | 0.20665 | 0.20508 | 0.2037 | 0.20125 | 0.19842 | 0.19562 | 0.19198 | 0.18806 | 0.18456 | 0.17953 | 0.1792 | 0.17885 | 0.036266 | 0.034863 | 0.033712 | 0.032139 | 0.030756 | 0.028177 | 0.025165 | 0.021902 | 0.017728 | 0.014136 | 0.010929 | 0.006574 | 0.0064502 | 0.0062836 | 0.21361 | 0.21213 | 0.21088 | 0.20919 | 0.20768 | 0.20492 | 0.2017 | 0.19827 | 0.19385 | 0.18998 | 0.18654 | 0.18162 | 0.18134 | 0.18102
|  | LUBNAIG | ST |  |  |  | 0 | 0.20961 | 0.20916 | 0.2086 | 0.20792 | 0.20718 | 0.20629 | 0.20526 | 0.20404 | 0.20246 | 0.2008 | 0.19898 | 0.19061 | 0.18917 | 0.18897 | 0.036964 | 0.036599 | 0.036127 | 0.035528 | 0.03487 | 0.034078 | 0.03314 | 0.032007 | 0.030521 | 0.028953 | 0.027239 | 0.019158 | 0.018066 | 0.017972 | 0.21437 | 0.21398 | 0.21347 | 0.21283 | 0.21213 | 0.2113 | 0.21029 | 0.20892 | 0.20716 | 0.2053 | 0.20328 | 0.19392 | 0.19243 | 0.19225
|  | LUBNAIG | FS |  |  |  | 0 | 0.20967 | 0.2093 | 0.20892 | 0.20844 | 0.20792 | 0.2073 | 0.20658 | 0.20564 | 0.20443 | 0.2032 | 0.20186 | 0.19375 | 0.18511 | 0.18262 | 0.036864 | 0.036479 | 0.036027 | 0.035459 | 0.034837 | 0.034093 | 0.033231 | 0.032176 | 0.0308 | 0.029392 | 0.027842 | 0.019256 | 0.01164 | 0.0098221 | 0.21426 | 0.21384 | 0.21336 | 0.21276 | 0.21209 | 0.2113 | 0.21038 | 0.20926 | 0.20779 | 0.2063 | 0.20465 | 0.19545 | 0.18712 | 0.18475
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.312 | 6.8512 | 6.7387 | 6.5286 | 6.1143 | 5.6601 | 5.1044 | 4.5148 | 3.9775 | 3.4203 | 2.9173 | 2.762 | 1.5134 | 1.0271 | 0.53395 | 7.782 | 7.6607 | 7.4877 | 7.2824 | 7.0609 | 6.7647 | 6.4295 | 6.0931 | 5.8001 | 5.4858 | 5.4687 | 4.7911 | 4.3785 | 3.8275 | 7.5882 | 7.3872 | 7.0577 | 6.6836 | 6.2761 | 5.7617 | 5.2223 | 4.7109 | 4.1727 | 3.6849 | 3.5771 | 2.4239 | 2.067 | 1.6211
|  | LUNANHEAD | CT |  |  |  | 0.312 | 6.9767 | 6.8463 | 6.6244 | 6.2143 | 5.7165 | 5.1599 | 4.5296 | 3.9775 | 3.5452 | 3.1377 | 3.0779 | 1.7094 | 1.0271 | 0.53395 | 7.89 | 7.7484 | 7.5648 | 7.3479 | 7.076 | 6.7737 | 6.4295 | 6.0931 | 5.8378 | 5.5776 | 5.6055 | 4.8164 | 4.3785 | 3.8275 | 7.6861 | 7.4619 | 7.1438 | 6.7707 | 6.3153 | 5.809 | 5.2355 | 4.7109 | 4.3028 | 3.9085 | 3.89 | 2.6482 | 2.067 | 1.6211
|  | LUNANHEAD | LW |  |  |  | 0.312 | 6.8512 | 6.7387 | 6.5286 | 6.1143 | 5.6601 | 5.1044 | 4.5148 | 3.9835 | 3.4203 | 2.9173 | 2.762 | 1.5134 | 1.1306 | 0.70348 | 7.782 | 7.6607 | 7.4877 | 7.2824 | 7.0609 | 6.7647 | 6.4577 | 6.1517 | 5.8001 | 5.4858 | 5.4687 | 4.7911 | 4.6152 | 4.3568 | 7.5882 | 7.3872 | 7.0577 | 6.6836 | 6.2761 | 5.7617 | 5.2223 | 4.7193 | 4.1727 | 3.6849 | 3.5771 | 2.4239 | 2.0864 | 1.6727
|  | LUNANHEAD | ST |  |  |  | 0.312 | 7.0091 | 6.9332 | 6.8648 | 6.7954 | 6.6138 | 6.3821 | 6.1684 | 5.9506 | 5.7129 | 5.499 | 5.2376 | 4.1438 | 3.3734 | 2.6572 | 7.9299 | 7.8457 | 7.7571 | 7.6688 | 7.5473 | 7.3918 | 7.2484 | 7.0942 | 6.9213 | 6.7727 | 6.5785 | 5.5875 | 5.1367 | 4.6328 | 7.7601 | 7.6266 | 7.4745 | 7.3266 | 7.1412 | 6.923 | 6.7203 | 6.5082 | 6.2713 | 6.0659 | 5.8055 | 4.6096 | 3.929 | 3.4592
|  | LUNANHEAD | FS |  |  |  | 0.312 | 7.1491 | 7.108 | 7.0703 | 7.0182 | 6.9478 | 6.8731 | 6.788 | 6.6501 | 6.4355 | 6.2065 | 5.9744 | 4.396 | 3.2068 | 2.2363 | 8.0815 | 8.0188 | 7.9641 | 7.8955 | 7.8055 | 7.7099 | 7.5972 | 7.483 | 7.3336 | 7.1709 | 7.0091 | 5.8666 | 4.9669 | 3.8442 | 7.9387 | 7.8468 | 7.7655 | 7.6751 | 7.5608 | 7.4416 | 7.3064 | 7.1431 | 6.9376 | 6.7181 | 6.5045 | 4.9996 | 3.9617 | 3.1069
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.087325 | 0.08315 | 0.078828 | 0.073747 | 0.067357 | 0.060973 | 0.060309 | 0.064941 | 0.061761 | 0.062244 | 0.059394 | 0.05923 | 0.058033 | 0.056676 | 0.068457 | 0.064538 | 0.06083 | 0.056799 | 0.051507 | 0.046322 | 0.051975 | 0.053206 | 0.048091 | 0.051486 | 0.047607 | 0.050424 | 0.048916 | 0.04793 | 0.087682 | 0.083561 | 0.079424 | 0.07489 | 0.068743 | 0.062588 | 0.060365 | 0.065283 | 0.061883 | 0.062563 | 0.05937 | 0.059677 | 0.058062 | 0.057687
|  | LUSSAGIVEN | CT |  |  |  | 0 | 0.087325 | 0.08315 | 0.078828 | 0.073747 | 0.067357 | 0.060973 | 0.060309 | 0.064941 | 0.061761 | 0.062244 | 0.059394 | 0.059235 | 0.058535 | 0.057398 | 0.068457 | 0.064538 | 0.06083 | 0.056799 | 0.051507 | 0.046322 | 0.051975 | 0.055142 | 0.052685 | 0.052922 | 0.050749 | 0.050424 | 0.049964 | 0.049119 | 0.087682 | 0.083561 | 0.079424 | 0.07489 | 0.068743 | 0.062588 | 0.060365 | 0.065283 | 0.061883 | 0.062563 | 0.059631 | 0.059677 | 0.059039 | 0.058087
|  | LUSSAGIVEN | LW |  |  |  | 0 | 0.087604 | 0.083957 | 0.08061 | 0.075877 | 0.071658 | 0.064392 | 0.0634 | 0.068116 | 0.062677 | 0.062794 | 0.059405 | 0.05923 | 0.058045 | 0.056676 | 0.068672 | 0.065238 | 0.06235 | 0.0584 | 0.055095 | 0.048807 | 0.054131 | 0.057283 | 0.05339 | 0.053272 | 0.050751 | 0.050492 | 0.049873 | 0.049052 | 0.087947 | 0.084344 | 0.081102 | 0.076752 | 0.072911 | 0.065834 | 0.063289 | 0.068097 | 0.062611 | 0.062786 | 0.05937 | 0.05975 | 0.058847 | 0.057687
|  | LUSSAGIVEN | ST |  |  |  | 0 | 0.088774 | 0.087358 | 0.085591 | 0.083389 | 0.080904 | 0.077899 | 0.074388 | 0.070239 | 0.064822 | 0.065765 | 0.060319 | 0.060323 | 0.058033 | 0.057955 | 0.069827 | 0.068595 | 0.067043 | 0.065062 | 0.062871 | 0.060216 | 0.057057 | 0.053206 | 0.048091 | 0.054921 | 0.051143 | 0.050706 | 0.048916 | 0.048631 | 0.089115 | 0.087741 | 0.086026 | 0.083875 | 0.081509 | 0.078672 | 0.075322 | 0.071295 | 0.06598 | 0.065389 | 0.060005 | 0.060282 | 0.058062 | 0.057938
|  | LUSSAGIVEN | FS |  |  |  | 0 | 0.089036 | 0.088049 | 0.086862 | 0.085375 | 0.083798 | 0.08193 | 0.079754 | 0.076941 | 0.073327 | 0.069607 | 0.06553 | 0.065554 | 0.059249 | 0.057401 | 0.070059 | 0.069068 | 0.067937 | 0.066509 | 0.064993 | 0.063189 | 0.061083 | 0.058443 | 0.055016 | 0.051486 | 0.047607 | 0.054175 | 0.049696 | 0.04793 | 0.089455 | 0.088381 | 0.087208 | 0.085733 | 0.084168 | 0.082312 | 0.080149 | 0.077374 | 0.073798 | 0.070117 | 0.06608 | 0.065208 | 0.059334 | 0.057779
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 0 | 9.4207 | 9.0689 | 8.9578 | 8.9086 | 8.7601 | 8.4383 | 8.1015 | 7.7598 | 7.3424 | 6.9864 | 6.6611 | 5.812 | 5.7041 | 5.4532 | 9.9266 | 9.5077 | 9.3898 | 9.3467 | 9.3088 | 9.1759 | 9.0244 | 8.8366 | 8.6446 | 8.4845 | 8.3306 | 7.7939 | 7.3818 | 5.9907 | 9.6345 | 9.2546 | 9.0362 | 8.8574 | 8.6748 | 8.4085 | 8.1353 | 7.8491 | 7.5032 | 7.215 | 6.9522 | 6.2476 | 6.1479 | 5.9522
|  | LYNDHURST | CT |  |  |  | 0 | 9.4924 | 9.2004 | 9.0707 | 8.9948 | 8.8884 | 8.5833 | 8.2327 | 7.8571 | 7.5193 | 7.227 | 6.9717 | 6.0706 | 5.7041 | 5.4532 | 9.9966 | 9.6542 | 9.5166 | 9.4488 | 9.3765 | 9.2361 | 9.0383 | 8.8366 | 8.6446 | 8.4961 | 8.3623 | 7.7939 | 7.3818 | 6.7525 | 9.7066 | 9.391 | 9.18 | 9.0086 | 8.8072 | 8.5459 | 8.2509 | 7.9305 | 7.6428 | 7.405 | 7.1992 | 6.4597 | 6.1479 | 5.9522
|  | LYNDHURST | LW |  |  |  | 0 | 9.4207 | 9.0689 | 8.9578 | 8.9086 | 8.7601 | 8.4383 | 8.1015 | 7.7598 | 7.3424 | 6.9864 | 6.6611 | 5.812 | 5.7344 | 5.552 | 9.9266 | 9.5077 | 9.3898 | 9.3467 | 9.3088 | 9.1759 | 9.0244 | 8.8691 | 8.6519 | 8.4845 | 8.3306 | 7.9104 | 7.8673 | 7.7841 | 9.6345 | 9.2546 | 9.0362 | 8.8574 | 8.6748 | 8.4085 | 8.1353 | 7.8491 | 7.5032 | 7.215 | 6.9522 | 6.2476 | 6.1741 | 6.0472
|  | LYNDHURST | ST |  |  |  | 0 | 9.5069 | 9.2445 | 9.1429 | 9.1122 | 9.0717 | 8.9714 | 8.8959 | 8.8156 | 8.7175 | 8.6472 | 8.5801 | 8.1107 | 7.7056 | 7.2422 | 10.0088 | 9.6909 | 9.5748 | 9.5419 | 9.4998 | 9.3979 | 9.3187 | 9.2358 | 9.1305 | 9.063 | 9.0007 | 8.5439 | 8.0995 | 7.3995 | 9.7424 | 9.4721 | 9.3703 | 9.3397 | 9.2987 | 9.1984 | 9.1229 | 9.0336 | 8.9243 | 8.8408 | 8.7638 | 8.1545 | 7.7871 | 7.3624
|  | LYNDHURST | FS |  |  |  | 0 | 9.5811 | 9.381 | 9.3053 | 9.2782 | 9.2413 | 9.1625 | 9.1101 | 9.0627 | 8.998 | 8.9515 | 8.8866 | 7.9678 | 7.1609 | 6.5224 | 10.0833 | 9.8383 | 9.751 | 9.7185 | 9.6782 | 9.5924 | 9.5319 | 9.4724 | 9.3933 | 9.3363 | 9.2619 | 8.4477 | 7.4748 | 5.9907 | 9.8165 | 9.6106 | 9.52 | 9.4781 | 9.4245 | 9.3329 | 9.2621 | 9.1806 | 9.0756 | 8.9909 | 8.8864 | 8.0281 | 7.3608 | 6.817
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0 | 0.04883 | 0.023761 | -0.011872 | -0.05371 | -0.10451 | -0.15898 | -0.21439 | -0.25941 | -0.28387 | -0.31958 | -0.35757 | -0.46318 | -0.51033 | -0.55451 | 0.16255 | 0.15193 | 0.13254 | 0.114 | 0.086758 | 0.0587 | 0.03219 | 0.0027101 | -0.01169 | -0.035318 | -0.061378 | -0.1183 | -0.1388 | -0.20416 | 0.063403 | 0.039735 | 0.0069135 | -0.02649 | -0.07142 | -0.11869 | -0.16194 | -0.20668 | -0.22791 | -0.26816 | -0.30517 | -0.39408 | -0.4286 | -0.46423
|  | LYNESS | CT |  |  |  | 0 | 0.04883 | 0.023761 | -0.011872 | -0.05371 | -0.10451 | -0.15898 | -0.21439 | -0.25941 | -0.28387 | -0.31653 | -0.34541 | -0.42822 | -0.47099 | -0.51045 | 0.16571 | 0.15193 | 0.13254 | 0.114 | 0.086758 | 0.0587 | 0.03219 | 0.0027101 | -0.01169 | -0.034094 | -0.054829 | -0.10391 | -0.13302 | -0.17285 | 0.063403 | 0.039735 | 0.0069135 | -0.02649 | -0.07142 | -0.11869 | -0.16194 | -0.20668 | -0.22791 | -0.26131 | -0.29162 | -0.35756 | -0.38979 | -0.42082
|  | LYNESS | LW |  |  |  | 0 | 0.054122 | 0.029005 | 0.00082667 | -0.043961 | -0.084234 | -0.14253 | -0.1954 | -0.23934 | -0.27812 | -0.31958 | -0.35757 | -0.46318 | -0.51033 | -0.55451 | 0.16838 | 0.15288 | 0.14011 | 0.11641 | 0.10074 | 0.068449 | 0.046686 | 0.017312 | -0.0066591 | -0.035318 | -0.061378 | -0.1183 | -0.1388 | -0.16072 | 0.06842 | 0.043696 | 0.01792 | -0.02196 | -0.053481 | -0.10624 | -0.14825 | -0.19102 | -0.2274 | -0.26816 | -0.30517 | -0.39408 | -0.4286 | -0.46423
|  | LYNESS | ST |  |  |  | 0 | 0.049771 | 0.041231 | 0.015137 | -0.013895 | -0.043283 | -0.075649 | -0.10641 | -0.13905 | -0.16605 | -0.20233 | -0.24122 | -0.40423 | -0.47276 | -0.50667 | 0.16255 | 0.16293 | 0.14985 | 0.13713 | 0.1245 | 0.1088 | 0.0951 | 0.075458 | 0.063175 | 0.041096 | 0.016682 | -0.090104 | -0.13633 | -0.17091 | 0.06621 | 0.056512 | 0.032332 | 0.0085201 | -0.015235 | -0.042884 | -0.067979 | -0.098214 | -0.11947 | -0.15333 | -0.18982 | -0.34041 | -0.39536 | -0.42063
|  | LYNESS | FS |  |  |  | 0 | 0.062499 | 0.059724 | 0.049921 | 0.040729 | 0.031447 | 0.017607 | 0.0050198 | -0.012724 | -0.03881 | -0.066314 | -0.084785 | -0.23679 | -0.39722 | -0.46028 | 0.16878 | 0.17143 | 0.16528 | 0.15964 | 0.15424 | 0.14432 | 0.13569 | 0.12605 | 0.10872 | 0.090947 | 0.084875 | -0.011097 | -0.12495 | -0.20416 | 0.077993 | 0.07384 | 0.064394 | 0.055534 | 0.046957 | 0.033099 | 0.020611 | 0.0041033 | -0.021582 | -0.047791 | -0.060491 | -0.20037 | -0.3408 | -0.38791
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.029 | 0.13028 | 0.10918 | 0.085731 | 0.06181 | 0.043576 | 0.029364 | 0.0063569 | -0.00084849 | -0.007184 | -0.015807 | -0.023645 | -0.061363 | -0.11317 | -0.17148 | 0.18163 | 0.15744 | 0.13182 | 0.10639 | 0.088079 | 0.068179 | 0.043691 | 0.039209 | 0.035716 | 0.028538 | 0.021983 | -0.012532 | -0.070691 | -0.1373 | 0.19065 | 0.16599 | 0.13883 | 0.11165 | 0.091411 | 0.065887 | 0.040532 | 0.033905 | 0.02838 | 0.018659 | 0.0098293 | -0.029566 | -0.090327 | -0.16037
|  | MAARUIG | CT |  |  |  | 0.029 | 0.13028 | 0.12244 | 0.11446 | 0.090892 | 0.077008 | 0.075983 | 0.062009 | 0.054886 | 0.045593 | 0.039739 | 0.031573 | 0.0031482 | -0.020806 | -0.043512 | 0.18163 | 0.17432 | 0.16829 | 0.14336 | 0.13149 | 0.12755 | 0.11529 | 0.1105 | 0.10211 | 0.098144 | 0.090184 | 0.068902 | 0.049022 | 0.025992 | 0.19065 | 0.18275 | 0.17515 | 0.14834 | 0.13434 | 0.12463 | 0.11126 | 0.10437 | 0.093671 | 0.08861 | 0.07878 | 0.05137 | 0.027509 | 0.0018515
|  | MAARUIG | LW |  |  |  | 0.029 | 0.13045 | 0.10918 | 0.085731 | 0.06181 | 0.043576 | 0.029364 | 0.0063569 | -0.00084849 | -0.007184 | -0.015807 | -0.023645 | -0.061363 | -0.11317 | -0.17148 | 0.18169 | 0.15744 | 0.13182 | 0.10639 | 0.088079 | 0.068179 | 0.043691 | 0.039209 | 0.035716 | 0.028538 | 0.021983 | -0.012532 | -0.070691 | -0.1373 | 0.19081 | 0.16599 | 0.13883 | 0.11165 | 0.091411 | 0.065887 | 0.040532 | 0.033905 | 0.02838 | 0.018659 | 0.0098293 | -0.029566 | -0.090327 | -0.16037
|  | MAARUIG | ST |  |  |  | 0.029 | 0.13278 | 0.12935 | 0.11614 | 0.10545 | 0.096829 | 0.089835 | 0.081943 | 0.083939 | 0.084001 | 0.076889 | 0.074872 | 0.017893 | -0.042608 | -0.098251 | 0.18372 | 0.18058 | 0.16563 | 0.15402 | 0.14509 | 0.13841 | 0.13084 | 0.1298 | 0.12982 | 0.12322 | 0.1221 | 0.062881 | -0.0041457 | -0.065361 | 0.19309 | 0.18955 | 0.17403 | 0.16184 | 0.15234 | 0.14507 | 0.13691 | 0.13174 | 0.13225 | 0.12434 | 0.12271 | 0.058144 | -0.013273 | -0.077842
|  | MAARUIG | FS |  |  |  | 0.029 | 0.1333 | 0.13117 | 0.12624 | 0.1208 | 0.11439 | 0.10746 | 0.09751 | 0.088594 | 0.077447 | 0.078812 | 0.083096 | 0.065402 | 0.049166 | 0.028177 | 0.18405 | 0.18232 | 0.17721 | 0.17159 | 0.16479 | 0.15748 | 0.14651 | 0.13766 | 0.12637 | 0.12474 | 0.12962 | 0.11768 | 0.10767 | 0.092442 | 0.19357 | 0.19152 | 0.18606 | 0.1801 | 0.17295 | 0.16529 | 0.15398 | 0.14443 | 0.13242 | 0.12579 | 0.13145 | 0.11418 | 0.098855 | 0.07963
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0.499 | 12.3439 | 12.1306 | 11.7174 | 11.2464 | 10.6822 | 10.0914 | 9.2255 | 8.4045 | 7.8795 | 7.1612 | 6.5015 | 4.7058 | 3.7056 | 3.0121 | 14.4891 | 14.3513 | 14.2817 | 14.0853 | 13.7588 | 13.4426 | 12.8943 | 12.3875 | 12.216 | 11.8331 | 11.4363 | 10.0807 | 9.0828 | 6.837 | 13.6205 | 13.4555 | 13.2664 | 12.9875 | 12.7267 | 12.3835 | 11.549 | 10.727 | 10.2784 | 9.5504 | 8.8796 | 7.1752 | 6.4925 | 5.8419
|  | MACALPINE ROAD | CT |  |  |  | 0.499 | 12.3474 | 12.1474 | 11.7487 | 11.2464 | 10.6822 | 10.0914 | 9.2255 | 8.4045 | 7.945 | 7.3553 | 6.8484 | 4.8565 | 3.7056 | 3.0121 | 14.4891 | 14.3615 | 14.2817 | 14.0853 | 13.7588 | 13.4426 | 12.8943 | 12.3875 | 12.216 | 11.8331 | 11.4718 | 10.0807 | 9.0828 | 7.6642 | 13.6205 | 13.4675 | 13.2664 | 12.9875 | 12.7267 | 12.3835 | 11.549 | 10.727 | 10.3949 | 9.8053 | 9.2869 | 7.4449 | 6.4925 | 5.8419
|  | MACALPINE ROAD | LW |  |  |  | 0.499 | 12.3439 | 12.1306 | 11.7174 | 11.2676 | 10.7675 | 10.1696 | 9.3351 | 8.5074 | 7.8795 | 7.1612 | 6.5015 | 4.7058 | 4.2112 | 3.7148 | 14.4958 | 14.3513 | 14.2844 | 14.1762 | 13.9224 | 13.5918 | 13.0603 | 12.5944 | 12.3031 | 11.855 | 11.4363 | 10.4278 | 10.2151 | 9.8501 | 13.6206 | 13.4555 | 13.2711 | 13.0769 | 12.8621 | 12.4658 | 11.6421 | 10.8253 | 10.2784 | 9.5504 | 8.8796 | 7.1752 | 6.7711 | 6.2238
|  | MACALPINE ROAD | ST |  |  |  | 0.499 | 12.4567 | 12.363 | 12.3135 | 12.2588 | 12.1927 | 12.1311 | 11.9292 | 11.7925 | 11.6305 | 11.4549 | 11.2584 | 9.9411 | 8.664 | 7.2377 | 14.5123 | 14.4238 | 14.3788 | 14.338 | 14.2923 | 14.2464 | 14.0702 | 13.9776 | 13.8403 | 13.6133 | 13.3488 | 12.0702 | 10.9312 | 9.4168 | 13.6755 | 13.5962 | 13.5409 | 13.4858 | 13.4216 | 13.3553 | 13.156 | 13.0291 | 12.8609 | 12.6929 | 12.5018 | 11.5749 | 10.6331 | 9.5499
|  | MACALPINE ROAD | FS |  |  |  | 0.499 | 12.4443 | 12.3596 | 12.26 | 12.1729 | 12.0756 | 11.9615 | 11.7912 | 11.6002 | 11.3645 | 11.1722 | 10.9383 | 9.5359 | 7.8938 | 6.332 | 14.5147 | 14.4445 | 14.4072 | 14.3791 | 14.3456 | 14.2996 | 14.1857 | 14.0251 | 13.7896 | 13.5952 | 13.3552 | 11.9674 | 9.797 | 6.837 | 13.6754 | 13.6115 | 13.5526 | 13.5013 | 13.4433 | 13.3723 | 13.2384 | 13.1305 | 12.9811 | 12.8588 | 12.7093 | 11.6143 | 10.008 | 8.679
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 0.94 | 8.2135 | 7.9237 | 7.3865 | 6.6978 | 5.9709 | 5.1572 | 3.9601 | 2.937 | 1.7355 | 0.76593 | 0.0088199 | -2.2019 | -3.3006 | -4.2825 | 12.3437 | 12.2461 | 12.1375 | 11.975 | 11.791 | 11.4879 | 10.7616 | 10.123 | 9.4185 | 8.8335 | 8.3771 | 7.1228 | 6.3739 | 5.4342 | 11.037 | 10.7678 | 10.2863 | 9.6643 | 9.0095 | 8.2732 | 7.1719 | 6.2453 | 5.1418 | 4.2456 | 3.5455 | 1.5279 | 0.59805 | -0.26912
|  | MACDUFF | CT |  |  |  | 0.94 | 8.2135 | 7.9237 | 7.3865 | 6.6978 | 5.9709 | 5.1572 | 3.9601 | 2.937 | 1.9157 | 1.0354 | 0.41059 | -1.9887 | -3.3006 | -4.2825 | 12.3437 | 12.2461 | 12.1375 | 11.975 | 11.791 | 11.4879 | 10.7616 | 10.123 | 9.4658 | 8.901 | 8.5217 | 7.1228 | 6.3739 | 5.4342 | 11.037 | 10.7678 | 10.2863 | 9.6643 | 9.0095 | 8.2732 | 7.1719 | 6.2453 | 5.3066 | 4.4949 | 3.918 | 1.7481 | 0.59805 | -0.26912
|  | MACDUFF | LW |  |  |  | 0.94 | 8.2312 | 7.9697 | 7.4348 | 6.7689 | 6.1006 | 5.2483 | 4.0427 | 2.9449 | 1.7355 | 0.76593 | 0.0088199 | -2.2019 | -2.9696 | -3.7629 | 12.3479 | 12.2677 | 12.2001 | 12.0991 | 12.015 | 11.6305 | 10.8884 | 10.1972 | 9.4185 | 8.8335 | 8.3771 | 7.1436 | 6.8231 | 6.345 | 11.0548 | 10.8133 | 10.3394 | 9.7436 | 9.1481 | 8.3723 | 7.2607 | 6.2632 | 5.1418 | 4.2456 | 3.5455 | 1.5279 | 0.85672 | 0.14699
|  | MACDUFF | ST |  |  |  | 0.94 | 8.3403 | 8.1902 | 8.0195 | 7.8179 | 7.6308 | 7.4084 | 6.9585 | 6.3502 | 5.7396 | 5.1957 | 5.056 | 3.0007 | 1.6079 | 0.2281 | 12.377 | 12.3391 | 12.2931 | 12.2313 | 12.1687 | 12.0869 | 11.7448 | 11.2066 | 10.6789 | 10.2048 | 9.9594 | 8.4192 | 7.8355 | 7.2036 | 11.1549 | 11.0199 | 10.8692 | 10.6885 | 10.5204 | 10.3142 | 9.8896 | 9.3167 | 8.7383 | 8.2228 | 8.1003 | 6.1675 | 4.9209 | 3.7223
|  | MACDUFF | FS |  |  |  | 0.94 | 8.4093 | 8.3015 | 8.1773 | 8.0292 | 7.8731 | 7.7378 | 7.4339 | 6.9218 | 6.4534 | 6.0036 | 5.5854 | 3.4202 | 1.1306 | -0.6949 | 12.3863 | 12.3577 | 12.3234 | 12.2776 | 12.2258 | 12.1777 | 11.955 | 11.6044 | 11.3084 | 11.0597 | 10.8368 | 9.439 | 7.6406 | 5.757 | 11.2151 | 11.1181 | 11.0087 | 10.8765 | 10.7349 | 10.612 | 10.3266 | 9.8507 | 9.4171 | 8.9994 | 8.6095 | 6.6122 | 4.5106 | 2.8712
| CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0.072 | 1.0647 | 1.0357 | 3.229 | 3.1811 | 3.1108 | 3.0509 | 2.962 | 2.9347 | 2.903 | 2.8717 | 2.8273 | 2.7505 | 2.7316 | 2.6853 | 1.5606 | 1.5407 | 3.9834 | 3.9595 | 3.9191 | 3.8884 | 3.8358 | 3.8117 | 3.7815 | 3.7445 | 3.7071 | 3.6444 | 3.6361 | 3.5922 | 1.2234 | 1.2145 | 3.5607 | 3.518 | 3.451 | 3.3958 | 3.3101 | 3.2825 | 3.2483 | 3.2118 | 3.1654 | 3.0897 | 3.0756 | 3.0345
|  | MACHRIE | CT |  |  |  | 0.072 | 1.0647 | 1.0357 | 3.229 | 3.1811 | 3.1108 | 3.0509 | 2.962 | 2.9347 | 2.903 | 2.8744 | 2.8443 | 2.7811 | 2.7642 | 2.727 | 1.5606 | 1.5407 | 3.9834 | 3.9595 | 3.9191 | 3.8884 | 3.8358 | 3.8117 | 3.7829 | 3.7555 | 3.7257 | 3.6569 | 3.6361 | 3.5922 | 1.2239 | 1.2147 | 3.5607 | 3.518 | 3.451 | 3.3958 | 3.3101 | 3.2825 | 3.2483 | 3.2188 | 3.1856 | 3.1186 | 3.1058 | 3.0744
|  | MACHRIE | LW |  |  |  | 0.072 | 1.0675 | 1.0416 | 3.2463 | 3.2044 | 3.1532 | 3.0906 | 3.0091 | 2.9785 | 2.9166 | 2.8717 | 2.8273 | 2.7505 | 2.7316 | 2.6853 | 1.562 | 1.5444 | 3.9935 | 3.9715 | 3.9429 | 3.9063 | 3.8556 | 3.8315 | 3.7815 | 3.7445 | 3.7071 | 3.6444 | 3.6365 | 3.6065 | 1.2234 | 1.2145 | 3.5681 | 3.5389 | 3.4907 | 3.4308 | 3.3514 | 3.3214 | 3.2566 | 3.2118 | 3.1654 | 3.0897 | 3.0756 | 3.0345
|  | MACHRIE | ST |  |  |  | 0.072 | 1.0775 | 1.0612 | 3.2993 | 3.284 | 3.2621 | 3.2486 | 3.2219 | 3.1899 | 3.1618 | 3.1214 | 3.1005 | 2.9463 | 2.9314 | 2.948 | 1.5696 | 1.5593 | 4.0264 | 4.0158 | 3.9999 | 3.9907 | 3.9708 | 3.9468 | 3.926 | 3.8951 | 3.8798 | 3.7445 | 3.7145 | 3.6985 | 1.2275 | 1.2237 | 3.5825 | 3.5775 | 3.57 | 3.5641 | 3.5538 | 3.5221 | 3.4939 | 3.4523 | 3.433 | 3.2753 | 3.2622 | 3.2805
|  | MACHRIE | FS |  |  |  | 0.072 | 1.0853 | 1.074 | 3.3173 | 3.3073 | 3.3008 | 3.2865 | 3.2694 | 3.2583 | 3.2293 | 3.2112 | 3.1811 | 3.039 | 2.9068 | 2.8735 | 1.5731 | 1.5654 | 4.0343 | 4.0254 | 4.0193 | 4.0069 | 3.9919 | 3.9842 | 3.9619 | 3.9483 | 3.925 | 3.8084 | 3.6905 | 3.6213 | 1.2283 | 1.2254 | 3.5847 | 3.5803 | 3.5766 | 3.5704 | 3.563 | 3.5583 | 3.5477 | 3.5396 | 3.509 | 3.3663 | 3.2372 | 3.2087
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 0.127 | 0.64826 | 0.60999 | 0.54542 | 0.47083 | 0.38573 | 0.30096 | 0.18969 | 0.1496 | 0.10919 | 0.062375 | 0.017567 | -0.1141 | -0.19047 | -0.28785 | 0.96411 | 0.9383 | 0.91541 | 0.89095 | 0.86802 | 0.81623 | 0.7452 | 0.71202 | 0.6583 | 0.61489 | 0.56379 | 0.43346 | 0.31451 | 0.25675 | 0.80291 | 0.77617 | 0.73737 | 0.67975 | 0.60422 | 0.5327 | 0.42541 | 0.37549 | 0.2929 | 0.22784 | 0.16389 | 0.0081323 | -0.057084 | -0.16337
|  | MALLAIG | CT |  |  |  | 0.127 | 0.64826 | 0.61053 | 0.54542 | 0.47083 | 0.38573 | 0.30096 | 0.18969 | 0.1496 | 0.1148 | 0.080505 | 0.057832 | -0.036655 | -0.091151 | -0.15999 | 0.96411 | 0.94673 | 0.92834 | 0.89985 | 0.86897 | 0.82556 | 0.75873 | 0.72431 | 0.6907 | 0.65428 | 0.62501 | 0.51394 | 0.47062 | 0.38581 | 0.80291 | 0.78555 | 0.74127 | 0.68011 | 0.60422 | 0.53556 | 0.43202 | 0.38263 | 0.33346 | 0.2803 | 0.23992 | 0.11028 | 0.066899 | 3.0011e-05
|  | MALLAIG | LW |  |  |  | 0.127 | 0.6542 | 0.60999 | 0.54875 | 0.48142 | 0.40826 | 0.31954 | 0.21191 | 0.16926 | 0.10919 | 0.062375 | 0.017567 | -0.1141 | -0.19047 | -0.28785 | 0.96414 | 0.9383 | 0.91541 | 0.89095 | 0.86802 | 0.81623 | 0.7452 | 0.71202 | 0.6583 | 0.61489 | 0.56379 | 0.44675 | 0.40223 | 0.32339 | 0.80353 | 0.77617 | 0.73737 | 0.67975 | 0.6156 | 0.5327 | 0.42541 | 0.37549 | 0.2929 | 0.22784 | 0.16389 | 0.0081323 | -0.057084 | -0.16337
|  | MALLAIG | ST |  |  |  | 0.127 | 0.65925 | 0.63592 | 0.60428 | 0.57097 | 0.54048 | 0.50403 | 0.47195 | 0.43108 | 0.38948 | 0.33964 | 0.28655 | 0.070627 | -0.015648 | -0.049986 | 0.96816 | 0.96099 | 0.94492 | 0.92807 | 0.91155 | 0.89128 | 0.87065 | 0.84114 | 0.80452 | 0.76206 | 0.71462 | 0.43346 | 0.31451 | 0.25675 | 0.80593 | 0.7972 | 0.78295 | 0.76712 | 0.73957 | 0.70236 | 0.67464 | 0.63069 | 0.5875 | 0.53188 | 0.47206 | 0.2216 | 0.091404 | 0.020925
|  | MALLAIG | FS |  |  |  | 0.127 | 0.67583 | 0.66159 | 0.65261 | 0.64119 | 0.63122 | 0.61645 | 0.5987 | 0.57361 | 0.53677 | 0.50572 | 0.46933 | 0.27685 | 0.067582 | -0.037639 | 0.97075 | 0.96634 | 0.95746 | 0.9467 | 0.9352 | 0.92069 | 0.90289 | 0.88584 | 0.85914 | 0.83409 | 0.80662 | 0.62587 | 0.44192 | 0.30814 | 0.81108 | 0.80576 | 0.80086 | 0.79411 | 0.78819 | 0.77862 | 0.7634 | 0.7421 | 0.70173 | 0.67099 | 0.63135 | 0.42359 | 0.21727 | 0.070749
| KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0.048 | 5.1536 | 5.0114 | 4.8106 | 4.5301 | 4.2318 | 3.9196 | 3.5331 | 3.3229 | 3.0983 | 2.9267 | 2.7804 | 2.3501 | 2.0289 | 1.6832 | 5.6048 | 5.5351 | 5.4426 | 5.3372 | 5.2286 | 5.0908 | 4.9035 | 4.7803 | 4.6288 | 4.5149 | 4.4123 | 4.1562 | 3.9872 | 3.6885 | 5.3794 | 5.2521 | 5.0651 | 4.8235 | 4.5601 | 4.2782 | 3.9272 | 3.7345 | 3.5241 | 3.3641 | 3.2179 | 2.8064 | 2.5178 | 2.1971
|  | MARNOCH | CT |  |  |  | 0.048 | 5.1536 | 5.0114 | 4.8106 | 4.5301 | 4.2318 | 3.9196 | 3.5331 | 3.3229 | 3.1458 | 3.002 | 2.8921 | 2.4727 | 2.2139 | 1.9273 | 5.6048 | 5.5448 | 5.4703 | 5.344 | 5.234 | 5.1237 | 4.9313 | 4.8025 | 4.6896 | 4.5912 | 4.5055 | 4.1979 | 3.9919 | 3.6885 | 5.3794 | 5.2521 | 5.0755 | 4.8235 | 4.5601 | 4.2869 | 3.9372 | 3.7458 | 3.5874 | 3.4536 | 3.3475 | 2.9486 | 2.7236 | 2.4701
|  | MARNOCH | LW |  |  |  | 0.048 | 5.1789 | 5.0385 | 4.8108 | 4.544 | 4.2537 | 3.9247 | 3.5417 | 3.3292 | 3.0983 | 2.9267 | 2.7804 | 2.3501 | 2.0289 | 1.6832 | 5.6081 | 5.5351 | 5.4426 | 5.3372 | 5.2286 | 5.0908 | 4.9035 | 4.7803 | 4.6288 | 4.5149 | 4.4123 | 4.1562 | 3.9872 | 3.7815 | 5.402 | 5.2719 | 5.0651 | 4.8284 | 4.5722 | 4.2782 | 3.9272 | 3.7345 | 3.5241 | 3.3641 | 3.2179 | 2.8064 | 2.5178 | 2.1971
|  | MARNOCH | ST |  |  |  | 0.048 | 5.2025 | 5.0913 | 4.9433 | 4.7779 | 4.6036 | 4.4388 | 4.2567 | 4.0964 | 3.9128 | 3.7468 | 3.5837 | 2.9249 | 2.5884 | 2.3584 | 5.6255 | 5.5883 | 5.53 | 5.4644 | 5.3945 | 5.3282 | 5.2389 | 5.1585 | 5.0397 | 4.9428 | 4.8439 | 4.3466 | 4.097 | 3.7918 | 5.4246 | 5.3262 | 5.1944 | 5.0503 | 4.8981 | 4.7571 | 4.596 | 4.453 | 4.2893 | 4.138 | 3.988 | 3.3536 | 3.0321 | 2.8163
|  | MARNOCH | FS |  |  |  | 0.048 | 5.2663 | 5.198 | 5.1504 | 5.0881 | 5.0166 | 4.9415 | 4.8731 | 4.749 | 4.5872 | 4.4489 | 4.342 | 3.691 | 3.0181 | 2.7081 | 5.6402 | 5.6165 | 5.5916 | 5.5586 | 5.5198 | 5.4776 | 5.4287 | 5.3716 | 5.2794 | 5.2082 | 5.1509 | 4.7537 | 4.203 | 3.6956 | 5.48 | 5.4201 | 5.3788 | 5.326 | 5.264 | 5.1982 | 5.1373 | 5.028 | 4.8828 | 4.7579 | 4.6641 | 4.0545 | 3.4328 | 3.1542
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 0.356 | 3.009 | 2.967 | 2.9059 | 2.8247 | 2.7458 | 2.6567 | 2.5584 | 2.5153 | 2.4657 | 2.4192 | 2.3746 | 2.2463 | 2.1431 | 2.0423 | 3.1546 | 3.1285 | 3.0945 | 3.0541 | 3.0192 | 2.9683 | 2.9146 | 2.8855 | 2.8522 | 2.8211 | 2.7926 | 2.7158 | 2.6532 | 2.6022 | 3.0543 | 3.02 | 2.9714 | 2.913 | 2.8377 | 2.7483 | 2.6497 | 2.604 | 2.5585 | 2.5157 | 2.4759 | 2.3676 | 2.2704 | 2.1898
|  | MARYBANK | CT |  |  |  | 0.356 | 3.009 | 2.967 | 2.9059 | 2.8247 | 2.7458 | 2.6567 | 2.5584 | 2.5153 | 2.4842 | 2.4534 | 2.4264 | 2.3069 | 2.2218 | 2.1418 | 3.1546 | 3.1334 | 3.107 | 3.064 | 3.0282 | 2.9867 | 2.9393 | 2.9112 | 2.8907 | 2.8684 | 2.8483 | 2.7857 | 2.7452 | 2.7143 | 3.0543 | 3.0218 | 2.9794 | 2.9159 | 2.8377 | 2.7483 | 2.6501 | 2.6076 | 2.5803 | 2.5511 | 2.5273 | 2.4345 | 2.3613 | 2.3003
|  | MARYBANK | LW |  |  |  | 0.356 | 3.0167 | 2.9719 | 2.9073 | 2.8312 | 2.758 | 2.6632 | 2.5639 | 2.5165 | 2.4657 | 2.4192 | 2.3746 | 2.2463 | 2.1431 | 2.0423 | 3.1571 | 3.1285 | 3.0945 | 3.0541 | 3.0192 | 2.9683 | 2.9146 | 2.8855 | 2.8522 | 2.8211 | 2.7926 | 2.7158 | 2.6532 | 2.6022 | 3.0587 | 3.02 | 2.9714 | 2.913 | 2.8447 | 2.749 | 2.6497 | 2.604 | 2.5585 | 2.5157 | 2.4759 | 2.3676 | 2.2704 | 2.1898
|  | MARYBANK | ST |  |  |  | 0.356 | 3.0233 | 2.9946 | 2.9497 | 2.9064 | 2.8611 | 2.8199 | 2.7719 | 2.7333 | 2.6839 | 2.6405 | 2.588 | 2.3487 | 2.2252 | 2.1609 | 3.1619 | 3.1492 | 3.1256 | 3.104 | 3.0815 | 3.0626 | 3.0384 | 3.0186 | 2.9902 | 2.9666 | 2.9361 | 2.7773 | 2.6932 | 2.6487 | 3.0659 | 3.0456 | 3.0112 | 2.9788 | 2.9443 | 2.9122 | 2.8653 | 2.8286 | 2.7809 | 2.7412 | 2.6918 | 2.4753 | 2.3602 | 2.2959
|  | MARYBANK | FS |  |  |  | 0.356 | 3.0419 | 3.0253 | 3.0107 | 2.9963 | 2.9795 | 2.9656 | 2.946 | 2.9117 | 2.8773 | 2.8385 | 2.8002 | 2.5942 | 2.365 | 2.2232 | 3.1686 | 3.1615 | 3.1526 | 3.1438 | 3.1331 | 3.1248 | 3.1116 | 3.093 | 3.0741 | 3.0516 | 3.0306 | 2.915 | 2.7899 | 2.6866 | 3.0772 | 3.0656 | 3.0529 | 3.0404 | 3.0252 | 3.0132 | 2.995 | 2.9674 | 2.9381 | 2.9049 | 2.8726 | 2.6936 | 2.4948 | 2.3516
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0.717 | 7.4481 | 7.1957 | 6.7432 | 6.2473 | 5.486 | 4.6435 | 3.9342 | 3.2669 | 2.7382 | 2.2796 | 1.7745 | 0.26985 | -0.33701 | -0.95133 | 8.4599 | 8.3046 | 8.0714 | 7.8153 | 7.2434 | 6.6795 | 6.2865 | 5.9022 | 5.5821 | 5.4088 | 5.1142 | 4.2862 | 3.8245 | 3.1816 | 8.416 | 8.1872 | 7.7802 | 7.3352 | 6.5528 | 5.697 | 5.0394 | 4.4249 | 3.9487 | 3.5298 | 3.0595 | 1.6777 | 1.1886 | 0.63167
|  | MARYTON | CT |  |  |  | 0.717 | 7.4481 | 7.1957 | 6.7568 | 6.2711 | 5.486 | 4.6903 | 3.9755 | 3.2978 | 2.7382 | 2.565 | 2.1637 | 0.49601 | -0.33701 | -0.95133 | 8.4599 | 8.3046 | 8.0737 | 7.8153 | 7.2434 | 6.6833 | 6.291 | 5.9022 | 5.5821 | 5.5487 | 5.3039 | 4.3546 | 3.8245 | 3.1816 | 8.416 | 8.1872 | 7.7956 | 7.3563 | 6.5528 | 5.7444 | 5.087 | 4.4625 | 3.9487 | 3.8122 | 3.4398 | 1.9262 | 1.1886 | 0.63167
|  | MARYTON | LW |  |  |  | 0.717 | 7.4587 | 7.2038 | 6.7432 | 6.2473 | 5.4958 | 4.6435 | 3.9342 | 3.2669 | 2.8604 | 2.2796 | 1.7745 | 0.26985 | -0.20121 | -0.77328 | 8.4684 | 8.3079 | 8.0714 | 7.8215 | 7.2842 | 6.6795 | 6.2865 | 5.9169 | 5.7403 | 5.4088 | 5.1142 | 4.2862 | 4.0576 | 3.6969 | 8.4267 | 8.1928 | 7.7802 | 7.3352 | 6.5647 | 5.697 | 5.0394 | 4.4249 | 4.0667 | 3.5298 | 3.0595 | 1.6777 | 1.2456 | 0.70544
|  | MARYTON | ST |  |  |  | 0.717 | 7.5373 | 7.3865 | 7.2029 | 7.0143 | 6.5921 | 6.1795 | 5.974 | 5.7427 | 5.5019 | 5.2065 | 4.8949 | 3.6143 | 2.7137 | 1.8832 | 8.5114 | 8.4267 | 8.3186 | 8.2029 | 7.8049 | 7.4149 | 7.2774 | 7.1182 | 6.949 | 6.7488 | 6.5347 | 5.6224 | 4.9626 | 4.2569 | 8.4992 | 8.3681 | 8.2066 | 8.0372 | 7.5625 | 7.098 | 6.9062 | 6.6905 | 6.4659 | 6.2032 | 5.9232 | 4.7109 | 3.8805 | 3.1303
|  | MARYTON | FS |  |  |  | 0.717 | 7.597 | 7.4891 | 7.364 | 7.2558 | 6.9408 | 6.553 | 6.4292 | 6.2012 | 5.9366 | 5.7187 | 5.4583 | 4.1156 | 2.5722 | 1.482 | 8.5368 | 8.4716 | 8.3895 | 8.3176 | 8.0002 | 7.6013 | 7.5022 | 7.3499 | 7.1649 | 7.0185 | 6.8427 | 5.948 | 4.7221 | 3.4484 | 8.5512 | 8.4578 | 8.3477 | 8.2521 | 7.8896 | 7.438 | 7.3198 | 7.1098 | 6.8636 | 6.6639 | 6.4287 | 5.2206 | 3.7942 | 2.7906
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0.193 | 4.5969 | 4.4554 | 4.2814 | 4.0613 | 3.7937 | 3.5115 | 3.166 | 2.973 | 2.8181 | 2.631 | 2.4638 | 2.0666 | 1.8421 | 1.5779 | 5.6591 | 5.5825 | 5.4928 | 5.3769 | 5.2368 | 5.1096 | 4.93 | 4.8021 | 4.711 | 4.5979 | 4.4972 | 4.2707 | 4.0876 | 3.7361 | 5.5003 | 5.3711 | 5.2148 | 5.0169 | 4.7758 | 4.5555 | 4.2561 | 4.0543 | 3.8772 | 3.6956 | 3.535 | 3.1657 | 2.9713 | 2.739
|  | MAUD | CT |  |  |  | 0.193 | 4.5969 | 4.4554 | 4.2814 | 4.0613 | 3.7937 | 3.5115 | 3.166 | 2.973 | 2.8498 | 2.7234 | 2.6059 | 2.192 | 1.9814 | 1.7256 | 5.6591 | 5.5825 | 5.4928 | 5.3769 | 5.2368 | 5.1096 | 4.93 | 4.8021 | 4.7311 | 4.6377 | 4.5549 | 4.2707 | 4.0876 | 3.8152 | 5.5003 | 5.3711 | 5.2148 | 5.0169 | 4.7758 | 4.5555 | 4.2561 | 4.0543 | 3.9416 | 3.7987 | 3.6751 | 3.2896 | 3.11 | 2.9035
|  | MAUD | LW |  |  |  | 0.193 | 4.6243 | 4.4827 | 4.3096 | 4.0795 | 3.8346 | 3.5406 | 3.1928 | 2.9948 | 2.8181 | 2.631 | 2.4638 | 2.0666 | 1.8421 | 1.5779 | 5.6741 | 5.5979 | 5.5126 | 5.395 | 5.2711 | 5.1297 | 4.9455 | 4.8204 | 4.711 | 4.5979 | 4.4972 | 4.2752 | 4.1714 | 4.0384 | 5.5258 | 5.3955 | 5.2409 | 5.0339 | 4.814 | 4.5684 | 4.2618 | 4.0574 | 3.8772 | 3.6956 | 3.535 | 3.1657 | 2.9713 | 2.739
|  | MAUD | ST |  |  |  | 0.193 | 4.6488 | 4.5536 | 4.4169 | 4.275 | 4.117 | 3.9647 | 3.7882 | 3.6325 | 3.4889 | 3.3283 | 3.1623 | 2.5036 | 2.2317 | 2.0703 | 5.6875 | 5.6376 | 5.5666 | 5.4931 | 5.4086 | 5.334 | 5.2374 | 5.1477 | 5.0663 | 4.9677 | 4.8636 | 4.4203 | 4.1888 | 3.9521 | 5.5491 | 5.4644 | 5.3419 | 5.2161 | 5.0745 | 4.9489 | 4.7989 | 4.6554 | 4.5302 | 4.3751 | 4.2124 | 3.5766 | 3.33 | 3.19
|  | MAUD | FS |  |  |  | 0.193 | 4.7063 | 4.6396 | 4.5949 | 4.5368 | 4.4672 | 4.4129 | 4.3355 | 4.2221 | 4.0874 | 3.9552 | 3.8598 | 3.2187 | 2.5604 | 2.304 | 5.7126 | 5.6752 | 5.6479 | 5.6127 | 5.5693 | 5.5353 | 5.4807 | 5.4115 | 5.3282 | 5.2458 | 5.1829 | 4.7474 | 4.2104 | 3.7361 | 5.5987 | 5.5388 | 5.4988 | 5.447 | 5.3839 | 5.3359 | 5.2638 | 5.1609 | 5.0372 | 4.9148 | 4.8292 | 4.2326 | 3.6242 | 3.394
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.177 | 0.056181 | 0.018259 | -0.033485 | -0.10131 | -0.1694 | -0.24675 | -0.33736 | -0.38846 | -0.44576 | -0.4785 | -0.51999 | -0.64632 | -0.72356 | -0.80942 | 0.31825 | 0.29296 | 0.26206 | 0.22102 | 0.18445 | 0.14424 | 0.091324 | 0.050594 | 0.00046555 | -0.018608 | -0.054211 | -0.14009 | -0.18409 | -0.24565 | 0.23018 | 0.19676 | 0.14724 | 0.088043 | 0.029717 | -0.039999 | -0.12126 | -0.16472 | -0.22681 | -0.25562 | -0.30147 | -0.42028 | -0.54041 | -0.60179
|  | MELVICH | CT |  |  |  | 0.177 | 0.056181 | 0.018259 | -0.031853 | -0.10033 | -0.16382 | -0.24031 | -0.32757 | -0.37843 | -0.4168 | -0.43876 | -0.46834 | -0.57916 | -0.63946 | -0.70275 | 0.31825 | 0.29714 | 0.27371 | 0.23315 | 0.20598 | 0.16647 | 0.12053 | 0.077626 | 0.045091 | 0.032062 | 0.0021269 | -0.07558 | -0.10729 | -0.15428 | 0.23018 | 0.19676 | 0.15387 | 0.0923 | 0.036243 | -0.029124 | -0.10656 | -0.15119 | -0.18419 | -0.20664 | -0.2376 | -0.34127 | -0.38697 | -0.44531
|  | MELVICH | LW |  |  |  | 0.177 | 0.063418 | 0.022946 | -0.033485 | -0.10131 | -0.1694 | -0.24675 | -0.33736 | -0.38846 | -0.44576 | -0.4785 | -0.51999 | -0.64632 | -0.72356 | -0.80942 | 0.32069 | 0.29296 | 0.26206 | 0.22102 | 0.18445 | 0.14424 | 0.091324 | 0.050594 | 0.00046555 | -0.018608 | -0.054211 | -0.14009 | -0.18409 | -0.24565 | 0.23599 | 0.19783 | 0.14724 | 0.088043 | 0.029717 | -0.039999 | -0.12126 | -0.16472 | -0.22681 | -0.25562 | -0.30147 | -0.42028 | -0.48768 | -0.57684
|  | MELVICH | ST |  |  |  | 0.177 | 0.069845 | 0.041912 | 0.0018581 | -0.036225 | -0.078492 | -0.11758 | -0.1635 | -0.19686 | -0.24384 | -0.28453 | -0.33327 | -0.56199 | -0.68492 | -0.74784 | 0.32825 | 0.31433 | 0.29323 | 0.27535 | 0.25185 | 0.23362 | 0.2067 | 0.19214 | 0.15999 | 0.13678 | 0.10349 | -0.062631 | -0.16006 | -0.20847 | 0.24095 | 0.21702 | 0.17993 | 0.14431 | 0.10593 | 0.069112 | 0.026337 | -0.0092078 | -0.056544 | -0.10076 | -0.15163 | -0.41549 | -0.54041 | -0.60179
|  | MELVICH | FS |  |  |  | 0.177 | 0.08236 | 0.070879 | 0.058038 | 0.044329 | 0.028976 | 0.010534 | -0.0055669 | -0.039068 | -0.06847 | -0.10549 | -0.14176 | -0.31963 | -0.53072 | -0.64943 | 0.32576 | 0.32492 | 0.31595 | 0.30608 | 0.29449 | 0.27887 | 0.26709 | 0.2449 | 0.23042 | 0.20485 | 0.18048 | 0.071216 | -0.052093 | -0.1273 | 0.2519 | 0.24193 | 0.22921 | 0.21543 | 0.20007 | 0.18203 | 0.16449 | 0.13307 | 0.10161 | 0.065232 | 0.0298 | -0.16681 | -0.38458 | -0.50453
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 0 | 12.0823 | 11.8115 | 11.2148 | 10.0623 | 8.9517 | 8.0934 | 7.1385 | 6.0376 | 4.8243 | 4.0474 | 2.8949 | 0.29291 | 0.084065 | -0.7639 | 13.2338 | 13.0539 | 12.6709 | 11.7656 | 10.8952 | 10.4791 | 9.9566 | 9.3062 | 8.5678 | 8.1317 | 7.3604 | 5.7197 | 5.0595 | 3.2347 | 13.23 | 12.96 | 12.4324 | 11.4157 | 10.3685 | 9.585 | 8.7086 | 7.6701 | 6.5131 | 5.7869 | 4.6943 | 2.2484 | 2.0593 | 1.2334
|  | MENZIESHILL | CT |  |  |  | 0 | 12.1193 | 11.8475 | 11.2836 | 10.1305 | 8.9636 | 8.2535 | 7.3922 | 6.3377 | 5.4968 | 4.6467 | 4.0575 | 1.2153 | 0.25929 | -0.59579 | 13.2513 | 13.0568 | 12.6746 | 11.7656 | 10.8952 | 10.4791 | 9.975 | 9.3342 | 8.8281 | 8.2893 | 7.8861 | 5.9791 | 5.0595 | 3.6871 | 13.2603 | 12.9869 | 12.4768 | 11.4549 | 10.3875 | 9.7354 | 8.9404 | 7.9469 | 7.1573 | 6.3524 | 5.8134 | 3.1791 | 2.328 | 1.5265
|  | MENZIESHILL | LW |  |  |  | 0 | 12.0823 | 11.8115 | 11.2148 | 10.0623 | 8.9517 | 8.0934 | 7.1385 | 6.0376 | 4.8243 | 4.0474 | 2.8949 | 0.29291 | 0.084065 | -0.7639 | 13.2338 | 13.0539 | 12.6709 | 11.7955 | 10.9963 | 10.503 | 9.9566 | 9.3062 | 8.5678 | 8.1317 | 7.3604 | 5.7197 | 5.6151 | 4.9971 | 13.23 | 12.96 | 12.4324 | 11.4157 | 10.3685 | 9.585 | 8.7086 | 7.6701 | 6.5131 | 5.7869 | 4.6943 | 2.2484 | 2.0593 | 1.2334
|  | MENZIESHILL | ST |  |  |  | 0 | 12.2367 | 12.1391 | 11.9346 | 11.2161 | 10.563 | 10.3691 | 10.1782 | 9.8919 | 9.5331 | 9.1782 | 8.5688 | 6.4958 | 5.4879 | 4.5037 | 13.3224 | 13.2453 | 13.0478 | 12.3664 | 11.7581 | 11.5911 | 11.4229 | 11.1875 | 10.9 | 10.6105 | 10.0932 | 8.3129 | 7.268 | 5.9659 | 13.3735 | 13.2762 | 13.0784 | 12.4312 | 11.8343 | 11.6329 | 11.4361 | 11.1439 | 10.7738 | 10.4175 | 9.8209 | 7.7542 | 6.7834 | 6.1278
|  | MENZIESHILL | FS |  |  |  | 0 | 12.269 | 12.19 | 12.0056 | 11.4307 | 10.8314 | 10.6211 | 10.402 | 10.1356 | 9.7685 | 9.3952 | 8.9084 | 6.2414 | 4.1779 | 2.4852 | 13.349 | 13.2803 | 13.1163 | 12.5838 | 12.0377 | 11.8565 | 11.664 | 11.4387 | 11.1339 | 10.8226 | 10.4075 | 8.2449 | 6.0316 | 3.2347 | 13.4006 | 13.3227 | 13.1522 | 12.6393 | 12.0995 | 11.8975 | 11.6829 | 11.4374 | 11.0878 | 10.7317 | 10.2722 | 7.7887 | 5.8731 | 4.321
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.126 | 0.97018 | 2.0607 | 1.9303 | 1.7721 | 1.6115 | 1.4268 | 1.2076 | 1.1158 | 1.0243 | 0.91329 | 0.81614 | 0.59254 | 0.41938 | 0.24089 | 1.4709 | 3.1262 | 3.0861 | 3.0302 | 2.9782 | 2.8911 | 2.7809 | 2.7253 | 2.6683 | 2.5954 | 2.5307 | 2.4126 | 2.2982 | 2.0556 | 0.63182 | 2.2694 | 2.2052 | 2.1196 | 2.0415 | 1.9565 | 1.8076 | 1.7282 | 1.6487 | 1.5496 | 1.4628 | 1.2444 | 1.104 | 0.94997
|  | METHLICK | CT |  |  |  | 0.126 | 0.97018 | 2.0607 | 1.9303 | 1.7721 | 1.6115 | 1.4268 | 1.2076 | 1.1158 | 1.0288 | 0.94629 | 0.87734 | 0.65698 | 0.50393 | 0.33924 | 1.4711 | 3.1262 | 3.0861 | 3.0302 | 2.9782 | 2.8911 | 2.7809 | 2.7253 | 2.6686 | 2.6103 | 2.558 | 2.4126 | 2.2982 | 2.1322 | 0.63182 | 2.2694 | 2.2052 | 2.1196 | 2.0415 | 1.9565 | 1.8076 | 1.7282 | 1.6509 | 1.578 | 1.5176 | 1.3167 | 1.1805 | 1.0373
|  | METHLICK | LW |  |  |  | 0.126 | 0.98592 | 2.0864 | 1.9594 | 1.8015 | 1.6558 | 1.4627 | 1.2489 | 1.1533 | 1.0243 | 0.91329 | 0.81614 | 0.59254 | 0.41938 | 0.24089 | 1.4709 | 3.1276 | 3.0943 | 3.0493 | 3.0088 | 2.9142 | 2.8065 | 2.7525 | 2.6683 | 2.5954 | 2.5307 | 2.4179 | 2.3469 | 2.2662 | 0.63452 | 2.2755 | 2.2195 | 2.1474 | 2.0791 | 1.98 | 1.8469 | 1.7638 | 1.6487 | 1.5496 | 1.4628 | 1.2444 | 1.104 | 0.94997
|  | METHLICK | ST |  |  |  | 0.126 | 0.99799 | 2.1205 | 2.0204 | 1.9269 | 1.8303 | 1.7217 | 1.6274 | 1.5293 | 1.4249 | 1.314 | 1.225 | 0.75452 | 0.5909 | 0.46752 | 1.4809 | 3.1543 | 3.129 | 3.1041 | 3.0756 | 3.0369 | 2.9927 | 2.9379 | 2.8777 | 2.8117 | 2.7629 | 2.4462 | 2.3253 | 2.1775 | 0.64715 | 2.3088 | 2.266 | 2.2236 | 2.1768 | 2.1217 | 2.0676 | 2.0067 | 1.9345 | 1.856 | 1.7814 | 1.3285 | 1.1692 | 1.0991
|  | METHLICK | FS |  |  |  | 0.126 | 1.045 | 2.1925 | 2.1562 | 2.1259 | 2.0862 | 2.053 | 2.0101 | 1.948 | 1.8653 | 1.7865 | 1.7006 | 1.2721 | 0.8033 | 0.65172 | 1.4885 | 3.1668 | 3.153 | 3.1401 | 3.1228 | 3.1061 | 3.0846 | 3.0607 | 3.0263 | 2.9929 | 2.9545 | 2.6727 | 2.3191 | 2.0556 | 0.66271 | 2.3337 | 2.3138 | 2.2951 | 2.2709 | 2.2474 | 2.2181 | 2.1815 | 2.132 | 2.0838 | 2.0295 | 1.7178 | 1.3758 | 1.1979
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0.003 | -0.07493 | -0.094454 | -0.13549 | -0.18418 | -0.22988 | -0.29124 | -0.36206 | -0.42918 | -0.49805 | -0.55382 | -0.61179 | -0.79473 | -0.90207 | -1.0046 | 0.30921 | 0.29329 | 0.27141 | 0.24578 | 0.22766 | 0.19646 | 0.1617 | 0.12905 | 0.092334 | 0.067894 | 0.039533 | -0.049279 | -0.10752 | -0.17031 | 0.18336 | 0.16185 | 0.13044 | 0.092228 | 0.0561 | 0.0029496 | -0.055379 | -0.11442 | -0.17622 | -0.22324 | -0.27222 | -0.41926 | -0.50212 | -0.5862
|  | MID YELL | CT |  |  |  | 0.003 | -0.07493 | -0.088438 | -0.12555 | -0.17968 | -0.22988 | -0.29124 | -0.36206 | -0.42918 | -0.48554 | -0.52836 | -0.57234 | -0.7664 | -0.90207 | -0.98303 | 0.30921 | 0.30175 | 0.28801 | 0.26055 | 0.24182 | 0.21708 | 0.18383 | 0.15058 | 0.1231 | 0.1039 | 0.080969 | -0.010438 | -0.072575 | -0.12302 | 0.1839 | 0.17123 | 0.1464 | 0.1021 | 0.061599 | 0.012528 | -0.04575 | -0.10121 | -0.14732 | -0.18253 | -0.21886 | -0.36985 | -0.47181 | -0.53792
|  | MID YELL | LW |  |  |  | 0.003 | -0.074455 | -0.094454 | -0.13549 | -0.18418 | -0.22669 | -0.28712 | -0.35171 | -0.42442 | -0.49805 | -0.55382 | -0.61179 | -0.79473 | -0.89894 | -1.0046 | 0.30932 | 0.29329 | 0.27141 | 0.24578 | 0.22766 | 0.19646 | 0.1617 | 0.12905 | 0.092334 | 0.067894 | 0.039533 | -0.049279 | -0.10752 | -0.17031 | 0.18336 | 0.16185 | 0.13044 | 0.092228 | 0.0561 | 0.0029496 | -0.055379 | -0.11442 | -0.17622 | -0.22324 | -0.27222 | -0.41926 | -0.50212 | -0.5862
|  | MID YELL | ST |  |  |  | 0.003 | -0.063563 | -0.069593 | -0.079599 | -0.091615 | -0.10307 | -0.11228 | -0.12554 | -0.13405 | -0.15083 | -0.16321 | -0.18056 | -0.38239 | -0.57838 | -0.73944 | 0.31422 | 0.31051 | 0.30198 | 0.2927 | 0.28442 | 0.27849 | 0.2693 | 0.26361 | 0.25137 | 0.24196 | 0.22947 | 0.11828 | 0.016868 | -0.074723 | 0.1919 | 0.18638 | 0.17545 | 0.16314 | 0.1511 | 0.14086 | 0.1262 | 0.11465 | 0.093923 | 0.075267 | 0.052367 | -0.1155 | -0.242 | -0.35582
|  | MID YELL | FS |  |  |  | 0.003 | -0.070787 | -0.074018 | -0.084409 | -0.095441 | -0.10708 | -0.11805 | -0.13279 | -0.15347 | -0.17172 | -0.19475 | -0.21633 | -0.33705 | -0.47903 | -0.63141 | 0.31057 | 0.30997 | 0.30398 | 0.29757 | 0.29053 | 0.28409 | 0.27418 | 0.26269 | 0.25284 | 0.23915 | 0.22772 | 0.16658 | 0.084826 | -0.0058326 | 0.1872 | 0.18502 | 0.17646 | 0.16709 | 0.15691 | 0.147 | 0.13306 | 0.11585 | 0.099646 | 0.07902 | 0.060039 | -0.051374 | -0.17833 | -0.30542
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.604 | 2.1308 | 1.9703 | 1.7489 | 1.5164 | 1.2564 | 0.96774 | 0.68613 | 0.5183 | 0.39845 | 0.28298 | 0.15532 | -0.22044 | -0.45182 | -0.68935 | 2.9557 | 2.8862 | 2.7957 | 2.6922 | 2.5871 | 2.4731 | 2.358 | 2.2584 | 2.1608 | 2.0757 | 1.9883 | 1.7794 | 1.7034 | 1.6381 | 2.6437 | 2.5627 | 2.4473 | 2.2597 | 2.0526 | 1.8227 | 1.588 | 1.4487 | 1.343 | 1.2372 | 1.1254 | 0.80831 | 0.63425 | 0.4509
|  | MIDMAR | CT |  |  |  | 0.604 | 2.1308 | 1.9703 | 1.7489 | 1.5164 | 1.2564 | 0.96774 | 0.68613 | 0.5183 | 0.39845 | 0.28766 | 0.22007 | -0.14215 | -0.35194 | -0.56974 | 2.9557 | 2.8862 | 2.7957 | 2.6922 | 2.5871 | 2.4731 | 2.358 | 2.2584 | 2.1904 | 2.1254 | 2.08 | 1.9142 | 1.8434 | 1.6914 | 2.6437 | 2.5627 | 2.4473 | 2.2597 | 2.0526 | 1.8227 | 1.588 | 1.4487 | 1.3501 | 1.2609 | 1.2078 | 0.92495 | 0.76558 | 0.58525
|  | MIDMAR | LW |  |  |  | 0.604 | 2.1467 | 1.9964 | 1.7773 | 1.5476 | 1.3073 | 1.0141 | 0.74592 | 0.57324 | 0.40026 | 0.28298 | 0.15532 | -0.22044 | -0.45182 | -0.68935 | 2.9576 | 2.8908 | 2.8065 | 2.7147 | 2.6203 | 2.4952 | 2.3776 | 2.2704 | 2.1608 | 2.0757 | 1.9883 | 1.7794 | 1.7034 | 1.6381 | 2.6449 | 2.5673 | 2.4749 | 2.2987 | 2.1067 | 1.8697 | 1.6402 | 1.4917 | 1.343 | 1.2372 | 1.1254 | 0.80831 | 0.63425 | 0.4509
|  | MIDMAR | ST |  |  |  | 0.604 | 2.1707 | 2.0439 | 1.8928 | 1.7366 | 1.5808 | 1.4329 | 1.2816 | 1.1384 | 0.98736 | 0.86314 | 0.703 | 0.087961 | -0.19993 | -0.3711 | 2.9735 | 2.9256 | 2.8684 | 2.8068 | 2.7433 | 2.6803 | 2.6124 | 2.535 | 2.4528 | 2.3807 | 2.2884 | 1.878 | 1.7243 | 1.6704 | 2.6655 | 2.6137 | 2.5511 | 2.4497 | 2.3255 | 2.2042 | 2.0765 | 1.9553 | 1.825 | 1.708 | 1.5674 | 0.97877 | 0.72163 | 0.59896
|  | MIDMAR | FS |  |  |  | 0.604 | 2.248 | 2.1653 | 2.1108 | 2.0398 | 1.9849 | 1.9196 | 1.8722 | 1.7583 | 1.6448 | 1.5275 | 1.4011 | 0.79437 | 0.1711 | -0.10777 | 2.9989 | 2.9664 | 2.9417 | 2.9085 | 2.8815 | 2.8487 | 2.8215 | 2.766 | 2.7105 | 2.6527 | 2.5888 | 2.2477 | 1.912 | 1.7007 | 2.6911 | 2.6555 | 2.6268 | 2.5878 | 2.5548 | 2.5149 | 2.4796 | 2.4159 | 2.3495 | 2.2616 | 2.1593 | 1.6202 | 1.0661 | 0.79534
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 2.116 | 3.2799 | 0.75803 | -2.0668 | -4.7934 | -6.8055 | -9.7392 | -13.7264 | -14.5176 | -15.2506 | -16.0278 | -16.7571 | -22.3233 | -29.519 | -37.6964 | 4.4983 | 1.4802 | -1.7887 | -4.892 | -7.0868 | -10.392 | -14.9713 | -15.5741 | -16.1175 | -16.7398 | -17.3319 | -23.0714 | -31.8067 | -41.693 | 4.2397 | 1.1765 | -2.2252 | -5.4747 | -7.8169 | -11.3027 | -16.0983 | -16.9061 | -17.641 | -18.445 | -19.2268 | -25.6024 | -34.4724 | -44.5188
|  | MILL RD | CT |  |  |  | 2.116 | 3.2799 | 2.9474 | 2.6 | -0.092306 | -0.97531 | -2.162 | -4.5969 | -5.396 | -6.3138 | -7.1734 | -8.0201 | -11.488 | -14.2982 | -17.3482 | 4.4983 | 4.2221 | 4.0197 | 0.9356 | 0.11749 | -1.05 | -3.7111 | -4.3177 | -5.1306 | -5.9123 | -6.7211 | -10.0194 | -13.0926 | -16.8505 | 4.2397 | 3.9213 | 3.6125 | 0.41523 | -0.53257 | -1.8593 | -4.7155 | -5.5222 | -6.5079 | -7.4387 | -8.3722 | -12.1861 | -15.3923 | -19.0145
|  | MILL RD | LW |  |  |  | 2.116 | 3.2891 | 0.75803 | -2.0668 | -4.7934 | -6.8055 | -9.7392 | -13.7264 | -14.5176 | -15.2506 | -16.0278 | -16.7571 | -22.3233 | -29.519 | -37.6964 | 4.5102 | 1.4802 | -1.7887 | -4.892 | -7.0868 | -10.392 | -14.9713 | -15.5741 | -16.1175 | -16.7398 | -17.3319 | -23.0714 | -31.8067 | -41.693 | 4.2489 | 1.1765 | -2.2252 | -5.4747 | -7.8169 | -11.3027 | -16.0983 | -16.9061 | -17.641 | -18.445 | -19.2268 | -25.6024 | -34.4724 | -44.5188
|  | MILL RD | ST |  |  |  | 2.116 | 3.3736 | 3.1735 | 1.5866 | 0.47505 | -0.25831 | -0.6455 | -1.0792 | -1.6608 | -2.2555 | -2.8372 | -3.2182 | -10.7598 | -19.1581 | -27.1591 | 4.5546 | 4.3738 | 2.4676 | 1.1642 | 0.33252 | -0.054245 | -0.51249 | -1.1537 | -1.8049 | -2.4339 | -2.8012 | -11.5235 | -21.5938 | -31.1826 | 4.3227 | 4.1204 | 2.1824 | 0.84623 | -0.018865 | -0.44212 | -0.9527 | -1.6515 | -2.3636 | -3.0622 | -3.5049 | -12.5721 | -22.7306 | -32.2354
|  | MILL RD | FS |  |  |  | 2.116 | 3.4238 | 3.3541 | 2.8332 | 2.3154 | 1.6829 | 1.052 | 0.087091 | -0.66515 | -1.5278 | -2.3603 | -2.6315 | -4.4761 | -6.3689 | -8.8044 | 4.5765 | 4.5268 | 3.9382 | 3.3532 | 2.6311 | 1.9069 | 0.76994 | -0.075502 | -1.0529 | -1.9969 | -2.2272 | -3.7003 | -5.3777 | -8.2444 | 4.3531 | 4.311 | 3.6985 | 3.0905 | 2.3451 | 1.5987 | 0.42803 | -0.45831 | -1.4864 | -2.4709 | -2.7558 | -4.5724 | -6.3421 | -8.9125
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 7.029 | -6.8638 | -8.4056 | -10.1737 | -12.256 | -14.1043 | -16.1324 | -19.0865 | -22.0731 | -24.7804 | -27.4284 | -30.1056 | -41.3237 | -46.7579 | -47.2618 | -2.6524 | -3.7374 | -5.1631 | -6.8293 | -8.2364 | -9.7768 | -12.0669 | -14.3881 | -16.5072 | -18.569 | -20.6215 | -29.3908 | -33.5637 | -33.9425 | -4.2832 | -5.3821 | -6.8589 | -8.54 | -10.3219 | -12.272 | -15.1237 | -18.0045 | -20.6164 | -23.1748 | -25.7603 | -36.6302 | -41.8821 | -42.3624
|  | MILNATHORT | CT |  |  |  | 7.029 | -6.8638 | -8.4056 | -10.1737 | -12.256 | -14.1043 | -16.1324 | -19.0865 | -22.0731 | -24.7804 | -27.4284 | -30.1056 | -39.2099 | -41.9171 | -42.0659 | -2.6227 | -3.7374 | -5.1631 | -6.8293 | -8.2364 | -9.7768 | -12.0669 | -14.3881 | -16.5072 | -18.569 | -20.6215 | -27.5527 | -29.5922 | -29.7013 | -4.2673 | -5.3821 | -6.8589 | -8.54 | -10.3219 | -12.272 | -15.1237 | -18.0045 | -20.6164 | -23.1748 | -25.7603 | -34.5454 | -37.1507 | -37.2866
|  | MILNATHORT | LW |  |  |  | 7.029 | -6.8147 | -8.2641 | -9.8195 | -11.4503 | -12.803 | -14.9183 | -17.6032 | -20.346 | -23.7086 | -26.9624 | -30.0798 | -39.6866 | -42.7277 | -43.0661 | -2.6524 | -3.6533 | -4.911 | -6.1925 | -7.1846 | -8.7999 | -10.9265 | -13.1 | -15.7243 | -18.2385 | -20.6203 | -27.9549 | -30.2703 | -30.5206 | -4.2832 | -5.3704 | -6.7767 | -8.2314 | -9.4055 | -11.0996 | -13.6447 | -16.3424 | -19.5875 | -22.7308 | -25.7413 | -35.0198 | -37.9554 | -38.2815
|  | MILNATHORT | ST |  |  |  | 7.029 | -5.5862 | -6.2666 | -7.3461 | -8.5936 | -9.7231 | -11.1287 | -13.0376 | -15.3087 | -18.0847 | -21.1617 | -24.283 | -41.3237 | -46.7579 | -47.2618 | -2.016 | -2.4959 | -3.2424 | -4.0119 | -4.8335 | -5.9762 | -7.5219 | -9.3126 | -11.4986 | -13.9 | -16.2959 | -29.3908 | -33.5637 | -33.9425 | -3.4824 | -4.1053 | -5.053 | -6.0281 | -6.8036 | -7.7512 | -9.2943 | -11.49 | -14.1713 | -17.1465 | -20.1582 | -36.6302 | -41.8821 | -42.3624
|  | MILNATHORT | FS |  |  |  | 7.029 | -5.1438 | -5.6391 | -6.2892 | -6.9551 | -7.6022 | -8.3634 | -9.3769 | -10.5218 | -11.9215 | -13.4455 | -15.0854 | -25.9317 | -37.0383 | -43.0855 | -1.7129 | -2.074 | -2.5695 | -3.0787 | -3.4291 | -3.8454 | -4.5775 | -5.5161 | -6.6573 | -7.8582 | -9.138 | -17.5471 | -26.057 | -30.7 | -3.0755 | -3.5285 | -4.1281 | -4.746 | -5.1961 | -5.7207 | -6.4197 | -7.2587 | -8.2165 | -9.6888 | -11.2717 | -21.743 | -32.4661 | -38.2965
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 2.087 | 2.7458 | 2.3495 | 1.8509 | 1.3067 | 0.84678 | 0.14657 | -0.91097 | -1.8317 | -2.6607 | -3.3965 | -4.407 | -6.422 | -6.7701 | -7.3422 | 5.9303 | 5.6023 | 5.2847 | 4.9055 | 4.6244 | 4.1878 | 3.4931 | 2.8761 | 2.3437 | 1.8602 | 1.1083 | -0.19508 | -0.95623 | -2.976 | 5.9598 | 5.58 | 5.1815 | 4.7228 | 4.3221 | 3.712 | 2.7668 | 1.9118 | 1.1044 | 0.35908 | -0.59371 | -2.4517 | -2.6469 | -3.2118
|  | MILTON OF CRAIGIE | CT |  |  |  | 2.087 | 2.7707 | 2.417 | 1.9521 | 1.3893 | 0.93764 | 0.29511 | -0.65978 | -1.5869 | -2.3093 | -2.9477 | -3.8236 | -5.9441 | -6.7701 | -7.3422 | 5.9351 | 5.6314 | 5.3018 | 4.9055 | 4.6244 | 4.1878 | 3.4931 | 2.8761 | 2.4058 | 1.9791 | 1.3032 | -0.19508 | -0.95623 | -2.0639 | 5.972 | 5.6173 | 5.2192 | 4.7272 | 4.3221 | 3.7623 | 2.9067 | 2.0845 | 1.4368 | 0.82628 | 0.027739 | -1.8145 | -2.3686 | -2.8949
|  | MILTON OF CRAIGIE | LW |  |  |  | 2.087 | 2.7458 | 2.3495 | 1.8509 | 1.3067 | 0.84678 | 0.14657 | -0.91097 | -1.8317 | -2.6607 | -3.3965 | -4.407 | -6.422 | -6.6708 | -7.1303 | 5.9303 | 5.6023 | 5.2847 | 4.9438 | 4.7004 | 4.2501 | 3.5004 | 2.8909 | 2.3437 | 1.8602 | 1.1083 | -0.17591 | -0.30684 | -0.6782 | 5.9598 | 5.58 | 5.1815 | 4.7228 | 4.333 | 3.712 | 2.7668 | 1.9118 | 1.1044 | 0.35908 | -0.59371 | -2.4517 | -2.6469 | -3.2118
|  | MILTON OF CRAIGIE | ST |  |  |  | 2.087 | 2.855 | 2.6223 | 2.4036 | 2.1672 | 2.0548 | 1.7787 | 1.3075 | 0.93451 | 0.63278 | 0.345 | -0.28465 | -2.2258 | -3.2886 | -4.3305 | 5.9914 | 5.7855 | 5.5872 | 5.3713 | 5.2693 | 5.014 | 4.5853 | 4.2457 | 3.9626 | 3.6933 | 3.1115 | 1.3707 | 0.38162 | -0.7826 | 6.0596 | 5.854 | 5.6595 | 5.4384 | 5.3168 | 5.0475 | 4.6126 | 4.2392 | 3.9161 | 3.5806 | 2.9627 | 0.90884 | 0.040681 | -0.63766
|  | MILTON OF CRAIGIE | FS |  |  |  | 2.087 | 2.9039 | 2.7234 | 2.5356 | 2.3367 | 2.2101 | 1.9608 | 1.6166 | 1.3112 | 1.0088 | 0.75089 | 0.28077 | -2.106 | -4.1541 | -5.7081 | 6.0198 | 5.8512 | 5.6919 | 5.5208 | 5.4154 | 5.1914 | 4.8763 | 4.609 | 4.3378 | 4.1044 | 3.678 | 1.647 | -0.51934 | -2.976 | 6.098 | 5.9314 | 5.7733 | 5.5999 | 5.4736 | 5.2561 | 4.9444 | 4.6668 | 4.3722 | 4.1281 | 3.6933 | 1.4801 | -0.36763 | -1.5757
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 1.215 | 4.5886 | 4.31 | 3.9033 | 3.5085 | 3.0053 | 2.4934 | 1.649 | 0.98823 | 0.39683 | 0.081466 | -0.46172 | -2.4389 | -4.0045 | -5.4001 | 8.0719 | 7.9176 | 7.7006 | 7.4915 | 7.2263 | 6.9659 | 6.3955 | 5.9486 | 5.5512 | 5.3908 | 5.0354 | 3.6304 | 2.4478 | 1.2129 | 8.1584 | 8.023 | 7.8213 | 7.5174 | 7.0655 | 6.5879 | 5.7619 | 5.146 | 4.6066 | 4.3615 | 3.8676 | 2.1028 | 0.66347 | -0.62695
|  | MINTLAW | CT |  |  |  | 1.215 | 4.5886 | 4.31 | 3.9033 | 3.5085 | 3.0053 | 2.4934 | 1.649 | 0.98823 | 0.39683 | 0.10316 | -0.39722 | -2.4389 | -4.0045 | -5.4001 | 8.0719 | 7.9176 | 7.7006 | 7.4915 | 7.2263 | 6.9659 | 6.3955 | 5.9486 | 5.5512 | 5.4005 | 5.05 | 3.6304 | 2.4478 | 1.2129 | 8.1603 | 8.023 | 7.8213 | 7.5174 | 7.0655 | 6.5879 | 5.7619 | 5.146 | 4.6066 | 4.38 | 3.9356 | 2.1028 | 0.66347 | -0.62695
|  | MINTLAW | LW |  |  |  | 1.215 | 4.5917 | 4.3217 | 3.9255 | 3.5322 | 3.0812 | 2.5762 | 1.7137 | 1.0409 | 0.65331 | 0.081466 | -0.46172 | -2.4234 | -3.8562 | -5.22 | 8.0737 | 7.9266 | 7.7217 | 7.5207 | 7.2905 | 7.0336 | 6.4265 | 5.9719 | 5.7613 | 5.3908 | 5.0354 | 3.7264 | 2.7186 | 1.7235 | 8.1584 | 8.0268 | 7.8539 | 7.5345 | 7.1323 | 6.6855 | 5.8514 | 5.2113 | 4.8783 | 4.3615 | 3.8676 | 2.1073 | 0.77815 | -0.48265
|  | MINTLAW | ST |  |  |  | 1.215 | 4.6664 | 4.4744 | 4.2361 | 4.0103 | 3.7617 | 3.5273 | 3.0384 | 2.6047 | 2.1926 | 1.7143 | 1.2331 | -0.69857 | -2.3931 | -3.9134 | 8.1123 | 8.0076 | 7.8808 | 7.7592 | 7.6236 | 7.4948 | 7.1051 | 6.7742 | 6.458 | 6.0885 | 5.7256 | 4.3049 | 3.0278 | 1.7477 | 8.1977 | 8.1116 | 8.003 | 7.9014 | 7.7513 | 7.5507 | 7.0994 | 6.6946 | 6.3046 | 5.8485 | 5.396 | 3.6082 | 2.0353 | 0.62968
|  | MINTLAW | FS |  |  |  | 1.215 | 4.7566 | 4.6191 | 4.4531 | 4.3334 | 4.1875 | 4.0268 | 3.7507 | 3.4254 | 3.0678 | 2.7469 | 2.3579 | 0.55142 | -1.7364 | -3.4435 | 8.1561 | 8.0775 | 7.9815 | 7.9125 | 7.826 | 7.7302 | 7.4922 | 7.2513 | 6.9841 | 6.7394 | 6.4443 | 4.9748 | 3.0981 | 1.4134 | 8.2349 | 8.1722 | 8.097 | 8.0396 | 7.9707 | 7.8944 | 7.6488 | 7.4063 | 7.0719 | 6.7813 | 6.4179 | 4.7349 | 2.6466 | 1.0788
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 0.655 | 3.0944 | 0.84304 | -1.465 | -2.0092 | -2.5355 | -3.0699 | -3.6955 | -4.3827 | -5.0881 | -5.4171 | -5.9567 | -7.4642 | -8.0404 | -8.5874 | 3.9491 | 1.3343 | -1.1208 | -1.3769 | -1.5896 | -1.7774 | -2.008 | -2.2492 | -2.5439 | -2.5752 | -2.7813 | -3.4674 | -3.8548 | -4.3016 | 3.5704 | 1.2341 | -0.93597 | -1.2715 | -1.6438 | -2.0047 | -2.4411 | -3.0096 | -3.5788 | -3.8934 | -4.3357 | -5.6202 | -6.0964 | -6.5525
|  | MONTROSE NORTH | CT |  |  |  | 0.655 | 3.7934 | 1.977 | -0.096615 | -0.79109 | -1.5775 | -2.4483 | -3.4153 | -4.3171 | -4.979 | -5.2127 | -5.6377 | -7.2267 | -8.0404 | -8.5874 | 4.7767 | 2.6848 | 0.49347 | 0.031114 | -0.47735 | -1.0952 | -1.7404 | -2.2391 | -2.5439 | -2.5752 | -2.7182 | -3.4176 | -3.8548 | -4.3016 | 4.3076 | 2.4314 | 0.47974 | -0.003567 | -0.64127 | -1.3784 | -2.175 | -2.9509 | -3.5115 | -3.7423 | -4.0838 | -5.3938 | -6.0964 | -6.5525
|  | MONTROSE NORTH | LW |  |  |  | 0.655 | 3.0944 | 0.84304 | -1.465 | -2.0092 | -2.5355 | -3.0699 | -3.6955 | -4.3827 | -5.0881 | -5.4171 | -5.9567 | -7.4642 | -7.8154 | -8.2017 | 3.9491 | 1.3343 | -1.1208 | -1.3769 | -1.5896 | -1.7774 | -2.008 | -2.2492 | -2.4993 | -2.571 | -2.7813 | -3.4674 | -3.6522 | -3.8197 | 3.5704 | 1.2341 | -0.93597 | -1.2715 | -1.6438 | -2.0047 | -2.4411 | -3.0096 | -3.5788 | -3.8934 | -4.3357 | -5.6202 | -5.9605 | -6.2782
|  | MONTROSE NORTH | ST |  |  |  | 0.655 | 3.8734 | 2.1497 | 0.36408 | 0.021159 | -0.36996 | -0.83247 | -1.2847 | -1.6537 | -1.9448 | -2.1713 | -2.4328 | -3.6549 | -4.3391 | -5.3395 | 4.8064 | 2.7612 | 0.65177 | 0.31161 | -0.081246 | -0.59047 | -1.0725 | -1.4298 | -1.6479 | -1.7657 | -1.9003 | -2.6412 | -2.9913 | -3.3938 | 4.3366 | 2.5156 | 0.62728 | 0.30728 | -0.061354 | -0.53185 | -0.98053 | -1.322 | -1.5582 | -1.7016 | -1.8695 | -2.9124 | -3.3335 | -4.0877
|  | MONTROSE NORTH | FS |  |  |  | 0.655 | 4.6416 | 3.3026 | 1.9707 | 1.6712 | 1.3611 | 1.004 | 0.62171 | 0.25105 | -0.10835 | -0.447 | -0.84514 | -3.7793 | -4.9486 | -6.1905 | 5.6926 | 4.1142 | 2.5643 | 2.2787 | 1.998 | 1.6519 | 1.2612 | 0.94131 | 0.65378 | 0.38981 | 0.042247 | -2.4414 | -3.0788 | -4.051 | 5.1402 | 3.7259 | 2.3443 | 2.0837 | 1.8258 | 1.5127 | 1.1601 | 0.8784 | 0.62044 | 0.38281 | 0.058351 | -2.5084 | -3.5067 | -4.5891
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 2.057 | -0.67718 | -0.79378 | -0.93818 | -1.1336 | -1.3215 | -1.5439 | -1.8146 | -1.9616 | -2.1888 | -2.326 | -2.4509 | -2.7664 | -3.0012 | -3.2563 | 0.12639 | 0.061372 | -0.023937 | -0.12881 | -0.21311 | -0.3427 | -0.49551 | -0.59062 | -0.75913 | -0.85719 | -0.94966 | -1.1354 | -1.2684 | -1.4292 | -0.22541 | -0.3325 | -0.46863 | -0.64674 | -0.80724 | -1.0234 | -1.2772 | -1.4134 | -1.6297 | -1.7681 | -1.8912 | -2.1883 | -2.4044 | -2.644
|  | MOSSAT | CT |  |  |  | 2.057 | -0.67718 | -0.79378 | -0.93818 | -1.1336 | -1.3215 | -1.5396 | -1.8067 | -1.9451 | -2.1134 | -2.2258 | -2.3195 | -2.6135 | -2.8016 | -3.005 | 0.12639 | 0.063908 | -0.0069268 | -0.11573 | -0.20491 | -0.31232 | -0.45616 | -0.54789 | -0.67338 | -0.75735 | -0.83485 | -1.0393 | -1.1748 | -1.3706 | -0.22541 | -0.3325 | -0.46261 | -0.64228 | -0.80724 | -1.0031 | -1.2497 | -1.3782 | -1.5373 | -1.6452 | -1.7428 | -2.0204 | -2.1808 | -2.3596
|  | MOSSAT | LW |  |  |  | 2.057 | -0.65898 | -0.77721 | -0.93376 | -1.1257 | -1.3047 | -1.5439 | -1.8146 | -1.9616 | -2.1888 | -2.326 | -2.4509 | -2.7664 | -3.0012 | -3.2563 | 0.13426 | 0.061372 | -0.023937 | -0.12881 | -0.21311 | -0.3427 | -0.49551 | -0.59062 | -0.75913 | -0.85719 | -0.94966 | -1.1354 | -1.2684 | -1.4292 | -0.20944 | -0.32276 | -0.46863 | -0.64674 | -0.80305 | -1.0234 | -1.2772 | -1.4134 | -1.6297 | -1.7681 | -1.8912 | -2.1883 | -2.4044 | -2.644
|  | MOSSAT | ST |  |  |  | 2.057 | -0.64185 | -0.72006 | -0.83224 | -0.95598 | -1.0717 | -1.1982 | -1.3109 | -1.4483 | -1.6314 | -1.7703 | -1.8834 | -2.4393 | -2.7177 | -2.8962 | 0.14472 | 0.10625 | 0.047737 | -0.01657 | -0.073503 | -0.13813 | -0.19252 | -0.27907 | -0.40581 | -0.49176 | -0.55629 | -0.95424 | -1.1802 | -1.3851 | -0.19278 | -0.26301 | -0.36411 | -0.47486 | -0.57695 | -0.69131 | -0.79251 | -0.91912 | -1.0901 | -1.2193 | -1.3224 | -1.8613 | -2.1244 | -2.2912
|  | MOSSAT | FS |  |  |  | 2.057 | -0.59216 | -0.63981 | -0.68357 | -0.72016 | -0.76911 | -0.81127 | -0.86794 | -0.95602 | -1.0929 | -1.1923 | -1.3005 | -1.8386 | -2.357 | -2.5842 | 0.16482 | 0.14047 | 0.1128 | 0.089865 | 0.057567 | 0.029959 | -0.010799 | -0.066477 | -0.16244 | -0.2262 | -0.29412 | -0.65656 | -1.0371 | -1.3554 | -0.14927 | -0.19187 | -0.23291 | -0.26665 | -0.31284 | -0.35236 | -0.40722 | -0.48758 | -0.61493 | -0.70743 | -0.80737 | -1.3056 | -1.7792 | -1.9843
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 1.285 | 8.5911 | 7.7349 | 6.8252 | 5.8294 | 5.6321 | 5.393 | 5.1204 | 4.9517 | 4.7569 | 4.5862 | 4.4636 | 4.0231 | 3.8198 | 3.613 | 9.0758 | 8.2754 | 7.4718 | 6.6133 | 6.5141 | 6.3942 | 6.2533 | 6.1632 | 6.0555 | 5.961 | 5.8999 | 5.6742 | 5.4927 | 5.2531 | 8.8163 | 7.9505 | 7.0793 | 6.1499 | 6.0222 | 5.8693 | 5.6934 | 5.5771 | 5.4429 | 5.3241 | 5.2321 | 4.8786 | 4.6989 | 4.4979
|  | MOUNT PLEASANT | CT |  |  |  | 1.285 | 8.725 | 8.0285 | 7.2174 | 6.1704 | 5.9002 | 5.5777 | 5.2131 | 4.9682 | 4.7848 | 4.6489 | 4.535 | 4.1087 | 3.8416 | 3.6149 | 9.2053 | 8.5738 | 7.8572 | 6.9444 | 6.7866 | 6.588 | 6.3651 | 6.1956 | 6.0783 | 5.9979 | 5.9265 | 5.6781 | 5.4927 | 5.2531 | 8.9639 | 8.2703 | 7.4917 | 6.5004 | 6.3152 | 6.084 | 5.829 | 5.637 | 5.5047 | 5.417 | 5.343 | 4.9765 | 4.7483 | 4.5437
|  | MOUNT PLEASANT | LW |  |  |  | 1.285 | 8.5911 | 7.7349 | 6.8252 | 5.8294 | 5.6321 | 5.393 | 5.1204 | 4.9517 | 4.7569 | 4.5862 | 4.4636 | 4.0231 | 3.8198 | 3.613 | 9.0758 | 8.2754 | 7.4718 | 6.6133 | 6.5141 | 6.3942 | 6.2533 | 6.1632 | 6.0555 | 5.961 | 5.8999 | 5.6742 | 5.5738 | 5.4551 | 8.8163 | 7.9505 | 7.0793 | 6.1499 | 6.0222 | 5.8693 | 5.6934 | 5.5771 | 5.4429 | 5.3241 | 5.2321 | 4.8786 | 4.6989 | 4.4979
|  | MOUNT PLEASANT | ST |  |  |  | 1.285 | 8.753 | 8.0827 | 7.3525 | 6.405 | 6.264 | 6.0711 | 5.896 | 5.7201 | 5.5837 | 5.4794 | 5.3993 | 4.8812 | 4.5717 | 4.3244 | 9.2244 | 8.6135 | 7.9264 | 7.0527 | 6.9534 | 6.8079 | 6.6755 | 6.5411 | 6.4462 | 6.3827 | 6.3322 | 5.9826 | 5.7471 | 5.4966 | 8.981 | 8.3184 | 7.5808 | 6.6456 | 6.5291 | 6.365 | 6.2127 | 6.0607 | 5.9467 | 5.8668 | 5.7982 | 5.369 | 5.152 | 5.0033
|  | MOUNT PLEASANT | FS |  |  |  | 1.285 | 8.9222 | 8.4234 | 7.9095 | 7.2692 | 7.1306 | 7.0321 | 6.8897 | 6.7362 | 6.5371 | 6.3815 | 6.2125 | 5.229 | 4.7328 | 4.4403 | 9.3606 | 8.9081 | 8.4155 | 7.7925 | 7.6718 | 7.5881 | 7.4635 | 7.3413 | 7.1805 | 7.0605 | 6.9292 | 6.1315 | 5.7382 | 5.3194 | 9.1273 | 8.6357 | 8.1131 | 7.4496 | 7.3202 | 7.2275 | 7.0952 | 6.9622 | 6.7891 | 6.6575 | 6.5152 | 5.663 | 5.3166 | 5.1053
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 2.199 | 7.2774 | 6.9579 | 6.4338 | 5.8545 | 5.173 | 4.4799 | 3.6376 | 3.146 | 2.7714 | 2.735 | 2.3581 | 1.1855 | 0.49034 | -0.16809 | 8.894 | 8.73 | 8.4839 | 8.2146 | 7.8934 | 7.5779 | 7.171 | 6.8897 | 6.6734 | 6.6842 | 6.47 | 5.8614 | 5.4437 | 4.8684 | 7.2276 | 6.9361 | 6.4782 | 5.983 | 5.3868 | 4.7891 | 4.0391 | 3.5612 | 3.1973 | 3.1317 | 2.759 | 1.6855 | 1.1087 | 0.52003
|  | MUIR OF ORD | CT |  |  |  | 2.199 | 7.2774 | 6.9579 | 6.4338 | 5.8545 | 5.173 | 4.4799 | 3.6376 | 3.146 | 2.7714 | 2.7644 | 2.5188 | 1.4467 | 0.70018 | 0.029839 | 8.894 | 8.73 | 8.4839 | 8.2146 | 7.8934 | 7.5779 | 7.171 | 6.8897 | 6.6734 | 6.7042 | 6.5483 | 5.9088 | 5.4437 | 4.8684 | 7.2276 | 6.9361 | 6.4782 | 5.983 | 5.3868 | 4.7891 | 4.0391 | 3.5612 | 3.1973 | 3.2134 | 2.9601 | 1.9707 | 1.3572 | 0.78322
|  | MUIR OF ORD | LW |  |  |  | 2.199 | 7.3223 | 7.0309 | 6.5338 | 5.9923 | 5.3988 | 4.7082 | 3.9163 | 3.3899 | 3.1526 | 2.735 | 2.3581 | 1.1855 | 0.49034 | -0.16809 | 8.9122 | 8.7587 | 8.5282 | 8.2835 | 8.014 | 7.686 | 7.2977 | 7.0112 | 6.9187 | 6.6842 | 6.47 | 5.8614 | 5.5545 | 5.2322 | 7.2659 | 6.9967 | 6.5638 | 6.0993 | 5.5864 | 4.9719 | 4.2566 | 3.7526 | 3.5437 | 3.1317 | 2.759 | 1.6855 | 1.1087 | 0.52003
|  | MUIR OF ORD | ST |  |  |  | 2.199 | 7.4039 | 7.1976 | 6.8931 | 6.566 | 6.2216 | 5.8903 | 5.5274 | 5.1947 | 4.8713 | 4.5099 | 4.1307 | 2.6727 | 1.7185 | 1.0444 | 8.9556 | 8.8572 | 8.7165 | 8.5607 | 8.3932 | 8.2377 | 8.0557 | 7.877 | 7.6996 | 7.495 | 7.2766 | 6.4303 | 5.8255 | 5.2615 | 7.3431 | 7.1652 | 6.9052 | 6.623 | 6.3227 | 6.0412 | 5.7179 | 5.4131 | 5.1104 | 4.7667 | 4.4033 | 3.0541 | 2.2328 | 1.6789
|  | MUIR OF ORD | FS |  |  |  | 2.199 | 7.5482 | 7.4132 | 7.2708 | 7.1325 | 6.9758 | 6.8046 | 6.6542 | 6.3763 | 6.0766 | 5.8143 | 5.5119 | 4.1379 | 2.5146 | 1.6004 | 9.0157 | 8.9467 | 8.8688 | 8.7941 | 8.706 | 8.6066 | 8.5198 | 8.3682 | 8.1982 | 8.0515 | 7.8782 | 7.0739 | 5.9562 | 4.9287 | 7.46 | 7.342 | 7.2136 | 7.0911 | 6.9517 | 6.7947 | 6.6628 | 6.4144 | 6.1395 | 5.9005 | 5.6205 | 4.3732 | 2.9109 | 2.125
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 0.177 | 0.088566 | -0.001454 | -0.15021 | -0.33404 | -0.5272 | -0.74121 | -0.98963 | -1.0729 | -1.1603 | -1.2786 | -1.3826 | -1.6429 | -1.8169 | -2.0112 | 1.152 | 1.0893 | 1.02 | 0.92936 | 0.84732 | 0.74688 | 0.60764 | 0.54 | 0.42328 | 0.31901 | 0.22558 | 0.073205 | -7.5869e-06 | -0.16168 | 0.44824 | 0.35154 | 0.22148 | 0.05559 | -0.11122 | -0.29808 | -0.52851 | -0.61911 | -0.74582 | -0.87009 | -0.98014 | -1.2306 | -1.3823 | -1.5668
|  | MUIREND | CT |  |  |  | 0.177 | 0.088566 | -0.001454 | -0.15021 | -0.33404 | -0.5272 | -0.74121 | -0.98963 | -1.0729 | -1.1469 | -1.2279 | -1.2934 | -1.5185 | -1.671 | -1.8328 | 1.152 | 1.0924 | 1.0253 | 0.93224 | 0.84732 | 0.74908 | 0.6164 | 0.5479 | 0.47767 | 0.39909 | 0.32336 | 0.14701 | 0.037641 | -0.1375 | 0.44824 | 0.35154 | 0.22148 | 0.05559 | -0.11122 | -0.29808 | -0.52851 | -0.61911 | -0.7059 | -0.79385 | -0.86828 | -1.0907 | -1.2195 | -1.3649
|  | MUIREND | LW |  |  |  | 0.177 | 0.098248 | 0.011033 | -0.13644 | -0.31029 | -0.47762 | -0.69032 | -0.93181 | -1.0244 | -1.1603 | -1.2786 | -1.3826 | -1.6429 | -1.8169 | -2.0112 | 1.1528 | 1.0893 | 1.02 | 0.92936 | 0.86216 | 0.74688 | 0.60764 | 0.54 | 0.42328 | 0.31901 | 0.22558 | 0.073205 | -7.5869e-06 | -0.11465 | 0.45517 | 0.35845 | 0.22811 | 0.068064 | -0.073199 | -0.2722 | -0.50393 | -0.60154 | -0.74582 | -0.87009 | -0.98014 | -1.2306 | -1.3823 | -1.5668
|  | MUIREND | ST |  |  |  | 0.177 | 0.11392 | 0.057755 | -0.042772 | -0.13893 | -0.23894 | -0.34666 | -0.44363 | -0.53874 | -0.63896 | -0.74555 | -0.83655 | -1.3333 | -1.54 | -1.6491 | 1.1694 | 1.1386 | 1.0866 | 1.0425 | 0.99447 | 0.93581 | 0.88936 | 0.82756 | 0.75818 | 0.68057 | 0.62833 | 0.22854 | 0.060928 | -0.09095 | 0.47747 | 0.41804 | 0.32636 | 0.24274 | 0.15437 | 0.054237 | -0.03228 | -0.12707 | -0.22932 | -0.34097 | -0.42396 | -0.9229 | -1.116 | -1.216
|  | MUIREND | FS |  |  |  | 0.177 | 0.16245 | 0.1254 | 0.099714 | 0.072862 | 0.039488 | 0.0081384 | -0.029801 | -0.10684 | -0.17736 | -0.25558 | -0.34342 | -0.78684 | -1.2709 | -1.4472 | 1.1924 | 1.1664 | 1.1452 | 1.1241 | 1.0917 | 1.0637 | 1.0244 | 0.9722 | 0.92928 | 0.87456 | 0.81464 | 0.49951 | 0.12268 | -0.16168 | 0.52788 | 0.48485 | 0.45569 | 0.42617 | 0.38387 | 0.34698 | 0.29914 | 0.22305 | 0.15696 | 0.07936 | -0.0044594 | -0.42308 | -0.8691 | -1.0257
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 0.445 | 4.1605 | 3.704 | 3.232 | 2.69 | 2.1303 | 1.3817 | 0.42462 | -0.22631 | -1.1299 | -1.9776 | -2.7293 | -5.0801 | -6.6575 | -7.733 | 6.2356 | 5.9665 | 5.7405 | 5.4741 | 5.2231 | 4.858 | 4.4205 | 4.1442 | 3.7149 | 3.3248 | 2.971 | 1.772 | 0.85586 | -0.1154 | 5.218 | 4.9496 | 4.8606 | 4.6784 | 4.1305 | 3.414 | 2.5206 | 1.968 | 1.0914 | 0.29711 | -0.4117 | -2.5456 | -3.7671 | -4.7192
|  | NAIRN CENTRAL | CT |  |  |  | 0.445 | 4.1939 | 3.7856 | 3.3415 | 2.7633 | 2.1303 | 1.3817 | 0.42462 | -0.22631 | -0.97348 | -1.6626 | -2.3034 | -4.9996 | -6.6575 | -7.733 | 6.2467 | 6.021 | 5.8114 | 5.5172 | 5.2231 | 4.8702 | 4.4205 | 4.1451 | 3.8044 | 3.48 | 3.1721 | 1.772 | 0.85586 | -0.1154 | 5.2373 | 5.0204 | 4.945 | 4.7396 | 4.1305 | 3.414 | 2.5206 | 1.968 | 1.286 | 0.64412 | 0.047732 | -2.3606 | -3.7671 | -4.7192
|  | NAIRN CENTRAL | LW |  |  |  | 0.445 | 4.1605 | 3.704 | 3.232 | 2.69 | 2.1339 | 1.4056 | 0.50043 | -0.19441 | -1.1299 | -1.9776 | -2.7293 | -5.0801 | -6.0881 | -7.0834 | 6.2356 | 5.9665 | 5.7405 | 5.4741 | 5.225 | 4.858 | 4.4256 | 4.1442 | 3.7149 | 3.3248 | 2.971 | 1.7728 | 1.3233 | 0.76818 | 5.218 | 4.9496 | 4.8606 | 4.6784 | 4.1541 | 3.4162 | 2.5575 | 1.9689 | 1.0914 | 0.29711 | -0.4117 | -2.5456 | -3.4251 | -4.356
|  | NAIRN CENTRAL | ST |  |  |  | 0.445 | 4.2881 | 3.9862 | 3.9039 | 3.8051 | 3.6996 | 3.5598 | 3.4009 | 3.2612 | 3.0526 | 2.8088 | 2.7658 | 0.7616 | -0.98494 | -2.6929 | 6.2702 | 6.1339 | 6.0715 | 5.9944 | 5.9167 | 5.8146 | 5.6953 | 5.5899 | 5.4279 | 5.2585 | 5.2153 | 3.9304 | 2.8994 | 1.7861 | 5.2666 | 5.1003 | 5.0471 | 4.9864 | 4.9258 | 4.8426 | 4.7431 | 4.6507 | 4.5089 | 4.3591 | 4.2987 | 2.4484 | 1.0146 | -0.31086
|  | NAIRN CENTRAL | FS |  |  |  | 0.445 | 4.3457 | 4.1155 | 4.0228 | 3.9064 | 3.7705 | 3.6302 | 3.4673 | 3.2371 | 3.0158 | 2.7633 | 2.4838 | 0.88643 | -1.1138 | -3.0861 | 6.2904 | 6.1812 | 6.1494 | 6.0732 | 5.9834 | 5.8902 | 5.7724 | 5.6242 | 5.4802 | 5.3111 | 5.1278 | 4.1514 | 2.5854 | 0.6715 | 5.2971 | 5.1635 | 5.1333 | 5.0876 | 5.0294 | 4.9685 | 4.889 | 4.8122 | 4.7317 | 4.6244 | 4.3211 | 2.836 | 0.96816 | -0.73558
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.051 | 2.0571 | 6.6724 | 6.5686 | 6.4583 | 6.3201 | 6.1843 | 6.0079 | 5.9025 | 5.8475 | 5.7468 | 5.649 | 5.4112 | 5.2882 | 5.1459 | 1.0969 | 5.9947 | 5.9379 | 5.8817 | 5.806 | 5.7492 | 5.6577 | 5.5746 | 5.5404 | 5.4677 | 5.398 | 5.2484 | 5.1602 | 4.9433 | 2.0275 | 6.8969 | 6.7981 | 6.6906 | 6.5596 | 6.4381 | 6.2774 | 6.1736 | 6.1199 | 6.0281 | 5.942 | 5.7195 | 5.6 | 5.4693
|  | NEW PITSLIGO | CT |  |  |  | 0.051 | 2.0571 | 6.6724 | 6.5686 | 6.4583 | 6.3201 | 6.1843 | 6.0079 | 5.9025 | 5.8475 | 5.772 | 5.6976 | 5.4717 | 5.3666 | 5.2406 | 1.0969 | 5.9947 | 5.9379 | 5.8817 | 5.806 | 5.7492 | 5.6577 | 5.5746 | 5.5404 | 5.4766 | 5.4179 | 5.2484 | 5.1602 | 5.0187 | 2.0275 | 6.8969 | 6.7981 | 6.6906 | 6.5596 | 6.4381 | 6.2774 | 6.1736 | 6.1199 | 6.0466 | 5.9843 | 5.779 | 5.6763 | 5.5588
|  | NEW PITSLIGO | LW |  |  |  | 0.051 | 2.0688 | 6.693 | 6.5948 | 6.4869 | 6.3658 | 6.2225 | 6.0531 | 5.9472 | 5.8564 | 5.7468 | 5.649 | 5.4112 | 5.2882 | 5.1459 | 1.102 | 6.0055 | 5.9559 | 5.9029 | 5.8427 | 5.7754 | 5.6874 | 5.609 | 5.5451 | 5.4677 | 5.398 | 5.2528 | 5.2033 | 5.1331 | 2.0399 | 6.9181 | 6.824 | 6.7203 | 6.6033 | 6.473 | 6.318 | 6.2143 | 6.1248 | 6.0281 | 5.942 | 5.7195 | 5.6 | 5.4693
|  | NEW PITSLIGO | ST |  |  |  | 0.051 | 2.0861 | 6.7235 | 6.6601 | 6.5979 | 6.5231 | 6.4503 | 6.3656 | 6.3004 | 6.2137 | 6.1293 | 6.035 | 5.664 | 5.5246 | 5.4538 | 1.1146 | 6.0271 | 5.9969 | 5.9674 | 5.9274 | 5.8917 | 5.8446 | 5.8112 | 5.7528 | 5.6971 | 5.6314 | 5.355 | 5.2326 | 5.1158 | 2.0542 | 6.9433 | 6.8816 | 6.8202 | 6.749 | 6.6819 | 6.6044 | 6.5459 | 6.464 | 6.3841 | 6.295 | 5.9569 | 5.8264 | 5.7623
|  | NEW PITSLIGO | FS |  |  |  | 0.051 | 2.1134 | 6.7723 | 6.7494 | 6.7176 | 6.6969 | 6.6628 | 6.6358 | 6.5747 | 6.5044 | 6.4566 | 6.3853 | 6.0332 | 5.6592 | 5.5109 | 1.1232 | 6.0461 | 6.031 | 6.0082 | 5.9946 | 5.9693 | 5.9491 | 5.9096 | 5.862 | 5.8337 | 5.7849 | 5.5255 | 5.2113 | 4.9433 | 2.0831 | 6.9928 | 6.9729 | 6.9458 | 6.927 | 6.8978 | 6.8745 | 6.8183 | 6.7547 | 6.7085 | 6.6438 | 6.3173 | 5.9645 | 5.8202
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0 | 0.21458 | 0.20613 | 0.19704 | 0.18361 | 0.16875 | 0.1504 | 0.13174 | 0.1215 | 0.11306 | 0.10882 | 0.096619 | 0.070032 | 0.063712 | 0.048965 | 0.24365 | 0.23766 | 0.23488 | 0.22851 | 0.2213 | 0.21117 | 0.20151 | 0.1922 | 0.18392 | 0.17618 | 0.16637 | 0.14675 | 0.14391 | 0.13378 | 0.23588 | 0.22727 | 0.22003 | 0.20786 | 0.1944 | 0.17756 | 0.16055 | 0.1505 | 0.14126 | 0.13363 | 0.12128 | 0.095397 | 0.088608 | 0.073552
|  | NEWTON | CT |  |  |  | 0 | 0.21458 | 0.20613 | 0.19704 | 0.18361 | 0.16875 | 0.1504 | 0.13174 | 0.1215 | 0.11306 | 0.10939 | 0.10241 | 0.077668 | 0.071051 | 0.059693 | 0.24365 | 0.23766 | 0.23502 | 0.22851 | 0.2213 | 0.21117 | 0.20151 | 0.1922 | 0.18392 | 0.17977 | 0.17183 | 0.15079 | 0.1451 | 0.13381 | 0.23588 | 0.22727 | 0.22003 | 0.20786 | 0.1944 | 0.17756 | 0.16055 | 0.1505 | 0.14126 | 0.13676 | 0.12787 | 0.1027 | 0.095616 | 0.083739
|  | NEWTON | LW |  |  |  | 0 | 0.21554 | 0.20832 | 0.2012 | 0.18879 | 0.17741 | 0.15833 | 0.14098 | 0.13022 | 0.1205 | 0.10882 | 0.096619 | 0.070032 | 0.063712 | 0.048965 | 0.24389 | 0.23872 | 0.2374 | 0.23101 | 0.22639 | 0.2144 | 0.20481 | 0.19577 | 0.18708 | 0.17618 | 0.16637 | 0.14675 | 0.14391 | 0.13378 | 0.2367 | 0.22895 | 0.22385 | 0.21254 | 0.20237 | 0.1846 | 0.16865 | 0.15806 | 0.14732 | 0.13363 | 0.12128 | 0.095397 | 0.088608 | 0.073552
|  | NEWTON | ST |  |  |  | 0 | 0.22142 | 0.21277 | 0.20184 | 0.20063 | 0.19786 | 0.18882 | 0.18218 | 0.17633 | 0.16899 | 0.15869 | 0.14944 | 0.10902 | 0.097817 | 0.095358 | 0.24956 | 0.24306 | 0.23488 | 0.23659 | 0.23693 | 0.23067 | 0.22683 | 0.22338 | 0.21839 | 0.21034 | 0.20362 | 0.17015 | 0.16021 | 0.15521 | 0.24256 | 0.23433 | 0.22394 | 0.22331 | 0.22107 | 0.21258 | 0.20648 | 0.20107 | 0.19419 | 0.18423 | 0.17491 | 0.13166 | 0.11992 | 0.11732
|  | NEWTON | FS |  |  |  | 0 | 0.2247 | 0.21832 | 0.21231 | 0.20484 | 0.20968 | 0.21137 | 0.20661 | 0.20219 | 0.19735 | 0.18958 | 0.18471 | 0.14828 | 0.10728 | 0.095352 | 0.2511 | 0.24598 | 0.24044 | 0.23346 | 0.23818 | 0.24051 | 0.23602 | 0.23338 | 0.23042 | 0.22439 | 0.22136 | 0.19316 | 0.16222 | 0.14586 | 0.2455 | 0.23937 | 0.23346 | 0.2261 | 0.22955 | 0.23268 | 0.22694 | 0.22304 | 0.21863 | 0.21043 | 0.20596 | 0.16862 | 0.1296 | 0.11701
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 1.696 | 1.9984 | 1.604 | 15.4247 | 14.5635 | 13.583 | 12.7003 | 11.2502 | 9.334 | 7.6309 | 6.4852 | 5.3924 | 2.2755 | -0.033838 | -1.1146 | 4.3259 | 4.1643 | 17.7826 | 17.5425 | 17.2845 | 17.1178 | 16.4206 | 15.1659 | 14.1006 | 13.5036 | 12.9297 | 11.6488 | 10.5193 | 9.656 | 3.6833 | 3.4577 | 17.1709 | 16.5633 | 15.8637 | 15.2246 | 14.1043 | 12.5323 | 11.1305 | 10.1695 | 9.1983 | 6.593 | 4.8407 | 3.9118
|  | NEWTONHILL | CT |  |  |  | 1.696 | 2.0332 | 1.6516 | 15.4673 | 14.6153 | 13.583 | 12.7003 | 11.2502 | 9.423 | 7.8885 | 6.7666 | 5.7534 | 2.2755 | -0.033838 | -1.1146 | 4.3493 | 4.1951 | 17.7948 | 17.5425 | 17.2845 | 17.1178 | 16.5005 | 15.3998 | 14.4647 | 13.8454 | 13.3012 | 11.6488 | 10.5193 | 9.656 | 3.7091 | 3.49 | 17.1709 | 16.5633 | 15.8637 | 15.2246 | 14.1043 | 12.6014 | 11.3637 | 10.4904 | 9.6082 | 6.7213 | 4.8407 | 3.9118
|  | NEWTONHILL | LW |  |  |  | 1.696 | 1.9984 | 1.604 | 15.4247 | 14.5635 | 13.5962 | 12.773 | 11.351 | 9.334 | 7.6309 | 6.4852 | 5.3924 | 2.2759 | 0.63341 | -0.14658 | 4.3259 | 4.1643 | 17.7826 | 17.5603 | 17.325 | 17.1311 | 16.4206 | 15.1659 | 14.1006 | 13.5036 | 12.9297 | 11.6771 | 10.9966 | 10.6146 | 3.6833 | 3.4577 | 17.1765 | 16.6063 | 15.9633 | 15.3503 | 14.2113 | 12.5323 | 11.1305 | 10.1695 | 9.1983 | 6.593 | 5.3034 | 4.6116
|  | NEWTONHILL | ST |  |  |  | 1.696 | 2.1365 | 1.8695 | 16.0807 | 15.7346 | 15.331 | 14.9142 | 14.2014 | 13.0554 | 12.3324 | 11.6781 | 11.0254 | 8.1604 | 6.0251 | 4.4726 | 4.3772 | 4.2812 | 17.9612 | 17.8321 | 17.6754 | 17.4996 | 16.984 | 15.9858 | 15.2666 | 14.762 | 14.2807 | 12.9895 | 12.3777 | 11.532 | 3.7621 | 3.6277 | 17.6325 | 17.4362 | 17.1901 | 16.9285 | 16.351 | 15.361 | 14.6362 | 14.0673 | 13.514 | 11.3441 | 9.7462 | 8.4315
|  | NEWTONHILL | FS |  |  |  | 1.696 | 2.2189 | 2.0199 | 16.3189 | 16.0576 | 15.7529 | 15.4348 | 14.9611 | 14.1062 | 13.3039 | 12.6694 | 12.3319 | 9.4412 | 7.1177 | 5.3545 | 4.4062 | 4.329 | 18.038 | 17.9383 | 17.8185 | 17.6894 | 17.3492 | 16.6957 | 16.1459 | 15.7661 | 15.4526 | 13.8013 | 12.7264 | 11.0378 | 3.8013 | 3.6985 | 17.7471 | 17.6101 | 17.4484 | 17.2693 | 16.8932 | 16.1964 | 15.564 | 15.089 | 14.7322 | 12.4733 | 10.6603 | 9.1422
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 8.5 | -8.9806 | -8.9884 | -8.9969 | -9.0048 | -9.0102 | -9.0184 | -9.03 | -9.031 | -9.0323 | -9.0335 | -9.0346 | -9.0491 | -9.0714 | -9.0961 | -8.6193 | -8.6287 | -8.639 | -8.6484 | -8.6547 | -8.6642 | -8.6778 | -8.6782 | -8.6787 | -8.6792 | -8.6796 | -8.6959 | -8.7235 | -8.7542 | -8.7219 | -8.7312 | -8.7416 | -8.751 | -8.7573 | -8.7669 | -8.7806 | -8.7811 | -8.7817 | -8.7823 | -8.7829 | -8.7993 | -8.827 | -8.8577
|  | NIGG | CT |  |  |  | 8.5 | -8.9806 | -8.981 | -8.9814 | -8.9895 | -8.9917 | -8.9947 | -9.0012 | -9.0029 | -9.0044 | -9.0059 | -9.0073 | -9.0147 | -9.0206 | -9.0289 | -8.6193 | -8.6195 | -8.6197 | -8.6292 | -8.6315 | -8.6348 | -8.6423 | -8.6437 | -8.6451 | -8.6465 | -8.6479 | -8.6566 | -8.6652 | -8.678 | -8.7218 | -8.722 | -8.7222 | -8.7317 | -8.734 | -8.7373 | -8.7448 | -8.7463 | -8.7476 | -8.749 | -8.7503 | -8.7583 | -8.7655 | -8.7758
|  | NIGG | LW |  |  |  | 8.5 | -8.9806 | -8.9884 | -8.9969 | -9.0048 | -9.0102 | -9.0184 | -9.03 | -9.031 | -9.0323 | -9.0335 | -9.0346 | -9.0491 | -9.0714 | -9.0961 | -8.6193 | -8.6287 | -8.639 | -8.6484 | -8.6547 | -8.6642 | -8.6778 | -8.6782 | -8.6787 | -8.6792 | -8.6796 | -8.6959 | -8.7235 | -8.7542 | -8.7219 | -8.7312 | -8.7416 | -8.751 | -8.7573 | -8.7669 | -8.7806 | -8.7811 | -8.7817 | -8.7823 | -8.7829 | -8.7993 | -8.827 | -8.8577
|  | NIGG | ST |  |  |  | 8.5 | -8.9804 | -8.9806 | -8.9858 | -8.9893 | -8.9913 | -8.9926 | -8.9939 | -8.9953 | -8.9969 | -8.9986 | -8.9995 | -9.024 | -9.05 | -9.073 | -8.6193 | -8.6194 | -8.6256 | -8.6298 | -8.6321 | -8.6333 | -8.6346 | -8.6359 | -8.6373 | -8.6387 | -8.6392 | -8.6665 | -8.6991 | -8.7302 | -8.7218 | -8.7219 | -8.7281 | -8.7323 | -8.7345 | -8.7357 | -8.7369 | -8.7382 | -8.7396 | -8.741 | -8.7415 | -8.7683 | -8.7997 | -8.8283
|  | NIGG | FS |  |  |  | 8.5 | -8.9804 | -8.9805 | -8.9823 | -8.9841 | -8.9859 | -8.9878 | -8.9906 | -8.9926 | -8.9955 | -8.9984 | -8.9989 | -9.0024 | -9.0056 | -9.0108 | -8.6193 | -8.6194 | -8.6215 | -8.6237 | -8.6259 | -8.6281 | -8.6314 | -8.6337 | -8.6371 | -8.6405 | -8.6409 | -8.6435 | -8.6476 | -8.6578 | -8.7218 | -8.7218 | -8.7239 | -8.7261 | -8.7282 | -8.7304 | -8.7336 | -8.7358 | -8.7391 | -8.7423 | -8.7426 | -8.7442 | -8.7458 | -8.7507
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 0 | 9.1637 | 8.886 | 8.528 | 8.0401 | 7.638 | 7.1538 | 6.6639 | 6.2669 | 5.7162 | 5.3172 | 4.9208 | 4.0356 | 3.6374 | 2.8262 | 9.5867 | 9.2586 | 8.9487 | 8.4595 | 8.1288 | 7.849 | 7.5604 | 7.4438 | 7.092 | 6.8479 | 6.6248 | 5.7784 | 5.367 | 4.1881 | 9.7659 | 9.4773 | 9.1627 | 8.6345 | 8.2145 | 7.7675 | 7.3028 | 6.9531 | 6.4553 | 6.1269 | 5.8114 | 4.9827 | 4.5283 | 3.8197
|  | NINEWELLS | CT |  |  |  | 0 | 9.2037 | 8.968 | 8.6527 | 8.1334 | 7.6958 | 7.2359 | 6.7724 | 6.3506 | 5.8937 | 5.603 | 5.3244 | 4.2768 | 3.7325 | 3.3875 | 9.6387 | 9.3714 | 9.0921 | 8.5613 | 8.2007 | 7.9162 | 7.647 | 7.4823 | 7.2342 | 7.0589 | 6.8976 | 6.2596 | 5.731 | 4.9666 | 9.8108 | 9.5737 | 9.3068 | 8.7474 | 8.2981 | 7.8608 | 7.4156 | 7.0376 | 6.6157 | 6.3602 | 6.1228 | 5.1773 | 4.6996 | 4.3993
|  | NINEWELLS | LW |  |  |  | 0 | 9.1637 | 8.886 | 8.528 | 8.0401 | 7.638 | 7.1538 | 6.6639 | 6.2669 | 5.7162 | 5.3172 | 4.9208 | 4.0356 | 3.8719 | 3.5227 | 9.5867 | 9.2586 | 8.9487 | 8.4595 | 8.1288 | 7.849 | 7.5604 | 7.4438 | 7.092 | 6.8479 | 6.6248 | 6.189 | 6.1478 | 6.0839 | 9.7659 | 9.4773 | 9.1627 | 8.6345 | 8.2145 | 7.7675 | 7.3028 | 6.9531 | 6.4553 | 6.1269 | 5.8114 | 4.9827 | 4.8007 | 4.5064
|  | NINEWELLS | ST |  |  |  | 0 | 9.2497 | 9.0611 | 8.8408 | 8.3915 | 8.0517 | 7.7195 | 7.393 | 7.1593 | 6.7539 | 6.4509 | 6.127 | 4.3784 | 3.6374 | 3.2445 | 9.6531 | 9.4134 | 9.1488 | 8.6543 | 8.3162 | 8.0512 | 7.8104 | 7.6839 | 7.4268 | 7.2888 | 7.0875 | 5.7784 | 5.367 | 5.2348 | 9.8288 | 9.6253 | 9.4002 | 8.9842 | 8.6929 | 8.4357 | 8.1971 | 8.0415 | 7.6821 | 7.4319 | 7.099 | 5.2302 | 4.5283 | 4.1687
|  | NINEWELLS | FS |  |  |  | 0 | 9.2838 | 9.1443 | 8.9901 | 8.6883 | 8.398 | 8.0928 | 7.8665 | 7.7047 | 7.4027 | 7.1861 | 6.9575 | 5.3639 | 3.8837 | 2.8262 | 9.7018 | 9.5224 | 9.3296 | 8.9662 | 8.6634 | 8.3984 | 8.2189 | 8.1166 | 7.8933 | 7.7624 | 7.6293 | 6.6196 | 5.735 | 4.1881 | 9.8703 | 9.7198 | 9.5572 | 9.253 | 8.9962 | 8.7426 | 8.5743 | 8.477 | 8.2547 | 8.0872 | 7.8757 | 6.2055 | 4.8067 | 3.8197
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0 | 0.17116 | 0.16294 | 0.15489 | 0.14599 | 0.13462 | 0.13479 | 0.13278 | 0.12803 | 0.12061 | 0.11787 | 0.11202 | 0.10215 | 0.097257 | 0.091107 | 0.17585 | 0.16924 | 0.16323 | 0.15671 | 0.14802 | 0.15015 | 0.15222 | 0.14576 | 0.14335 | 0.14248 | 0.13782 | 0.13389 | 0.13228 | 0.12927 | 0.16823 | 0.16067 | 0.15346 | 0.14473 | 0.13365 | 0.13023 | 0.1307 | 0.12629 | 0.11847 | 0.11663 | 0.11043 | 0.10304 | 0.099375 | 0.094202
|  | NORTH HOY | CT |  |  |  | 0 | 0.17116 | 0.16294 | 0.15489 | 0.14599 | 0.13462 | 0.13479 | 0.13278 | 0.12803 | 0.12232 | 0.12063 | 0.11573 | 0.10446 | 0.099368 | 0.094135 | 0.17585 | 0.16924 | 0.16323 | 0.15671 | 0.14802 | 0.15015 | 0.15222 | 0.14924 | 0.14466 | 0.14442 | 0.14022 | 0.13487 | 0.13305 | 0.13065 | 0.16823 | 0.16067 | 0.15346 | 0.14473 | 0.13365 | 0.13023 | 0.1307 | 0.12629 | 0.12014 | 0.11921 | 0.11376 | 0.10451 | 0.10063 | 0.096363
|  | NORTH HOY | LW |  |  |  | 0 | 0.17198 | 0.16462 | 0.15722 | 0.14776 | 0.13893 | 0.13616 | 0.13347 | 0.12892 | 0.12061 | 0.11787 | 0.11202 | 0.10215 | 0.097257 | 0.091107 | 0.17625 | 0.17029 | 0.1651 | 0.15815 | 0.15208 | 0.15135 | 0.15298 | 0.15033 | 0.14335 | 0.14248 | 0.13782 | 0.13389 | 0.13228 | 0.12927 | 0.16889 | 0.16212 | 0.15562 | 0.1465 | 0.13792 | 0.13172 | 0.13165 | 0.12759 | 0.11847 | 0.11663 | 0.11043 | 0.10304 | 0.099375 | 0.094202
|  | NORTH HOY | ST |  |  |  | 0 | 0.17378 | 0.16997 | 0.16472 | 0.15875 | 0.1524 | 0.14527 | 0.13728 | 0.12868 | 0.1306 | 0.13226 | 0.12877 | 0.10597 | 0.10101 | 0.097088 | 0.178 | 0.1755 | 0.17219 | 0.16817 | 0.16379 | 0.15864 | 0.15266 | 0.14576 | 0.14803 | 0.15239 | 0.15092 | 0.13532 | 0.13534 | 0.13399 | 0.17066 | 0.16738 | 0.16292 | 0.15758 | 0.15132 | 0.14425 | 0.13628 | 0.1277 | 0.12644 | 0.13063 | 0.12794 | 0.1056 | 0.10337 | 0.10044
|  | NORTH HOY | FS |  |  |  | 0 | 0.1755 | 0.17295 | 0.17039 | 0.16735 | 0.16413 | 0.16045 | 0.15619 | 0.15012 | 0.1427 | 0.14446 | 0.14802 | 0.12865 | 0.11023 | 0.10305 | 0.17879 | 0.17694 | 0.17491 | 0.17242 | 0.16976 | 0.16664 | 0.16295 | 0.15816 | 0.15204 | 0.15515 | 0.15966 | 0.14771 | 0.13814 | 0.13481 | 0.17209 | 0.16974 | 0.16741 | 0.1646 | 0.16162 | 0.15818 | 0.15417 | 0.14859 | 0.14116 | 0.13951 | 0.14405 | 0.12585 | 0.10999 | 0.10433
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 0 | 3.1614 | 3.0793 | 2.9648 | 2.8218 | 2.6801 | 2.5137 | 2.3192 | 2.2139 | 2.1364 | 2.0362 | 1.9477 | 1.6998 | 1.5569 | 1.4036 | 3.4888 | 3.4451 | 3.387 | 3.3121 | 3.241 | 3.1574 | 3.0507 | 2.9781 | 2.9221 | 2.8529 | 2.7911 | 2.6414 | 2.5664 | 2.4623 | 3.3234 | 3.2494 | 3.1528 | 3.0269 | 2.9047 | 2.7652 | 2.5888 | 2.4734 | 2.3842 | 2.2768 | 2.1819 | 1.9546 | 1.8389 | 1.706
|  | NORTH KESSOCK | CT |  |  |  | 0 | 3.1614 | 3.0793 | 2.9648 | 2.8218 | 2.6801 | 2.5137 | 2.3192 | 2.2139 | 2.17 | 2.0973 | 2.037 | 1.8088 | 1.6849 | 1.5599 | 3.4888 | 3.4451 | 3.3911 | 3.3156 | 3.2487 | 3.1667 | 3.0655 | 2.9923 | 2.9644 | 2.9094 | 2.86 | 2.6951 | 2.5994 | 2.4623 | 3.3234 | 3.2494 | 3.1528 | 3.0269 | 2.9108 | 2.7676 | 2.5961 | 2.4835 | 2.4418 | 2.3606 | 2.29 | 2.0717 | 1.9776 | 1.8779
|  | NORTH KESSOCK | LW |  |  |  | 0 | 3.1748 | 3.0942 | 2.9775 | 2.8356 | 2.6919 | 2.5291 | 2.3341 | 2.2234 | 2.1364 | 2.0362 | 1.9477 | 1.6998 | 1.5569 | 1.4036 | 3.494 | 3.446 | 3.387 | 3.3121 | 3.241 | 3.1574 | 3.0507 | 2.9781 | 2.9221 | 2.8529 | 2.7911 | 2.6414 | 2.5664 | 2.4719 | 3.3326 | 3.2568 | 3.1563 | 3.0289 | 2.9047 | 2.7652 | 2.5888 | 2.4734 | 2.3842 | 2.2768 | 2.1819 | 1.9546 | 1.8389 | 1.706
|  | NORTH KESSOCK | ST |  |  |  | 0 | 3.1923 | 3.1312 | 3.0496 | 2.971 | 2.8828 | 2.8005 | 2.7046 | 2.6355 | 2.54 | 2.4495 | 2.3492 | 1.9496 | 1.7693 | 1.6689 | 3.5066 | 3.4763 | 3.4348 | 3.3963 | 3.3507 | 3.3101 | 3.2585 | 3.222 | 3.1639 | 3.1096 | 3.0472 | 2.768 | 2.6211 | 2.4893 | 3.3539 | 3.3004 | 3.2311 | 3.1668 | 3.0895 | 3.0199 | 2.9334 | 2.876 | 2.7835 | 2.6978 | 2.5995 | 2.2041 | 2.0474 | 1.9649
|  | NORTH KESSOCK | FS |  |  |  | 0 | 3.2312 | 3.1914 | 3.1645 | 3.1293 | 3.1053 | 3.0679 | 3.0365 | 2.9684 | 2.9094 | 2.8355 | 2.7611 | 2.4048 | 2.0091 | 1.8705 | 3.5218 | 3.5002 | 3.4828 | 3.4586 | 3.4432 | 3.4169 | 3.3942 | 3.3526 | 3.3174 | 3.2701 | 3.2232 | 2.9891 | 2.6951 | 2.4716 | 3.3841 | 3.348 | 3.3228 | 3.2869 | 3.2671 | 3.2292 | 3.1991 | 3.1355 | 3.0861 | 3.0158 | 2.9449 | 2.6145 | 2.2568 | 2.1495
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0.425 | -1.7998 | -2.0112 | -2.2836 | -2.4354 | -2.6308 | -2.8183 | -3.055 | -3.171 | -3.2548 | -3.3369 | -3.4413 | -3.7263 | -3.8627 | -4.0622 | -1.2296 | -1.405 | -1.6093 | -1.6846 | -1.7619 | -1.8573 | -1.9853 | -2.0725 | -2.1868 | -2.253 | -2.3396 | -2.5459 | -2.6189 | -2.7535 | -1.4561 | -1.6222 | -1.837 | -1.9644 | -2.1333 | -2.2812 | -2.4859 | -2.6059 | -2.7179 | -2.7942 | -2.9007 | -3.1592 | -3.2784 | -3.4697
|  | NOSTIE BRIDGE | CT |  |  |  | 0.425 | -1.7998 | -1.9894 | -2.2592 | -2.4354 | -2.6308 | -2.8183 | -3.055 | -3.171 | -3.2548 | -3.2991 | -3.3616 | -3.5871 | -3.7031 | -3.8571 | -1.2296 | -1.3739 | -1.5553 | -1.6511 | -1.7531 | -1.8483 | -1.9741 | -2.0698 | -2.1446 | -2.1886 | -2.2541 | -2.4561 | -2.5438 | -2.6905 | -1.4561 | -1.6055 | -1.818 | -1.9644 | -2.1333 | -2.2812 | -2.4859 | -2.6059 | -2.6931 | -2.735 | -2.8069 | -3.0256 | -3.1118 | -3.2511
|  | NOSTIE BRIDGE | LW |  |  |  | 0.425 | -1.787 | -2.0112 | -2.2836 | -2.4298 | -2.5851 | -2.7705 | -2.9969 | -3.1105 | -3.2522 | -3.3369 | -3.4413 | -3.7263 | -3.8627 | -4.0622 | -1.2245 | -1.405 | -1.6093 | -1.6846 | -1.7619 | -1.8573 | -1.9853 | -2.0725 | -2.1868 | -2.253 | -2.3396 | -2.5459 | -2.6189 | -2.7535 | -1.4462 | -1.6222 | -1.837 | -1.9629 | -2.0963 | -2.2534 | -2.4582 | -2.5709 | -2.7179 | -2.7942 | -2.9007 | -3.1592 | -3.2784 | -3.4697
|  | NOSTIE BRIDGE | ST |  |  |  | 0.425 | -1.7717 | -1.9312 | -2.1229 | -2.2152 | -2.2911 | -2.3757 | -2.4728 | -2.5683 | -2.6577 | -2.7538 | -2.8609 | -3.3023 | -3.4707 | -3.5412 | -1.2129 | -1.3347 | -1.487 | -1.5454 | -1.5891 | -1.6386 | -1.6955 | -1.7543 | -1.8119 | -1.8768 | -1.9511 | -2.2945 | -2.4404 | -2.5447 | -1.4301 | -1.5496 | -1.6952 | -1.7765 | -1.8362 | -1.9066 | -1.9932 | -2.0819 | -2.1565 | -2.246 | -2.3486 | -2.7678 | -2.9125 | -2.9764
|  | NOSTIE BRIDGE | FS |  |  |  | 0.425 | -1.739 | -1.8559 | -1.9675 | -2.007 | -2.0345 | -2.0784 | -2.1218 | -2.198 | -2.2854 | -2.3496 | -2.4281 | -2.8902 | -3.3136 | -3.4934 | -1.2007 | -1.2933 | -1.3888 | -1.4201 | -1.4404 | -1.4754 | -1.5111 | -1.5636 | -1.6265 | -1.6679 | -1.7222 | -2.0668 | -2.3895 | -2.619 | -1.4043 | -1.4918 | -1.5758 | -1.6141 | -1.6361 | -1.678 | -1.7162 | -1.785 | -1.8665 | -1.9175 | -1.9911 | -2.4003 | -2.7771 | -2.9232
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 0.666 | 6.9148 | 4.5573 | 1.8175 | -0.82828 | -2.8425 | -5.6721 | -9.4947 | -10.482 | -11.4432 | -11.8338 | -12.5629 | -17.3351 | -23.6787 | -31.1665 | 12.4117 | 9.7089 | 6.6932 | 3.8366 | 1.7961 | -1.1869 | -5.2901 | -6.0156 | -6.6664 | -6.9916 | -7.5306 | -12.66 | -20.3845 | -29.2805 | 10.5875 | 7.9063 | 4.895 | 2.0225 | -0.28023 | -3.5863 | -8.0906 | -9.0961 | -10.0624 | -10.4627 | -11.2031 | -16.7219 | -24.5378 | -33.6642
|  | OBAN | CT |  |  |  | 0.666 | 6.9148 | 6.4789 | 5.8381 | 3.2025 | 2.0648 | 0.77466 | -1.7171 | -2.6771 | -3.5963 | -4.0036 | -4.772 | -7.6838 | -9.9506 | -12.7209 | 12.4117 | 12.1239 | 11.7814 | 8.9645 | 8.1076 | 6.9846 | 4.5503 | 3.8467 | 3.0435 | 2.5672 | 1.8446 | -1.1466 | -3.9252 | -7.4253 | 10.5923 | 10.3363 | 9.9944 | 7.1113 | 5.9436 | 4.516 | 1.6679 | 0.74927 | -0.24886 | -0.72315 | -1.5708 | -4.8258 | -7.5103 | -10.7832
|  | OBAN | LW |  |  |  | 0.666 | 6.9288 | 4.5573 | 1.8175 | -0.82828 | -2.8425 | -5.6721 | -9.4947 | -10.482 | -11.4432 | -11.8338 | -12.5629 | -17.3351 | -23.6787 | -31.1665 | 12.4226 | 9.7089 | 6.6932 | 3.8366 | 1.7961 | -1.1869 | -5.2901 | -6.0156 | -6.6664 | -6.9916 | -7.5306 | -12.66 | -20.3845 | -29.2805 | 10.5875 | 7.9063 | 4.895 | 2.0225 | -0.28023 | -3.5863 | -8.0906 | -9.0961 | -10.0624 | -10.4627 | -11.2031 | -16.7219 | -24.5378 | -33.6642
|  | OBAN | ST |  |  |  | 0.666 | 7.0297 | 6.7601 | 5.2161 | 4.1352 | 3.362 | 2.978 | 2.4993 | 1.7029 | 0.94613 | 0.23383 | -0.31113 | -6.9498 | -13.9901 | -20.3057 | 12.4706 | 12.2682 | 10.516 | 9.3214 | 8.5307 | 8.1804 | 7.7697 | 6.989 | 6.2814 | 5.6845 | 5.3271 | -2.2269 | -11.0818 | -19.3977 | 10.624 | 10.4444 | 8.7315 | 7.5775 | 6.832 | 6.5303 | 6.0851 | 5.2116 | 4.3746 | 3.6052 | 3.057 | -4.8561 | -13.7926 | -21.8453
|  | OBAN | FS |  |  |  | 0.666 | 7.1226 | 6.9888 | 6.4716 | 5.9764 | 5.3808 | 4.7936 | 3.9446 | 3.108 | 2.1864 | 1.3054 | 0.98648 | -1.1596 | -2.6404 | -4.6771 | 12.5189 | 12.4436 | 11.8963 | 11.3617 | 10.7123 | 10.0659 | 9.0771 | 8.1848 | 7.2342 | 6.3365 | 6.111 | 4.574 | 3.0641 | 0.21629 | 10.6638 | 10.6064 | 10.094 | 9.5968 | 8.9871 | 8.3873 | 7.4513 | 6.6238 | 5.6587 | 4.6502 | 4.3365 | 2.2243 | 0.80552 | -1.5355
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 0.303 | 5.8869 | 5.7101 | 5.4255 | 5.0982 | 4.7048 | 4.2034 | 3.6508 | 2.9857 | 2.2314 | 1.5564 | 1.3838 | -0.043741 | -0.41111 | -0.88593 | 7.887 | 7.7729 | 7.6681 | 7.5736 | 7.4246 | 7.279 | 7.0982 | 6.8332 | 6.5264 | 6.1221 | 6.018 | 4.9395 | 4.1914 | 2.0509 | 7.9369 | 7.7888 | 7.4975 | 7.1619 | 6.7876 | 6.2773 | 5.7338 | 5.0972 | 4.3984 | 3.771 | 3.5294 | 2.1031 | 1.7632 | 1.3282
|  | OLD CRAIGIE ROAD | CT |  |  |  | 0.303 | 5.8939 | 5.7101 | 5.4255 | 5.1112 | 4.7048 | 4.2733 | 3.7621 | 3.0982 | 2.5646 | 2.0252 | 1.9668 | 0.29736 | -0.41111 | -0.88593 | 7.887 | 7.7729 | 7.6681 | 7.5736 | 7.4246 | 7.279 | 7.0982 | 6.8332 | 6.5624 | 6.2164 | 6.1537 | 4.9395 | 4.1914 | 3.112 | 7.9471 | 7.7942 | 7.5156 | 7.196 | 6.7998 | 6.3721 | 5.8656 | 5.2298 | 4.7115 | 4.2038 | 4.0716 | 2.3889 | 1.7632 | 1.3282
|  | OLD CRAIGIE ROAD | LW |  |  |  | 0.303 | 5.8869 | 5.7114 | 5.4259 | 5.0982 | 4.7316 | 4.2034 | 3.6508 | 2.9857 | 2.2314 | 1.5564 | 1.3838 | -0.043741 | -0.1772 | -0.59284 | 7.892 | 7.7896 | 7.7076 | 7.6144 | 7.5151 | 7.3215 | 7.1314 | 6.8818 | 6.5264 | 6.1221 | 6.018 | 5.1708 | 5.0938 | 4.8265 | 7.9369 | 7.7888 | 7.4975 | 7.1619 | 6.7876 | 6.2773 | 5.7338 | 5.0972 | 4.3984 | 3.771 | 3.5294 | 2.1031 | 1.9645 | 1.5755
|  | OLD CRAIGIE ROAD | ST |  |  |  | 0.303 | 5.9585 | 5.8952 | 5.834 | 5.7657 | 5.669 | 5.5406 | 5.4234 | 5.2343 | 4.9794 | 4.7649 | 4.4706 | 3.2471 | 2.5321 | 1.836 | 7.9194 | 7.8824 | 7.836 | 7.7856 | 7.7163 | 7.6271 | 7.5488 | 7.4257 | 7.2603 | 7.1242 | 6.936 | 6.3647 | 5.492 | 4.3047 | 8.0057 | 7.9513 | 7.9028 | 7.8475 | 7.7691 | 7.6647 | 7.5501 | 7.3623 | 7.1081 | 6.8944 | 6.6018 | 5.4251 | 4.765 | 4.0836
|  | OLD CRAIGIE ROAD | FS |  |  |  | 0.303 | 5.9735 | 5.9243 | 5.8527 | 5.7567 | 5.6795 | 5.5717 | 5.4405 | 5.2999 | 5.0887 | 4.8718 | 4.6348 | 3.0029 | 1.875 | 0.81424 | 7.925 | 7.8947 | 7.8578 | 7.8041 | 7.7649 | 7.7032 | 7.6249 | 7.5599 | 7.4457 | 7.3277 | 7.1966 | 6.1168 | 4.4592 | 2.0509 | 8.0197 | 7.9777 | 7.9113 | 7.8259 | 7.7533 | 7.6568 | 7.5424 | 7.4048 | 7.2137 | 7.0176 | 6.7994 | 5.2344 | 4.0399 | 2.8764
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 1.199 | 1.2147 | 0.95924 | 0.5966 | 0.18227 | -0.31414 | -0.81629 | -1.3382 | -2.0763 | -2.509 | -2.8416 | -2.8872 | -3.8121 | -4.3752 | -4.7837 | 2.7973 | 2.699 | 2.5734 | 2.4043 | 2.1918 | 1.9459 | 1.6973 | 1.157 | 0.79748 | 0.65288 | 0.67557 | 0.1824 | -0.16744 | -0.56333 | 2.3872 | 2.1652 | 1.8461 | 1.4935 | 1.0612 | 0.62027 | 0.15048 | -0.52685 | -0.94458 | -1.2446 | -1.2694 | -2.1013 | -2.5525 | -2.9111
|  | OLDMELDRUM | CT |  |  |  | 1.199 | 1.22 | 0.96543 | 0.5966 | 0.18227 | -0.31414 | -0.81629 | -1.3382 | -2.0763 | -2.509 | -2.8416 | -2.8293 | -3.7982 | -4.3752 | -4.7837 | 2.8041 | 2.7019 | 2.5734 | 2.4043 | 2.1918 | 1.9459 | 1.6973 | 1.1603 | 0.875 | 0.65288 | 0.71916 | 0.1824 | -0.16744 | -0.56333 | 2.3872 | 2.1652 | 1.8461 | 1.4935 | 1.0612 | 0.62027 | 0.15048 | -0.52685 | -0.92668 | -1.2446 | -1.1938 | -2.0502 | -2.5525 | -2.9111
|  | OLDMELDRUM | LW |  |  |  | 1.199 | 1.2147 | 0.95924 | 0.60364 | 0.21938 | -0.21424 | -0.69355 | -1.1614 | -1.9902 | -2.5088 | -2.5814 | -2.8872 | -3.8121 | -4.2489 | -4.6431 | 2.7973 | 2.699 | 2.6005 | 2.4459 | 2.2405 | 1.9785 | 1.7438 | 1.157 | 0.79748 | 0.84526 | 0.67557 | 0.20238 | 0.032521 | -0.12789 | 2.3874 | 2.1662 | 1.8634 | 1.5383 | 1.1655 | 0.73347 | 0.3078 | -0.44954 | -0.94458 | -0.97853 | -1.2694 | -2.1013 | -2.4663 | -2.8079
|  | OLDMELDRUM | ST |  |  |  | 1.199 | 1.2944 | 1.1086 | 0.91022 | 0.72376 | 0.50759 | 0.30349 | 0.1281 | -0.39152 | -0.71031 | -0.91431 | -1.1724 | -2.051 | -2.7336 | -3.2944 | 2.8323 | 2.7738 | 2.7118 | 2.6489 | 2.5715 | 2.4571 | 2.3642 | 1.9224 | 1.6852 | 1.534 | 1.3597 | 0.71625 | 0.43566 | -0.0074447 | 2.4241 | 2.3055 | 2.136 | 1.9776 | 1.7933 | 1.6098 | 1.4558 | 0.98245 | 0.68051 | 0.4836 | 0.23387 | -0.5835 | -1.174 | -1.6379
|  | OLDMELDRUM | FS |  |  |  | 1.199 | 1.3852 | 1.2524 | 1.1473 | 1.0386 | 0.90276 | 0.78246 | 0.65499 | 0.29639 | 0.043476 | -0.17987 | -0.39126 | -1.6469 | -2.4948 | -3.2729 | 2.8561 | 2.8126 | 2.7743 | 2.7318 | 2.6777 | 2.6269 | 2.5567 | 2.2614 | 2.1139 | 1.9787 | 1.8523 | 0.97622 | 0.36723 | -0.47849 | 2.4476 | 2.3993 | 2.3287 | 2.2363 | 2.1182 | 2.0121 | 1.892 | 1.5789 | 1.347 | 1.1403 | 0.9483 | -0.23368 | -0.96175 | -1.6339
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 0.947 | 9.2408 | 9.0096 | 8.6134 | 8.1168 | 7.587 | 7.0028 | 6.3004 | 5.6964 | 5.2184 | 4.762 | 4.6146 | 3.1268 | 2.5997 | 2.1179 | 9.9389 | 9.7815 | 9.5583 | 9.2765 | 8.9802 | 8.6589 | 8.256 | 7.8814 | 7.5899 | 7.2956 | 7.2677 | 6.4093 | 5.667 | 5.1924 | 9.4092 | 9.1774 | 8.8335 | 8.3607 | 7.923 | 7.4456 | 6.8236 | 6.2818 | 5.8672 | 5.4649 | 5.2656 | 3.8365 | 3.4259 | 3.1528
|  | ORMLIE | CT |  |  |  | 0.947 | 9.2408 | 9.0096 | 8.6134 | 8.1168 | 7.587 | 7.0028 | 6.3004 | 5.6964 | 5.2184 | 4.762 | 4.6639 | 3.3848 | 2.6934 | 2.1615 | 9.9389 | 9.7815 | 9.5583 | 9.2765 | 8.9802 | 8.6589 | 8.256 | 7.8814 | 7.5899 | 7.2956 | 7.2677 | 6.4688 | 6.0204 | 5.4596 | 9.4092 | 9.1774 | 8.8335 | 8.3607 | 7.923 | 7.4456 | 6.8236 | 6.2818 | 5.8672 | 5.4649 | 5.2752 | 4.3063 | 3.8313 | 3.3532
|  | ORMLIE | LW |  |  |  | 0.947 | 9.2589 | 9.0618 | 8.718 | 8.3044 | 7.8881 | 7.3202 | 6.7061 | 6.1142 | 5.4571 | 4.8665 | 4.6146 | 3.1268 | 2.5997 | 2.1179 | 9.9496 | 9.8178 | 9.6387 | 9.4152 | 9.2126 | 8.8903 | 8.5413 | 8.1889 | 7.7771 | 7.4053 | 7.2938 | 6.41 | 6.145 | 5.8521 | 9.4238 | 9.2286 | 8.9721 | 8.6554 | 8.3423 | 7.8747 | 7.3483 | 6.823 | 6.2068 | 5.6416 | 5.2656 | 3.8365 | 3.4259 | 3.1564
|  | ORMLIE | ST |  |  |  | 0.947 | 9.3235 | 9.2101 | 9.0875 | 8.9554 | 8.8017 | 8.6201 | 8.4308 | 8.1983 | 7.9046 | 7.6224 | 7.2658 | 4.9547 | 3.9935 | 3.5186 | 9.9892 | 9.9218 | 9.8396 | 9.7511 | 9.6431 | 9.5115 | 9.3789 | 9.2043 | 8.9779 | 8.7595 | 8.4189 | 6.4093 | 5.667 | 5.4762 | 9.4916 | 9.3996 | 9.2723 | 9.1298 | 8.9573 | 8.749 | 8.5167 | 8.2326 | 7.8603 | 7.4699 | 7.0124 | 4.6498 | 3.6196 | 3.1528
|  | ORMLIE | FS |  |  |  | 0.947 | 9.3831 | 9.3066 | 9.2428 | 9.162 | 9.0866 | 8.991 | 8.8757 | 8.7022 | 8.4795 | 8.2495 | 8.0036 | 6.3849 | 4.8911 | 3.5041 | 10.0159 | 9.9666 | 9.9159 | 9.8492 | 9.789 | 9.7084 | 9.6071 | 9.4892 | 9.3235 | 9.1514 | 8.9658 | 7.7522 | 6.5455 | 5.1924 | 9.5313 | 9.4694 | 9.3929 | 9.2998 | 9.2042 | 9.0848 | 8.9426 | 8.7668 | 8.532 | 8.2865 | 8.0168 | 6.2239 | 4.4748 | 3.1709
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0.431 | -0.64378 | -0.65329 | -0.68518 | -0.72255 | -0.76639 | -0.81429 | -0.86831 | -0.9068 | -0.93217 | -0.9736 | -1.011 | -1.1047 | -1.1356 | -1.1919 | -0.37613 | -0.37902 | -0.39541 | -0.41488 | -0.43888 | -0.46521 | -0.49511 | -0.52851 | -0.5572 | -0.59384 | -0.62762 | -0.701 | -0.7117 | -0.75118 | -0.53939 | -0.55118 | -0.57919 | -0.612 | -0.65136 | -0.69454 | -0.74356 | -0.78636 | -0.8196 | -0.86607 | -0.9085 | -1.0074 | -1.0319 | -1.089
|  | OTTER FERRY | CT |  |  |  | 0.431 | -0.64378 | -0.65329 | -0.68518 | -0.72255 | -0.76639 | -0.81429 | -0.86831 | -0.9068 | -0.92601 | -0.95386 | -0.97802 | -1.0497 | -1.0815 | -1.1275 | -0.37613 | -0.37902 | -0.39541 | -0.41488 | -0.43888 | -0.46521 | -0.49511 | -0.52851 | -0.54333 | -0.56955 | -0.59391 | -0.65423 | -0.67255 | -0.71046 | -0.53939 | -0.55118 | -0.57919 | -0.612 | -0.65136 | -0.69454 | -0.74356 | -0.78636 | -0.80603 | -0.83826 | -0.86726 | -0.94397 | -0.97026 | -1.0143
|  | OTTER FERRY | LW |  |  |  | 0.431 | -0.63997 | -0.64723 | -0.67561 | -0.70983 | -0.74859 | -0.7988 | -0.85246 | -0.89348 | -0.93217 | -0.9736 | -1.011 | -1.1047 | -1.1356 | -1.1919 | -0.37453 | -0.37617 | -0.38977 | -0.40768 | -0.42843 | -0.45878 | -0.49084 | -0.52512 | -0.5572 | -0.59384 | -0.62762 | -0.701 | -0.7117 | -0.75118 | -0.53641 | -0.54613 | -0.57056 | -0.60089 | -0.6356 | -0.68271 | -0.73307 | -0.77792 | -0.8196 | -0.86607 | -0.9085 | -1.0074 | -1.0319 | -1.089
|  | OTTER FERRY | ST |  |  |  | 0.431 | -0.62768 | -0.64894 | -0.65137 | -0.66839 | -0.68549 | -0.70714 | -0.72719 | -0.74936 | -0.77304 | -0.80166 | -0.8325 | -0.94912 | -0.97729 | -0.98609 | -0.36286 | -0.3775 | -0.37298 | -0.38217 | -0.39113 | -0.40513 | -0.4173 | -0.43239 | -0.44904 | -0.4709 | -0.49498 | -0.59391 | -0.61492 | -0.62725 | -0.52389 | -0.54297 | -0.5461 | -0.56143 | -0.57662 | -0.59761 | -0.61637 | -0.6381 | -0.66189 | -0.69164 | -0.72399 | -0.84997 | -0.87638 | -0.8836
|  | OTTER FERRY | FS |  |  |  | 0.431 | -0.6188 | -0.63411 | -0.63404 | -0.63639 | -0.64267 | -0.64916 | -0.65993 | -0.67457 | -0.69363 | -0.71443 | -0.73164 | -0.8453 | -0.95547 | -1.0068 | -0.35934 | -0.37077 | -0.37108 | -0.37175 | -0.37687 | -0.38207 | -0.39204 | -0.40116 | -0.41456 | -0.43007 | -0.44165 | -0.53062 | -0.61275 | -0.66655 | -0.51697 | -0.53104 | -0.53552 | -0.53707 | -0.54381 | -0.5507 | -0.56298 | -0.57658 | -0.59532 | -0.61649 | -0.63324 | -0.7501 | -0.8564 | -0.90526
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 4.022 | 18.4279 | 18.3029 | 17.9501 | 17.7176 | 17.4621 | 17.0946 | 16.6714 | 16.2139 | 15.675 | 15.1835 | 14.7229 | 13.4641 | 13.3344 | 12.8748 | 19.9606 | 19.8563 | 19.5448 | 19.3413 | 19.1292 | 18.8911 | 18.601 | 18.2566 | 17.9698 | 17.6747 | 17.3893 | 15.9233 | 12.7899 | 7.3701 | 19.1482 | 19.0571 | 18.7011 | 18.5122 | 18.3059 | 18.0269 | 17.63 | 17.192 | 16.6726 | 16.198 | 15.7526 | 14.5502 | 14.4291 | 13.9774
|  | OVERGATE | CT |  |  |  | 4.022 | 18.4794 | 18.3307 | 18.0069 | 17.7388 | 17.466 | 17.1627 | 16.7787 | 16.3049 | 15.9364 | 15.5652 | 15.2301 | 14.0568 | 13.7011 | 13.2754 | 19.9843 | 19.8563 | 19.5448 | 19.3413 | 19.1292 | 18.8911 | 18.601 | 18.2566 | 17.9698 | 17.6747 | 17.3893 | 15.9233 | 14.4675 | 11.9409 | 19.2004 | 19.0903 | 18.7728 | 18.5549 | 18.339 | 18.0834 | 17.7166 | 17.2655 | 16.916 | 16.5611 | 16.2397 | 15.1344 | 14.8151 | 14.4118
|  | OVERGATE | LW |  |  |  | 4.022 | 18.4279 | 18.3029 | 17.9501 | 17.7176 | 17.4621 | 17.0946 | 16.6714 | 16.2139 | 15.675 | 15.1835 | 14.7229 | 13.4641 | 13.3344 | 12.8748 | 19.9606 | 19.8846 | 19.5693 | 19.4502 | 19.3155 | 19.1045 | 18.8602 | 18.5879 | 18.2566 | 17.9605 | 17.6817 | 16.9404 | 16.853 | 16.5749 | 19.1482 | 19.0571 | 18.7011 | 18.5122 | 18.3059 | 18.0269 | 17.63 | 17.192 | 16.6726 | 16.198 | 15.7526 | 14.5502 | 14.4291 | 13.9774
|  | OVERGATE | ST |  |  |  | 4.022 | 18.5156 | 18.4701 | 18.2577 | 18.1679 | 18.0625 | 17.9245 | 17.7687 | 17.5945 | 17.37 | 17.1511 | 16.8953 | 15.5739 | 15.045 | 14.6705 | 19.9979 | 19.9417 | 19.69 | 19.5871 | 19.4705 | 19.3263 | 19.1724 | 18.9894 | 18.7634 | 18.5368 | 18.2741 | 16.5537 | 14.9384 | 12.4627 | 19.2228 | 19.1883 | 18.9644 | 18.8848 | 18.7952 | 18.6822 | 18.5619 | 18.4234 | 18.2484 | 18.0571 | 17.8072 | 16.5191 | 16.0209 | 15.6897
|  | OVERGATE | FS |  |  |  | 4.022 | 18.5892 | 18.556 | 18.3972 | 18.3338 | 18.2417 | 18.1526 | 18.0322 | 17.8948 | 17.7257 | 17.561 | 17.3707 | 15.971 | 14.693 | 13.7625 | 20.0483 | 19.9949 | 19.7888 | 19.7 | 19.5828 | 19.4609 | 19.2802 | 19.0657 | 18.8115 | 18.5635 | 18.286 | 16.23 | 12.7899 | 7.3701 | 19.2914 | 19.2746 | 19.1028 | 19.0491 | 18.9723 | 18.9026 | 18.8045 | 18.6926 | 18.5525 | 18.4228 | 18.272 | 16.945 | 15.7333 | 14.8625
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0 | 0.15809 | 0.14935 | 0.1397 | 0.13045 | 0.12379 | 0.11358 | 0.099684 | 0.096752 | 0.093064 | 0.089921 | 0.087137 | 0.070762 | 0.048043 | 0.022885 | 0.14827 | 0.13791 | 0.12667 | 0.11608 | 0.10872 | 0.097265 | 0.081344 | 0.078588 | 0.075059 | 0.07204 | 0.069341 | 0.050003 | 0.022149 | -0.0097235 | 0.15025 | 0.13968 | 0.12817 | 0.11726 | 0.10956 | 0.097682 | 0.0813 | 0.078251 | 0.074388 | 0.071071 | 0.068116 | 0.048483 | 0.020472 | -0.011311
|  | OVERSCAIG | CT |  |  |  | 0 | 0.15809 | 0.15662 | 0.15485 | 0.14549 | 0.14149 | 0.13667 | 0.12779 | 0.12417 | 0.12132 | 0.11823 | 0.11539 | 0.10583 | 0.099522 | 0.090674 | 0.14827 | 0.14703 | 0.14581 | 0.13528 | 0.1315 | 0.12672 | 0.11708 | 0.1133 | 0.11024 | 0.10684 | 0.10363 | 0.092104 | 0.084559 | 0.073433 | 0.15027 | 0.14884 | 0.14727 | 0.13627 | 0.1321 | 0.12695 | 0.11691 | 0.11295 | 0.10977 | 0.10634 | 0.10314 | 0.091702 | 0.083861 | 0.072347
|  | OVERSCAIG | LW |  |  |  | 0 | 0.15811 | 0.14935 | 0.1397 | 0.13045 | 0.12379 | 0.11358 | 0.099684 | 0.096752 | 0.093064 | 0.089921 | 0.087137 | 0.070762 | 0.048043 | 0.022885 | 0.14827 | 0.13791 | 0.12667 | 0.11608 | 0.10872 | 0.097265 | 0.081344 | 0.078588 | 0.075059 | 0.07204 | 0.069341 | 0.050003 | 0.022149 | -0.0097235 | 0.15025 | 0.13968 | 0.12817 | 0.11726 | 0.10956 | 0.097682 | 0.0813 | 0.078251 | 0.074388 | 0.071071 | 0.068116 | 0.048483 | 0.020472 | -0.011311
|  | OVERSCAIG | ST |  |  |  | 0 | 0.15856 | 0.15796 | 0.15231 | 0.14814 | 0.14551 | 0.14351 | 0.14133 | 0.13892 | 0.13606 | 0.13307 | 0.1307 | 0.099807 | 0.072928 | 0.049843 | 0.14866 | 0.14823 | 0.14158 | 0.13683 | 0.13404 | 0.1321 | 0.12999 | 0.12767 | 0.12493 | 0.12209 | 0.1201 | 0.086014 | 0.053448 | 0.024766 | 0.15073 | 0.15019 | 0.14338 | 0.13845 | 0.13545 | 0.13329 | 0.13092 | 0.1283 | 0.1252 | 0.12196 | 0.11952 | 0.083251 | 0.050335 | 0.021563
|  | OVERSCAIG | FS |  |  |  | 0 | 0.15878 | 0.15834 | 0.15626 | 0.15407 | 0.15185 | 0.14951 | 0.14625 | 0.14354 | 0.13973 | 0.13588 | 0.13437 | 0.12598 | 0.1184 | 0.11314 | 0.14876 | 0.14841 | 0.146 | 0.14348 | 0.14093 | 0.13827 | 0.13449 | 0.13156 | 0.12735 | 0.12312 | 0.12183 | 0.11469 | 0.10851 | 0.10328 | 0.15088 | 0.15047 | 0.14798 | 0.14538 | 0.14273 | 0.13997 | 0.13608 | 0.13298 | 0.12856 | 0.1241 | 0.12258 | 0.11401 | 0.10639 | 0.10037
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0.086 | -1.4364 | -1.5237 | -1.6714 | -1.8631 | -2.0441 | -2.2376 | -2.4795 | -2.6119 | -2.7617 | -2.916 | -3.0172 | -3.4157 | -3.6609 | -3.9027 | -0.38798 | -0.44206 | -0.50188 | -0.57666 | -0.64423 | -0.74193 | -0.86744 | -0.95084 | -1.0627 | -1.1664 | -1.2507 | -1.5054 | -1.6242 | -1.7298 | -0.81232 | -0.88812 | -1.0093 | -1.1672 | -1.3147 | -1.4728 | -1.6723 | -1.7906 | -1.9393 | -2.0796 | -2.1925 | -2.5635 | -2.7677 | -2.949
|  | PARK | CT |  |  |  | 0.086 | -1.4364 | -1.5237 | -1.6688 | -1.8631 | -2.0441 | -2.2376 | -2.4795 | -2.6119 | -2.7372 | -2.8546 | -2.9538 | -3.2923 | -3.5362 | -3.7344 | -0.38759 | -0.42772 | -0.4811 | -0.57666 | -0.64423 | -0.72846 | -0.84595 | -0.92443 | -0.99512 | -1.0639 | -1.1231 | -1.2922 | -1.4448 | -1.6361 | -0.81232 | -0.88284 | -0.99897 | -1.1672 | -1.3147 | -1.4728 | -1.6723 | -1.7906 | -1.8964 | -1.9938 | -2.0748 | -2.3622 | -2.5452 | -2.7075
|  | PARK | LW |  |  |  | 0.086 | -1.428 | -1.5222 | -1.6714 | -1.8373 | -2.0181 | -2.2201 | -2.4497 | -2.5881 | -2.7617 | -2.916 | -3.0172 | -3.4157 | -3.6609 | -3.9027 | -0.38798 | -0.44206 | -0.50188 | -0.5687 | -0.63728 | -0.74193 | -0.86744 | -0.95084 | -1.0627 | -1.1664 | -1.2507 | -1.5054 | -1.6242 | -1.7298 | -0.80649 | -0.88812 | -1.0093 | -1.1456 | -1.2895 | -1.461 | -1.6585 | -1.7855 | -1.9393 | -2.0796 | -2.1925 | -2.5635 | -2.7677 | -2.949
|  | PARK | ST |  |  |  | 0.086 | -1.4068 | -1.4607 | -1.5452 | -1.6383 | -1.7232 | -1.8073 | -1.8787 | -1.9636 | -2.0563 | -2.1552 | -2.2304 | -2.8104 | -3.1298 | -3.3962 | -0.37535 | -0.39318 | -0.42899 | -0.467 | -0.50302 | -0.53979 | -0.57709 | -0.62612 | -0.69174 | -0.76379 | -0.829 | -1.2761 | -1.472 | -1.5994 | -0.78793 | -0.82864 | -0.89717 | -0.96932 | -1.038 | -1.1078 | -1.1755 | -1.2513 | -1.3389 | -1.4321 | -1.5154 | -2.089 | -2.3986 | -2.6109
|  | PARK | FS |  |  |  | 0.086 | -1.3828 | -1.4188 | -1.4651 | -1.505 | -1.5558 | -1.5924 | -1.6433 | -1.704 | -1.7887 | -1.8686 | -1.9516 | -2.3804 | -2.8639 | -3.1351 | -0.37076 | -0.38257 | -0.40274 | -0.42201 | -0.44718 | -0.46914 | -0.50004 | -0.53007 | -0.57322 | -0.61542 | -0.6582 | -0.93967 | -1.2743 | -1.5831 | -0.76993 | -0.7968 | -0.8302 | -0.86177 | -0.90041 | -0.93408 | -0.97836 | -1.034 | -1.1057 | -1.1759 | -1.2473 | -1.6535 | -2.1018 | -2.3909
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 0.034 | 1.5177 | 1.4544 | 1.3617 | 1.2713 | 1.1683 | 1.0469 | 0.89545 | 0.83485 | 0.75364 | 0.66516 | 0.58789 | 0.40083 | 0.31434 | 0.19108 | 2.1548 | 2.1133 | 2.0598 | 2.0111 | 1.9567 | 1.8847 | 1.7904 | 1.7459 | 1.6752 | 1.6082 | 1.5485 | 1.4126 | 1.3583 | 1.2662 | 1.8737 | 1.8143 | 1.7297 | 1.6449 | 1.5498 | 1.4379 | 1.2956 | 1.2339 | 1.1404 | 1.0521 | 0.97447 | 0.7874 | 0.70265 | 0.57596
|  | PEDDIESTON | CT |  |  |  | 0.034 | 1.5177 | 1.4544 | 1.3617 | 1.2713 | 1.1683 | 1.0469 | 0.89545 | 0.83485 | 0.77092 | 0.71373 | 0.65718 | 0.48494 | 0.41525 | 0.32546 | 2.1548 | 2.1159 | 2.0659 | 2.0162 | 1.9613 | 1.8956 | 1.8063 | 1.7601 | 1.7102 | 1.6633 | 1.614 | 1.4713 | 1.4123 | 1.3143 | 1.8737 | 1.8143 | 1.7297 | 1.6449 | 1.5498 | 1.4379 | 1.2956 | 1.2339 | 1.17 | 1.112 | 1.0539 | 0.8815 | 0.81674 | 0.72891
|  | PEDDIESTON | LW |  |  |  | 0.034 | 1.525 | 1.4601 | 1.3692 | 1.282 | 1.1833 | 1.0616 | 0.91165 | 0.84839 | 0.75364 | 0.66516 | 0.58789 | 0.40083 | 0.31434 | 0.19108 | 2.1579 | 2.1133 | 2.0598 | 2.0111 | 1.9567 | 1.8847 | 1.7904 | 1.7459 | 1.6752 | 1.6082 | 1.5485 | 1.4126 | 1.3583 | 1.2662 | 1.88 | 1.8167 | 1.7312 | 1.6491 | 1.5574 | 1.4418 | 1.298 | 1.2347 | 1.1404 | 1.0521 | 0.97447 | 0.7874 | 0.70265 | 0.57596
|  | PEDDIESTON | ST |  |  |  | 0.034 | 1.5331 | 1.4999 | 1.4466 | 1.3956 | 1.3384 | 1.2921 | 1.2282 | 1.1768 | 1.1036 | 1.0277 | 0.97994 | 0.65782 | 0.54396 | 0.48993 | 2.1636 | 2.1471 | 2.1154 | 2.0863 | 2.0526 | 2.0277 | 1.9888 | 1.9565 | 1.907 | 1.855 | 1.824 | 1.5714 | 1.4654 | 1.3832 | 1.888 | 1.8581 | 1.8081 | 1.7608 | 1.7078 | 1.6651 | 1.6054 | 1.5564 | 1.4862 | 1.4133 | 1.3665 | 1.0461 | 0.93165 | 0.8768
|  | PEDDIESTON | FS |  |  |  | 0.034 | 1.5553 | 1.5294 | 1.5099 | 1.4858 | 1.4666 | 1.4361 | 1.4183 | 1.3693 | 1.3241 | 1.2682 | 1.2123 | 0.948 | 0.67244 | 0.58036 | 2.1728 | 2.1578 | 2.1438 | 2.1256 | 2.1112 | 2.0879 | 2.0731 | 2.0402 | 2.0089 | 1.9695 | 1.9306 | 1.7372 | 1.5199 | 1.3765 | 1.9075 | 1.8839 | 1.8652 | 1.8417 | 1.823 | 1.7934 | 1.7752 | 1.7289 | 1.6851 | 1.6314 | 1.5781 | 1.3229 | 1.0614 | 0.97358
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 3.097 | 7.043 | 6.6785 | 5.8491 | 4.806 | 3.6534 | 2.7391 | 0.95939 | -0.89215 | -2.7343 | -4.3827 | -5.8346 | -10.7397 | -13.88 | -16.0283 | 9.9339 | 9.6736 | 9.2561 | 8.7092 | 8.1058 | 7.7694 | 6.6869 | 5.5761 | 4.4787 | 3.4529 | 2.5617 | -0.68459 | -2.8561 | -4.9448 | 9.2704 | 8.9389 | 8.2161 | 7.29 | 6.2601 | 5.4793 | 3.8591 | 2.1976 | 0.51294 | -0.9904 | -2.3126 | -6.7456 | -9.4893 | -11.4183
|  | PETERHEAD GRANGE | CT |  |  |  | 3.097 | 7.0617 | 6.6833 | 5.8604 | 4.812 | 3.6534 | 2.7391 | 0.95939 | -0.83253 | -2.4157 | -3.9418 | -5.198 | -10.6668 | -13.88 | -16.0283 | 9.9343 | 9.6736 | 9.2561 | 8.7092 | 8.1058 | 7.7694 | 6.6869 | 5.5761 | 4.5874 | 3.5793 | 2.7491 | -0.68459 | -2.8561 | -4.9448 | 9.2814 | 8.9389 | 8.2161 | 7.29 | 6.2601 | 5.4793 | 3.8591 | 2.2336 | 0.79843 | -0.59315 | -1.7373 | -6.6504 | -9.4893 | -11.4183
|  | PETERHEAD GRANGE | LW |  |  |  | 3.097 | 7.043 | 6.6785 | 5.8491 | 4.806 | 3.7312 | 2.7984 | 0.999 | -0.89215 | -2.7343 | -4.3827 | -5.8346 | -10.7397 | -12.8636 | -14.6011 | 9.9339 | 9.6969 | 9.311 | 8.795 | 8.2786 | 7.9151 | 6.7877 | 5.6376 | 4.4787 | 3.4529 | 2.5617 | -0.46395 | -1.858 | -3.1053 | 9.2704 | 8.9445 | 8.2232 | 7.3106 | 6.3643 | 5.5591 | 3.9134 | 2.1976 | 0.51294 | -0.9904 | -2.3126 | -6.7456 | -8.6317 | -10.2105
|  | PETERHEAD GRANGE | ST |  |  |  | 3.097 | 7.2398 | 7.0571 | 6.7921 | 6.464 | 6.1651 | 5.8365 | 5.0671 | 4.2284 | 3.6625 | 2.7879 | 2.0217 | -2.31 | -5.485 | -8.7576 | 10.0278 | 9.9101 | 9.7463 | 9.5332 | 9.3411 | 9.1108 | 8.4691 | 7.7677 | 7.3082 | 6.5658 | 5.9178 | 2.5092 | 0.20488 | -2.2286 | 9.4438 | 9.2876 | 9.0667 | 8.789 | 8.5349 | 8.2449 | 7.5274 | 6.752 | 6.2452 | 5.4318 | 4.7186 | 0.72467 | -2.111 | -5.0153
|  | PETERHEAD GRANGE | FS |  |  |  | 3.097 | 7.2991 | 7.1495 | 6.899 | 6.6392 | 6.3564 | 6.1038 | 5.5375 | 4.8233 | 4.0505 | 3.5671 | 2.8365 | -1.9453 | -6.685 | -10.2826 | 10.0599 | 9.9581 | 9.8022 | 9.6385 | 9.4509 | 9.2853 | 8.821 | 8.2799 | 7.681 | 7.3425 | 6.7762 | 3.1368 | -0.74982 | -4.3414 | 9.4911 | 9.3633 | 9.1507 | 8.9347 | 8.6924 | 8.4743 | 7.9532 | 7.3065 | 6.6018 | 6.1853 | 5.5205 | 1.1502 | -3.1591 | -6.3879
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 5.886 | 2.6907 | 2.5631 | 2.3822 | 2.0805 | 1.8698 | 1.6346 | 1.2824 | 1.0153 | 0.77928 | 0.41081 | 0.080033 | -1.0085 | -1.1309 | -1.2995 | 7.0546 | 6.9653 | 6.8362 | 6.6225 | 6.4711 | 6.2781 | 5.9838 | 5.7378 | 5.5513 | 5.3784 | 5.227 | 4.0969 | 1.3487 | -4.0565 | 3.7496 | 3.6188 | 3.4249 | 3.1464 | 2.8741 | 2.5911 | 2.1912 | 1.753 | 1.3556 | 0.89938 | 0.50373 | -0.72648 | -0.85637 | -1.194
|  | PETERHEAD NORTH STREET | CT |  |  |  | 5.886 | 2.6907 | 2.5631 | 2.3822 | 2.0805 | 1.8698 | 1.6346 | 1.2824 | 1.0153 | 0.81169 | 0.52963 | 0.27691 | -0.7072 | -1.0371 | -1.2496 | 7.0546 | 6.9653 | 6.8362 | 6.6225 | 6.4711 | 6.2781 | 5.9838 | 5.7378 | 5.5513 | 5.3784 | 5.227 | 4.0969 | 2.7589 | 0.33799 | 3.7553 | 3.6188 | 3.4249 | 3.1464 | 2.8741 | 2.5911 | 2.1912 | 1.753 | 1.3959 | 1.0752 | 0.76509 | -0.31578 | -0.60954 | -0.90965
|  | PETERHEAD NORTH STREET | LW |  |  |  | 5.886 | 2.6998 | 2.6123 | 2.5323 | 2.4015 | 2.168 | 1.8629 | 1.528 | 1.1724 | 0.77928 | 0.41081 | 0.080033 | -1.0085 | -1.1309 | -1.2995 | 7.0664 | 7.007 | 6.9522 | 6.8751 | 6.7915 | 6.6106 | 6.4017 | 6.1621 | 5.8606 | 5.5678 | 5.2925 | 4.458 | 4.281 | 4.2168 | 3.7496 | 3.6349 | 3.4599 | 3.229 | 2.9874 | 2.6389 | 2.2566 | 1.8436 | 1.3556 | 0.89938 | 0.50373 | -0.72648 | -0.85637 | -1.194
|  | PETERHEAD NORTH STREET | ST |  |  |  | 5.886 | 2.7342 | 2.7 | 2.6533 | 2.5918 | 2.5172 | 2.4187 | 2.3042 | 2.1561 | 1.9611 | 1.7367 | 1.4745 | 0.048807 | -0.42895 | -0.49006 | 7.0794 | 7.0531 | 7.0195 | 6.9763 | 6.9252 | 6.8529 | 6.7695 | 6.662 | 6.5223 | 6.3337 | 6.1086 | 4.8748 | 3.4805 | 1.1166 | 3.7978 | 3.7498 | 3.7011 | 3.6346 | 3.5639 | 3.4642 | 3.3589 | 3.2208 | 3.0553 | 2.8593 | 2.6424 | 1.488 | 1.0014 | 0.65634
|  | PETERHEAD NORTH STREET | FS |  |  |  | 5.886 | 2.7486 | 2.7266 | 2.6957 | 2.6587 | 2.6101 | 2.5559 | 2.4881 | 2.4121 | 2.3056 | 2.1894 | 2.0604 | 1.0852 | -0.068612 | -0.88053 | 7.0857 | 7.064 | 7.0362 | 7.0039 | 6.9633 | 6.918 | 6.8481 | 6.7611 | 6.6516 | 6.536 | 6.4131 | 4.6611 | 1.3487 | -4.0565 | 3.8322 | 3.802 | 3.7546 | 3.7026 | 3.6349 | 3.5691 | 3.4821 | 3.382 | 3.2471 | 3.1059 | 2.9688 | 1.7659 | 0.5242 | -0.35812
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 0.869 | 5.5205 | 5.4481 | 5.3369 | 5.1491 | 4.8995 | 4.618 | 4.211 | 4.0231 | 3.8469 | 3.5861 | 3.3946 | 2.8153 | 2.617 | 2.2237 | 6.7196 | 6.6723 | 6.6291 | 6.5711 | 6.4022 | 6.2286 | 6.0011 | 5.8709 | 5.7265 | 5.5542 | 5.4027 | 4.9782 | 4.8875 | 4.6241 | 5.5225 | 5.4656 | 5.3801 | 5.1233 | 4.8281 | 4.5182 | 4.1394 | 4.0049 | 3.8453 | 3.5816 | 3.3938 | 2.8294 | 2.6658 | 2.2902
|  | PINEGROVE | CT |  |  |  | 0.869 | 5.5205 | 5.4481 | 5.3369 | 5.1491 | 4.8995 | 4.618 | 4.211 | 4.0231 | 3.8631 | 3.6941 | 3.5493 | 3.1613 | 2.9811 | 2.6793 | 6.7207 | 6.681 | 6.6397 | 6.5711 | 6.4022 | 6.2286 | 6.0011 | 5.8709 | 5.759 | 5.638 | 5.5293 | 5.1681 | 5.0067 | 4.6617 | 5.5225 | 5.4709 | 5.3801 | 5.1233 | 4.8281 | 4.5182 | 4.1394 | 4.0049 | 3.8939 | 3.7255 | 3.5703 | 3.1807 | 3.0336 | 2.7633
|  | PINEGROVE | LW |  |  |  | 0.869 | 5.5263 | 5.4519 | 5.3517 | 5.2317 | 5.0249 | 4.7494 | 4.3543 | 4.1438 | 3.8469 | 3.5861 | 3.3946 | 2.8153 | 2.617 | 2.2237 | 6.7196 | 6.6723 | 6.6291 | 6.5786 | 6.4769 | 6.2851 | 6.0566 | 5.9197 | 5.7265 | 5.5542 | 5.4027 | 4.9782 | 4.8875 | 4.6241 | 5.5237 | 5.4656 | 5.4004 | 5.2101 | 4.969 | 4.66 | 4.3029 | 4.1445 | 3.8453 | 3.5816 | 3.3938 | 2.8294 | 2.6658 | 2.2902
|  | PINEGROVE | ST |  |  |  | 0.869 | 5.5494 | 5.5126 | 5.4582 | 5.3973 | 5.3359 | 5.2648 | 5.1918 | 5.1101 | 5.0092 | 4.8572 | 4.7065 | 3.9503 | 3.7445 | 3.7104 | 6.7343 | 6.7182 | 6.6931 | 6.6635 | 6.6344 | 6.5978 | 6.5599 | 6.5089 | 6.4028 | 6.2872 | 6.1863 | 5.6253 | 5.3841 | 5.1751 | 5.5335 | 5.5053 | 5.4854 | 5.4597 | 5.4366 | 5.342 | 5.2442 | 5.1262 | 4.9688 | 4.7968 | 4.6533 | 3.9166 | 3.727 | 3.7059
|  | PINEGROVE | FS |  |  |  | 0.869 | 5.5677 | 5.5432 | 5.514 | 5.4856 | 5.4505 | 5.4148 | 5.3704 | 5.3154 | 5.2437 | 5.1732 | 5.0981 | 4.5323 | 3.8854 | 3.6059 | 6.7383 | 6.7265 | 6.7092 | 6.6924 | 6.6703 | 6.6477 | 6.6176 | 6.5885 | 6.5456 | 6.5036 | 6.445 | 5.9233 | 5.3399 | 4.7943 | 5.5472 | 5.5285 | 5.5235 | 5.5208 | 5.5114 | 5.503 | 5.4859 | 5.4631 | 5.3597 | 5.2468 | 5.1217 | 4.4502 | 3.8567 | 3.6044
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 1.163 | 1.705 | 1.6214 | 1.4587 | 1.262 | 1.05 | 0.81061 | 0.54818 | 0.35334 | 0.14309 | -0.084903 | -0.32708 | -0.9363 | -1.1527 | -1.4375 | 2.2914 | 2.2212 | 2.1133 | 1.9914 | 1.8511 | 1.695 | 1.5206 | 1.3522 | 1.1585 | 1.0119 | 0.84844 | 0.46649 | 0.35078 | 0.096171 | 2.2238 | 2.113 | 1.9335 | 1.7479 | 1.5182 | 1.2609 | 0.98777 | 0.71975 | 0.42359 | 0.22898 | 0.0059202 | -0.53674 | -0.71172 | -0.98049
|  | PITLOCHRY | CT |  |  |  | 1.163 | 1.705 | 1.6214 | 1.4587 | 1.262 | 1.05 | 0.81061 | 0.54818 | 0.35334 | 0.19229 | 0.040018 | -0.14227 | -0.78581 | -1.0507 | -1.3109 | 2.2914 | 2.2212 | 2.1133 | 1.9914 | 1.8511 | 1.695 | 1.5206 | 1.3522 | 1.2146 | 1.1033 | 0.97225 | 0.54689 | 0.35997 | 0.096171 | 2.2238 | 2.113 | 1.9335 | 1.7479 | 1.5182 | 1.2609 | 0.98777 | 0.71975 | 0.50564 | 0.36244 | 0.18932 | -0.39072 | -0.60711 | -0.85258
|  | PITLOCHRY | LW |  |  |  | 1.163 | 1.7133 | 1.6298 | 1.4717 | 1.2956 | 1.1035 | 0.8645 | 0.62012 | 0.41148 | 0.14309 | -0.084903 | -0.32708 | -0.9363 | -1.1527 | -1.4375 | 2.2966 | 2.2238 | 2.1184 | 2.0064 | 1.8861 | 1.7138 | 1.5425 | 1.3731 | 1.1585 | 1.0119 | 0.84844 | 0.46649 | 0.35078 | 0.16645 | 2.2306 | 2.1183 | 1.9431 | 1.7609 | 1.563 | 1.2786 | 1.0097 | 0.73522 | 0.42359 | 0.22898 | 0.0059202 | -0.53674 | -0.71172 | -0.98049
|  | PITLOCHRY | ST |  |  |  | 1.163 | 1.7406 | 1.6893 | 1.6231 | 1.5543 | 1.4796 | 1.4054 | 1.323 | 1.2358 | 1.1302 | 1.0441 | 0.93679 | 0.33724 | 0.021661 | -0.21491 | 2.3177 | 2.2778 | 2.2303 | 2.1788 | 2.1188 | 2.0638 | 1.9939 | 1.9171 | 1.8133 | 1.7353 | 1.6207 | 1.0504 | 0.791 | 0.55722 | 2.2569 | 2.2037 | 2.1351 | 2.0573 | 1.9649 | 1.8865 | 1.7803 | 1.6673 | 1.5178 | 1.4217 | 1.2748 | 0.6097 | 0.34427 | 0.15492
|  | PITLOCHRY | FS |  |  |  | 1.163 | 1.7646 | 1.7292 | 1.6969 | 1.6582 | 1.6213 | 1.5775 | 1.5376 | 1.4573 | 1.3689 | 1.2816 | 1.1918 | 0.66949 | 0.026676 | -0.37839 | 2.3305 | 2.3001 | 2.2727 | 2.2349 | 2.2011 | 2.156 | 2.1176 | 2.0479 | 1.9682 | 1.8867 | 1.7956 | 1.2773 | 0.73869 | 0.25251 | 2.2678 | 2.2444 | 2.2087 | 2.1537 | 2.1081 | 2.0441 | 1.9993 | 1.898 | 1.7865 | 1.6721 | 1.5525 | 0.90957 | 0.34213 | 0.012699
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0.412 | 1.6736 | 1.524 | 1.3627 | 1.1619 | 0.97709 | 0.73808 | 0.43217 | 0.19416 | -0.23664 | -0.65679 | -0.89684 | -1.5136 | -1.9356 | -2.2477 | 2.6603 | 2.534 | 2.4459 | 2.3321 | 2.2504 | 2.1063 | 1.9303 | 1.8024 | 1.4827 | 1.1823 | 1.0358 | 0.72186 | 0.57527 | 0.35926 | 2.3527 | 2.1971 | 2.0473 | 1.8571 | 1.706 | 1.4768 | 1.1977 | 0.98185 | 0.56096 | 0.1635 | -0.063666 | -0.59863 | -0.87698 | -1.2003
|  | POLLACHAR | CT |  |  |  | 0.412 | 1.6736 | 1.5446 | 1.377 | 1.1908 | 0.97709 | 0.73808 | 0.43217 | 0.19416 | -0.15345 | -0.53991 | -0.70065 | -1.4467 | -1.9356 | -2.2477 | 2.6603 | 2.5626 | 2.4737 | 2.3741 | 2.2625 | 2.1375 | 1.9625 | 1.8275 | 1.5842 | 1.2958 | 1.202 | 0.7893 | 0.58408 | 0.36068 | 2.3527 | 2.2243 | 2.0688 | 1.9012 | 1.706 | 1.486 | 1.1977 | 0.98185 | 0.65361 | 0.28469 | 0.14699 | -0.52725 | -0.87698 | -1.1196
|  | POLLACHAR | LW |  |  |  | 0.412 | 1.6774 | 1.524 | 1.3627 | 1.1619 | 0.99304 | 0.74554 | 0.45518 | 0.21494 | -0.23664 | -0.65679 | -0.89684 | -1.5136 | -1.8187 | -2.2148 | 2.6608 | 2.534 | 2.4459 | 2.3321 | 2.2504 | 2.1063 | 1.9303 | 1.8024 | 1.4827 | 1.1823 | 1.0358 | 0.72186 | 0.57527 | 0.35926 | 2.3562 | 2.1971 | 2.0473 | 1.8571 | 1.7088 | 1.4768 | 1.2004 | 0.98702 | 0.56096 | 0.1635 | -0.063666 | -0.59863 | -0.86426 | -1.2003
|  | POLLACHAR | ST |  |  |  | 0.412 | 1.7181 | 1.6308 | 1.5584 | 1.4746 | 1.4041 | 1.3168 | 1.2409 | 1.144 | 0.90974 | 0.62201 | 0.52539 | -0.28743 | -0.82665 | -1.24 | 2.6871 | 2.619 | 2.5724 | 2.518 | 2.4742 | 2.4164 | 2.368 | 2.297 | 2.1034 | 1.8628 | 1.7917 | 1.2412 | 0.9205 | 0.64742 | 2.3968 | 2.3083 | 2.2402 | 2.1586 | 2.0926 | 2.0075 | 1.9395 | 1.8436 | 1.6183 | 1.3398 | 1.2544 | 0.50405 | 0.041682 | -0.3206
|  | POLLACHAR | FS |  |  |  | 0.412 | 1.7364 | 1.6711 | 1.6165 | 1.5702 | 1.5128 | 1.4598 | 1.3889 | 1.3116 | 1.1239 | 0.93657 | 0.80751 | 0.025007 | -0.65673 | -1.1767 | 2.6971 | 2.6463 | 2.6098 | 2.5804 | 2.5399 | 2.5028 | 2.4486 | 2.4013 | 2.2559 | 2.1101 | 2.0189 | 1.4623 | 0.99207 | 0.57813 | 2.4129 | 2.3474 | 2.2934 | 2.2517 | 2.1947 | 2.1444 | 2.073 | 2.0046 | 1.8241 | 1.6465 | 1.5232 | 0.78488 | 0.17609 | -0.26438
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0 | 0.10148 | 0.092937 | 0.083752 | 0.074856 | 0.068485 | 0.05864 | 0.045159 | 0.042375 | 0.038889 | 0.035947 | 0.03336 | 0.017566 | -0.0051037 | -0.030324 | -3.2997 | -3.3099 | -3.321 | -3.3313 | -3.3384 | -3.3495 | -3.365 | -3.3676 | -3.3709 | -3.3736 | -3.3761 | -3.3943 | -3.4219 | -3.4526 | 0.096042 | 0.08563 | 0.074317 | 0.063652 | 0.056229 | 0.044629 | 0.028583 | 0.025838 | 0.02239 | 0.019481 | 0.016921 | -0.0018329 | -0.029936 | -0.061048
|  | POOR HOUSE | CT |  |  |  | 0 | 0.10148 | 0.1002 | 0.099012 | 0.09014 | 0.086525 | 0.082099 | 0.073548 | 0.069801 | 0.066814 | 0.063508 | 0.060354 | 0.050161 | 0.04384 | 0.034829 | -3.2996 | -3.3008 | -3.3018 | -3.3121 | -3.3156 | -3.32 | -3.3293 | -3.3331 | -3.3362 | -3.3396 | -3.3429 | -3.3541 | -3.3616 | -3.3724 | 0.096042 | 0.094706 | 0.093434 | 0.082846 | 0.078985 | 0.074029 | 0.064142 | 0.060225 | 0.057061 | 0.053572 | 0.050228 | 0.038695 | 0.031018 | 0.020303
|  | POOR HOUSE | LW |  |  |  | 0 | 0.1015 | 0.092937 | 0.083752 | 0.074856 | 0.068485 | 0.05864 | 0.045159 | 0.042375 | 0.038889 | 0.035947 | 0.03336 | 0.017566 | -0.0051037 | -0.030324 | -3.2997 | -3.3099 | -3.321 | -3.3313 | -3.3384 | -3.3495 | -3.365 | -3.3676 | -3.3709 | -3.3736 | -3.3761 | -3.3943 | -3.4219 | -3.4526 | 0.096071 | 0.08563 | 0.074317 | 0.063652 | 0.056229 | 0.044629 | 0.028583 | 0.025838 | 0.02239 | 0.019481 | 0.016921 | -0.0018329 | -0.029936 | -0.061048
|  | POOR HOUSE | ST |  |  |  | 0 | 0.10189 | 0.10142 | 0.095896 | 0.091834 | 0.089191 | 0.087202 | 0.085033 | 0.082666 | 0.079847 | 0.076913 | 0.074598 | 0.043987 | 0.017491 | -0.0057758 | -3.2993 | -3.2997 | -3.3063 | -3.311 | -3.3138 | -3.3157 | -3.3178 | -3.3201 | -3.3229 | -3.3258 | -3.3279 | -3.3627 | -3.395 | -3.4241 | 0.096459 | 0.095945 | 0.089141 | 0.084226 | 0.081268 | 0.079162 | 0.076868 | 0.074335 | 0.071351 | 0.068253 | 0.065979 | 0.030482 | -0.0020359 | -0.030901
|  | POOR HOUSE | FS |  |  |  | 0 | 0.10201 | 0.10164 | 0.099596 | 0.097446 | 0.09526 | 0.092971 | 0.089754 | 0.087147 | 0.08344 | 0.079696 | 0.078269 | 0.069212 | 0.061645 | 0.057279 | -3.2992 | -3.2996 | -3.302 | -3.3045 | -3.307 | -3.3097 | -3.3135 | -3.3164 | -3.3207 | -3.3249 | -3.3263 | -3.3345 | -3.3414 | -3.3471 | 0.096616 | 0.096228 | 0.093764 | 0.091198 | 0.088595 | 0.085891 | 0.082054 | 0.079001 | 0.074643 | 0.070249 | 0.068784 | 0.059866 | 0.052591 | 0.047495
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | YES | 2.175 | -2.1985 | -2.2142 | -2.2466 | -2.2873 | -2.329 | -2.3786 | -2.4519 | -2.4874 | -2.516 | -2.5527 | -2.6034 | -2.7743 | -2.878 | -2.9473 | -2.0124 | -2.0179 | -2.0437 | -2.0704 | -2.1059 | -2.1315 | -2.1774 | -2.2068 | -2.2365 | -2.2787 | -2.3175 | -2.4208 | -2.4941 | -2.5546 | -2.027 | -2.0386 | -2.0768 | -2.123 | -2.175 | -2.2251 | -2.2934 | -2.323 | -2.3557 | -2.3948 | -2.4437 | -2.6089 | -2.7075 | -2.7745
|  | PORT ASKAIG | CT |  |  |  | 2.175 | -2.1901 | -2.2142 | -2.2466 | -2.2873 | -2.329 | -2.3786 | -2.4519 | -2.4874 | -2.516 | -2.5484 | -2.5783 | -2.6447 | -2.6653 | -2.6861 | -1.9986 | -2.0179 | -2.0437 | -2.0704 | -2.1059 | -2.1315 | -2.1774 | -2.2068 | -2.2344 | -2.2648 | -2.2929 | -2.3475 | -2.3725 | -2.4176 | -2.0118 | -2.0386 | -2.0768 | -2.123 | -2.175 | -2.2251 | -2.2934 | -2.323 | -2.3557 | -2.3895 | -2.4187 | -2.4823 | -2.5007 | -2.5191
|  | PORT ASKAIG | LW |  |  |  | 2.175 | -2.1896 | -2.2093 | -2.2331 | -2.2616 | -2.2927 | -2.338 | -2.4045 | -2.4426 | -2.4978 | -2.5527 | -2.6034 | -2.7124 | -2.7435 | -2.7687 | -1.9992 | -2.0133 | -2.0338 | -2.0568 | -2.0833 | -2.1143 | -2.1589 | -2.1892 | -2.2365 | -2.2787 | -2.3175 | -2.38 | -2.3953 | -2.4294 | -2.0125 | -2.0328 | -2.0619 | -2.0978 | -2.14 | -2.1895 | -2.253 | -2.2863 | -2.3419 | -2.3948 | -2.4437 | -2.5476 | -2.5759 | -2.5989
|  | PORT ASKAIG | ST |  |  |  | 2.175 | -2.1844 | -2.1947 | -2.2091 | -2.227 | -2.2484 | -2.2739 | -2.3019 | -2.3351 | -2.3767 | -2.4257 | -2.4784 | -2.7743 | -2.878 | -2.9083 | -1.9965 | -2.0032 | -2.0113 | -2.0232 | -2.0373 | -2.0556 | -2.0723 | -2.0964 | -2.1269 | -2.1633 | -2.2025 | -2.4208 | -2.4941 | -2.5132 | -2.0102 | -2.0181 | -2.0347 | -2.0552 | -2.0792 | -2.1076 | -2.1378 | -2.1737 | -2.2166 | -2.2677 | -2.3223 | -2.6089 | -2.7075 | -2.7356
|  | PORT ASKAIG | FS |  |  |  | 2.175 | -2.1985 | -2.1853 | -2.194 | -2.2039 | -2.2152 | -2.2289 | -2.2458 | -2.2654 | -2.2938 | -2.3196 | -2.3524 | -2.5673 | -2.7888 | -2.9473 | -2.0124 | -1.9961 | -2.0022 | -2.0089 | -2.0171 | -2.0271 | -2.0396 | -2.0532 | -2.0737 | -2.0921 | -2.116 | -2.2759 | -2.4366 | -2.5546 | -2.027 | -2.0106 | -2.0152 | -2.0253 | -2.037 | -2.0511 | -2.0686 | -2.0898 | -2.1204 | -2.1473 | -2.1818 | -2.4036 | -2.6233 | -2.7745
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 1.717 | -0.26075 | -0.28884 | -0.32942 | -0.52489 | -0.68589 | -0.84635 | -1.0154 | -1.09 | -1.1485 | -1.2 | -1.2685 | -1.4337 | -1.5309 | -1.6669 | -0.31518 | -0.33721 | -0.36279 | -0.40216 | -0.42556 | -0.4583 | -0.50709 | -0.54481 | -0.59385 | -0.63814 | -0.67895 | -0.77727 | -0.86673 | -0.91425 | -0.43317 | -0.47173 | -0.5296 | -0.62258 | -0.69388 | -0.76555 | -0.89179 | -0.97807 | -1.0605 | -1.1562 | -1.2419 | -1.4129 | -1.497 | -1.6371
|  | PORT ELLEN | CT |  |  |  | 1.717 | -0.25863 | -0.28211 | -0.32942 | -0.52489 | -0.68589 | -0.84635 | -1.0154 | -1.09 | -1.1485 | -1.2 | -1.2408 | -1.3537 | -1.4261 | -1.5275 | -0.314 | -0.32856 | -0.34779 | -0.39014 | -0.41502 | -0.44787 | -0.50342 | -0.54384 | -0.57555 | -0.60631 | -0.63292 | -0.69171 | -0.71148 | -0.78132 | -0.43317 | -0.46845 | -0.52745 | -0.62258 | -0.69388 | -0.76555 | -0.89179 | -0.97807 | -1.0478 | -1.1166 | -1.1767 | -1.3096 | -1.3694 | -1.4646
|  | PORT ELLEN | LW |  |  |  | 1.717 | -0.26075 | -0.28884 | -0.32272 | -0.50134 | -0.64035 | -0.79641 | -0.95158 | -1.026 | -1.1181 | -1.1981 | -1.2685 | -1.4337 | -1.5309 | -1.6669 | -0.31518 | -0.33721 | -0.36279 | -0.40216 | -0.42556 | -0.4583 | -0.50709 | -0.54481 | -0.59385 | -0.63814 | -0.67895 | -0.77727 | -0.82477 | -0.87116 | -0.43178 | -0.47173 | -0.5296 | -0.61265 | -0.67405 | -0.75014 | -0.86777 | -0.95165 | -1.0605 | -1.1562 | -1.2419 | -1.4129 | -1.497 | -1.6371
|  | PORT ELLEN | ST |  |  |  | 1.717 | -0.25226 | -0.26264 | -0.28894 | -0.32753 | -0.39634 | -0.46287 | -0.52366 | -0.59239 | -0.67306 | -0.73412 | -0.81348 | -1.1375 | -1.2734 | -1.3384 | -0.30992 | -0.31632 | -0.33585 | -0.36026 | -0.3745 | -0.38832 | -0.40182 | -0.42084 | -0.44711 | -0.48394 | -0.52864 | -0.76628 | -0.86673 | -0.91425 | -0.4225 | -0.44165 | -0.48175 | -0.53025 | -0.56665 | -0.60359 | -0.64085 | -0.68462 | -0.73943 | -0.78936 | -0.84922 | -1.1533 | -1.2804 | -1.3393
|  | PORT ELLEN | FS |  |  |  | 1.717 | -0.24771 | -0.25385 | -0.2712 | -0.29684 | -0.3169 | -0.33015 | -0.3506 | -0.37369 | -0.40019 | -0.4569 | -0.51769 | -0.81875 | -1.1091 | -1.2455 | -0.30758 | -0.31136 | -0.32361 | -0.341 | -0.35496 | -0.36359 | -0.37816 | -0.39386 | -0.41216 | -0.43222 | -0.44976 | -0.59056 | -0.74794 | -0.85162 | -0.41094 | -0.42214 | -0.44255 | -0.46976 | -0.49346 | -0.51126 | -0.53681 | -0.56975 | -0.60671 | -0.64701 | -0.68604 | -0.91121 | -1.1274 | -1.2611
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 1.089 | 1.2342 | 0.66164 | 0.41107 | 0.14893 | -0.15251 | -0.52889 | -1.165 | -1.4183 | -1.5973 | -1.7816 | -2.0007 | -2.5601 | -2.8305 | -3.1772 | 2.9575 | 2.5565 | 2.5157 | 2.4771 | 2.4292 | 2.3435 | 2.0941 | 1.9078 | 1.7492 | 1.6139 | 1.4596 | 1.0927 | 0.95954 | 0.68429 | 2.4519 | 2.0071 | 1.9228 | 1.7111 | 1.4467 | 1.1214 | 0.59714 | 0.4119 | 0.18679 | 0.0015491 | -0.22232 | -0.7312 | -0.92462 | -1.2257
|  | PORTREE | CT |  |  |  | 1.089 | 1.2686 | 0.76076 | 0.48549 | 0.18951 | -0.14593 | -0.52889 | -1.165 | -1.4183 | -1.5973 | -1.7221 | -1.894 | -2.3959 | -2.6348 | -2.9204 | 3.0198 | 2.698 | 2.6444 | 2.5936 | 2.5413 | 2.3857 | 2.0941 | 1.9078 | 1.7745 | 1.6779 | 1.5488 | 1.1668 | 0.97912 | 0.68429 | 2.518 | 2.1554 | 2.0012 | 1.7534 | 1.4585 | 1.1214 | 0.59714 | 0.4119 | 0.22527 | 0.10142 | -0.082248 | -0.56824 | -0.73761 | -0.96542
|  | PORTREE | LW |  |  |  | 1.089 | 1.2342 | 0.66164 | 0.41107 | 0.14893 | -0.15251 | -0.49245 | -1.0727 | -1.3199 | -1.5862 | -1.7816 | -2.0007 | -2.5601 | -2.8305 | -3.1772 | 2.9575 | 2.5565 | 2.5157 | 2.4771 | 2.4292 | 2.3435 | 2.0977 | 1.9363 | 1.7492 | 1.6139 | 1.4596 | 1.0927 | 0.95954 | 0.74564 | 2.4519 | 2.0071 | 1.9228 | 1.7111 | 1.4467 | 1.1466 | 0.68529 | 0.4687 | 0.18679 | 0.0015491 | -0.22232 | -0.7312 | -0.92462 | -1.2257
|  | PORTREE | ST |  |  |  | 1.089 | 1.3176 | 0.86042 | 0.7115 | 0.57148 | 0.41798 | 0.2513 | -0.042377 | -0.22313 | -0.43346 | -0.60876 | -0.84324 | -1.6917 | -1.9962 | -2.1123 | 3.0305 | 2.7271 | 2.6887 | 2.6629 | 2.6296 | 2.5795 | 2.472 | 2.3959 | 2.3236 | 2.2724 | 2.1283 | 1.5094 | 1.241 | 1.033 | 2.5343 | 2.2018 | 2.1523 | 2.0608 | 1.9289 | 1.7789 | 1.5477 | 1.3789 | 1.2032 | 1.0516 | 0.86364 | 0.057493 | -0.23112 | -0.36331
|  | PORTREE | FS |  |  |  | 1.089 | 1.4563 | 1.1299 | 1.0824 | 1.0311 | 0.97207 | 0.89798 | 0.76726 | 0.62109 | 0.47112 | 0.31792 | 0.12874 | -0.85429 | -1.6471 | -1.999 | 3.0911 | 2.8586 | 2.8309 | 2.8051 | 2.7703 | 2.7242 | 2.6548 | 2.5989 | 2.5509 | 2.5063 | 2.4436 | 1.9091 | 1.3017 | 0.79592 | 2.6006 | 2.3461 | 2.312 | 2.278 | 2.2342 | 2.1761 | 2.0841 | 2.011 | 1.939 | 1.7972 | 1.6256 | 0.72841 | 0.060126 | -0.2042
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 0.082 | -0.20412 | -0.26002 | -0.37598 | -0.51292 | -0.64258 | -0.81543 | -1.0039 | -1.1843 | -1.3483 | -1.5083 | -1.6518 | -2.1192 | -2.3932 | -2.6453 | 0.30341 | 0.26123 | 0.19684 | 0.11979 | 0.054239 | -0.0516 | -0.17053 | -0.27316 | -0.35979 | -0.45587 | -0.54688 | -0.79726 | -0.97644 | -1.2138 | 0.0096994 | -0.06329 | -0.1697 | -0.30564 | -0.41716 | -0.5929 | -0.78777 | -0.96996 | -1.1305 | -1.2966 | -1.4461 | -1.8925 | -2.1366 | -2.3863
|  | PORTSOY | CT |  |  |  | 0.082 | -0.20412 | -0.25518 | -0.35438 | -0.49268 | -0.62584 | -0.7801 | -0.97204 | -1.1331 | -1.2785 | -1.4123 | -1.5273 | -2.0346 | -2.3865 | -2.6262 | 0.30341 | 0.27146 | 0.2238 | 0.1405 | 0.071812 | -0.012024 | -0.12772 | -0.213 | -0.29853 | -0.38379 | -0.46113 | -0.7623 | -0.97644 | -1.2138 | 0.0096994 | -0.057132 | -0.14785 | -0.28255 | -0.39832 | -0.5476 | -0.74154 | -0.89707 | -1.0436 | -1.1842 | -1.3085 | -1.7955 | -2.0998 | -2.3205
|  | PORTSOY | LW |  |  |  | 0.082 | -0.19961 | -0.26002 | -0.37598 | -0.51292 | -0.64258 | -0.81543 | -1.0039 | -1.1843 | -1.3483 | -1.5083 | -1.6518 | -2.1192 | -2.3932 | -2.6453 | 0.30645 | 0.26123 | 0.19684 | 0.11979 | 0.054239 | -0.0516 | -0.17053 | -0.27316 | -0.35979 | -0.45587 | -0.54688 | -0.79726 | -0.9394 | -1.1005 | 0.014393 | -0.06329 | -0.1697 | -0.30564 | -0.41716 | -0.5929 | -0.78777 | -0.96996 | -1.1305 | -1.2966 | -1.4461 | -1.8925 | -2.1366 | -2.3863
|  | PORTSOY | ST |  |  |  | 0.082 | -0.18624 | -0.21508 | -0.26175 | -0.30161 | -0.34218 | -0.38759 | -0.43564 | -0.47688 | -0.53221 | -0.59233 | -0.65513 | -1.1425 | -1.5736 | -1.9304 | 0.31356 | 0.29724 | 0.26379 | 0.23716 | 0.21087 | 0.18091 | 0.14285 | 0.11272 | 0.065659 | 0.014142 | -0.042927 | -0.44235 | -0.70609 | -0.96591 | 0.032525 | 0.0026803 | -0.052406 | -0.093425 | -0.13728 | -0.19357 | -0.25633 | -0.29952 | -0.3739 | -0.45818 | -0.54782 | -1.0588 | -1.3844 | -1.6562
|  | PORTSOY | FS |  |  |  | 0.082 | -0.17196 | -0.19427 | -0.2197 | -0.24433 | -0.27572 | -0.30429 | -0.34116 | -0.3976 | -0.44949 | -0.51119 | -0.56677 | -0.92941 | -1.3394 | -1.7022 | 0.31937 | 0.30551 | 0.28841 | 0.27175 | 0.24904 | 0.22814 | 0.19629 | 0.15299 | 0.11492 | 0.065425 | 0.02161 | -0.27208 | -0.6518 | -1.0518 | 0.044314 | 0.016927 | -0.011295 | -0.036651 | -0.076031 | -0.10847 | -0.15754 | -0.22207 | -0.27165 | -0.34481 | -0.40839 | -0.81639 | -1.2292 | -1.4993
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 1.053 | 0.71075 | 0.41675 | 17.0051 | 16.2465 | 15.4162 | 14.2647 | 12.8758 | 11.4268 | 10.0845 | 8.6245 | 7.2744 | 3.5792 | 3.3782 | 2.22 | 4.3711 | 4.1287 | 19.954 | 19.5628 | 19.2128 | 18.7297 | 17.8697 | 16.9129 | 16.0591 | 15.0703 | 14.1484 | 11.6647 | 9.2808 | 2.5771 | 2.5743 | 2.2889 | 18.5107 | 17.9332 | 17.1593 | 16.071 | 14.7528 | 13.3791 | 12.1083 | 10.713 | 9.4206 | 5.9323 | 5.729 | 4.5806
|  | QUEENS LANE NORTH | CT |  |  |  | 1.053 | 0.71502 | 0.41675 | 17.0631 | 16.4328 | 15.6272 | 14.8142 | 13.6694 | 12.1791 | 10.9708 | 10.112 | 9.0751 | 5.1391 | 3.974 | 2.9507 | 4.3711 | 4.1287 | 19.954 | 19.5628 | 19.2128 | 18.7297 | 17.9172 | 16.9129 | 16.0941 | 15.5153 | 14.7502 | 11.6647 | 9.8154 | 6.7894 | 2.5779 | 2.2889 | 18.5107 | 18.0676 | 17.3221 | 16.5559 | 15.4671 | 14.062 | 12.9272 | 12.1308 | 11.1476 | 7.4998 | 6.4601 | 5.4925
|  | QUEENS LANE NORTH | LW |  |  |  | 1.053 | 0.71075 | 0.43192 | 17.0051 | 16.2465 | 15.4162 | 14.2647 | 12.8758 | 11.4268 | 10.0845 | 8.6245 | 7.2744 | 3.5792 | 3.3782 | 2.22 | 4.3775 | 4.1395 | 20.0358 | 19.7797 | 19.3851 | 18.7416 | 17.8697 | 16.9303 | 16.0591 | 15.0703 | 14.1484 | 11.8071 | 11.6217 | 10.7017 | 2.5743 | 2.3006 | 18.6019 | 17.9332 | 17.1593 | 16.071 | 14.7528 | 13.3791 | 12.1083 | 10.713 | 9.4206 | 5.9323 | 5.729 | 4.5806
|  | QUEENS LANE NORTH | ST |  |  |  | 1.053 | 0.80244 | 0.69351 | 17.5084 | 17.3098 | 17.0789 | 16.8051 | 16.4513 | 16.0004 | 15.3656 | 14.6568 | 13.8446 | 9.1912 | 7.4273 | 6.825 | 4.4279 | 4.3464 | 20.3257 | 20.1563 | 19.9566 | 19.7199 | 19.4163 | 19.0381 | 18.5407 | 17.9851 | 17.3494 | 13.6606 | 11.3412 | 8.3046 | 2.663 | 2.5581 | 18.9407 | 18.7492 | 18.525 | 18.2598 | 17.9175 | 17.4384 | 16.7578 | 16.0058 | 15.1446 | 10.5709 | 8.8586 | 8.2776
|  | QUEENS LANE NORTH | FS |  |  |  | 1.053 | 0.83183 | 0.75266 | 17.6152 | 17.4858 | 17.3386 | 17.1607 | 16.9537 | 16.7011 | 16.2588 | 15.7617 | 15.2663 | 11.1767 | 7.6109 | 4.7631 | 4.4427 | 4.376 | 20.3851 | 20.2831 | 20.1648 | 20.0192 | 19.836 | 19.4898 | 19.0473 | 18.595 | 18.1156 | 14.2285 | 9.2808 | 2.5771 | 2.6908 | 2.6148 | 19.0448 | 18.9211 | 18.7783 | 18.6053 | 18.4045 | 18.1599 | 17.8299 | 17.4177 | 16.9556 | 13.0806 | 9.7433 | 7.1002
| QUOICH | QUOICH | MINIMUM HEADROOM | NH 11700 01900 | YES | YES | 0.015 | 0.98131 | 0.97146 | 0.96011 | 0.94882 | 0.9401 | 0.92711 | 0.91007 | 0.90483 | 0.8983 | 0.89269 | 0.89376 | 0.87308 | 0.84906 | 0.82117 | 0.98271 | 0.97154 | 0.95934 | 0.94753 | 0.93903 | 0.92576 | 0.90772 | 0.90299 | 0.89701 | 0.89188 | 0.89657 | 0.87537 | 0.84698 | 0.81419 | 0.98161 | 0.97003 | 0.95686 | 0.944 | 0.93433 | 0.9198 | 0.90043 | 0.89522 | 0.88878 | 0.88311 | 0.88402 | 0.86057 | 0.83128 | 0.79745
|  | QUOICH | CT |  |  |  | 0.015 | 0.98131 | 0.97832 | 0.9749 | 0.96375 | 0.95748 | 0.95024 | 0.93832 | 0.93243 | 0.92777 | 0.92268 | 0.91803 | 0.9095 | 0.9017 | 0.89089 | 0.98271 | 0.98043 | 0.97814 | 0.96644 | 0.96118 | 0.95489 | 0.94323 | 0.93742 | 0.93278 | 0.92763 | 0.92279 | 0.91722 | 0.90716 | 0.89179 | 0.98161 | 0.97877 | 0.97558 | 0.96286 | 0.95647 | 0.94894 | 0.93593 | 0.92988 | 0.92505 | 0.9198 | 0.91495 | 0.9049 | 0.8959 | 0.88323
|  | QUOICH | LW |  |  |  | 0.015 | 0.98159 | 0.97146 | 0.96011 | 0.94882 | 0.9401 | 0.92711 | 0.91007 | 0.90483 | 0.8983 | 0.89269 | 0.89376 | 0.87308 | 0.84906 | 0.82117 | 0.98284 | 0.97154 | 0.95934 | 0.94753 | 0.93903 | 0.92576 | 0.90772 | 0.90299 | 0.89701 | 0.89188 | 0.89657 | 0.87537 | 0.84698 | 0.81419 | 0.98185 | 0.97003 | 0.95686 | 0.944 | 0.93433 | 0.9198 | 0.90043 | 0.89522 | 0.88878 | 0.88311 | 0.88402 | 0.86057 | 0.83128 | 0.79745
|  | QUOICH | ST |  |  |  | 0.015 | 0.98224 | 0.98068 | 0.97364 | 0.96802 | 0.96389 | 0.96031 | 0.95646 | 0.95261 | 0.9481 | 0.94344 | 0.93933 | 0.90719 | 0.87843 | 0.85408 | 0.98342 | 0.98244 | 0.97504 | 0.96946 | 0.96578 | 0.96286 | 0.95965 | 0.9562 | 0.95209 | 0.94781 | 0.94425 | 0.91209 | 0.87703 | 0.84441 | 0.9825 | 0.98107 | 0.97299 | 0.96673 | 0.96237 | 0.95878 | 0.95492 | 0.951 | 0.94643 | 0.9417 | 0.93772 | 0.9007 | 0.86611 | 0.83623
|  | QUOICH | FS |  |  |  | 0.015 | 0.98308 | 0.98201 | 0.97943 | 0.97669 | 0.97388 | 0.97091 | 0.96696 | 0.96313 | 0.95806 | 0.95296 | 0.95012 | 0.93475 | 0.92024 | 0.91345 | 0.98375 | 0.98299 | 0.98017 | 0.97718 | 0.97411 | 0.97087 | 0.96638 | 0.96251 | 0.95717 | 0.95179 | 0.94928 | 0.93496 | 0.91938 | 0.9046 | 0.98324 | 0.98225 | 0.97931 | 0.97622 | 0.97305 | 0.96972 | 0.9652 | 0.96107 | 0.9555 | 0.9499 | 0.94717 | 0.93235 | 0.91855 | 0.91121
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0 | 0.079099 | 0.074167 | 0.069361 | 0.064076 | 0.05727 | 0.050372 | 0.040664 | 0.043857 | 0.046967 | 0.040705 | 0.041559 | 0.033501 | 0.03082 | 0.027271 | 0.084379 | 0.080407 | 0.076813 | 0.072941 | 0.067732 | 0.062608 | 0.054897 | 0.058347 | 0.061009 | 0.055274 | 0.058443 | 0.053161 | 0.052231 | 0.050514 | 0.080033 | 0.075474 | 0.071144 | 0.066416 | 0.059838 | 0.053064 | 0.043536 | 0.043017 | 0.046986 | 0.041694 | 0.041745 | 0.033922 | 0.031828 | 0.028824
|  | RACKWICK | CT |  |  |  | 0 | 0.079099 | 0.074167 | 0.069361 | 0.064076 | 0.05727 | 0.050372 | 0.040664 | 0.051572 | 0.047883 | 0.043523 | 0.043467 | 0.033942 | 0.031276 | 0.02827 | 0.084379 | 0.080407 | 0.076813 | 0.072941 | 0.067732 | 0.062608 | 0.054897 | 0.066089 | 0.062938 | 0.059322 | 0.059811 | 0.053239 | 0.052231 | 0.050893 | 0.080033 | 0.075474 | 0.071144 | 0.066416 | 0.059838 | 0.053064 | 0.043536 | 0.052107 | 0.047954 | 0.043316 | 0.043617 | 0.034124 | 0.031888 | 0.029425
|  | RACKWICK | LW |  |  |  | 0 | 0.079611 | 0.075215 | 0.070788 | 0.065136 | 0.059875 | 0.051483 | 0.041876 | 0.043857 | 0.046967 | 0.041926 | 0.041559 | 0.033501 | 0.03082 | 0.027271 | 0.084627 | 0.081056 | 0.077954 | 0.073791 | 0.070171 | 0.063624 | 0.05604 | 0.058347 | 0.062162 | 0.058069 | 0.058443 | 0.053161 | 0.052264 | 0.050514 | 0.080444 | 0.07637 | 0.072466 | 0.0674 | 0.062374 | 0.054143 | 0.044733 | 0.043017 | 0.046986 | 0.041694 | 0.041745 | 0.033922 | 0.031828 | 0.028824
|  | RACKWICK | ST |  |  |  | 0 | 0.080677 | 0.078394 | 0.075254 | 0.071683 | 0.067887 | 0.063622 | 0.058844 | 0.053809 | 0.047445 | 0.040705 | 0.044331 | 0.038077 | 0.032927 | 0.030644 | 0.085675 | 0.08418 | 0.082199 | 0.079796 | 0.077177 | 0.0741 | 0.070524 | 0.066417 | 0.061009 | 0.055274 | 0.058978 | 0.056846 | 0.054142 | 0.053421 | 0.081503 | 0.079531 | 0.07685 | 0.073742 | 0.070213 | 0.066011 | 0.061309 | 0.056354 | 0.050095 | 0.04351 | 0.043515 | 0.038663 | 0.034105 | 0.0324
|  | RACKWICK | FS |  |  |  | 0 | 0.081722 | 0.080198 | 0.078681 | 0.076873 | 0.074967 | 0.07277 | 0.070233 | 0.066619 | 0.062188 | 0.057632 | 0.052682 | 0.048135 | 0.037796 | 0.034074 | 0.086147 | 0.085046 | 0.083843 | 0.082354 | 0.080773 | 0.078908 | 0.076711 | 0.073852 | 0.070193 | 0.06641 | 0.062244 | 0.061629 | 0.055602 | 0.05387 | 0.082369 | 0.08096 | 0.079567 | 0.077885 | 0.076105 | 0.074037 | 0.071631 | 0.068314 | 0.064184 | 0.059931 | 0.055287 | 0.047648 | 0.03775 | 0.034569
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 0 | 0.97417 | 0.96514 | 0.9556 | 0.94641 | 0.93979 | 0.92925 | 0.91476 | 0.91067 | 0.90554 | 0.90102 | 0.89691 | 0.87744 | 0.85456 | 0.82935 | -2.409 | -2.4196 | -2.4308 | -2.4415 | -2.4489 | -2.4606 | -2.4768 | -2.4801 | -2.4843 | -2.488 | -2.4913 | -2.5117 | -2.5395 | -2.5704 | 0.97276 | 0.96183 | 0.95016 | 0.93902 | 0.93105 | 0.91865 | 0.90164 | 0.89766 | 0.89265 | 0.88824 | 0.88423 | 0.86201 | 0.83372 | 0.80248
|  | RAHOY | CT |  |  |  | 0 | 0.97426 | 0.97255 | 0.97091 | 0.9615 | 0.95765 | 0.95291 | 0.94383 | 0.939 | 0.93516 | 0.93104 | 0.92718 | 0.91487 | 0.90834 | 0.89952 | -2.4089 | -2.4103 | -2.4116 | -2.4224 | -2.4262 | -2.431 | -2.4407 | -2.4451 | -2.4486 | -2.4524 | -2.456 | -2.4682 | -2.4755 | -2.486 | 0.97283 | 0.97105 | 0.96932 | 0.95796 | 0.95358 | 0.94823 | 0.93783 | 0.93289 | 0.92892 | 0.92466 | 0.92066 | 0.90714 | 0.89929 | 0.88851
|  | RAHOY | LW |  |  |  | 0 | 0.97417 | 0.96514 | 0.9556 | 0.94641 | 0.93979 | 0.92925 | 0.91476 | 0.91067 | 0.90554 | 0.90102 | 0.89691 | 0.87744 | 0.85456 | 0.82935 | -2.409 | -2.4196 | -2.4308 | -2.4415 | -2.4489 | -2.4606 | -2.4768 | -2.4801 | -2.4843 | -2.488 | -2.4913 | -2.5117 | -2.5395 | -2.5704 | 0.97276 | 0.96183 | 0.95016 | 0.93902 | 0.93105 | 0.91865 | 0.90164 | 0.89766 | 0.89265 | 0.88824 | 0.88423 | 0.86201 | 0.83372 | 0.80248
|  | RAHOY | ST |  |  |  | 0 | 0.97475 | 0.97409 | 0.96835 | 0.96403 | 0.96118 | 0.95889 | 0.95631 | 0.95327 | 0.94952 | 0.94556 | 0.94207 | 0.90482 | 0.8761 | 0.85269 | -2.4085 | -2.409 | -2.4157 | -2.4206 | -2.4236 | -2.4257 | -2.4282 | -2.4309 | -2.4342 | -2.4377 | -2.4405 | -2.479 | -2.5125 | -2.5413 | 0.97334 | 0.97263 | 0.96558 | 0.96037 | 0.95702 | 0.95444 | 0.95157 | 0.94839 | 0.94451 | 0.94044 | 0.93705 | 0.89539 | 0.86074 | 0.83169
|  | RAHOY | FS |  |  |  | 0 | 0.97492 | 0.97442 | 0.97223 | 0.9699 | 0.96749 | 0.96493 | 0.96139 | 0.95842 | 0.95423 | 0.94999 | 0.94801 | 0.93462 | 0.92305 | 0.9157 | -2.4084 | -2.4088 | -2.4113 | -2.4139 | -2.4166 | -2.4194 | -2.4234 | -2.4265 | -2.431 | -2.4356 | -2.4372 | -2.448 | -2.4568 | -2.4635 | 0.97355 | 0.97302 | 0.9704 | 0.96764 | 0.9648 | 0.96181 | 0.95764 | 0.9542 | 0.94934 | 0.94443 | 0.94238 | 0.92923 | 0.91804 | 0.91009
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 8.167 | 1.3131 | 0.25417 | -1.0543 | -3.3632 | -5.2334 | -7.185 | -9.9294 | -12.6323 | -14.6104 | -16.5826 | -18.1392 | -28.1203 | -32.6847 | -33.3616 | 12.1821 | 10.9836 | 9.7821 | 7.9804 | 6.5514 | 5.0563 | 2.9468 | 0.88154 | -0.62075 | -2.119 | -3.306 | -11.122 | -14.6417 | -15.1651 | 2.0395 | 1.0277 | -0.47442 | -2.6942 | -4.486 | -6.356 | -8.9967 | -11.5931 | -13.4895 | -15.3836 | -16.8816 | -26.5471 | -30.9591 | -31.6123
|  | RAIGMORE | CT |  |  |  | 8.167 | 1.4519 | 0.34268 | -1.0543 | -3.3632 | -5.2334 | -7.185 | -9.9294 | -12.6323 | -14.6104 | -16.5826 | -18.1392 | -21.7547 | -21.8507 | -21.93 | 12.3192 | 11.042 | 9.7821 | 7.9804 | 6.5514 | 5.0563 | 2.9468 | 0.88154 | -0.62075 | -2.119 | -3.306 | -6.0517 | -6.1065 | -6.1698 | 2.1793 | 1.0744 | -0.47442 | -2.6942 | -4.486 | -6.356 | -8.9967 | -11.5931 | -13.4895 | -15.3836 | -16.8816 | -20.3598 | -20.4457 | -20.5194
|  | RAIGMORE | LW |  |  |  | 8.167 | 1.3131 | 0.25417 | -0.58184 | -1.8598 | -3.0401 | -5.041 | -7.3608 | -9.8314 | -12.9081 | -15.6633 | -18.0373 | -23.8735 | -24.5356 | -24.9543 | 12.1821 | 10.9836 | 10.1468 | 9.0727 | 8.1828 | 6.6626 | 4.8925 | 3.0161 | 0.67053 | -1.4309 | -3.2478 | -7.7187 | -8.2225 | -8.5425 | 2.0395 | 1.0277 | 0.075527 | -1.2314 | -2.3569 | -4.2777 | -6.5108 | -8.8826 | -11.8412 | -14.491 | -16.7787 | -22.4128 | -23.0536 | -23.4608
|  | RAIGMORE | ST |  |  |  | 8.167 | 1.6787 | 1.0726 | 0.43701 | -0.34412 | -1.2626 | -2.6082 | -4.2441 | -6.0994 | -8.5076 | -11.0739 | -13.8911 | -28.1203 | -32.6847 | -33.3616 | 12.5998 | 11.9498 | 11.2809 | 10.4405 | 9.5924 | 8.5254 | 7.2532 | 5.823 | 3.9731 | 2.0046 | -0.16372 | -11.122 | -14.6417 | -15.1651 | 2.3898 | 1.809 | 1.2203 | 0.4187 | -0.62896 | -1.9437 | -3.5152 | -5.2961 | -7.612 | -10.0828 | -12.8033 | -26.5471 | -30.9591 | -31.6123
|  | RAIGMORE | FS |  |  |  | 8.167 | 1.9332 | 1.4772 | 1.0362 | 0.48599 | -0.01402 | -0.67178 | -1.5205 | -2.5506 | -3.879 | -5.2438 | -6.7231 | -16.1063 | -24.1783 | -28.1548 | 12.8654 | 12.3817 | 11.9252 | 11.3465 | 10.8055 | 10.1655 | 9.427 | 8.6328 | 7.6116 | 6.5582 | 5.4076 | -1.8667 | -8.0755 | -11.1471 | 2.6347 | 2.1965 | 1.7881 | 1.2749 | 0.7918 | 0.0083929 | -0.90195 | -1.8861 | -3.1587 | -4.4675 | -5.8913 | -14.9369 | -22.7271 | -26.5605
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0.096 | -1.9192 | -2.019 | -2.1517 | -2.296 | -2.472 | -2.6595 | -2.8857 | -3.025 | -3.2044 | -3.3617 | -3.462 | -3.8467 | -4.0333 | -4.2174 | -1.1039 | -1.1731 | -1.2411 | -1.3123 | -1.3954 | -1.5067 | -1.6185 | -1.7215 | -1.851 | -1.9629 | -2.0117 | -2.2156 | -2.2954 | -2.4742 | -1.7178 | -1.8079 | -1.9296 | -2.0618 | -2.2178 | -2.393 | -2.5958 | -2.7346 | -2.903 | -3.0507 | -3.1426 | -3.4966 | -3.6685 | -3.8424
|  | REDFORD | CT |  |  |  | 0.096 | -1.9192 | -2.0176 | -2.143 | -2.289 | -2.472 | -2.6595 | -2.8857 | -3.0206 | -3.1487 | -3.2717 | -3.3822 | -3.7655 | -4.0008 | -4.1883 | -1.1017 | -1.1652 | -1.2278 | -1.2972 | -1.3954 | -1.4875 | -1.6185 | -1.6978 | -1.7846 | -1.8778 | -1.9651 | -2.166 | -2.2879 | -2.4742 | -1.7178 | -1.8062 | -1.9192 | -2.0523 | -2.2178 | -2.3874 | -2.5958 | -2.72 | -2.8392 | -2.955 | -3.0589 | -3.4058 | -3.6147 | -3.7842
|  | REDFORD | LW |  |  |  | 0.096 | -1.9187 | -2.019 | -2.1517 | -2.296 | -2.4576 | -2.6564 | -2.8577 | -3.025 | -3.2044 | -3.3617 | -3.462 | -3.8467 | -4.0333 | -4.2174 | -1.1039 | -1.1731 | -1.2411 | -1.3123 | -1.3937 | -1.5067 | -1.6124 | -1.7215 | -1.851 | -1.9629 | -2.0117 | -2.2156 | -2.2954 | -2.3949 | -1.7156 | -1.8079 | -1.9296 | -2.0618 | -2.2091 | -2.393 | -2.5792 | -2.7346 | -2.903 | -3.0507 | -3.1426 | -3.4966 | -3.6685 | -3.8424
|  | REDFORD | ST |  |  |  | 0.096 | -1.8868 | -1.9505 | -2.0241 | -2.11 | -2.1914 | -2.2822 | -2.3564 | -2.4368 | -2.5338 | -2.6341 | -2.7122 | -3.2295 | -3.5383 | -3.7968 | -1.0812 | -1.1154 | -1.1521 | -1.2029 | -1.2458 | -1.3014 | -1.3384 | -1.3918 | -1.4653 | -1.5425 | -1.5885 | -1.9602 | -2.1521 | -2.3568 | -1.6879 | -1.7432 | -1.8106 | -1.8894 | -1.9623 | -2.0452 | -2.1125 | -2.1874 | -2.2787 | -2.3732 | -2.4447 | -2.9283 | -3.2171 | -3.4525
|  | REDFORD | FS |  |  |  | 0.096 | -1.8444 | -1.8863 | -1.9278 | -1.9658 | -2.0084 | -2.0606 | -2.1146 | -2.1741 | -2.26 | -2.3394 | -2.429 | -2.8894 | -3.3384 | -3.6178 | -1.0658 | -1.0895 | -1.1201 | -1.1429 | -1.1708 | -1.2099 | -1.2532 | -1.2849 | -1.3457 | -1.3995 | -1.4624 | -1.7836 | -2.1053 | -2.4466 | -1.653 | -1.6889 | -1.7278 | -1.762 | -1.7999 | -1.8476 | -1.8973 | -1.9521 | -2.0309 | -2.1056 | -2.1866 | -2.612 | -3.0225 | -3.2733
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 2.362 | 5.5105 | 4.9294 | 4.3882 | 3.7054 | 2.9723 | 2.1094 | 1.1621 | 0.31495 | -0.49028 | -1.4089 | -1.7888 | -3.7575 | -4.3581 | -4.8542 | 7.6296 | 7.1259 | 6.7714 | 6.3733 | 5.9551 | 5.4532 | 4.9018 | 4.3768 | 3.8454 | 3.2196 | 3.0367 | 1.7625 | 1.3442 | 0.84415 | 6.9138 | 6.3453 | 5.89 | 5.3717 | 4.816 | 4.1716 | 3.4023 | 2.7633 | 2.1463 | 1.3198 | 1.0789 | -0.64633 | -1.1357 | -1.5781
|  | REDGORTON | CT |  |  |  | 2.362 | 5.5931 | 5.0844 | 4.5555 | 3.8485 | 3.056 | 2.1372 | 1.1621 | 0.31495 | -0.42941 | -1.2823 | -1.5955 | -3.6551 | -4.3581 | -4.8542 | 7.7139 | 7.2806 | 6.9215 | 6.4971 | 6.0289 | 5.498 | 4.9161 | 4.3768 | 3.9082 | 3.3083 | 3.144 | 1.7733 | 1.3442 | 0.84415 | 7.0014 | 6.5093 | 6.0462 | 5.4763 | 4.8709 | 4.1732 | 3.4023 | 2.7633 | 2.2053 | 1.5289 | 1.2283 | -0.52861 | -1.1357 | -1.5781
|  | REDGORTON | LW |  |  |  | 2.362 | 5.5105 | 4.9294 | 4.3882 | 3.7054 | 2.9723 | 2.1094 | 1.2003 | 0.36207 | -0.49028 | -1.4089 | -1.7888 | -3.7575 | -4.302 | -4.7681 | 7.6296 | 7.1259 | 6.7714 | 6.3733 | 5.9551 | 5.4532 | 4.9018 | 4.3905 | 3.8454 | 3.2196 | 3.0367 | 1.7625 | 1.5163 | 1.2537 | 6.9138 | 6.3453 | 5.89 | 5.3717 | 4.816 | 4.1716 | 3.4489 | 2.8223 | 2.1463 | 1.3198 | 1.0789 | -0.64633 | -1.1239 | -1.5506
|  | REDGORTON | ST |  |  |  | 2.362 | 5.6509 | 5.2111 | 4.8937 | 4.5071 | 4.0655 | 3.5577 | 3.0689 | 2.5645 | 2.0421 | 1.4028 | 0.91128 | -0.86344 | -1.5277 | -1.9992 | 7.749 | 7.3777 | 7.1206 | 6.8328 | 6.5246 | 6.1679 | 5.8078 | 5.4458 | 5.0673 | 4.5831 | 4.2131 | 2.8635 | 2.3726 | 1.9103 | 7.0552 | 6.631 | 6.3286 | 5.9911 | 5.6364 | 5.2345 | 4.8171 | 4.4172 | 4.0039 | 3.4485 | 3.0362 | 1.4016 | 0.84007 | 0.46175
|  | REDGORTON | FS |  |  |  | 2.362 | 5.8211 | 5.5005 | 5.3137 | 5.084 | 4.8067 | 4.4385 | 4.1116 | 3.738 | 3.3101 | 2.8095 | 2.3658 | 0.059356 | -1.1274 | -1.8882 | 7.8594 | 7.5874 | 7.4188 | 7.1994 | 6.9655 | 6.6752 | 6.4123 | 6.1515 | 5.8439 | 5.4698 | 5.1376 | 3.3378 | 2.3734 | 1.4282 | 7.2123 | 6.9002 | 6.7141 | 6.4859 | 6.234 | 5.9283 | 5.6579 | 5.3721 | 5.0476 | 4.6479 | 4.2933 | 2.3499 | 1.2575 | 0.57589
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 7.485 | 14.0118 | 11.8057 | 9.3491 | 6.8629 | 4.7546 | 1.9327 | -2.8764 | -4.6556 | -6.3317 | -7.576 | -8.8374 | -15.6709 | -22.6624 | -29.7152 | 14.0399 | 11.5252 | 8.7459 | 6.092 | 4.1751 | 1.5205 | -2.904 | -4.402 | -5.8998 | -6.9862 | -8.055 | -15.0294 | -22.9916 | -31.0068 | 13.4836 | 10.9181 | 8.1346 | 5.4698 | 3.306 | 0.28812 | -4.7824 | -6.4908 | -8.0679 | -9.4354 | -10.7978 | -18.3399 | -26.5542 | -34.744
|  | REDMOSS | CT |  |  |  | 7.485 | 14.0397 | 13.5977 | 13.0193 | 10.3943 | 9.3124 | 7.7371 | 4.2887 | 2.6347 | 0.88651 | -0.51011 | -1.8223 | -7.2818 | -11.096 | -14.3182 | 14.0488 | 13.7455 | 13.3985 | 10.7545 | 9.9358 | 8.8113 | 6.0491 | 4.6902 | 3.1817 | 1.9735 | 0.82435 | -3.7892 | -7.5029 | -11.2461 | 13.5041 | 13.1514 | 12.7699 | 10.0512 | 9.1041 | 7.5681 | 4.1714 | 2.5908 | 0.87652 | -0.49852 | -1.7918 | -7.2662 | -11.2451 | -14.763
|  | REDMOSS | LW |  |  |  | 7.485 | 14.0118 | 11.8057 | 9.3491 | 6.8629 | 4.7546 | 1.9327 | -2.8764 | -4.6556 | -6.3317 | -7.576 | -8.8374 | -15.6709 | -22.6624 | -29.7152 | 14.0399 | 11.5252 | 8.7459 | 6.092 | 4.1751 | 1.5205 | -2.904 | -4.402 | -5.8998 | -6.9862 | -8.055 | -15.0294 | -22.9916 | -31.0068 | 13.4836 | 10.9181 | 8.1346 | 5.4698 | 3.306 | 0.28812 | -4.7824 | -6.4908 | -8.0679 | -9.4354 | -10.7978 | -18.3399 | -26.5542 | -34.744
|  | REDMOSS | ST |  |  |  | 7.485 | 14.1249 | 13.8625 | 12.408 | 11.3269 | 10.4884 | 9.9244 | 8.7389 | 7.3797 | 5.8461 | 4.7068 | 3.6167 | -6.2164 | -14.4223 | -21.2466 | 14.0928 | 13.8705 | 12.2164 | 11.0525 | 10.2487 | 9.8303 | 8.8535 | 7.5429 | 6.1493 | 5.1446 | 4.176 | -6.0945 | -15.3291 | -23.047 | 13.5579 | 13.3224 | 11.6383 | 10.4372 | 9.5906 | 9.1174 | 8.0635 | 6.7848 | 5.3824 | 4.3727 | 3.3175 | -7.4753 | -17.2721 | -25.4358
|  | REDMOSS | FS |  |  |  | 7.485 | 14.1727 | 14.0265 | 13.4863 | 12.9245 | 12.2836 | 11.6285 | 10.3402 | 9.1913 | 7.8494 | 6.6715 | 6.0211 | 1.3373 | -2.6963 | -6.0488 | 14.1278 | 14.0239 | 13.4629 | 12.8896 | 12.2274 | 11.5548 | 10.2364 | 9.019 | 7.6669 | 6.4998 | 6.0151 | 2.1439 | -1.2249 | -4.2264 | 13.5937 | 13.4775 | 12.8939 | 12.2958 | 11.6059 | 10.908 | 9.5431 | 8.3733 | 7.0489 | 5.8947 | 5.3988 | 1.1609 | -2.9308 | -6.3545
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 0.226 | -0.77356 | -0.8295 | -0.90238 | -0.99926 | -1.0963 | -1.2039 | -1.3291 | -1.4015 | -1.4727 | -1.5462 | -1.6117 | -1.793 | -1.932 | -2.0047 | -0.50839 | -0.54823 | -0.5983 | -0.64537 | -0.69805 | -0.76852 | -0.86255 | -0.91085 | -0.98699 | -1.0577 | -1.1221 | -1.2737 | -1.3308 | -1.4281 | -0.79819 | -0.85899 | -0.93543 | -1.0159 | -1.1064 | -1.2131 | -1.3565 | -1.4196 | -1.5167 | -1.6072 | -1.6884 | -1.8875 | -1.9748 | -2.0993
|  | RHICONICH | CT |  |  |  | 0.226 | -0.77356 | -0.8295 | -0.90238 | -0.99926 | -1.0963 | -1.2039 | -1.3291 | -1.4015 | -1.4529 | -1.5039 | -1.5456 | -1.6757 | -1.7523 | -1.8254 | -0.50839 | -0.54695 | -0.58267 | -0.64112 | -0.69393 | -0.75635 | -0.82601 | -0.89488 | -0.94209 | -0.99931 | -1.0525 | -1.1756 | -1.2331 | -1.3265 | -0.79819 | -0.85899 | -0.92204 | -1.0159 | -1.1064 | -1.2129 | -1.3263 | -1.4166 | -1.4753 | -1.546 | -1.6093 | -1.7511 | -1.8185 | -1.9048
|  | RHICONICH | LW |  |  |  | 0.226 | -0.76534 | -0.82212 | -0.90061 | -0.98534 | -1.0762 | -1.1893 | -1.3227 | -1.3898 | -1.4727 | -1.5462 | -1.6117 | -1.793 | -1.8909 | -2.0041 | -0.50466 | -0.54823 | -0.5983 | -0.64537 | -0.69805 | -0.76852 | -0.86255 | -0.91085 | -0.98699 | -1.0577 | -1.1221 | -1.2737 | -1.3308 | -1.4281 | -0.79345 | -0.8537 | -0.93543 | -1.0123 | -1.1016 | -1.2131 | -1.3565 | -1.4196 | -1.5167 | -1.6072 | -1.6884 | -1.8875 | -1.9748 | -2.0993
|  | RHICONICH | ST |  |  |  | 0.226 | -0.75768 | -0.79174 | -0.84358 | -0.89588 | -0.95217 | -1.0077 | -1.0725 | -1.1322 | -1.2087 | -1.2818 | -1.3665 | -1.7707 | -1.932 | -2.0047 | -0.49862 | -0.51433 | -0.54396 | -0.57153 | -0.60424 | -0.62906 | -0.66755 | -0.69985 | -0.75065 | -0.78629 | -0.84003 | -1.1162 | -1.2255 | -1.2992 | -0.78504 | -0.81144 | -0.8596 | -0.90512 | -0.95817 | -0.99794 | -1.0574 | -1.1075 | -1.1832 | -1.2546 | -1.3401 | -1.7768 | -1.9453 | -2.0186
|  | RHICONICH | FS |  |  |  | 0.226 | -0.73472 | -0.75685 | -0.77475 | -0.79521 | -0.81929 | -0.84624 | -0.87241 | -0.92018 | -0.97239 | -1.029 | -1.087 | -1.4159 | -1.7413 | -1.9224 | -0.48975 | -0.50353 | -0.51491 | -0.5291 | -0.54847 | -0.5709 | -0.58677 | -0.619 | -0.65052 | -0.69014 | -0.72996 | -0.94317 | -1.1442 | -1.2911 | -0.76949 | -0.78684 | -0.80424 | -0.82432 | -0.8486 | -0.87621 | -0.90326 | -0.9466 | -0.99685 | -1.051 | -1.1068 | -1.4337 | -1.7452 | -1.933
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 0.849 | 9.9284 | 8.0918 | 5.654 | 3.1728 | 1.0364 | -1.9927 | -5.9214 | -7.9919 | -10.3176 | -12.4977 | -14.5265 | -21.8881 | -25.9671 | -32.1869 | 12.5354 | 10.6938 | 8.4507 | 6.1284 | 4.3163 | 1.564 | -2.1512 | -3.5349 | -5.1439 | -6.6816 | -8.1263 | -14.1375 | -19.3209 | -26.421 | 11.5186 | 9.6374 | 7.5789 | 5.2426 | 2.9685 | -0.30909 | -4.5747 | -6.5471 | -8.7853 | -10.8974 | -12.8668 | -20.4986 | -25.6134 | -32.9621
|  | ROSEBANK STREET | CT |  |  |  | 0.849 | 9.9964 | 9.5048 | 8.7056 | 6.4174 | 5.1218 | 3.5316 | 0.93039 | -1.1665 | -3.0396 | -4.8879 | -6.5984 | -13.2483 | -16.0942 | -19.1307 | 12.5354 | 12.3279 | 11.9315 | 9.6362 | 8.6225 | 7.3376 | 4.9702 | 3.5726 | 2.2449 | 0.88612 | -0.43047 | -5.5485 | -8.8846 | -13.6822 | 11.5186 | 11.2767 | 11.0148 | 9.0667 | 7.845 | 6.2621 | 3.5002 | 1.4971 | -0.33105 | -2.1417 | -3.8345 | -10.3552 | -13.3432 | -16.6763
|  | ROSEBANK STREET | LW |  |  |  | 0.849 | 9.9284 | 8.0918 | 5.654 | 3.1728 | 1.0364 | -1.9927 | -5.9214 | -7.9919 | -10.3176 | -12.4977 | -14.5265 | -21.8881 | -25.9671 | -32.1869 | 12.5425 | 10.6938 | 8.4507 | 6.1284 | 4.3163 | 1.564 | -2.1512 | -3.5349 | -5.1439 | -6.6816 | -8.1263 | -14.1375 | -19.3209 | -26.421 | 11.5236 | 9.6374 | 7.5789 | 5.2426 | 2.9685 | -0.30909 | -4.5747 | -6.5471 | -8.7853 | -10.8974 | -12.8668 | -20.4986 | -25.6134 | -32.9621
|  | ROSEBANK STREET | ST |  |  |  | 0.849 | 10.1247 | 9.9043 | 8.7805 | 7.9229 | 7.2567 | 6.7418 | 6.1407 | 5.3737 | 4.4319 | 3.4797 | 2.6242 | -5.199 | -11.5726 | -17.6318 | 12.5816 | 12.4669 | 11.2359 | 10.4254 | 9.8273 | 9.3447 | 8.7614 | 8.0125 | 7.1187 | 6.224 | 5.4665 | -2.8805 | -10.5835 | -18.3665 | 11.5783 | 11.4559 | 10.2271 | 9.4026 | 8.8472 | 8.5392 | 8.1841 | 7.6888 | 6.7225 | 5.709 | 4.839 | -3.8903 | -11.1281 | -17.7749
|  | ROSEBANK STREET | FS |  |  |  | 0.849 | 10.2713 | 10.1908 | 9.6981 | 9.2137 | 8.6201 | 8.0064 | 7.1517 | 6.319 | 5.3568 | 4.3962 | 3.7142 | -1.753 | -6.825 | -11.0021 | 12.5897 | 12.5522 | 12.1342 | 11.7641 | 11.3073 | 10.6667 | 9.7215 | 8.8784 | 7.8874 | 6.9112 | 6.3086 | 1.9939 | -3.2291 | -10.013 | 11.5895 | 11.5482 | 11.1333 | 10.757 | 10.2907 | 9.8166 | 9.0851 | 8.5178 | 7.7988 | 6.7785 | 6.1213 | 1.065 | -3.6936 | -7.7559
| KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 1.573 | -0.21489 | -0.46277 | -0.649 | -0.88711 | -1.0929 | -1.3297 | -1.6297 | -1.7846 | -1.9223 | -2.0482 | -2.1959 | -2.5993 | -2.8378 | -3.0543 | 1.1913 | 0.96517 | 0.90284 | 0.81546 | 0.72723 | 0.60633 | 0.45378 | 0.34376 | 0.20033 | 0.066117 | -0.059054 | -0.37087 | -0.49453 | -0.5897 | 0.41946 | 0.18024 | 0.077392 | -0.067006 | -0.18902 | -0.32837 | -0.52497 | -0.66456 | -0.79858 | -0.96214 | -1.1151 | -1.5038 | -1.6527 | -1.759
|  | ROTHES | CT |  |  |  | 1.573 | -0.21489 | -0.43256 | -0.63568 | -0.88711 | -1.0929 | -1.3297 | -1.6297 | -1.7846 | -1.9223 | -2.0396 | -2.1368 | -2.4717 | -2.7105 | -2.9197 | 1.1913 | 1.0179 | 0.94522 | 0.82097 | 0.72723 | 0.61702 | 0.45798 | 0.34376 | 0.24696 | 0.16176 | 0.088661 | -0.095515 | -0.16236 | -0.22454 | 0.41946 | 0.227 | 0.10743 | -0.067006 | -0.18902 | -0.32837 | -0.52497 | -0.66456 | -0.77981 | -0.88231 | -0.96932 | -1.1931 | -1.3133 | -1.4998
|  | ROTHES | LW |  |  |  | 1.573 | -0.20182 | -0.46277 | -0.649 | -0.87213 | -1.0488 | -1.2843 | -1.5505 | -1.6988 | -1.8836 | -2.0482 | -2.1959 | -2.5993 | -2.8378 | -3.0543 | 1.1914 | 0.96517 | 0.90284 | 0.81546 | 0.73409 | 0.60633 | 0.45378 | 0.34447 | 0.20033 | 0.066117 | -0.059054 | -0.37087 | -0.49453 | -0.5897 | 0.42218 | 0.18024 | 0.077392 | -0.046827 | -0.1499 | -0.30415 | -0.48716 | -0.62342 | -0.79858 | -0.96214 | -1.1151 | -1.5038 | -1.6527 | -1.759
|  | ROTHES | ST |  |  |  | 1.573 | -0.18477 | -0.36306 | -0.47654 | -0.57475 | -0.65248 | -0.74339 | -0.83337 | -0.93797 | -1.0513 | -1.1616 | -1.2527 | -1.8878 | -2.2177 | -2.4633 | 1.2062 | 1.0638 | 1.0138 | 0.97329 | 0.93847 | 0.89394 | 0.82936 | 0.74863 | 0.65221 | 0.55778 | 0.46552 | -0.11856 | -0.35039 | -0.45701 | 0.44189 | 0.28983 | 0.21901 | 0.15703 | 0.1016 | 0.034254 | -0.044187 | -0.13864 | -0.25205 | -0.36574 | -0.48071 | -1.18 | -1.4529 | -1.575
|  | ROTHES | FS |  |  |  | 1.573 | -0.15071 | -0.28505 | -0.33603 | -0.38584 | -0.42733 | -0.47279 | -0.52813 | -0.61906 | -0.69877 | -0.78596 | -0.87406 | -1.4061 | -1.919 | -2.2469 | 1.2105 | 1.1009 | 1.0745 | 1.047 | 1.0224 | 0.98845 | 0.94925 | 0.90144 | 0.85265 | 0.80137 | 0.74129 | 0.31675 | -0.069079 | -0.32027 | 0.45444 | 0.33856 | 0.30326 | 0.26625 | 0.23176 | 0.1879 | 0.13696 | 0.069908 | 0.00044489 | -0.072481 | -0.14714 | -0.65803 | -1.138 | -1.4526
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0.535 | 17.856 | 8.9381 | 8.5748 | 8.125 | 7.6358 | 7.019 | 6.2875 | 5.5526 | 4.7823 | 4.0531 | 3.3497 | 1.3361 | 0.85133 | 0.1899 | 18.3433 | 9.8965 | 9.7189 | 9.4819 | 9.2016 | 8.8874 | 8.4414 | 7.9745 | 7.4499 | 6.9404 | 6.4677 | 5.2796 | 4.9895 | 4.2894 | 17.5576 | 9.4725 | 9.1432 | 8.7318 | 8.2848 | 7.7139 | 7.0326 | 6.3443 | 5.59 | 4.8556 | 4.1792 | 2.2916 | 1.9596 | 1.3182
|  | ROTHESAY | CT |  |  |  | 0.535 | 17.8734 | 8.9543 | 8.6533 | 8.2677 | 7.8222 | 7.3753 | 6.7721 | 5.9957 | 5.394 | 4.7746 | 4.2138 | 1.8029 | 0.85133 | 0.1899 | 18.3433 | 9.8965 | 9.7189 | 9.4819 | 9.2016 | 8.9432 | 8.5508 | 8.061 | 7.7058 | 7.2971 | 6.9172 | 5.5315 | 4.9895 | 4.2894 | 17.5719 | 9.4841 | 9.2055 | 8.8469 | 8.4322 | 8.0191 | 7.4544 | 6.7219 | 6.1476 | 5.5404 | 4.9919 | 2.7679 | 1.9596 | 1.3182
|  | ROTHESAY | LW |  |  |  | 0.535 | 17.856 | 8.9381 | 8.5748 | 8.125 | 7.6358 | 7.019 | 6.2875 | 5.5526 | 4.7823 | 4.0531 | 3.3497 | 1.3361 | 1.0775 | 0.32489 | 18.3468 | 9.9134 | 9.7433 | 9.5042 | 9.2447 | 8.8874 | 8.4414 | 7.9745 | 7.4499 | 6.9404 | 6.4677 | 5.2796 | 5.1639 | 4.6337 | 17.5576 | 9.4725 | 9.1432 | 8.7318 | 8.2848 | 7.7139 | 7.0326 | 6.3443 | 5.59 | 4.8556 | 4.1792 | 2.2916 | 2.0585 | 1.3321
|  | ROTHESAY | ST |  |  |  | 0.535 | 17.9091 | 9.0857 | 8.991 | 8.889 | 8.763 | 8.6376 | 8.4752 | 8.2829 | 8.0631 | 7.8068 | 7.5238 | 5.8866 | 5.0516 | 4.2488 | 18.3893 | 10.0468 | 9.9714 | 9.8885 | 9.7803 | 9.6745 | 9.5287 | 9.3543 | 9.1561 | 8.9174 | 8.6517 | 7.3025 | 6.727 | 6.1916 | 17.609 | 9.6171 | 9.5277 | 9.4308 | 9.3099 | 9.1888 | 9.031 | 8.8441 | 8.6094 | 8.3149 | 7.9883 | 6.3377 | 5.6265 | 4.9832
|  | ROTHESAY | FS |  |  |  | 0.535 | 17.9802 | 9.1975 | 9.1198 | 9.0307 | 8.9255 | 8.8243 | 8.6939 | 8.5093 | 8.2856 | 8.0577 | 7.8426 | 5.8568 | 3.7685 | 2.2013 | 18.409 | 10.0797 | 10.0259 | 9.9582 | 9.8732 | 9.7926 | 9.6769 | 9.5395 | 9.3608 | 9.1774 | 9.0104 | 7.6274 | 6.124 | 4.7319 | 17.6715 | 9.7159 | 9.6437 | 9.5602 | 9.4605 | 9.3642 | 9.2389 | 9.0655 | 8.8534 | 8.637 | 8.4334 | 6.5205 | 4.5738 | 3.1673
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0 | -0.49997 | -0.51318 | -0.53753 | -0.56753 | -0.60369 | -0.63786 | -0.6886 | -0.71227 | -0.73789 | -0.76273 | -0.79038 | -0.86905 | -0.90315 | -0.93511 | -0.085698 | -0.090685 | -0.10365 | -0.11973 | -0.14111 | -0.15587 | -0.18402 | -0.19633 | -0.21624 | -0.23158 | -0.24921 | -0.29202 | -0.30687 | -0.33597 | -0.37821 | -0.38971 | -0.41227 | -0.44008 | -0.47485 | -0.50277 | -0.54807 | -0.56745 | -0.59713 | -0.61811 | -0.64593 | -0.71202 | -0.73698 | -0.76289
|  | ROUSAY | CT |  |  |  | 0 | -0.49997 | -0.51318 | -0.53753 | -0.56753 | -0.60369 | -0.63786 | -0.6886 | -0.71227 | -0.73756 | -0.76273 | -0.77536 | -0.84872 | -0.87901 | -0.90743 | -0.085698 | -0.090685 | -0.10365 | -0.11973 | -0.14111 | -0.15587 | -0.18402 | -0.19633 | -0.21281 | -0.23158 | -0.23848 | -0.28369 | -0.30257 | -0.32798 | -0.37821 | -0.38971 | -0.41227 | -0.44008 | -0.47485 | -0.50277 | -0.54807 | -0.56745 | -0.59214 | -0.61793 | -0.62913 | -0.69527 | -0.71813 | -0.74056
|  | ROUSAY | LW |  |  |  | 0 | -0.4967 | -0.50687 | -0.52971 | -0.55868 | -0.59 | -0.62774 | -0.67715 | -0.70077 | -0.73789 | -0.76166 | -0.79038 | -0.86905 | -0.90315 | -0.93511 | -0.084383 | -0.087586 | -0.098979 | -0.11488 | -0.13184 | -0.15094 | -0.17877 | -0.1896 | -0.21624 | -0.22952 | -0.24921 | -0.29202 | -0.30687 | -0.32287 | -0.37523 | -0.38389 | -0.40516 | -0.43298 | -0.46277 | -0.49622 | -0.54108 | -0.55995 | -0.59713 | -0.61811 | -0.64593 | -0.71202 | -0.73698 | -0.76289
|  | ROUSAY | ST |  |  |  | 0 | -0.49078 | -0.50609 | -0.52015 | -0.5356 | -0.55891 | -0.57967 | -0.6055 | -0.62598 | -0.65426 | -0.68359 | -0.70361 | -0.82631 | -0.87683 | -0.90084 | -0.079905 | -0.088104 | -0.092997 | -0.099088 | -0.11258 | -0.1225 | -0.13531 | -0.14521 | -0.16322 | -0.18216 | -0.18903 | -0.26728 | -0.29953 | -0.32089 | -0.36661 | -0.38384 | -0.39629 | -0.41018 | -0.43283 | -0.45134 | -0.47355 | -0.4906 | -0.51743 | -0.54539 | -0.55948 | -0.67144 | -0.71179 | -0.72972
|  | ROUSAY | FS |  |  |  | 0 | -0.48164 | -0.49154 | -0.49419 | -0.502 | -0.50835 | -0.51975 | -0.5273 | -0.54317 | -0.56401 | -0.57785 | -0.59917 | -0.70491 | -0.81675 | -0.86362 | -0.075706 | -0.08118 | -0.08128 | -0.086232 | -0.089819 | -0.098164 | -0.10255 | -0.11194 | -0.12593 | -0.13331 | -0.14753 | -0.21402 | -0.2848 | -0.33597 | -0.35818 | -0.37013 | -0.37195 | -0.37948 | -0.38543 | -0.39699 | -0.40383 | -0.41918 | -0.4398 | -0.45255 | -0.4735 | -0.57357 | -0.66719 | -0.7021
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 1.676 | 5.6561 | 5.3631 | 4.848 | 4.1953 | 3.5102 | 2.6257 | 1.556 | 0.41542 | -0.44159 | -1.5037 | -2.4742 | -5.058 | -5.4123 | -6.2945 | 18.5747 | 18.3359 | 18.0669 | 17.6949 | 17.3079 | 16.8388 | 16.1804 | 15.4892 | 15.0579 | 14.4005 | 13.7944 | 12.0502 | 10.6636 | 6.8435 | 15.141 | 14.8561 | 14.3827 | 13.7776 | 13.1459 | 12.3189 | 11.3131 | 10.2461 | 9.4562 | 8.4551 | 7.5388 | 5.1301 | 4.8908 | 4.0927
|  | RUTHRIESTON | CT |  |  |  | 1.676 | 5.6936 | 5.4184 | 4.9745 | 4.3891 | 3.7485 | 3.0255 | 2.0967 | 0.94789 | 0.37457 | -0.4927 | -1.2639 | -4.2509 | -5.4123 | -6.2945 | 18.5747 | 18.3359 | 18.0669 | 17.6949 | 17.3079 | 16.8683 | 16.2663 | 15.5424 | 15.2881 | 14.7251 | 14.2002 | 12.0502 | 10.6636 | 8.5532 | 15.1715 | 14.9057 | 14.4962 | 13.9479 | 13.3544 | 12.6844 | 11.8142 | 10.7421 | 10.2345 | 9.4247 | 8.7016 | 5.9602 | 4.9285 | 4.1059
|  | RUTHRIESTON | LW |  |  |  | 1.676 | 5.6561 | 5.3631 | 4.848 | 4.1953 | 3.5102 | 2.6257 | 1.556 | 0.41542 | -0.44159 | -1.5037 | -2.4742 | -5.058 | -5.3082 | -6.1158 | 18.5786 | 18.3466 | 18.0821 | 17.7133 | 17.3458 | 16.8388 | 16.1804 | 15.4892 | 15.0579 | 14.4005 | 13.7944 | 12.2952 | 12.1288 | 11.5075 | 15.141 | 14.8561 | 14.3827 | 13.7776 | 13.1459 | 12.3189 | 11.3131 | 10.2461 | 9.4562 | 8.4551 | 7.5388 | 5.1301 | 4.8908 | 4.0927
|  | RUTHRIESTON | ST |  |  |  | 1.676 | 5.8079 | 5.6927 | 5.5828 | 5.4426 | 5.2726 | 5.1103 | 4.8777 | 4.641 | 4.2908 | 3.9215 | 3.515 | 1.6496 | 0.39474 | -1.0096 | 18.6591 | 18.5537 | 18.4414 | 18.2964 | 18.1224 | 17.9564 | 17.7208 | 17.4871 | 17.1395 | 16.7694 | 16.3604 | 14.5023 | 12.9729 | 10.8488 | 15.2811 | 15.1724 | 15.0648 | 14.9276 | 14.7619 | 14.6047 | 14.3776 | 14.1462 | 13.8021 | 13.4145 | 12.983 | 11.2351 | 10.0766 | 8.8274
|  | RUTHRIESTON | FS |  |  |  | 1.676 | 5.8637 | 5.7797 | 5.6582 | 5.5113 | 5.3397 | 5.1799 | 4.9644 | 4.6811 | 4.3429 | 4.0441 | 3.6882 | 1.3635 | -1.1312 | -3.0726 | 18.681 | 18.5906 | 18.4868 | 18.3523 | 18.1939 | 18.0394 | 17.8177 | 17.5474 | 17.2204 | 16.9293 | 16.5803 | 14.4491 | 11.1885 | 6.8435 | 15.329 | 15.2494 | 15.1363 | 14.9978 | 14.8359 | 14.6855 | 14.4801 | 14.2129 | 13.8911 | 13.608 | 13.2691 | 11.1071 | 8.7941 | 7.0318
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 0.163 | 5.9269 | 5.8674 | 5.7743 | 5.6585 | 5.5366 | 5.417 | 5.2846 | 5.2225 | 5.1827 | 5.1424 | 5.1102 | 4.98 | 4.909 | 4.823 | 6.5668 | 6.5239 | 6.474 | 6.4064 | 6.3392 | 6.2697 | 6.1936 | 6.1254 | 6.0795 | 6.0083 | 5.9405 | 5.8181 | 5.786 | 5.7152 | 6.2212 | 6.1574 | 6.0787 | 5.973 | 5.8619 | 5.748 | 5.6251 | 5.5322 | 5.47 | 5.3803 | 5.29 | 5.124 | 5.0661 | 4.9603
|  | SALEN | CT |  |  |  | 0.163 | 5.9269 | 5.8674 | 5.7743 | 5.6585 | 5.5366 | 5.417 | 5.2846 | 5.2225 | 5.1827 | 5.1424 | 5.1102 | 5.0245 | 4.9671 | 4.8916 | 6.5668 | 6.5239 | 6.474 | 6.4064 | 6.3392 | 6.2697 | 6.1936 | 6.1254 | 6.0795 | 6.025 | 5.9751 | 5.8697 | 5.8278 | 5.7494 | 6.2212 | 6.1574 | 6.0787 | 5.973 | 5.8619 | 5.748 | 5.6251 | 5.5322 | 5.47 | 5.3986 | 5.3347 | 5.2056 | 5.1551 | 5.0715
|  | SALEN | LW |  |  |  | 0.163 | 5.9338 | 5.8798 | 5.7988 | 5.6971 | 5.5935 | 5.4803 | 5.3658 | 5.3018 | 5.2332 | 5.1701 | 5.1147 | 4.98 | 4.909 | 4.823 | 6.5694 | 6.5301 | 6.4885 | 6.4286 | 6.3752 | 6.2996 | 6.2285 | 6.1608 | 6.0826 | 6.0083 | 5.9405 | 5.8181 | 5.786 | 5.7152 | 6.2254 | 6.1664 | 6.099 | 6.0041 | 5.9145 | 5.7946 | 5.6812 | 5.5872 | 5.4803 | 5.3803 | 5.29 | 5.124 | 5.0661 | 4.9603
|  | SALEN | ST |  |  |  | 0.163 | 5.9411 | 5.9029 | 5.8586 | 5.8136 | 5.7628 | 5.727 | 5.6812 | 5.6379 | 5.5806 | 5.5324 | 5.4699 | 5.2406 | 5.1938 | 5.1925 | 6.5768 | 6.5567 | 6.5291 | 6.5012 | 6.466 | 6.4428 | 6.4065 | 6.3743 | 6.324 | 6.2865 | 6.2308 | 5.9802 | 5.9322 | 5.8966 | 6.2357 | 6.2039 | 6.1623 | 6.1205 | 6.0685 | 6.0343 | 5.9805 | 5.9328 | 5.8614 | 5.809 | 5.7314 | 5.4049 | 5.3601 | 5.3475
|  | SALEN | FS |  |  |  | 0.163 | 5.9646 | 5.9404 | 5.9246 | 5.9083 | 5.8879 | 5.8785 | 5.8613 | 5.8239 | 5.7854 | 5.7424 | 5.6961 | 5.4734 | 5.2324 | 5.1167 | 6.5864 | 6.5725 | 6.557 | 6.5416 | 6.5208 | 6.5096 | 6.4882 | 6.458 | 6.4283 | 6.3915 | 6.3509 | 6.1419 | 5.9397 | 5.796 | 6.2527 | 6.2315 | 6.2109 | 6.1905 | 6.1626 | 6.1493 | 6.1218 | 6.0792 | 6.0384 | 5.9873 | 5.9314 | 5.6559 | 5.4031 | 5.2809
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | YES | 0.226 | 0.15793 | 0.11077 | 0.021574 | -0.080224 | -0.19159 | -0.30442 | -0.44405 | -0.48334 | -0.51458 | -0.54869 | -0.59208 | -0.7188 | -0.81964 | -0.88928 | 0.59949 | 0.56298 | 0.51098 | 0.46052 | 0.39769 | 0.33027 | 0.23297 | 0.18258 | 0.10064 | 0.034546 | -0.030356 | -0.1837 | -0.23718 | -0.34226 | 0.28318 | 0.24648 | 0.19844 | 0.1445 | 0.083797 | 0.023787 | -0.064029 | -0.11508 | -0.18569 | -0.24508 | -0.3008 | -0.4922 | -0.63452 | -0.6995
|  | SALEN 2 | CT |  |  |  | 0.226 | 0.15793 | 0.11077 | 0.021574 | -0.080224 | -0.19159 | -0.30442 | -0.44405 | -0.48334 | -0.51458 | -0.53878 | -0.55872 | -0.6424 | -0.70504 | -0.77217 | 0.59949 | 0.56631 | 0.51696 | 0.463 | 0.39769 | 0.33923 | 0.24905 | 0.19992 | 0.15186 | 0.10432 | 0.056133 | -0.083714 | -0.13126 | -0.21679 | 0.28318 | 0.25033 | 0.20402 | 0.1445 | 0.083797 | 0.024876 | -0.057654 | -0.10766 | -0.1481 | -0.18774 | -0.22391 | -0.32097 | -0.35092 | -0.38828
|  | SALEN 2 | LW |  |  |  | 0.226 | 0.16581 | 0.11707 | 0.03288 | -0.055721 | -0.15054 | -0.26331 | -0.39496 | -0.44089 | -0.50228 | -0.54869 | -0.59208 | -0.7188 | -0.80444 | -0.88839 | 0.60221 | 0.56298 | 0.51098 | 0.46052 | 0.40503 | 0.33027 | 0.23297 | 0.18258 | 0.10064 | 0.034546 | -0.030356 | -0.1837 | -0.23718 | -0.34226 | 0.28519 | 0.24648 | 0.19844 | 0.14752 | 0.095556 | 0.023787 | -0.064029 | -0.11508 | -0.18569 | -0.24508 | -0.3008 | -0.4341 | -0.48697 | -0.54903
|  | SALEN 2 | ST |  |  |  | 0.226 | 0.17307 | 0.14012 | 0.095091 | 0.048916 | -0.00057699 | -0.047734 | -0.1032 | -0.15277 | -0.21604 | -0.28223 | -0.34293 | -0.67156 | -0.81964 | -0.88928 | 0.612 | 0.59378 | 0.56851 | 0.54153 | 0.51019 | 0.48518 | 0.44789 | 0.41536 | 0.36608 | 0.31403 | 0.27617 | 0.0061219 | -0.098074 | -0.16139 | 0.29325 | 0.27537 | 0.24612 | 0.2153 | 0.18115 | 0.14699 | 0.10417 | 0.060978 | 0.0015189 | -0.062068 | -0.12535 | -0.4922 | -0.63452 | -0.6995
|  | SALEN 2 | FS |  |  |  | 0.226 | 0.19499 | 0.17464 | 0.15906 | 0.14101 | 0.12367 | 0.10157 | 0.081398 | 0.039981 | -0.0083262 | -0.051856 | -0.10037 | -0.36332 | -0.6581 | -0.821 | 0.62013 | 0.60724 | 0.5943 | 0.5779 | 0.56333 | 0.54181 | 0.52553 | 0.495 | 0.45643 | 0.42596 | 0.38804 | 0.18557 | -0.026351 | -0.15222 | 0.30191 | 0.29056 | 0.27611 | 0.25899 | 0.241 | 0.21858 | 0.1957 | 0.16325 | 0.12159 | 0.082563 | 0.039532 | -0.22199 | -0.47525 | -0.62932
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0.053 | 0.14414 | 0.10156 | 0.049388 | -0.014314 | -0.084031 | -0.16103 | -0.26081 | -0.31013 | -0.37777 | -0.43781 | -0.47309 | -0.6343 | -0.71809 | -0.81341 | 0.3631 | 0.33727 | 0.30346 | 0.26894 | 0.23285 | 0.19317 | 0.13292 | 0.10356 | 0.057409 | 0.016276 | -0.0033962 | -0.10668 | -0.16281 | -0.24213 | 0.27404 | 0.24054 | 0.19179 | 0.13706 | 0.077448 | 0.0027849 | -0.092775 | -0.13735 | -0.19834 | -0.25259 | -0.28426 | -0.43689 | -0.52259 | -0.61833
|  | SANDAY | CT |  |  |  | 0.053 | 0.14414 | 0.10156 | 0.055427 | -0.012254 | -0.084031 | -0.1482 | -0.24306 | -0.29345 | -0.34154 | -0.38983 | -0.41375 | -0.56616 | -0.63028 | -0.69429 | 0.3631 | 0.33982 | 0.3197 | 0.28019 | 0.24096 | 0.21266 | 0.15805 | 0.12649 | 0.094924 | 0.06132 | 0.045623 | -0.053191 | -0.09705 | -0.15784 | 0.27404 | 0.24054 | 0.20317 | 0.1465 | 0.082769 | 0.022189 | -0.067281 | -0.11296 | -0.1568 | -0.20049 | -0.22177 | -0.36314 | -0.42508 | -0.48684
|  | SANDAY | LW |  |  |  | 0.053 | 0.15278 | 0.10861 | 0.049388 | -0.014314 | -0.083429 | -0.16103 | -0.26081 | -0.31013 | -0.37777 | -0.43781 | -0.47309 | -0.6343 | -0.71809 | -0.81341 | 0.36658 | 0.33727 | 0.30346 | 0.26894 | 0.23285 | 0.19317 | 0.13292 | 0.10356 | 0.057409 | 0.016276 | -0.0033962 | -0.10668 | -0.16005 | -0.22908 | 0.28159 | 0.24348 | 0.19179 | 0.13706 | 0.077448 | 0.0027849 | -0.092775 | -0.13735 | -0.19834 | -0.25259 | -0.28426 | -0.43689 | -0.52259 | -0.61833
|  | SANDAY | ST |  |  |  | 0.053 | 0.15132 | 0.12907 | 0.083547 | 0.038274 | -0.0081542 | -0.052136 | -0.10373 | -0.1395 | -0.19225 | -0.24736 | -0.29561 | -0.56608 | -0.70344 | -0.78478 | 0.36362 | 0.35819 | 0.33505 | 0.31281 | 0.29023 | 0.26961 | 0.24223 | 0.22392 | 0.19192 | 0.15794 | 0.12987 | -0.058237 | -0.16281 | -0.24213 | 0.28076 | 0.26005 | 0.21896 | 0.17924 | 0.13981 | 0.10251 | 0.060752 | 0.029022 | -0.019699 | -0.07061 | -0.11503 | -0.37016 | -0.50673 | -0.5905
|  | SANDAY | FS |  |  |  | 0.053 | 0.17212 | 0.16007 | 0.14491 | 0.12891 | 0.11108 | 0.090346 | 0.072418 | 0.036317 | -0.0060106 | -0.036987 | -0.078213 | -0.31263 | -0.54674 | -0.67619 | 0.37168 | 0.36985 | 0.36044 | 0.35031 | 0.33858 | 0.32347 | 0.31169 | 0.28971 | 0.26213 | 0.24864 | 0.22403 | 0.073807 | -0.082933 | -0.2138 | 0.29878 | 0.28695 | 0.27449 | 0.26164 | 0.24765 | 0.23057 | 0.21422 | 0.18068 | 0.14058 | 0.11793 | 0.080856 | -0.12748 | -0.3452 | -0.46867
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.383 | 3.7419 | 3.6265 | 3.4742 | 3.3083 | 3.0992 | 2.891 | 2.6595 | 2.4457 | 2.2387 | 2.0193 | 1.8772 | 1.4069 | 1.2653 | 1.0351 | 4.9626 | 4.8874 | 4.8004 | 4.7076 | 4.5873 | 4.467 | 4.3351 | 4.1893 | 4.0527 | 3.9002 | 3.7996 | 3.4954 | 3.3788 | 3.1693 | 4.4976 | 4.3888 | 4.2493 | 4.0981 | 3.9054 | 3.7122 | 3.4979 | 3.2926 | 3.09 | 2.8775 | 2.7409 | 2.2941 | 2.1678 | 1.9504
|  | SANDBANK | CT |  |  |  | 0.383 | 3.7419 | 3.6265 | 3.4742 | 3.3083 | 3.0992 | 2.891 | 2.6595 | 2.4457 | 2.2786 | 2.1077 | 1.9535 | 1.5095 | 1.3095 | 1.1133 | 4.9626 | 4.8874 | 4.8004 | 4.7076 | 4.5873 | 4.467 | 4.3351 | 4.1893 | 4.075 | 3.9528 | 3.8391 | 3.5276 | 3.3788 | 3.1693 | 4.4976 | 4.3888 | 4.2493 | 4.0981 | 3.9054 | 3.7122 | 3.4979 | 3.2926 | 3.1324 | 2.9668 | 2.8167 | 2.3992 | 2.2206 | 2.0386
|  | SANDBANK | LW |  |  |  | 0.383 | 3.7517 | 3.6444 | 3.5028 | 3.3391 | 3.152 | 2.9278 | 2.6646 | 2.4875 | 2.2387 | 2.0193 | 1.8772 | 1.4069 | 1.2653 | 1.0351 | 4.9686 | 4.9 | 4.8234 | 4.7342 | 4.6312 | 4.4976 | 4.3371 | 4.2247 | 4.0527 | 3.9002 | 3.7996 | 3.4954 | 3.4277 | 3.2846 | 4.5065 | 4.4056 | 4.277 | 4.1281 | 3.9571 | 3.747 | 3.4993 | 3.3308 | 3.09 | 2.8775 | 2.7409 | 2.2941 | 2.1678 | 1.9504
|  | SANDBANK | ST |  |  |  | 0.383 | 3.7781 | 3.714 | 3.6502 | 3.5683 | 3.4929 | 3.4108 | 3.3425 | 3.2499 | 3.1273 | 2.9991 | 2.9018 | 2.3297 | 2.1175 | 2.0111 | 4.9871 | 4.9493 | 4.9115 | 4.8594 | 4.8117 | 4.7557 | 4.7096 | 4.645 | 4.5567 | 4.4634 | 4.3951 | 3.947 | 3.7648 | 3.619 | 4.5324 | 4.474 | 4.4161 | 4.3403 | 4.2709 | 4.1926 | 4.1281 | 4.0394 | 3.9209 | 3.7967 | 3.7035 | 3.1474 | 2.9494 | 2.8553
|  | SANDBANK | FS |  |  |  | 0.383 | 3.8048 | 3.7599 | 3.7141 | 3.6771 | 3.6355 | 3.5889 | 3.5336 | 3.4726 | 3.3746 | 3.2836 | 3.1782 | 2.6066 | 2.0729 | 1.7675 | 4.999 | 4.9706 | 4.9381 | 4.912 | 4.8818 | 4.8455 | 4.8015 | 4.76 | 4.6899 | 4.625 | 4.5486 | 4.1215 | 3.6757 | 3.2922 | 4.5563 | 4.5151 | 4.4723 | 4.4381 | 4.3994 | 4.354 | 4.3002 | 4.2436 | 4.1505 | 4.064 | 3.9635 | 3.4166 | 2.9144 | 2.6318
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0.158 | -0.52372 | -0.57005 | -0.68034 | 4.1346 | 3.9835 | 3.8053 | 3.5952 | 3.4023 | 3.2572 | 3.0911 | 2.9262 | 2.4142 | 2.0323 | 1.7996 | 2.0378 | 2.0046 | 1.9533 | 6.4507 | 6.3961 | 6.3065 | 6.1902 | 6.0714 | 5.9735 | 5.8574 | 5.7463 | 5.4867 | 5.312 | 5.124 | -0.18823 | -0.23271 | -0.32005 | 4.3309 | 4.2129 | 4.0625 | 3.8864 | 3.722 | 3.6014 | 3.4469 | 3.3077 | 2.8913 | 2.5872 | 2.4045
|  | SANDWICK | CT |  |  |  | 0.158 | -0.52372 | -0.56892 | -0.68034 | 4.1346 | 3.9835 | 3.8053 | 3.5952 | 3.4023 | 3.2572 | 3.1114 | 2.9865 | 2.4254 | 2.0323 | 1.7996 | 2.0378 | 2.0125 | 1.9663 | 6.4578 | 6.3961 | 6.3065 | 6.1902 | 6.0714 | 5.9988 | 5.9048 | 5.8193 | 5.5042 | 5.312 | 5.124 | -0.18823 | -0.22634 | -0.31197 | 4.3309 | 4.2129 | 4.0625 | 3.8864 | 3.722 | 3.6014 | 3.478 | 3.3726 | 2.9097 | 2.5872 | 2.4045
|  | SANDWICK | LW |  |  |  | 0.158 | -0.5204 | -0.57005 | -0.68002 | 4.1489 | 4.023 | 3.8577 | 3.6744 | 3.4652 | 3.2749 | 3.0911 | 2.9262 | 2.4142 | 2.1447 | 1.8818 | 2.0381 | 2.0046 | 1.9533 | 6.4507 | 6.3977 | 6.3127 | 6.2 | 6.0804 | 5.9735 | 5.8574 | 5.7463 | 5.4867 | 5.3795 | 5.2324 | -0.18707 | -0.23271 | -0.32005 | 4.3359 | 4.2376 | 4.095 | 3.9372 | 3.7612 | 3.6022 | 3.4469 | 3.3077 | 2.8913 | 2.6739 | 2.4669
|  | SANDWICK | ST |  |  |  | 0.158 | -0.49436 | -0.51357 | -0.5483 | 4.3813 | 4.3521 | 4.316 | 4.2765 | 4.247 | 4.2034 | 4.156 | 4.106 | 3.5571 | 3.0256 | 2.5908 | 2.0505 | 2.041 | 2.0191 | 6.5614 | 6.5449 | 6.5234 | 6.4989 | 6.4803 | 6.4364 | 6.3795 | 6.3119 | 5.9161 | 5.688 | 5.474 | -0.16567 | -0.18117 | -0.21141 | 4.5221 | 4.4963 | 4.4646 | 4.429 | 4.4001 | 4.3578 | 4.3111 | 4.2612 | 3.8466 | 3.4652 | 3.1383
|  | SANDWICK | FS |  |  |  | 0.158 | -0.49876 | -0.52156 | -0.55005 | 4.382 | 4.35 | 4.3204 | 4.2839 | 4.2266 | 4.173 | 4.1109 | 4.0513 | 3.6824 | 3.2626 | 2.8318 | 2.0494 | 2.038 | 2.0236 | 6.5695 | 6.5519 | 6.5364 | 6.5149 | 6.4855 | 6.4493 | 6.4005 | 6.3554 | 6.0657 | 5.723 | 5.3865 | -0.16887 | -0.18688 | -0.21007 | 4.5269 | 4.5 | 4.4749 | 4.4433 | 4.3963 | 4.351 | 4.2984 | 4.2488 | 3.9355 | 3.5681 | 3.2016
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0.252 | -3.4248 | -3.4815 | -3.6355 | 2.943 | 2.7345 | 2.4984 | 2.2323 | 1.9841 | 1.7689 | 1.5258 | 1.3279 | 0.66723 | 0.19091 | -0.10428 | -1.9734 | -2.0075 | -2.0518 | 4.2607 | 4.2129 | 4.1424 | 4.0656 | 3.9859 | 3.8935 | 3.796 | 3.6933 | 3.3586 | 3.12 | 2.8711 | -2.928 | -2.9807 | -3.0982 | 3.3209 | 3.1618 | 2.9828 | 2.7821 | 2.5938 | 2.4253 | 2.2359 | 2.0823 | 1.5727 | 1.1925 | 0.96996
|  | SCALLOWAY | CT |  |  |  | 0.252 | -3.4248 | -3.4815 | -3.6355 | 2.943 | 2.7345 | 2.4984 | 2.2323 | 1.9841 | 1.7689 | 1.5686 | 1.4262 | 0.67065 | 0.19091 | -0.10428 | -1.9722 | -1.9976 | -2.0375 | 4.2681 | 4.216 | 4.1593 | 4.0918 | 4.0164 | 3.9567 | 3.8532 | 3.7723 | 3.3632 | 3.12 | 2.8711 | -2.928 | -2.9756 | -3.0941 | 3.3209 | 3.1618 | 2.9828 | 2.7821 | 2.5938 | 2.4371 | 2.2882 | 2.1776 | 1.5836 | 1.1925 | 0.96996
|  | SCALLOWAY | LW |  |  |  | 0.252 | -3.4201 | -3.4802 | -3.6298 | 2.967 | 2.7904 | 2.5743 | 2.3447 | 2.0705 | 1.7832 | 1.5258 | 1.3279 | 0.66723 | 0.36782 | 0.050984 | -1.9734 | -2.0075 | -2.0518 | 4.2607 | 4.2129 | 4.1424 | 4.0656 | 3.9859 | 3.8935 | 3.796 | 3.6933 | 3.3586 | 3.2328 | 3.0603 | -2.9262 | -2.9807 | -3.0982 | 3.334 | 3.1968 | 3.0249 | 2.8428 | 2.6361 | 2.4253 | 2.2359 | 2.0823 | 1.5727 | 1.3289 | 1.0958
|  | SCALLOWAY | ST |  |  |  | 0.252 | -3.4071 | -3.4169 | -3.452 | 3.2607 | 3.2207 | 3.1709 | 3.1277 | 3.0783 | 3.0164 | 2.967 | 2.9017 | 2.2327 | 1.619 | 1.0693 | -1.9607 | -1.9716 | -1.9904 | 4.347 | 4.3277 | 4.3022 | 4.2782 | 4.2467 | 4.2035 | 4.1665 | 4.1181 | 3.8369 | 3.6637 | 3.3523 | -2.8965 | -2.9188 | -2.9533 | 3.5666 | 3.5318 | 3.4886 | 3.4495 | 3.4034 | 3.3439 | 3.2961 | 3.2317 | 2.7157 | 2.3105 | 1.9513
|  | SCALLOWAY | FS |  |  |  | 0.252 | -3.4056 | -3.418 | -3.4588 | 3.264 | 3.227 | 3.1827 | 3.1347 | 3.0689 | 2.9895 | 2.9074 | 2.8249 | 2.3067 | 1.749 | 1.2033 | -1.9604 | -1.9699 | -1.9853 | 4.3609 | 4.3461 | 4.3265 | 4.3032 | 4.2804 | 4.2477 | 4.2129 | 4.1782 | 3.9707 | 3.6324 | 3.166 | -2.9003 | -2.9231 | -2.9559 | 3.5739 | 3.543 | 3.5058 | 3.4646 | 3.4112 | 3.345 | 3.2762 | 3.2072 | 2.7938 | 2.3523 | 1.9284
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.054896 | 0.047245 | 0.039449 | 0.030454 | 0.028523 | 0.03081 | 0.025616 | 0.022003 | 0.019279 | 0.014464 | 0.014457 | 0.0056223 | 0.0031705 | 0.00021509 | 0.060708 | 0.053616 | 0.047083 | 0.040192 | 0.045837 | 0.042764 | 0.03628 | 0.039406 | 0.040395 | 0.037005 | 0.036968 | 0.029342 | 0.0255 | 0.013622 | 0.041175 | 0.033656 | 0.026267 | 0.018402 | 0.015888 | 0.01851 | 0.013708 | 0.009994 | 0.0074992 | 0.0026098 | 0.0026433 | -0.0058867 | -0.00806 | -0.010744
|  | SCAMMADALE | CT |  |  |  | 0 | 0.054896 | 0.047245 | 0.039449 | 0.030454 | 0.028523 | 0.03081 | 0.025616 | 0.023468 | 0.019279 | 0.014512 | 0.014745 | 0.0056223 | 0.0031705 | 0.00021509 | 0.060708 | 0.053616 | 0.047083 | 0.040192 | 0.045837 | 0.047837 | 0.044877 | 0.043334 | 0.040395 | 0.037005 | 0.036968 | 0.029342 | 0.0255 | 0.01918 | 0.041175 | 0.033656 | 0.026267 | 0.018402 | 0.015888 | 0.01851 | 0.013708 | 0.011632 | 0.0074992 | 0.002768 | 0.0029964 | -0.0058867 | -0.00806 | -0.010744
|  | SCAMMADALE | LW |  |  |  | 0 | 0.05537 | 0.048497 | 0.042044 | 0.032798 | 0.032882 | 0.032985 | 0.028201 | 0.022003 | 0.019893 | 0.014464 | 0.014457 | 0.0069522 | 0.0044442 | 0.0010818 | 0.061069 | 0.054732 | 0.049381 | 0.042097 | 0.048931 | 0.049483 | 0.046816 | 0.042732 | 0.041315 | 0.03767 | 0.037699 | 0.032919 | 0.031746 | 0.029875 | 0.041612 | 0.034853 | 0.028644 | 0.020397 | 0.020109 | 0.02052 | 0.016083 | 0.009994 | 0.0079635 | 0.0026098 | 0.0026433 | -0.0045687 | -0.0067772 | -0.0098713
|  | SCAMMADALE | ST |  |  |  | 0 | 0.057225 | 0.054205 | 0.050316 | 0.045373 | 0.039784 | 0.033298 | 0.025833 | 0.02752 | 0.031401 | 0.029589 | 0.024078 | 0.012221 | 0.0079742 | 0.0068435 | 0.062854 | 0.060272 | 0.056978 | 0.052824 | 0.048251 | 0.042764 | 0.03628 | 0.044671 | 0.047288 | 0.046096 | 0.04237 | 0.033102 | 0.027892 | 0.022533 | 0.043464 | 0.040556 | 0.036819 | 0.032225 | 0.027218 | 0.021297 | 0.014379 | 0.014827 | 0.018814 | 0.017129 | 0.011756 | 0.00033143 | -0.0036618 | -0.0046551
|  | SCAMMADALE | FS |  |  |  | 0 | 0.058221 | 0.055956 | 0.05357 | 0.050603 | 0.047468 | 0.043771 | 0.039385 | 0.033547 | 0.034069 | 0.038928 | 0.034555 | 0.02464 | 0.011468 | 0.0082579 | 0.06343 | 0.061379 | 0.059063 | 0.056156 | 0.053071 | 0.049412 | 0.045012 | 0.039406 | 0.047358 | 0.050465 | 0.047357 | 0.039027 | 0.025532 | 0.013622 | 0.04437 | 0.042171 | 0.039822 | 0.036892 | 0.033794 | 0.030133 | 0.025783 | 0.02005 | 0.020752 | 0.025696 | 0.021439 | 0.012076 | -0.00041154 | -0.0033387
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 3.046 | 6.8585 | 6.6611 | 6.2678 | 5.8132 | 5.3168 | 4.6884 | 4.064 | 3.2945 | 2.4941 | 2.0366 | 1.4572 | -0.58548 | -1.7118 | -2.4423 | 7.5099 | 7.3638 | 7.1686 | 6.9485 | 6.6725 | 6.3613 | 6.0179 | 5.5924 | 5.1359 | 4.8785 | 4.6791 | 3.699 | 3.0819 | 2.4154 | 7.641 | 7.4414 | 7.1116 | 6.7361 | 6.3093 | 5.7681 | 5.2182 | 4.5324 | 3.7897 | 3.425 | 2.9572 | 1.1897 | 0.35643 | -0.27922
|  | SCONE | CT |  |  |  | 3.046 | 6.8978 | 6.706 | 6.3233 | 5.8779 | 5.3299 | 4.7171 | 4.064 | 3.3042 | 2.6545 | 2.0366 | 1.8229 | -0.48533 | -1.7118 | -2.4423 | 7.5323 | 7.3862 | 7.185 | 6.9627 | 6.6725 | 6.3613 | 6.0179 | 5.5924 | 5.241 | 4.8785 | 4.8864 | 3.7325 | 3.0819 | 2.4154 | 7.6715 | 7.4758 | 7.1483 | 6.7801 | 6.3093 | 5.7928 | 5.2292 | 4.5514 | 3.9846 | 3.425 | 3.3375 | 1.3578 | 0.35643 | -0.27922
|  | SCONE | LW |  |  |  | 3.046 | 6.8585 | 6.6611 | 6.2678 | 5.8132 | 5.3168 | 4.6884 | 4.0673 | 3.2945 | 2.4941 | 2.0843 | 1.4572 | -0.58548 | -1.324 | -2.0019 | 7.5099 | 7.3638 | 7.1686 | 6.9485 | 6.7107 | 6.3672 | 6.0313 | 5.6124 | 5.1359 | 5.0301 | 4.6791 | 3.699 | 3.4163 | 3.0489 | 7.641 | 7.4414 | 7.1116 | 6.7361 | 6.3241 | 5.7681 | 5.2182 | 4.5324 | 3.7897 | 3.5189 | 2.9572 | 1.1897 | 0.57892 | -0.043013
|  | SCONE | ST |  |  |  | 3.046 | 6.9608 | 6.8537 | 6.7213 | 6.5905 | 6.43 | 6.2417 | 6.0935 | 5.8823 | 5.6677 | 5.4177 | 5.1303 | 3.6216 | 2.5181 | 1.5681 | 7.5787 | 7.5081 | 7.412 | 7.3194 | 7.2013 | 7.0586 | 6.9461 | 6.7804 | 6.6096 | 6.4017 | 6.176 | 5.1949 | 4.5152 | 3.8599 | 7.7379 | 7.641 | 7.5152 | 7.3944 | 7.2431 | 7.0606 | 6.9198 | 6.7076 | 6.4902 | 6.2286 | 5.9467 | 4.6107 | 3.6682 | 2.9326
|  | SCONE | FS |  |  |  | 3.046 | 7.0253 | 6.9424 | 6.8333 | 6.7104 | 6.5698 | 6.4191 | 6.2667 | 6.07 | 5.8231 | 5.5661 | 5.3356 | 3.6753 | 2.5166 | 1.238 | 7.6148 | 7.557 | 7.4848 | 7.4023 | 7.3026 | 7.1936 | 7.0722 | 6.9484 | 6.7699 | 6.5821 | 6.4192 | 5.2061 | 4.3346 | 3.1361 | 7.7866 | 7.7122 | 7.6148 | 7.5066 | 7.3769 | 7.2379 | 7.0888 | 6.9231 | 6.6917 | 6.4504 | 6.2414 | 4.6941 | 3.7687 | 2.7731
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0 | 0.68286 | 0.67181 | 0.64916 | 0.62104 | 0.5881 | 0.55904 | 0.5161 | 0.49749 | 0.47632 | 0.45163 | 0.43716 | 0.37401 | 0.34526 | 0.32151 | 0.82058 | 0.81716 | 0.80613 | 0.79252 | 0.77393 | 0.76134 | 0.73726 | 0.72639 | 0.71255 | 0.69338 | 0.68685 | 0.65327 | 0.63678 | 0.59634 | 0.74056 | 0.73193 | 0.71293 | 0.68949 | 0.65965 | 0.63673 | 0.59791 | 0.58292 | 0.5597 | 0.53265 | 0.52097 | 0.46831 | 0.44397 | 0.42193
|  | SHAPINSAY | CT |  |  |  | 0 | 0.68286 | 0.67181 | 0.64916 | 0.62104 | 0.5881 | 0.55904 | 0.5161 | 0.49749 | 0.47632 | 0.45522 | 0.44593 | 0.38631 | 0.36101 | 0.33906 | 0.82058 | 0.81716 | 0.80615 | 0.79252 | 0.77393 | 0.76134 | 0.73726 | 0.72639 | 0.71255 | 0.69775 | 0.69204 | 0.65436 | 0.63678 | 0.61345 | 0.74056 | 0.73193 | 0.71293 | 0.68949 | 0.65965 | 0.63673 | 0.59791 | 0.58292 | 0.56191 | 0.53987 | 0.53167 | 0.47754 | 0.45859 | 0.43852
|  | SHAPINSAY | LW |  |  |  | 0 | 0.68555 | 0.67815 | 0.6531 | 0.6298 | 0.60074 | 0.56852 | 0.5274 | 0.50917 | 0.47855 | 0.45163 | 0.43716 | 0.37401 | 0.34526 | 0.32151 | 0.82167 | 0.81986 | 0.80613 | 0.79677 | 0.78236 | 0.76666 | 0.74299 | 0.73527 | 0.7128 | 0.69338 | 0.68685 | 0.65327 | 0.64072 | 0.62979 | 0.743 | 0.73687 | 0.71418 | 0.69558 | 0.67047 | 0.64294 | 0.60509 | 0.59091 | 0.5597 | 0.53265 | 0.52097 | 0.46831 | 0.44397 | 0.42193
|  | SHAPINSAY | ST |  |  |  | 0 | 0.68993 | 0.67787 | 0.66412 | 0.64508 | 0.62722 | 0.60845 | 0.58704 | 0.57038 | 0.54654 | 0.52178 | 0.50629 | 0.40433 | 0.36211 | 0.34168 | 0.82508 | 0.81861 | 0.81498 | 0.80598 | 0.79848 | 0.79027 | 0.77939 | 0.77125 | 0.75551 | 0.73893 | 0.73343 | 0.66619 | 0.63737 | 0.61578 | 0.75106 | 0.73597 | 0.72624 | 0.71017 | 0.69583 | 0.68061 | 0.66198 | 0.64806 | 0.625 | 0.60094 | 0.59028 | 0.49636 | 0.45595 | 0.43715
|  | SHAPINSAY | FS |  |  |  | 0 | 0.69861 | 0.69012 | 0.68847 | 0.68188 | 0.67682 | 0.66693 | 0.66091 | 0.64649 | 0.62817 | 0.61549 | 0.59678 | 0.50374 | 0.41117 | 0.37295 | 0.8291 | 0.82456 | 0.8249 | 0.82058 | 0.81765 | 0.81016 | 0.80658 | 0.79847 | 0.78605 | 0.78005 | 0.76751 | 0.71032 | 0.64577 | 0.59634 | 0.75814 | 0.74758 | 0.74664 | 0.74023 | 0.73544 | 0.7253 | 0.71983 | 0.70685 | 0.68896 | 0.67873 | 0.66067 | 0.57667 | 0.49885 | 0.46831
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0.069 | 0.046714 | 0.035973 | 0.010561 | -0.015929 | -0.039538 | -0.074587 | -0.11292 | -0.1319 | -0.15503 | -0.16356 | -0.17969 | -0.2291 | -0.26397 | -0.31038 | 0.45538 | 0.44706 | 0.42859 | 0.41007 | 0.39571 | 0.37102 | 0.34278 | 0.32748 | 0.30819 | 0.30181 | 0.28811 | 0.24569 | 0.21317 | 0.16903 | 0.45462 | 0.43694 | 0.41193 | 0.38639 | 0.36551 | 0.33115 | 0.29386 | 0.27316 | 0.24745 | 0.2424 | 0.22512 | 0.17501 | 0.13823 | 0.089444
|  | SHIELDAIG | CT |  |  |  | 0.069 | 0.046714 | 0.040618 | 0.019877 | -0.0085259 | -0.034473 | -0.063381 | -0.098452 | -0.11623 | -0.12895 | -0.14264 | -0.14285 | -0.1785 | -0.19657 | -0.22249 | 0.45538 | 0.45507 | 0.44487 | 0.426 | 0.41217 | 0.3962 | 0.37424 | 0.35842 | 0.34646 | 0.3331 | 0.3314 | 0.29746 | 0.28197 | 0.25647 | 0.45462 | 0.44394 | 0.42589 | 0.39956 | 0.37704 | 0.35147 | 0.31935 | 0.29896 | 0.2841 | 0.26758 | 0.27016 | 0.23212 | 0.21587 | 0.19155
|  | SHIELDAIG | LW |  |  |  | 0.069 | 0.047841 | 0.035973 | 0.010561 | -0.015929 | -0.039538 | -0.074587 | -0.11292 | -0.1319 | -0.15503 | -0.16356 | -0.17969 | -0.2291 | -0.26397 | -0.31038 | 0.45548 | 0.44706 | 0.42859 | 0.41007 | 0.39571 | 0.37102 | 0.34278 | 0.32748 | 0.30819 | 0.30181 | 0.28811 | 0.24569 | 0.21317 | 0.16903 | 0.45538 | 0.43694 | 0.41193 | 0.38639 | 0.36551 | 0.33115 | 0.29386 | 0.27316 | 0.24745 | 0.2424 | 0.22512 | 0.17501 | 0.13823 | 0.089444
|  | SHIELDAIG | ST |  |  |  | 0.069 | 0.057185 | 0.043604 | 0.032101 | 0.022944 | 0.01128 | 0.00054239 | -0.014796 | -0.025727 | -0.040795 | -0.053091 | -0.069879 | -0.1513 | -0.19625 | -0.22581 | 0.46447 | 0.45436 | 0.44766 | 0.44212 | 0.43485 | 0.42871 | 0.41845 | 0.41142 | 0.40076 | 0.39242 | 0.38037 | 0.31011 | 0.26464 | 0.22829 | 0.4645 | 0.45226 | 0.43435 | 0.42727 | 0.41659 | 0.40733 | 0.39186 | 0.38209 | 0.36722 | 0.35613 | 0.3389 | 0.25554 | 0.20773 | 0.17467
|  | SHIELDAIG | FS |  |  |  | 0.069 | 0.062231 | 0.052203 | 0.040543 | 0.047532 | 0.039215 | 0.033515 | 0.0273 | 0.014946 | 0.0040085 | -0.0084746 | -0.020943 | -0.083869 | -0.13398 | -0.15807 | 0.46679 | 0.45882 | 0.44788 | 0.45665 | 0.44944 | 0.44461 | 0.43897 | 0.42962 | 0.42135 | 0.41172 | 0.40286 | 0.35724 | 0.32245 | 0.29512 | 0.46853 | 0.45932 | 0.44785 | 0.45008 | 0.44047 | 0.43481 | 0.42867 | 0.41565 | 0.40533 | 0.39297 | 0.3802 | 0.31796 | 0.2762 | 0.25569
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | YES | 0.028 | 2.4873 | 2.4727 | 2.4379 | 2.3976 | 2.3622 | 2.3103 | 2.2588 | 2.2305 | 2.198 | 2.1794 | 2.1559 | 2.084 | 2.0349 | 1.9767 | 2.4305 | 2.4145 | 2.3926 | 2.3668 | 2.3486 | 2.313 | 2.2818 | 2.2581 | 2.2286 | 2.2136 | 2.1922 | 2.1365 | 2.1008 | 2.0522 | 2.4683 | 2.4575 | 2.4254 | 2.3875 | 2.3579 | 2.3067 | 2.2615 | 2.2299 | 2.1918 | 2.173 | 2.1459 | 2.0741 | 2.0283 | 1.9704
|  | SHIN | CT |  |  |  | 0.028 | 2.4952 | 2.474 | 2.445 | 2.4038 | 2.3664 | 2.3217 | 2.274 | 2.2463 | 2.2255 | 2.2132 | 2.1965 | 2.1345 | 2.1021 | 2.0644 | 2.4344 | 2.421 | 2.4073 | 2.3817 | 2.3629 | 2.3377 | 2.3131 | 2.2879 | 2.2686 | 2.257 | 2.2385 | 2.1854 | 2.1632 | 2.1283 | 2.4818 | 2.4617 | 2.4372 | 2.3995 | 2.3676 | 2.3272 | 2.2878 | 2.2555 | 2.2313 | 2.2181 | 2.1965 | 2.1319 | 2.1063 | 2.0736
|  | SHIN | LW |  |  |  | 0.028 | 2.4988 | 2.4727 | 2.4379 | 2.3976 | 2.3622 | 2.3103 | 2.2588 | 2.2305 | 2.198 | 2.1794 | 2.1559 | 2.084 | 2.0349 | 1.9767 | 2.4356 | 2.4145 | 2.3926 | 2.3668 | 2.3486 | 2.313 | 2.2818 | 2.2581 | 2.2286 | 2.2136 | 2.1922 | 2.1365 | 2.1008 | 2.0522 | 2.4817 | 2.4575 | 2.4254 | 2.3875 | 2.3579 | 2.3067 | 2.2615 | 2.2299 | 2.1918 | 2.173 | 2.1459 | 2.0741 | 2.0283 | 1.9704
|  | SHIN | ST |  |  |  | 0.028 | 2.4873 | 2.4886 | 2.4653 | 2.4435 | 2.4233 | 2.4014 | 2.3766 | 2.3584 | 2.3325 | 2.3149 | 2.2894 | 2.1713 | 2.11 | 2.0711 | 2.4305 | 2.4326 | 2.418 | 2.4057 | 2.3953 | 2.3831 | 2.3673 | 2.3568 | 2.3372 | 2.3284 | 2.3095 | 2.2075 | 2.1523 | 2.1085 | 2.4683 | 2.4783 | 2.4566 | 2.4373 | 2.4201 | 2.4007 | 2.3767 | 2.3604 | 2.3329 | 2.32 | 2.2937 | 2.1676 | 2.1069 | 2.0678
|  | SHIN | FS |  |  |  | 0.028 | 2.489 | 2.4968 | 2.4927 | 2.4846 | 2.4774 | 2.4695 | 2.4586 | 2.4399 | 2.4231 | 2.4019 | 2.3806 | 2.2955 | 2.1958 | 2.1575 | 2.4343 | 2.43 | 2.4284 | 2.4215 | 2.4161 | 2.4098 | 2.4 | 2.3863 | 2.3747 | 2.3581 | 2.3434 | 2.2841 | 2.211 | 2.1672 | 2.4707 | 2.4792 | 2.4772 | 2.4684 | 2.4615 | 2.4538 | 2.442 | 2.4228 | 2.4072 | 2.3849 | 2.3643 | 2.2849 | 2.1915 | 2.1609
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0 | 0.092456 | 0.083988 | 0.074137 | 0.064707 | 0.057774 | 0.047479 | 0.033138 | 0.030049 | 0.026145 | 0.022761 | 0.019721 | 0.0011953 | -0.022508 | -0.049794 | 0.092169 | 0.082061 | 0.071135 | 0.060437 | 0.052886 | 0.041347 | 0.025354 | 0.022734 | 0.019462 | 0.016649 | 0.014131 | -0.0055575 | -0.033864 | -0.066067 | 0.086351 | 0.075967 | 0.0644 | 0.053279 | 0.045281 | 0.033327 | 0.01692 | 0.014297 | 0.011138 | 0.0084443 | 0.0060617 | -0.014892 | -0.044097 | -0.077226
|  | SHONA BEG | CT |  |  |  | 0 | 0.092456 | 0.09101 | 0.089286 | 0.079992 | 0.075989 | 0.071068 | 0.061593 | 0.057468 | 0.054064 | 0.050399 | 0.046946 | 0.03414 | 0.026628 | 0.016239 | 0.092177 | 0.091206 | 0.09019 | 0.079545 | 0.075644 | 0.070702 | 0.060891 | 0.05708 | 0.05394 | 0.050509 | 0.047218 | 0.034648 | 0.026244 | 0.014106 | 0.086351 | 0.084942 | 0.083453 | 0.072459 | 0.068203 | 0.062852 | 0.052671 | 0.048948 | 0.045885 | 0.042631 | 0.039572 | 0.025929 | 0.017017 | 0.0047705
|  | SHONA BEG | LW |  |  |  | 0 | 0.092519 | 0.083988 | 0.074137 | 0.064707 | 0.057774 | 0.047479 | 0.033138 | 0.030049 | 0.026145 | 0.022761 | 0.019721 | 0.0011953 | -0.022508 | -0.049794 | 0.092169 | 0.082061 | 0.071135 | 0.060437 | 0.052886 | 0.041347 | 0.025354 | 0.022734 | 0.019462 | 0.016649 | 0.014131 | -0.0055575 | -0.033864 | -0.066067 | 0.086456 | 0.075967 | 0.0644 | 0.053279 | 0.045281 | 0.033327 | 0.01692 | 0.014297 | 0.011138 | 0.0084443 | 0.0060617 | -0.014892 | -0.044097 | -0.077226
|  | SHONA BEG | ST |  |  |  | 0 | 0.092846 | 0.092254 | 0.086074 | 0.081409 | 0.07831 | 0.075895 | 0.073338 | 0.070811 | 0.067927 | 0.064706 | 0.062126 | 0.030549 | 0.0024933 | -0.021837 | 0.092481 | 0.092152 | 0.08561 | 0.080713 | 0.077661 | 0.075484 | 0.073147 | 0.070708 | 0.06788 | 0.064953 | 0.062877 | 0.028297 | -0.0048345 | -0.034666 | 0.086782 | 0.086091 | 0.078969 | 0.073604 | 0.070212 | 0.06771 | 0.065066 | 0.062426 | 0.059429 | 0.056342 | 0.054119 | 0.019252 | -0.014065 | -0.043667
|  | SHONA BEG | FS |  |  |  | 0 | 0.093087 | 0.092678 | 0.090648 | 0.088536 | 0.086391 | 0.084077 | 0.080824 | 0.077947 | 0.074035 | 0.070094 | 0.068502 | 0.05778 | 0.048212 | 0.042346 | 0.092542 | 0.092278 | 0.089934 | 0.08751 | 0.085057 | 0.082522 | 0.07888 | 0.075842 | 0.071507 | 0.067139 | 0.065719 | 0.057022 | 0.049152 | 0.04208 | 0.087126 | 0.086645 | 0.084159 | 0.081593 | 0.078993 | 0.076311 | 0.072518 | 0.069426 | 0.064988 | 0.060509 | 0.058991 | 0.050085 | 0.042056 | 0.035814
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 6.2 | 9.7827 | 9.5393 | 9.2441 | 8.8059 | 8.3614 | 7.9026 | 7.2654 | 6.5446 | 5.5811 | 4.7335 | 3.9555 | 2.0274 | 1.3258 | 0.48829 | 12.8691 | 12.7318 | 12.6168 | 12.4653 | 12.3014 | 12.0284 | 11.5329 | 11.171 | 10.716 | 10.3276 | 9.9591 | 8.9648 | 8.1801 | 7.3112 | 11.2073 | 10.9722 | 10.6938 | 10.2887 | 9.8755 | 9.3755 | 8.6198 | 7.8758 | 6.9732 | 6.1805 | 5.4524 | 3.7451 | 3.3897 | 3.0025
|  | SKENE | CT |  |  |  | 6.2 | 9.8118 | 9.5844 | 9.253 | 8.8059 | 8.3614 | 7.9026 | 7.2654 | 6.5758 | 5.8923 | 5.2831 | 4.7603 | 2.6124 | 1.3258 | 0.48829 | 12.8855 | 12.7653 | 12.6424 | 12.4653 | 12.3014 | 12.0284 | 11.5329 | 11.171 | 10.8199 | 10.5102 | 10.2044 | 8.9648 | 8.1801 | 7.3112 | 11.2343 | 11.0184 | 10.7098 | 10.2887 | 9.8755 | 9.3755 | 8.6198 | 7.9367 | 7.3365 | 6.7925 | 6.3202 | 4.6644 | 3.7928 | 3.1143
|  | SKENE | LW |  |  |  | 6.2 | 9.7827 | 9.5393 | 9.2441 | 8.8942 | 8.5202 | 7.9722 | 7.3985 | 6.5446 | 5.5811 | 4.7335 | 3.9555 | 2.0274 | 1.5239 | 1.003 | 12.8691 | 12.7318 | 12.6168 | 12.4822 | 12.3467 | 12.092 | 11.741 | 11.1822 | 10.716 | 10.3276 | 9.9591 | 9.0049 | 8.7108 | 8.3338 | 11.2073 | 10.9722 | 10.6938 | 10.3646 | 10.0149 | 9.4627 | 8.8095 | 7.8758 | 6.9732 | 6.1805 | 5.4524 | 3.7451 | 3.3897 | 3.0025
|  | SKENE | ST |  |  |  | 6.2 | 9.8736 | 9.8039 | 9.6844 | 9.5481 | 9.3754 | 9.1739 | 8.8978 | 8.4677 | 8.0337 | 7.7205 | 7.2588 | 4.6891 | 3.642 | 2.7973 | 12.9178 | 12.8692 | 12.8007 | 12.7261 | 12.6309 | 12.5211 | 12.3392 | 12.0373 | 11.7691 | 11.6098 | 11.3496 | 9.7805 | 9.2222 | 8.6146 | 11.3123 | 11.2265 | 11.1101 | 10.9789 | 10.8135 | 10.6203 | 10.3552 | 9.9411 | 9.5226 | 9.2245 | 8.7808 | 6.3101 | 5.0998 | 4.2637
|  | SKENE | FS |  |  |  | 6.2 | 9.8966 | 9.828 | 9.7353 | 9.6185 | 9.494 | 9.3416 | 9.1364 | 8.8455 | 8.5448 | 8.2472 | 7.9187 | 5.9965 | 3.8698 | 2.054 | 12.9329 | 12.8906 | 12.8484 | 12.7903 | 12.7298 | 12.6509 | 12.5187 | 12.3395 | 12.1728 | 12.0128 | 11.8361 | 10.9003 | 9.2709 | 7.3674 | 11.3261 | 11.2491 | 11.1615 | 11.051 | 10.9335 | 10.7887 | 10.5915 | 10.3151 | 10.0282 | 9.7442 | 9.4317 | 7.5099 | 5.3319 | 3.6543
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 2.531 | -4.4434 | -4.5372 | -4.7054 | -4.8904 | -5.1043 | -5.3227 | -5.5889 | -5.7306 | -5.8383 | -5.9497 | -6.0648 | -6.3603 | -6.4913 | -6.7004 | -3.3425 | -3.3972 | -3.4789 | -3.571 | -3.6795 | -3.778 | -3.9176 | -4.0271 | -4.1296 | -4.2403 | -4.3353 | -4.5525 | -4.6217 | -4.7651 | -3.8625 | -3.9464 | -4.0901 | -4.2444 | -4.4294 | -4.6014 | -4.8304 | -4.9724 | -5.0797 | -5.2069 | -5.324 | -5.5962 | -5.7012 | -5.884
|  | SKULAMUS | CT |  |  |  | 2.531 | -4.4434 | -4.5372 | -4.7054 | -4.8904 | -5.1043 | -5.3227 | -5.5889 | -5.7306 | -5.8383 | -5.902 | -5.9717 | -6.2186 | -6.3316 | -6.4924 | -3.3425 | -3.397 | -3.4789 | -3.571 | -3.6795 | -3.778 | -3.9176 | -4.0271 | -4.1117 | -4.1664 | -4.238 | -4.4559 | -4.5418 | -4.6951 | -3.8625 | -3.9464 | -4.0901 | -4.2444 | -4.4294 | -4.6014 | -4.8304 | -4.9724 | -5.0797 | -5.1371 | -5.2163 | -5.457 | -5.5423 | -5.6726
|  | SKULAMUS | LW |  |  |  | 2.531 | -4.4324 | -4.5251 | -4.6781 | -4.8449 | -5.0238 | -5.2473 | -5.5015 | -5.6594 | -5.8062 | -5.9497 | -6.0648 | -6.3603 | -6.4913 | -6.7004 | -3.3384 | -3.3972 | -3.4766 | -3.562 | -3.6514 | -3.7683 | -3.9123 | -4.0244 | -4.1296 | -4.2403 | -4.3353 | -4.5525 | -4.6217 | -4.7651 | -3.8541 | -3.9396 | -4.0728 | -4.2152 | -4.3675 | -4.5544 | -4.7784 | -4.9309 | -5.065 | -5.2069 | -5.324 | -5.5962 | -5.7012 | -5.884
|  | SKULAMUS | ST |  |  |  | 2.531 | -4.4095 | -4.4736 | -4.5528 | -4.6311 | -4.7208 | -4.8166 | -4.9221 | -5.0306 | -5.1342 | -5.2464 | -5.3623 | -5.8328 | -6.0018 | -6.0703 | -3.321 | -3.3541 | -3.3965 | -3.437 | -3.487 | -3.5383 | -3.6003 | -3.6687 | -3.7314 | -3.8058 | -3.8863 | -4.2517 | -4.3994 | -4.5035 | -3.8292 | -3.8854 | -3.9531 | -4.0171 | -4.0959 | -4.1754 | -4.2696 | -4.3695 | -4.4556 | -4.5585 | -4.6695 | -5.1182 | -5.2653 | -5.3213
|  | SKULAMUS | FS |  |  |  | 2.531 | -4.3757 | -4.4156 | -4.4466 | -4.487 | -4.5192 | -4.5698 | -4.6147 | -4.6979 | -4.793 | -4.8664 | -4.9529 | -5.3941 | -5.8317 | -6.0044 | -3.31 | -3.3313 | -3.3526 | -3.3819 | -3.4034 | -3.4398 | -3.4728 | -3.5256 | -3.5895 | -3.6344 | -3.6933 | -4.0068 | -4.3396 | -4.5648 | -3.805 | -3.8392 | -3.8675 | -3.9073 | -3.9331 | -3.981 | -4.0211 | -4.0963 | -4.1851 | -4.2434 | -4.3242 | -4.725 | -5.1199 | -5.2575
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 6.345 | -1.0713 | 15.8064 | 14.3937 | 12.9912 | 11.2353 | 9.1638 | 7.1381 | 4.689 | 2.1305 | -0.22304 | -2.4076 | -8.959 | -12.5841 | -15.5175 | 2.3539 | 19.2953 | 18.5476 | 17.8719 | 16.9594 | 15.8094 | 14.6379 | 13.3116 | 11.849 | 10.5045 | 9.2531 | 5.7449 | 3.4751 | 0.93828 | 1.1991 | 18.44 | 17.2118 | 16.0034 | 14.4677 | 12.6431 | 10.8288 | 8.649 | 6.3823 | 4.2935 | 2.3145 | -3.4624 | -6.5155 | -9.0523
|  | SPRINGHILL | CT |  |  |  | 6.345 | -0.96116 | 15.9786 | 14.6696 | 13.3675 | 11.5806 | 9.7058 | 7.7478 | 5.288 | 3.1492 | 1.1255 | -0.74016 | -8.0056 | -12.5841 | -15.5175 | 2.3978 | 19.3615 | 18.6361 | 17.9768 | 17.0033 | 15.9884 | 14.8649 | 13.5166 | 12.3588 | 11.2151 | 10.1386 | 6.0418 | 3.4751 | 0.93828 | 1.2805 | 18.5729 | 17.4402 | 16.3111 | 14.7533 | 13.1028 | 11.3521 | 9.1634 | 7.2624 | 5.4725 | 3.8318 | -2.5955 | -6.5155 | -9.0523
|  | SPRINGHILL | LW |  |  |  | 6.345 | -1.0713 | 15.8064 | 14.3937 | 12.9912 | 11.2353 | 9.1638 | 7.1381 | 4.689 | 2.1305 | -0.22304 | -2.4076 | -8.959 | -11.7113 | -13.9319 | 2.3539 | 19.2953 | 18.5476 | 17.8719 | 16.9594 | 15.8094 | 14.6379 | 13.3116 | 11.849 | 10.5045 | 9.2531 | 5.7449 | 4.4188 | 3.104 | 1.1991 | 18.44 | 17.2118 | 16.0034 | 14.4677 | 12.6431 | 10.8288 | 8.649 | 6.3823 | 4.2935 | 2.3145 | -3.4624 | -5.7725 | -7.7526
|  | SPRINGHILL | ST |  |  |  | 6.345 | -0.72107 | 16.5253 | 15.9363 | 15.318 | 14.5962 | 13.8708 | 13.6483 | 12.8995 | 12.0263 | 11.136 | 10.1693 | 3.9957 | -0.39337 | -4.2076 | 2.5495 | 19.7366 | 19.3613 | 18.9668 | 18.4945 | 17.9992 | 17.855 | 17.3277 | 16.698 | 16.0456 | 15.333 | 11.0499 | 8.1845 | 5.373 | 1.4992 | 19.0641 | 18.5875 | 18.0956 | 17.5151 | 16.924 | 16.7634 | 16.1532 | 15.4343 | 14.6457 | 13.7721 | 8.1977 | 4.3929 | 1.0885
|  | SPRINGHILL | FS |  |  |  | 6.345 | -0.52323 | 16.8409 | 16.383 | 15.8119 | 15.2438 | 14.6347 | 14.0848 | 13.6654 | 12.8352 | 11.9992 | 11.1151 | 5.4577 | -0.25627 | -5.1452 | 2.6516 | 19.8848 | 19.6018 | 19.2357 | 18.8715 | 18.4601 | 18.0532 | 17.8117 | 17.2386 | 16.6577 | 16.0388 | 12.1029 | 7.5615 | 2.7022 | 1.6554 | 19.3259 | 18.9523 | 18.4906 | 18.0391 | 17.5403 | 17.0717 | 16.7503 | 16.0609 | 15.3651 | 14.6311 | 9.632 | 4.542 | 0.23219
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 0.447 | 5.5228 | 5.4211 | 5.2848 | 5.106 | 4.9261 | 4.7164 | 4.4741 | 4.3421 | 4.2275 | 4.1296 | 4.0447 | 3.84 | 3.6888 | 3.5342 | 5.7132 | 5.6516 | 5.577 | 5.4818 | 5.4037 | 5.2858 | 5.1404 | 5.042 | 4.9581 | 4.8856 | 4.8213 | 4.6987 | 4.5993 | 4.3916 | 5.8199 | 5.736 | 5.6131 | 5.4526 | 5.2982 | 5.1116 | 4.8897 | 4.7658 | 4.6402 | 4.53 | 4.4333 | 4.2312 | 4.0966 | 3.9459
|  | ST CYRUS | CT |  |  |  | 0.447 | 5.5228 | 5.4211 | 5.2848 | 5.1086 | 4.9261 | 4.7164 | 4.4741 | 4.3452 | 4.2558 | 4.1743 | 4.1048 | 3.9048 | 3.7755 | 3.6459 | 5.7132 | 5.6547 | 5.5868 | 5.4931 | 5.4062 | 5.3011 | 5.1629 | 5.0657 | 5 | 4.934 | 4.8738 | 4.716 | 4.5993 | 4.4304 | 5.8199 | 5.736 | 5.6154 | 5.4575 | 5.2982 | 5.1163 | 4.8976 | 4.7784 | 4.6934 | 4.6016 | 4.5204 | 4.3182 | 4.207 | 4.0883
|  | ST CYRUS | LW |  |  |  | 0.447 | 5.5312 | 5.4287 | 5.2856 | 5.106 | 4.9357 | 4.7181 | 4.4757 | 4.3421 | 4.2275 | 4.1296 | 4.0447 | 3.84 | 3.6888 | 3.5342 | 5.7155 | 5.6516 | 5.577 | 5.4818 | 5.4037 | 5.2858 | 5.1404 | 5.042 | 4.9581 | 4.8856 | 4.8213 | 4.6987 | 4.6175 | 4.5202 | 5.8285 | 5.7416 | 5.6131 | 5.4526 | 5.3042 | 5.1116 | 4.8897 | 4.7658 | 4.6402 | 4.53 | 4.4333 | 4.2312 | 4.0966 | 3.9459
|  | ST CYRUS | ST |  |  |  | 0.447 | 5.5474 | 5.4735 | 5.3746 | 5.281 | 5.1831 | 5.0666 | 4.9603 | 4.8313 | 4.7343 | 4.6335 | 4.5557 | 4.1639 | 4.0356 | 3.9552 | 5.7272 | 5.6903 | 5.6343 | 5.5852 | 5.5339 | 5.4689 | 5.4064 | 5.3151 | 5.2514 | 5.1838 | 5.1349 | 4.8123 | 4.677 | 4.5177 | 5.8412 | 5.7799 | 5.6955 | 5.6162 | 5.5312 | 5.4327 | 5.34 | 5.2212 | 5.1318 | 5.0339 | 4.9621 | 4.5335 | 4.4085 | 4.3244
|  | ST CYRUS | FS |  |  |  | 0.447 | 5.5972 | 5.5496 | 5.5121 | 5.4771 | 5.4325 | 5.3803 | 5.3162 | 5.2318 | 5.1496 | 5.0703 | 4.985 | 4.6024 | 4.1987 | 4.0575 | 5.7475 | 5.7212 | 5.6926 | 5.6675 | 5.6333 | 5.5973 | 5.5457 | 5.4874 | 5.4307 | 5.3758 | 5.3166 | 5.024 | 4.6757 | 4.3916 | 5.8836 | 5.8449 | 5.8149 | 5.787 | 5.7467 | 5.7 | 5.6379 | 5.5625 | 5.4823 | 5.4071 | 5.3241 | 4.9428 | 4.5542 | 4.4319
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 0.358 | 17.6903 | 17.6356 | 17.5448 | 17.4235 | 17.297 | 17.1429 | 16.9715 | 16.7998 | 16.6953 | 16.5644 | 16.4343 | 16.0928 | 15.8357 | 15.6528 | 30.4138 | 30.3779 | 30.3288 | 30.2644 | 30.2067 | 30.1285 | 30.0376 | 29.934 | 29.8905 | 29.8037 | 29.725 | 29.5349 | 29.4005 | 29.2335 | 38.5577 | 38.5063 | 38.4235 | 38.3185 | 38.2112 | 38.0747 | 37.92 | 37.763 | 37.6695 | 37.5457 | 37.4256 | 37.1206 | 36.9043 | 36.7454
|  | ST FERGUS GAS TERM | CT |  |  |  | 0.358 | 17.6903 | 17.6356 | 17.5448 | 17.4235 | 17.297 | 17.1429 | 16.9715 | 16.7998 | 16.6953 | 16.5762 | 16.4703 | 16.0928 | 15.8357 | 15.6528 | 30.4138 | 30.3779 | 30.3288 | 30.2644 | 30.2067 | 30.1285 | 30.0376 | 29.934 | 29.8905 | 29.8137 | 29.7426 | 29.5349 | 29.4005 | 29.2335 | 38.5577 | 38.5063 | 38.4239 | 38.3185 | 38.2112 | 38.0747 | 37.92 | 37.763 | 37.6695 | 37.5586 | 37.4609 | 37.1208 | 36.9043 | 36.7454
|  | ST FERGUS GAS TERM | LW |  |  |  | 0.358 | 17.6924 | 17.6415 | 17.5452 | 17.4384 | 17.3141 | 17.1779 | 17.0214 | 16.8466 | 16.7086 | 16.5644 | 16.4343 | 16.0975 | 15.9237 | 15.7663 | 30.4151 | 30.3824 | 30.329 | 30.2738 | 30.2103 | 30.146 | 30.0605 | 29.962 | 29.8912 | 29.8037 | 29.725 | 29.5657 | 29.5091 | 29.4454 | 38.5597 | 38.5119 | 38.4235 | 38.3293 | 38.222 | 38.1063 | 37.9639 | 37.8052 | 37.6788 | 37.5457 | 37.4256 | 37.1206 | 36.9736 | 36.8378
|  | ST FERGUS GAS TERM | ST |  |  |  | 0.358 | 17.7175 | 17.6799 | 17.6404 | 17.6042 | 17.5526 | 17.5064 | 17.4476 | 17.4072 | 17.3397 | 17.279 | 17.2039 | 16.7707 | 16.5115 | 16.2658 | 30.4316 | 30.4072 | 30.3828 | 30.3614 | 30.3267 | 30.2978 | 30.2571 | 30.2307 | 30.1788 | 30.1323 | 30.0738 | 29.7727 | 29.6152 | 29.4406 | 38.5837 | 38.5486 | 38.5122 | 38.4796 | 38.4307 | 38.3888 | 38.3331 | 38.2964 | 38.2305 | 38.1719 | 38.0991 | 37.6922 | 37.4692 | 37.2751
|  | ST FERGUS GAS TERM | FS |  |  |  | 0.358 | 17.7236 | 17.6996 | 17.6714 | 17.6322 | 17.6092 | 17.5681 | 17.5366 | 17.4769 | 17.4369 | 17.3756 | 17.3187 | 16.9754 | 16.63 | 16.352 | 30.4334 | 30.4179 | 30.3997 | 30.3725 | 30.3583 | 30.329 | 30.3061 | 30.265 | 30.238 | 30.1937 | 30.1526 | 29.8928 | 29.5919 | 29.283 | 38.5888 | 38.5667 | 38.5407 | 38.5037 | 38.483 | 38.4442 | 38.4156 | 38.3599 | 38.3232 | 38.2653 | 38.2118 | 37.8872 | 37.5636 | 37.3276
| ST FILLANS | ST FILLANS | MINIMUM HEADROOM | NN 6942 2464 | YES | NO | 0 | 8.8402 | 8.8246 | 8.808 | 8.7898 | 8.783 | 8.7755 | 8.7585 | 8.7554 | 8.7465 | 8.7445 | 8.7385 | 8.7148 | 8.6888 | 8.6599 | 8.1682 | 8.1518 | 8.1355 | 8.118 | 8.1147 | 8.1069 | 8.0902 | 8.0884 | 8.0818 | 8.0807 | 8.0764 | 8.0539 | 8.0249 | 7.9919 | 8.5033 | 8.4861 | 8.4679 | 8.4483 | 8.4404 | 8.4315 | 8.4123 | 8.4094 | 8.4007 | 8.3989 | 8.3931 | 8.3669 | 8.3359 | 8.3012
|  | ST FILLANS | CT |  |  |  | 0 | 8.8402 | 8.8311 | 8.8224 | 8.8055 | 8.7998 | 8.7998 | 8.788 | 8.7785 | 8.7773 | 8.7702 | 8.7693 | 8.75 | 8.7403 | 8.7283 | 8.1682 | 8.1607 | 8.154 | 8.1376 | 8.1364 | 8.1368 | 8.1264 | 8.1189 | 8.1181 | 8.1124 | 8.1115 | 8.0947 | 8.0838 | 8.0673 | 8.5033 | 8.4946 | 8.4862 | 8.468 | 8.4618 | 8.4617 | 8.449 | 8.4394 | 8.4382 | 8.4311 | 8.4301 | 8.41 | 8.3994 | 8.3857
|  | ST FILLANS | LW |  |  |  | 0 | 8.8406 | 8.8246 | 8.808 | 8.7898 | 8.783 | 8.7755 | 8.7585 | 8.7554 | 8.7465 | 8.7445 | 8.7385 | 8.7148 | 8.6888 | 8.6599 | 8.1683 | 8.1518 | 8.1355 | 8.118 | 8.1147 | 8.1069 | 8.0902 | 8.0884 | 8.0818 | 8.0807 | 8.0764 | 8.0539 | 8.0249 | 7.9919 | 8.5036 | 8.4861 | 8.4679 | 8.4483 | 8.4404 | 8.4315 | 8.4123 | 8.4094 | 8.4007 | 8.3989 | 8.3931 | 8.3669 | 8.3359 | 8.3012
|  | ST FILLANS | ST |  |  |  | 0 | 8.8429 | 8.8386 | 8.8279 | 8.8179 | 8.8092 | 8.8003 | 8.7904 | 8.79 | 8.7931 | 8.7897 | 8.7826 | 8.7464 | 8.7146 | 8.6884 | 8.1705 | 8.1675 | 8.1575 | 8.1487 | 8.1415 | 8.1343 | 8.1262 | 8.1288 | 8.1317 | 8.1292 | 8.1242 | 8.0884 | 8.052 | 8.0179 | 8.5059 | 8.5019 | 8.4904 | 8.48 | 8.4712 | 8.4625 | 8.4529 | 8.4518 | 8.455 | 8.4515 | 8.4447 | 8.4046 | 8.3672 | 8.3357
|  | ST FILLANS | FS |  |  |  | 0 | 8.8448 | 8.8418 | 8.8372 | 8.832 | 8.8266 | 8.8206 | 8.8132 | 8.8047 | 8.8005 | 8.8034 | 8.7978 | 8.7812 | 8.7654 | 8.757 | 8.1713 | 8.169 | 8.1644 | 8.1593 | 8.1539 | 8.1479 | 8.1403 | 8.1323 | 8.1323 | 8.1341 | 8.1301 | 8.1184 | 8.1048 | 8.0889 | 8.5076 | 8.5047 | 8.4998 | 8.4943 | 8.4887 | 8.4824 | 8.4745 | 8.4658 | 8.4609 | 8.4634 | 8.458 | 8.4424 | 8.4278 | 8.4191
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | YES | 0.385 | 14.3476 | 14.0891 | 13.7987 | 12.9581 | 12.0333 | 10.7768 | 9.278 | 7.6567 | 5.72 | 4.1241 | 2.6117 | -1.421 | -1.305 | -2.5828 | 14.9841 | 14.7767 | 14.5369 | 14.0348 | 13.4697 | 12.7763 | 11.8362 | 10.7741 | 9.4721 | 8.3715 | 7.3162 | 4.6708 | 3.2851 | -2.517 | 14.1673 | 13.9126 | 13.5293 | 12.7412 | 11.8835 | 10.7011 | 9.2851 | 7.7756 | 6.0308 | 4.4977 | 3.0413 | -0.79702 | -0.72461 | -2.0203
|  | ST MACHAR | CT |  |  |  | 0.385 | 14.36 | 14.0895 | 13.7987 | 13.3121 | 12.4886 | 11.6382 | 10.4901 | 8.7649 | 7.3338 | 6.0722 | 4.9029 | 0.44793 | -0.64273 | -1.6549 | 14.9902 | 14.7783 | 14.5518 | 14.0348 | 13.4697 | 12.891 | 12.086 | 10.9714 | 10.0399 | 9.1598 | 8.3111 | 4.9733 | 3.2851 | 0.44611 | 14.1779 | 13.9154 | 13.6336 | 13.0372 | 12.2607 | 11.4608 | 10.3695 | 8.8164 | 7.5289 | 6.3421 | 5.2291 | 1.0833 | 0.10035 | -0.88748
|  | ST MACHAR | LW |  |  |  | 0.385 | 14.3476 | 14.0891 | 13.8065 | 12.9581 | 12.0333 | 10.7768 | 9.278 | 7.6567 | 5.72 | 4.1241 | 2.6117 | -1.421 | -1.305 | -2.5828 | 14.9841 | 14.7767 | 14.5369 | 14.0703 | 13.5462 | 12.7763 | 11.8362 | 10.7741 | 9.4721 | 8.3715 | 7.3162 | 4.6708 | 4.5992 | 3.4867 | 14.1673 | 13.9126 | 13.5293 | 12.7412 | 11.8835 | 10.7011 | 9.2851 | 7.7756 | 6.0308 | 4.4977 | 3.0413 | -0.79702 | -0.72461 | -2.0203
|  | ST MACHAR | ST |  |  |  | 0.385 | 14.4395 | 14.3392 | 14.2027 | 14.0334 | 13.8185 | 13.5624 | 13.2427 | 12.8183 | 12.2624 | 11.6917 | 10.9339 | 7.056 | 5.4371 | 4.1053 | 15.0525 | 14.9733 | 14.8614 | 14.7253 | 14.5549 | 14.3019 | 13.9519 | 13.5042 | 12.9378 | 12.3998 | 11.7578 | 7.9877 | 5.7443 | 3.0565 | 14.2554 | 14.1584 | 14.0238 | 13.8583 | 13.6495 | 13.4012 | 13.0912 | 12.6831 | 12.1049 | 11.5183 | 10.7994 | 6.9756 | 5.4799 | 4.3087
|  | ST MACHAR | FS |  |  |  | 0.385 | 14.4783 | 14.4055 | 14.3145 | 14.1971 | 14.0569 | 13.8869 | 13.6905 | 13.436 | 13.0633 | 12.584 | 12.0934 | 7.6508 | 3.5079 | 0.64833 | 15.0794 | 15.021 | 14.9473 | 14.8528 | 14.7258 | 14.5134 | 14.2149 | 13.8085 | 13.325 | 12.8591 | 12.3769 | 8.5731 | 3.5937 | -2.517 | 14.2913 | 14.2211 | 14.1326 | 14.0187 | 13.8827 | 13.7176 | 13.5264 | 13.2821 | 12.8208 | 12.3619 | 11.8931 | 7.8255 | 3.9316 | 1.2737
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 0.094 | -2.2392 | -2.3917 | -2.5669 | -2.7633 | -3.0033 | -3.2539 | -3.5654 | -3.7292 | -3.9145 | -4.1023 | -4.2332 | -4.7107 | -4.9453 | -5.1722 | -1.9541 | -2.0349 | -2.1143 | -2.1982 | -2.3167 | -2.4353 | -2.594 | -2.6885 | -2.7926 | -2.9179 | -2.9892 | -3.2489 | -3.375 | -3.6289 | -2.2302 | -2.3656 | -2.5116 | -2.6662 | -2.8705 | -3.0771 | -3.3465 | -3.4965 | -3.6909 | -3.8751 | -3.9786 | -4.3788 | -4.5581 | -4.7662
|  | ST MARYS | CT |  |  |  | 0.094 | -2.2392 | -2.3917 | -2.5669 | -2.7633 | -3.0033 | -3.2539 | -3.5654 | -3.7292 | -3.8821 | -4.03 | -4.1599 | -4.6155 | -4.8486 | -5.0531 | -1.9541 | -2.0349 | -2.1143 | -2.1982 | -2.3167 | -2.4353 | -2.594 | -2.6885 | -2.7819 | -2.8789 | -2.9678 | -3.2308 | -3.375 | -3.5593 | -2.2302 | -2.3656 | -2.5116 | -2.6662 | -2.8705 | -3.0771 | -3.3465 | -3.4965 | -3.6421 | -3.7903 | -3.9237 | -4.2941 | -4.4742 | -4.6656
|  | ST MARYS | LW |  |  |  | 0.094 | -2.2154 | -2.3448 | -2.523 | -2.7238 | -2.9506 | -3.224 | -3.5355 | -3.7001 | -3.9145 | -4.1023 | -4.2332 | -4.7107 | -4.9453 | -5.1722 | -1.9449 | -2.0172 | -2.0922 | -2.1746 | -2.2725 | -2.4065 | -2.5637 | -2.6549 | -2.7926 | -2.9179 | -2.9892 | -3.2489 | -3.3441 | -3.4535 | -2.2093 | -2.3299 | -2.4759 | -2.6379 | -2.8242 | -3.0585 | -3.3304 | -3.4788 | -3.6909 | -3.8751 | -3.9786 | -4.3788 | -4.5581 | -4.7662
|  | ST MARYS | ST |  |  |  | 0.094 | -2.1944 | -2.2965 | -2.4406 | -2.5993 | -2.7518 | -2.9193 | -3.0745 | -3.2199 | -3.3887 | -3.5621 | -3.7069 | -4.462 | -4.807 | -4.9966 | -1.9277 | -1.9738 | -2.0294 | -2.1011 | -2.1693 | -2.2506 | -2.3222 | -2.3991 | -2.4953 | -2.5958 | -2.6732 | -3.1424 | -3.3572 | -3.5236 | -2.1871 | -2.2734 | -2.3867 | -2.519 | -2.6425 | -2.7848 | -2.9076 | -3.0339 | -3.1878 | -3.3468 | -3.469 | -4.1395 | -4.4603 | -4.6454
|  | ST MARYS | FS |  |  |  | 0.094 | -2.1344 | -2.192 | -2.2447 | -2.289 | -2.3488 | -2.4012 | -2.4679 | -2.5694 | -2.6973 | -2.8191 | -2.9537 | -3.6683 | -4.3978 | -4.7136 | -1.9029 | -1.9345 | -1.9681 | -1.9913 | -2.0283 | -2.0571 | -2.1014 | -2.1444 | -2.2167 | -2.2823 | -2.3602 | -2.7963 | -3.2728 | -3.6289 | -2.1317 | -2.1875 | -2.2392 | -2.2789 | -2.3346 | -2.3812 | -2.4453 | -2.5252 | -2.64 | -2.7464 | -2.868 | -3.5068 | -4.103 | -4.3601
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 0.385 | 8.467 | 8.1846 | 7.7149 | 7.1207 | 6.4044 | 5.4747 | 4.6252 | 3.7795 | 2.7563 | 1.8116 | 0.93112 | -1.4665 | -1.6043 | -2.5703 | 12.0558 | 11.9088 | 11.6014 | 11.1596 | 10.7001 | 10.1818 | 9.6336 | 8.9743 | 8.3262 | 7.6503 | 7.0156 | 4.7161 | 1.6042 | -5.6753 | 10.7041 | 10.4113 | 9.9585 | 9.4281 | 8.8487 | 8.053 | 7.201 | 6.3623 | 5.375 | 4.4625 | 3.6107 | 1.3152 | 1.1712 | 0.20138
|  | ST NICHOLAS | CT |  |  |  | 0.385 | 8.5152 | 8.2703 | 7.9014 | 7.3649 | 6.7307 | 5.997 | 5.317 | 4.4257 | 3.6823 | 2.9461 | 2.2598 | -0.17476 | -0.85764 | -1.6896 | 12.0558 | 11.909 | 11.6014 | 11.1596 | 10.7001 | 10.1818 | 9.6336 | 8.9743 | 8.4146 | 7.8295 | 7.26 | 4.7161 | 2.735 | -0.78489 | 10.7432 | 10.4868 | 10.1201 | 9.6476 | 9.1465 | 8.4889 | 7.8061 | 6.9539 | 6.2539 | 5.5542 | 4.9034 | 2.618 | 2.002 | 1.2025
|  | ST NICHOLAS | LW |  |  |  | 0.385 | 8.467 | 8.1846 | 7.7149 | 7.1207 | 6.4044 | 5.4747 | 4.6252 | 3.7795 | 2.7563 | 1.8116 | 0.93112 | -1.4665 | -1.6043 | -2.5703 | 12.0573 | 11.9088 | 11.6365 | 11.2466 | 10.8255 | 10.2281 | 9.6396 | 9.0502 | 8.3262 | 7.6503 | 7.0156 | 5.3918 | 5.254 | 4.4263 | 10.7041 | 10.4113 | 9.9585 | 9.4281 | 8.8487 | 8.053 | 7.201 | 6.3623 | 5.375 | 4.4625 | 3.6107 | 1.3152 | 1.1712 | 0.20138
|  | ST NICHOLAS | ST |  |  |  | 0.385 | 8.5666 | 8.3992 | 8.2044 | 8.0134 | 7.81 | 7.5184 | 7.2916 | 7.0117 | 6.6684 | 6.2905 | 5.8426 | 3.6793 | 2.7399 | 1.9238 | 12.0819 | 11.9811 | 11.8595 | 11.6927 | 11.4499 | 11.1557 | 10.9034 | 10.5975 | 10.2254 | 9.8233 | 9.368 | 6.6486 | 4.3743 | 1.0247 | 10.768 | 10.6471 | 10.4598 | 10.2689 | 10.0645 | 9.8207 | 9.6472 | 9.4338 | 9.08 | 8.6938 | 8.2609 | 6.1379 | 5.2397 | 4.4959
|  | ST NICHOLAS | FS |  |  |  | 0.385 | 8.6783 | 8.585 | 8.4449 | 8.3064 | 8.1421 | 7.9743 | 7.7942 | 7.5591 | 7.2546 | 6.9514 | 6.6164 | 4.194 | 1.9289 | 0.30385 | 12.1167 | 12.0356 | 11.9354 | 11.8223 | 11.6013 | 11.3534 | 11.0683 | 10.745 | 10.3443 | 9.9417 | 9.5012 | 6.4458 | 1.6042 | -5.6753 | 10.797 | 10.723 | 10.6473 | 10.5416 | 10.377 | 10.207 | 10.0435 | 9.8573 | 9.6211 | 9.3587 | 9.0241 | 6.724 | 4.5857 | 3.0691
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0.179 | 0.40839 | 0.36779 | 0.30912 | 0.24542 | 0.19459 | 0.10995 | 0.020611 | -0.060288 | -0.12899 | -0.20363 | -0.27091 | -0.45961 | -0.57152 | -0.7025 | 0.52182 | 0.49368 | 0.45197 | 0.40348 | 0.37576 | 0.31513 | 0.25142 | 0.20117 | 0.16394 | 0.11582 | 0.072339 | -0.03579 | -0.11368 | -0.21266 | 0.39499 | 0.36173 | 0.31559 | 0.25867 | 0.21475 | 0.13365 | 0.048599 | -0.025014 | -0.084107 | -0.15442 | -0.2179 | -0.39796 | -0.51298 | -0.64899
|  | STOCKINISH | CT |  |  |  | 0.179 | 0.40839 | 0.37854 | 0.33445 | 0.2695 | 0.21463 | 0.1436 | 0.059815 | -0.017694 | -0.082009 | -0.12527 | -0.17921 | -0.38082 | -0.50789 | -0.59641 | 0.52224 | 0.51088 | 0.48611 | 0.43743 | 0.41052 | 0.36926 | 0.31771 | 0.26745 | 0.22599 | 0.20473 | 0.16655 | 0.05614 | -0.010729 | -0.083736 | 0.39505 | 0.37818 | 0.35114 | 0.29126 | 0.2459 | 0.18384 | 0.1092 | 0.037842 | -0.02158 | -0.061896 | -0.11347 | -0.30051 | -0.4143 | -0.49847
|  | STOCKINISH | LW |  |  |  | 0.179 | 0.4096 | 0.36779 | 0.30912 | 0.24542 | 0.19459 | 0.10995 | 0.020611 | -0.060288 | -0.12899 | -0.20363 | -0.27091 | -0.45961 | -0.57152 | -0.7025 | 0.52182 | 0.49368 | 0.45197 | 0.40348 | 0.37576 | 0.31513 | 0.25142 | 0.20117 | 0.16394 | 0.11582 | 0.072339 | -0.03579 | -0.11368 | -0.21266 | 0.39499 | 0.36173 | 0.31559 | 0.25867 | 0.21475 | 0.13365 | 0.048599 | -0.025014 | -0.084107 | -0.15442 | -0.2179 | -0.39796 | -0.51298 | -0.64899
|  | STOCKINISH | ST |  |  |  | 0.179 | 0.41746 | 0.40688 | 0.37481 | 0.34834 | 0.32733 | 0.30084 | 0.27122 | 0.25358 | 0.21654 | 0.19087 | 0.15378 | -0.076989 | -0.24789 | -0.39969 | 0.52462 | 0.52015 | 0.49399 | 0.47824 | 0.4654 | 0.44813 | 0.4254 | 0.41326 | 0.38331 | 0.36352 | 0.33449 | 0.16168 | 0.03994 | -0.074073 | 0.39965 | 0.39247 | 0.36427 | 0.3443 | 0.3273 | 0.30968 | 0.28802 | 0.2706 | 0.23386 | 0.20866 | 0.17252 | -0.057021 | -0.22324 | -0.35573
|  | STOCKINISH | FS |  |  |  | 0.179 | 0.42119 | 0.4097 | 0.39187 | 0.37734 | 0.36026 | 0.34547 | 0.32048 | 0.29033 | 0.26809 | 0.23425 | 0.20241 | 0.038626 | -0.14065 | -0.28171 | 0.52562 | 0.52241 | 0.50919 | 0.50154 | 0.4919 | 0.48222 | 0.46202 | 0.43879 | 0.42334 | 0.3968 | 0.37356 | 0.26366 | 0.14593 | 0.031823 | 0.40152 | 0.39591 | 0.3815 | 0.37105 | 0.35836 | 0.34573 | 0.32661 | 0.30693 | 0.28592 | 0.25241 | 0.22196 | 0.071718 | -0.084129 | -0.2067
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.32915 | 0.32603 | 0.32293 | 0.31946 | 0.31494 | 0.31032 | 0.066435 | -0.18012 | -0.16576 | -0.16569 | -0.17799 | -0.17195 | -0.17255 | -0.17316 | 0.30355 | 0.30074 | 0.29813 | 0.29524 | 0.29141 | 0.28765 | 0.01968 | -0.25539 | -0.24107 | -0.23963 | -0.25314 | -0.24312 | -0.24334 | -0.24686 | 0.32208 | 0.31899 | 0.31599 | 0.31263 | 0.30825 | 0.30389 | 0.062204 | -0.18631 | -0.17136 | -0.17081 | -0.1845 | -0.17548 | -0.17552 | -0.17617
|  | STONEFIELD | CT |  |  |  | 0 | 0.32917 | 0.32603 | 0.32293 | 0.31946 | 0.31494 | 0.31032 | 0.11485 | -0.10531 | -0.12563 | -0.15399 | -0.16478 | -0.16808 | -0.16866 | -0.16933 | 0.30355 | 0.30074 | 0.29813 | 0.29524 | 0.29141 | 0.28765 | 0.073722 | -0.17189 | -0.19711 | -0.22834 | -0.23975 | -0.24233 | -0.24329 | -0.24499 | 0.32208 | 0.31899 | 0.31599 | 0.31263 | 0.30825 | 0.30389 | 0.11016 | -0.11044 | -0.13131 | -0.15958 | -0.17005 | -0.17254 | -0.17303 | -0.17405
|  | STONEFIELD | LW |  |  |  | 0 | 0.32915 | 0.32632 | 0.32355 | 0.31985 | 0.31647 | 0.31067 | 0.066435 | -0.18012 | -0.16576 | -0.16569 | -0.16785 | -0.17195 | -0.17255 | -0.17316 | 0.30361 | 0.30098 | 0.29871 | 0.29562 | 0.29292 | 0.28797 | 0.01968 | -0.25539 | -0.24107 | -0.23963 | -0.24094 | -0.24312 | -0.24334 | -0.24397 | 0.32217 | 0.31925 | 0.31659 | 0.313 | 0.30975 | 0.30409 | 0.062204 | -0.18631 | -0.17136 | -0.17081 | -0.17254 | -0.17548 | -0.17552 | -0.17617
|  | STONEFIELD | ST |  |  |  | 0 | 0.33013 | 0.32897 | 0.32752 | 0.32574 | 0.32377 | 0.32146 | 0.12714 | -0.090039 | -0.13031 | -0.16117 | -0.17799 | -0.16869 | -0.17097 | -0.17129 | 0.30445 | 0.30344 | 0.3022 | 0.30065 | 0.29891 | 0.29684 | 0.084425 | -0.15817 | -0.20214 | -0.23554 | -0.25314 | -0.24087 | -0.24237 | -0.24349 | 0.32308 | 0.3219 | 0.3205 | 0.31878 | 0.31686 | 0.3146 | 0.12185 | -0.096755 | -0.13705 | -0.16786 | -0.1845 | -0.17332 | -0.17484 | -0.17487
|  | STONEFIELD | FS |  |  |  | 0 | 0.33037 | 0.32956 | 0.32862 | 0.32746 | 0.3262 | 0.32471 | 0.20052 | 0.066156 | 0.036954 | -0.0019753 | -0.04359 | -0.15985 | -0.16834 | -0.17104 | 0.30469 | 0.30387 | 0.30297 | 0.30185 | 0.30065 | 0.29922 | 0.16514 | 0.015015 | -0.017047 | -0.059949 | -0.10578 | -0.23558 | -0.24315 | -0.24686 | 0.32346 | 0.32255 | 0.32164 | 0.32049 | 0.31925 | 0.31779 | 0.19439 | 0.059994 | 0.030753 | -0.0082825 | -0.050007 | -0.16624 | -0.17303 | -0.17478
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 2.414 | 9.3988 | 9.0229 | 8.3383 | 7.5813 | 6.7922 | 5.8242 | 4.524 | 3.4633 | 2.0566 | 1.1403 | 0.30747 | -2.136 | -3.5702 | -4.7019 | 11.0411 | 10.7955 | 10.4524 | 10.0585 | 9.6438 | 9.1676 | 8.39 | 7.7917 | 6.8476 | 6.3113 | 5.8189 | 4.539 | 3.656 | 2.618 | 10.0719 | 9.706 | 9.1266 | 8.4543 | 7.7267 | 6.8713 | 5.654 | 4.7501 | 3.4066 | 2.5012 | 1.6752 | -0.57492 | -1.4901 | -2.4922
|  | STONEHAVEN | CT |  |  |  | 2.414 | 9.3988 | 9.0239 | 8.3553 | 7.6093 | 6.7922 | 5.8594 | 4.5908 | 3.5807 | 2.4211 | 1.6148 | 0.91015 | -1.9433 | -3.5702 | -4.7019 | 11.0411 | 10.7955 | 10.4524 | 10.0585 | 9.6438 | 9.1676 | 8.3936 | 7.8216 | 7.0629 | 6.5696 | 6.1321 | 4.5656 | 3.656 | 2.618 | 10.0719 | 9.706 | 9.1266 | 8.4565 | 7.7267 | 6.8936 | 5.7243 | 4.8652 | 3.8083 | 3.0344 | 2.35 | -0.19217 | -1.4901 | -2.4922
|  | STONEHAVEN | LW |  |  |  | 2.414 | 9.4113 | 9.0229 | 8.3383 | 7.5813 | 6.8138 | 5.8242 | 4.524 | 3.4633 | 2.0566 | 1.1403 | 0.30747 | -2.136 | -3.0556 | -4.0567 | 11.057 | 10.8074 | 10.4804 | 10.0979 | 9.7405 | 9.2111 | 8.39 | 7.7917 | 6.8476 | 6.3113 | 5.8189 | 4.539 | 4.1669 | 3.6257 | 10.0882 | 9.7101 | 9.1311 | 8.4543 | 7.7904 | 6.8713 | 5.654 | 4.7501 | 3.4066 | 2.5012 | 1.6752 | -0.57492 | -1.31 | -2.2502
|  | STONEHAVEN | ST |  |  |  | 2.414 | 9.5296 | 9.3028 | 9.0141 | 8.7584 | 8.5163 | 8.2218 | 7.7481 | 7.1486 | 6.4381 | 6.0056 | 5.8623 | 3.5423 | 1.8623 | 0.17286 | 11.1219 | 10.9881 | 10.819 | 10.6575 | 10.5044 | 10.3069 | 9.932 | 9.4371 | 8.8389 | 8.4865 | 8.3996 | 6.723 | 5.6738 | 4.5283 | 10.2049 | 10.0067 | 9.7541 | 9.5116 | 9.2878 | 8.9991 | 8.5518 | 7.9742 | 7.2759 | 6.812 | 6.6961 | 4.3369 | 2.9154 | 1.5944
|  | STONEHAVEN | FS |  |  |  | 2.414 | 9.594 | 9.4283 | 9.2222 | 9.0267 | 8.8427 | 8.6248 | 8.2638 | 7.7845 | 7.1951 | 6.7779 | 6.3154 | 3.9634 | 1.406 | -0.79225 | 11.147 | 11.0385 | 10.9147 | 10.7877 | 10.6675 | 10.517 | 10.224 | 9.87 | 9.413 | 9.1072 | 8.7624 | 7.1214 | 5.1442 | 3.0285 | 10.2554 | 10.1067 | 9.9274 | 9.7453 | 9.5776 | 9.3661 | 9.0221 | 8.5884 | 8.036 | 7.63 | 7.1794 | 4.9862 | 2.6252 | 0.76641
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | -2.4259 | -2.4267 | -2.4276 | -2.4289 | -2.4301 | -2.4319 | -2.434 | -2.4357 | -2.4378 | -2.4396 | -2.4412 | -2.444 | -2.4449 | -2.446 | -2.1521 | -2.1531 | -2.1543 | -2.1556 | -2.1573 | -2.159 | -2.1612 | -2.1634 | -2.1654 | -2.1675 | -2.1697 | -2.1844 | -2.2176 | -2.2729 | -2.36 | -2.3609 | -2.3618 | -2.363 | -2.3643 | -2.3662 | -2.3682 | -2.37 | -2.3722 | -2.3741 | -2.3757 | -2.3786 | -2.3794 | -2.3804
|  | STONEYHILL | CT |  |  |  | 0 | -2.4259 | -2.4267 | -2.4276 | -2.4287 | -2.4301 | -2.4316 | -2.4334 | -2.4351 | -2.4364 | -2.4378 | -2.4391 | -2.442 | -2.4428 | -2.4437 | -2.1521 | -2.1531 | -2.1543 | -2.1556 | -2.1573 | -2.159 | -2.1612 | -2.1634 | -2.1654 | -2.1675 | -2.1697 | -2.1813 | -2.1961 | -2.222 | -2.36 | -2.3608 | -2.3618 | -2.3629 | -2.3643 | -2.3658 | -2.3677 | -2.3694 | -2.3708 | -2.3722 | -2.3735 | -2.3764 | -2.3772 | -2.378
|  | STONEYHILL | LW |  |  |  | 0 | -2.4259 | -2.4267 | -2.4276 | -2.4289 | -2.4301 | -2.4319 | -2.434 | -2.4357 | -2.4378 | -2.4396 | -2.4412 | -2.444 | -2.4449 | -2.446 | -2.1519 | -2.1526 | -2.1533 | -2.1544 | -2.1554 | -2.1569 | -2.1587 | -2.1603 | -2.1622 | -2.1639 | -2.1653 | -2.1677 | -2.1684 | -2.1692 | -2.36 | -2.3609 | -2.3618 | -2.363 | -2.3643 | -2.3662 | -2.3682 | -2.37 | -2.3722 | -2.3741 | -2.3757 | -2.3786 | -2.3794 | -2.3804
|  | STONEYHILL | ST |  |  |  | 0 | -2.4257 | -2.4261 | -2.4266 | -2.4272 | -2.4279 | -2.4288 | -2.4296 | -2.4306 | -2.4318 | -2.4331 | -2.4344 | -2.4409 | -2.443 | -2.4444 | -2.1519 | -2.1526 | -2.1534 | -2.1543 | -2.1553 | -2.1565 | -2.1578 | -2.1593 | -2.1612 | -2.1631 | -2.1653 | -2.1802 | -2.1962 | -2.2228 | -2.3598 | -2.3602 | -2.3608 | -2.3614 | -2.3621 | -2.3629 | -2.3638 | -2.3648 | -2.3661 | -2.3674 | -2.3688 | -2.3755 | -2.3777 | -2.3791
|  | STONEYHILL | FS |  |  |  | 0 | -2.4255 | -2.4258 | -2.4262 | -2.4266 | -2.427 | -2.4275 | -2.4281 | -2.4288 | -2.4296 | -2.4305 | -2.4314 | -2.4364 | -2.4409 | -2.4428 | -2.152 | -2.1526 | -2.1534 | -2.1543 | -2.1554 | -2.1566 | -2.1581 | -2.1601 | -2.1624 | -2.1647 | -2.1672 | -2.1844 | -2.2176 | -2.2729 | -2.3597 | -2.36 | -2.3603 | -2.3607 | -2.3611 | -2.3616 | -2.3622 | -2.3629 | -2.3638 | -2.3647 | -2.3656 | -2.3708 | -2.3755 | -2.3775
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 2.834 | 12.6795 | 10.677 | 8.4384 | 6.1231 | 3.9985 | 1.3678 | -2.0291 | -3.1447 | -4.0398 | -4.9297 | -5.9379 | -10.9677 | -16.6377 | -22.4856 | 13.8135 | 11.473 | 8.8496 | 6.4395 | 4.4638 | 1.786 | -1.683 | -2.3732 | -3.0525 | -3.7853 | -4.6277 | -9.4662 | -15.9929 | -23.0265 | 11.6942 | 9.2909 | 6.6266 | 4.0749 | 1.797 | -1.159 | -4.9765 | -5.9705 | -6.7724 | -7.5864 | -8.5061 | -13.8664 | -20.6739 | -27.8938
|  | STONEYWOOD T1&T2 | CT |  |  |  | 2.834 | 12.7147 | 12.3447 | 11.884 | 9.7476 | 8.5449 | 7.1817 | 4.8762 | 3.7674 | 2.7231 | 1.758 | 0.67369 | -3.1756 | -5.8247 | -8.0397 | 13.8374 | 13.5322 | 13.1541 | 10.7204 | 9.796 | 8.7547 | 6.635 | 5.952 | 5.1998 | 4.4835 | 3.5941 | 0.72282 | -1.9098 | -4.7647 | 11.7257 | 11.3597 | 10.9271 | 8.4136 | 7.3619 | 5.9816 | 3.5454 | 2.5496 | 1.5435 | 0.61217 | -0.44119 | -4.2235 | -7.068 | -9.68
|  | STONEYWOOD T1&T2 | LW |  |  |  | 2.834 | 12.6795 | 10.677 | 8.4384 | 6.1231 | 3.9985 | 1.3678 | -2.0291 | -3.1447 | -4.0398 | -4.9297 | -5.9379 | -10.9677 | -16.6377 | -22.4856 | 13.8135 | 11.473 | 8.8496 | 6.4395 | 4.4638 | 1.786 | -1.683 | -2.3732 | -3.0525 | -3.7853 | -4.6277 | -9.4662 | -15.9929 | -23.0265 | 11.6942 | 9.2909 | 6.6266 | 4.0749 | 1.797 | -1.159 | -4.9765 | -5.9705 | -6.7724 | -7.5864 | -8.5061 | -13.8664 | -20.6739 | -27.8938
|  | STONEYWOOD T1&T2 | ST |  |  |  | 2.834 | 12.7686 | 12.5266 | 11.1251 | 10.1353 | 9.2569 | 8.7763 | 8.1359 | 7.3846 | 6.6595 | 5.9053 | 5.1687 | -2.7932 | -9.7829 | -15.6588 | 13.8792 | 13.6741 | 12.056 | 10.9636 | 10.0491 | 9.6123 | 9.0521 | 8.3429 | 7.5736 | 6.8262 | 6.2019 | -1.8863 | -9.7778 | -16.6115 | 11.7778 | 11.5356 | 9.8889 | 8.7436 | 7.7729 | 7.2745 | 6.6418 | 5.893 | 5.0829 | 4.2604 | 3.5386 | -5.2278 | -13.4029 | -20.3805
|  | STONEYWOOD T1&T2 | FS |  |  |  | 2.834 | 12.8183 | 12.6741 | 12.1274 | 11.6203 | 10.9027 | 10.2978 | 9.3508 | 8.6285 | 7.7541 | 6.8716 | 6.3442 | 3.7358 | 0.89371 | -1.9373 | 13.9136 | 13.8126 | 13.2279 | 12.7024 | 11.9454 | 11.3034 | 10.3004 | 9.5598 | 8.6895 | 7.8087 | 7.3856 | 5.2563 | 3.2186 | 0.82217 | 11.8229 | 11.6919 | 11.0861 | 10.5201 | 9.7209 | 9.0363 | 7.9666 | 7.1653 | 6.2501 | 5.3402 | 4.8817 | 2.3178 | -0.25306 | -3.0537
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | YES | YES | 0.095 | 8.7421 | 8.6997 | 8.6326 | 8.5555 | 8.475 | 8.3592 | 8.234 | 8.1115 | 7.9831 | 7.8573 | 7.7412 | 7.4382 | 7.3802 | 7.2391 | 5.9188 | 5.8843 | 5.8353 | 5.7823 | 5.7299 | 5.6473 | 5.5575 | 5.4786 | 5.3932 | 5.3071 | 5.227 | 5.0255 | 4.8996 | 4.405 | -6.6437 | -6.681 | -6.7335 | -6.7921 | -6.8488 | -6.9358 | -7.0373 | -7.1248 | -7.2252 | -7.3226 | -7.4136 | -7.6467 | -7.7168 | -7.7955
|  | STONEYWOOD T3 | CT |  |  |  | 0.095 | 8.7441 | 8.7141 | 8.6644 | 8.5864 | 8.5088 | 8.4341 | 8.3189 | 8.2072 | 8.1091 | 8.0109 | 7.9222 | 7.5999 | 7.49 | 7.389 | 5.9217 | 5.8961 | 5.8614 | 5.8009 | 5.7471 | 5.6969 | 5.6123 | 5.5369 | 5.4684 | 5.3965 | 5.3285 | 5.0704 | 4.8996 | 4.6252 | -6.6326 | -6.6613 | -6.7013 | -6.7771 | -6.8312 | -6.8865 | -6.9711 | -7.0496 | -7.1154 | -7.18 | -7.2368 | -7.4089 | -7.4575 | -7.4983
|  | STONEYWOOD T3 | LW |  |  |  | 0.095 | 8.7421 | 8.6997 | 8.6326 | 8.5555 | 8.475 | 8.3592 | 8.234 | 8.1115 | 7.9831 | 7.8573 | 7.7412 | 7.4382 | 7.3802 | 7.2391 | 5.9234 | 5.8843 | 5.8353 | 5.7823 | 5.7299 | 5.6473 | 5.5575 | 5.4786 | 5.3932 | 5.3071 | 5.227 | 5.0255 | 4.9582 | 4.8249 | -6.6358 | -6.681 | -6.7335 | -6.7921 | -6.8488 | -6.9358 | -7.0373 | -7.1248 | -7.2252 | -7.3226 | -7.4136 | -7.6467 | -7.7168 | -7.7955
|  | STONEYWOOD T3 | ST |  |  |  | 0.095 | 8.7452 | 8.7426 | 8.7252 | 8.7044 | 8.6789 | 8.6516 | 8.6183 | 8.5741 | 8.5206 | 8.459 | 8.3908 | 7.9925 | 7.8207 | 7.7079 | 5.9188 | 5.9181 | 5.8969 | 5.8739 | 5.8479 | 5.8229 | 5.7963 | 5.7591 | 5.7217 | 5.6739 | 5.6227 | 5.2956 | 5.0759 | 4.7813 | -6.6437 | -6.6347 | -6.6585 | -6.6824 | -6.7083 | -6.7354 | -6.7672 | -6.8088 | -6.8597 | -6.9173 | -6.9806 | -7.358 | -7.522 | -7.6147
|  | STONEYWOOD T3 | FS |  |  |  | 0.095 | 8.7504 | 8.7514 | 8.7353 | 8.7186 | 8.6999 | 8.6766 | 8.6448 | 8.616 | 8.5726 | 8.5282 | 8.4975 | 8.1792 | 7.874 | 7.6513 | 5.922 | 5.9231 | 5.9072 | 5.8904 | 5.8703 | 5.8461 | 5.8119 | 5.7797 | 5.7351 | 5.6894 | 5.6555 | 5.3548 | 4.9508 | 4.405 | -6.6393 | -6.6282 | -6.6418 | -6.657 | -6.6751 | -6.6964 | -6.7245 | -6.7524 | -6.7905 | -6.8297 | -6.8638 | -7.1291 | -7.3829 | -7.5622
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.137 | 0.14521 | 0.12483 | 0.089745 | 0.055402 | 0.0070424 | -0.028017 | -0.088757 | -0.11866 | -0.1478 | -0.18821 | -0.20113 | -0.2722 | -0.29329 | -0.32981 | 0.45579 | 0.44586 | 0.43006 | 0.41365 | 0.39243 | 0.3757 | 0.34933 | 0.33875 | 0.32828 | 0.31751 | 0.31581 | 0.27375 | 0.25743 | 0.21727 | 0.31731 | 0.30497 | 0.2833 | 0.24967 | 0.20295 | 0.16893 | 0.11033 | 0.081126 | 0.053014 | 0.014215 | 0.00080741 | -0.068827 | -0.090365 | -0.12613
|  | STRACHUR | CT |  |  |  | 0.137 | 0.14521 | 0.12483 | 0.089745 | 0.055402 | 0.0070424 | -0.028017 | -0.088757 | -0.11866 | -0.1478 | -0.17925 | -0.1837 | -0.2483 | -0.26947 | -0.29937 | 0.45579 | 0.44586 | 0.43006 | 0.41365 | 0.39243 | 0.3757 | 0.34933 | 0.33875 | 0.32828 | 0.31751 | 0.31581 | 0.28077 | 0.25743 | 0.21727 | 0.31731 | 0.30497 | 0.2833 | 0.24967 | 0.20295 | 0.16893 | 0.11033 | 0.081126 | 0.053014 | 0.022735 | 0.017674 | -0.045164 | -0.06672 | -0.096654
|  | STRACHUR | LW |  |  |  | 0.137 | 0.14554 | 0.1306 | 0.10104 | 0.069033 | 0.03186 | -0.007938 | -0.065484 | -0.096299 | -0.14567 | -0.18821 | -0.20113 | -0.2722 | -0.29329 | -0.32981 | 0.45738 | 0.44891 | 0.43584 | 0.42158 | 0.40521 | 0.3882 | 0.36456 | 0.35374 | 0.33664 | 0.32193 | 0.31698 | 0.27375 | 0.26414 | 0.24104 | 0.31777 | 0.30681 | 0.2943 | 0.26306 | 0.22706 | 0.18858 | 0.13309 | 0.10289 | 0.055297 | 0.014215 | 0.00080741 | -0.068827 | -0.090365 | -0.12613
|  | STRACHUR | ST |  |  |  | 0.137 | 0.14592 | 0.14479 | 0.13279 | 0.11811 | 0.10126 | 0.086233 | 0.06335 | 0.037896 | 0.021137 | -0.0090929 | -0.030286 | -0.13957 | -0.16579 | -0.16711 | 0.45702 | 0.45381 | 0.44774 | 0.44126 | 0.43391 | 0.42712 | 0.41763 | 0.40727 | 0.40021 | 0.38806 | 0.3792 | 0.33177 | 0.309 | 0.28483 | 0.31988 | 0.31799 | 0.3132 | 0.30748 | 0.29358 | 0.27846 | 0.25605 | 0.23138 | 0.21506 | 0.18582 | 0.1648 | 0.056696 | 0.029187 | 0.025553
|  | STRACHUR | FS |  |  |  | 0.137 | 0.14794 | 0.14468 | 0.1463 | 0.14415 | 0.13588 | 0.12723 | 0.12081 | 0.10225 | 0.079457 | 0.069777 | 0.047134 | -0.068509 | -0.15713 | -0.19278 | 0.46056 | 0.45781 | 0.45684 | 0.45436 | 0.45046 | 0.44697 | 0.44403 | 0.43583 | 0.42607 | 0.42116 | 0.41139 | 0.35954 | 0.29576 | 0.22461 | 0.32162 | 0.31728 | 0.31762 | 0.31385 | 0.30658 | 0.30066 | 0.29759 | 0.28722 | 0.27163 | 0.26207 | 0.24009 | 0.12709 | 0.039668 | 0.0033368
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0.073 | 0.12286 | 0.099219 | 0.041676 | -0.034717 | -0.099841 | -0.1938 | -0.29205 | -0.34526 | -0.40326 | -0.43586 | -0.47873 | -0.61789 | -0.72801 | -0.85803 | 0.43315 | 0.40675 | 0.37968 | 0.33901 | 0.30548 | 0.24423 | 0.17928 | 0.14142 | 0.09719 | 0.076745 | 0.043822 | -0.052578 | -0.12823 | -0.22869 | 0.38084 | 0.34056 | 0.28949 | 0.22472 | 0.16354 | 0.072655 | -0.023698 | -0.073977 | -0.12917 | -0.15963 | -0.20066 | -0.33628 | -0.44805 | -0.58084
|  | STRATHDON | CT |  |  |  | 0.073 | 0.1234 | 0.10987 | 0.060844 | -0.014203 | -0.076947 | -0.15445 | -0.24285 | -0.2953 | -0.33766 | -0.3617 | -0.3958 | -0.52189 | -0.59988 | -0.68725 | 0.43373 | 0.42446 | 0.4162 | 0.37148 | 0.34184 | 0.29986 | 0.24782 | 0.20863 | 0.17619 | 0.15939 | 0.12924 | 0.040404 | -0.013633 | -0.089494 | 0.38084 | 0.35355 | 0.32082 | 0.25354 | 0.19661 | 0.12495 | 0.041173 | -0.0085317 | -0.049133 | -0.07201 | -0.1054 | -0.22483 | -0.29772 | -0.37997
|  | STRATHDON | LW |  |  |  | 0.073 | 0.12286 | 0.099219 | 0.041676 | -0.034717 | -0.099841 | -0.1938 | -0.29205 | -0.34526 | -0.40326 | -0.43586 | -0.47873 | -0.61789 | -0.72801 | -0.85803 | 0.43315 | 0.40675 | 0.37968 | 0.33901 | 0.30548 | 0.24423 | 0.17928 | 0.14142 | 0.09719 | 0.076745 | 0.043822 | -0.052578 | -0.12823 | -0.22869 | 0.38229 | 0.34056 | 0.28949 | 0.22472 | 0.16354 | 0.072655 | -0.023698 | -0.073977 | -0.12917 | -0.15963 | -0.20066 | -0.33628 | -0.44805 | -0.58084
|  | STRATHDON | ST |  |  |  | 0.073 | 0.12681 | 0.12123 | 0.087569 | 0.04061 | -0.0020655 | -0.048097 | -0.095828 | -0.13071 | -0.17936 | -0.21929 | -0.26716 | -0.49244 | -0.62606 | -0.72862 | 0.43677 | 0.43186 | 0.41622 | 0.4023 | 0.38347 | 0.35848 | 0.33136 | 0.3132 | 0.28078 | 0.25682 | 0.22556 | 0.050653 | -0.06152 | -0.16618 | 0.38797 | 0.3715 | 0.33688 | 0.29656 | 0.26046 | 0.22268 | 0.17866 | 0.14655 | 0.10073 | 0.063745 | 0.019282 | -0.20224 | -0.3388 | -0.44506
|  | STRATHDON | FS |  |  |  | 0.073 | 0.1281 | 0.12441 | 0.11834 | 0.1115 | 0.10278 | 0.092077 | 0.066472 | 0.029823 | 0.00042123 | -0.038721 | -0.075391 | -0.25128 | -0.44244 | -0.53289 | 0.43761 | 0.43455 | 0.42836 | 0.42144 | 0.41272 | 0.40416 | 0.3905 | 0.37363 | 0.35521 | 0.32774 | 0.30369 | 0.18969 | 0.060162 | -0.041196 | 0.39058 | 0.38496 | 0.37587 | 0.36256 | 0.34683 | 0.33129 | 0.30932 | 0.28233 | 0.25573 | 0.22448 | 0.19164 | 0.030103 | -0.14419 | -0.22749
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.205 | 8.5386 | 8.3848 | 8.1741 | 7.9159 | 7.6107 | 7.3331 | 6.8704 | 6.5321 | 6.1406 | 5.8571 | 5.6615 | 5.0786 | 4.7204 | 4.4344 | 7.0991 | 7.0155 | 6.9122 | 6.7805 | 6.6201 | 6.4886 | 6.2224 | 5.979 | 5.6997 | 5.4952 | 5.3581 | 5.0437 | 4.8593 | 4.6082 | 8.8018 | 8.6595 | 8.4598 | 8.2145 | 7.9295 | 7.6575 | 7.2336 | 6.9163 | 6.5569 | 6.2908 | 6.1054 | 5.5831 | 5.2852 | 5.0345
|  | STRICHEN | CT |  |  |  | 0.205 | 8.5386 | 8.3848 | 8.1741 | 7.9159 | 7.6107 | 7.3331 | 6.8704 | 6.5321 | 6.206 | 5.9349 | 5.7676 | 5.1712 | 4.8194 | 4.5421 | 7.0991 | 7.0155 | 6.9122 | 6.7805 | 6.6201 | 6.4886 | 6.2224 | 5.979 | 5.766 | 5.562 | 5.4313 | 5.0607 | 4.8593 | 4.6082 | 8.8018 | 8.6595 | 8.4598 | 8.2145 | 7.9295 | 7.6575 | 7.2336 | 6.9163 | 6.625 | 6.372 | 6.2125 | 5.6771 | 5.3838 | 5.1447
|  | STRICHEN | LW |  |  |  | 0.205 | 8.5647 | 8.4103 | 8.2032 | 7.9387 | 7.6544 | 7.3592 | 6.8985 | 6.5712 | 6.1406 | 5.8571 | 5.6615 | 5.0786 | 4.7204 | 4.4344 | 7.1135 | 7.0264 | 6.9298 | 6.7965 | 6.6553 | 6.5069 | 6.2246 | 6.0173 | 5.6997 | 5.4952 | 5.3581 | 5.0437 | 4.9121 | 4.7748 | 8.8281 | 8.689 | 8.493 | 8.2461 | 7.9789 | 7.6948 | 7.2569 | 6.9605 | 6.5569 | 6.2908 | 6.1054 | 5.5831 | 5.2852 | 5.0345
|  | STRICHEN | ST |  |  |  | 0.205 | 8.5895 | 8.4819 | 8.3322 | 8.1638 | 8.0088 | 7.8328 | 7.5827 | 7.3082 | 6.9754 | 6.6875 | 6.4735 | 5.6789 | 5.284 | 5.0594 | 7.1299 | 7.0779 | 7.0078 | 6.9225 | 6.8495 | 6.7565 | 6.5923 | 6.4055 | 6.1861 | 5.9896 | 5.8483 | 5.2977 | 5.0324 | 4.7966 | 8.8483 | 8.7462 | 8.605 | 8.4489 | 8.3031 | 8.1406 | 7.8939 | 7.636 | 7.3335 | 7.0702 | 6.8725 | 6.136 | 5.7878 | 5.5923
|  | STRICHEN | FS |  |  |  | 0.205 | 8.6539 | 8.5713 | 8.5087 | 8.4356 | 8.3483 | 8.2838 | 8.1452 | 7.9573 | 7.7085 | 7.5403 | 7.355 | 6.4666 | 5.6847 | 5.3545 | 7.1549 | 7.108 | 7.072 | 7.0281 | 6.9725 | 6.9341 | 6.8275 | 6.6989 | 6.5174 | 6.4043 | 6.2788 | 5.6639 | 5.0865 | 4.645 | 8.9127 | 8.8381 | 8.784 | 8.7226 | 8.6497 | 8.5943 | 8.4647 | 8.2844 | 8.0469 | 7.8819 | 7.7113 | 6.8916 | 6.1622 | 5.8489
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 0.079 | 1.7346 | 1.0889 | 0.38396 | -0.38485 | -1.1646 | -1.6337 | -2.2402 | -2.7782 | -3.163 | -3.5654 | -3.9252 | -4.8115 | -5.2398 | -5.6878 | 3.2543 | 2.7603 | 2.2619 | 1.7517 | 1.2399 | 1.0168 | 0.69656 | 0.32218 | 0.10462 | -0.16272 | -0.40553 | -0.88891 | -1.1311 | -1.5684 | 2.7978 | 2.2454 | 1.6242 | 0.90041 | 0.16529 | -0.27653 | -0.84265 | -1.3416 | -1.6731 | -2.0282 | -2.3439 | -3.1465 | -3.5597 | -3.963
|  | STROMNESS | CT |  |  |  | 0.079 | 1.8651 | 1.2712 | 0.62479 | -0.15934 | -1.0261 | -1.5433 | -2.2146 | -2.7498 | -3.067 | -3.4123 | -3.7094 | -4.6295 | -5.0663 | -5.4679 | 3.3939 | 2.9721 | 2.5309 | 1.9911 | 1.3846 | 1.0981 | 0.7122 | 0.3348 | 0.14344 | -0.09306 | -0.30381 | -0.8563 | -1.1311 | -1.5007 | 2.9129 | 2.4036 | 1.854 | 1.1146 | 0.30183 | -0.19288 | -0.8221 | -1.3155 | -1.5982 | -1.9045 | -2.1632 | -2.9936 | -3.4141 | -3.7842
|  | STROMNESS | LW |  |  |  | 0.079 | 1.7346 | 1.0889 | 0.38396 | -0.38485 | -1.1646 | -1.6337 | -2.2402 | -2.7782 | -3.163 | -3.5654 | -3.9252 | -4.8115 | -5.2398 | -5.6878 | 3.2543 | 2.7603 | 2.2619 | 1.7517 | 1.2399 | 1.0168 | 0.69656 | 0.32218 | 0.10462 | -0.16272 | -0.40553 | -0.88891 | -1.0609 | -1.2842 | 2.7978 | 2.2454 | 1.6242 | 0.90041 | 0.16529 | -0.27653 | -0.84265 | -1.3416 | -1.6731 | -2.0282 | -2.3439 | -3.1465 | -3.5597 | -3.963
|  | STROMNESS | ST |  |  |  | 0.079 | 1.9443 | 1.4409 | 0.83999 | 0.14647 | -0.55741 | -0.93846 | -1.3684 | -1.8187 | -2.1529 | -2.5325 | -2.9123 | -4.2591 | -4.8734 | -5.2395 | 3.4341 | 3.0736 | 2.6635 | 2.1643 | 1.6301 | 1.408 | 1.14 | 0.81555 | 0.61962 | 0.38154 | 0.14795 | -0.68122 | -1.0483 | -1.3771 | 2.982 | 2.5688 | 2.0418 | 1.387 | 0.72089 | 0.35818 | -0.048977 | -0.48053 | -0.78751 | -1.1391 | -1.4878 | -2.7019 | -3.2861 | -3.6206
|  | STROMNESS | FS |  |  |  | 0.079 | 2.2804 | 1.9093 | 1.5655 | 1.1457 | 0.6771 | 0.48952 | 0.27849 | -0.096436 | -0.39704 | -0.70481 | -1.0716 | -2.7862 | -4.1475 | -4.6958 | 3.6584 | 3.3885 | 3.1183 | 2.749 | 2.3251 | 2.1821 | 2.0243 | 1.7743 | 1.6116 | 1.4098 | 1.1731 | 0.019508 | -0.89782 | -1.5684 | 3.2558 | 2.9488 | 2.6572 | 2.3008 | 1.8991 | 1.7426 | 1.5473 | 1.1925 | 0.91492 | 0.62193 | 0.28026 | -1.3026 | -2.569 | -3.0924
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0.012 | 0.62591 | 0.60603 | 0.58076 | 0.5504 | 0.51892 | 0.48057 | 0.44382 | 0.41275 | 0.38785 | 0.36938 | 0.34484 | 0.28038 | 0.24879 | 0.22125 | 0.75239 | 0.74334 | 0.7309 | 0.71593 | 0.70119 | 0.68097 | 0.66653 | 0.64383 | 0.62565 | 0.61555 | 0.59784 | 0.56095 | 0.54619 | 0.51083 | 0.65888 | 0.63764 | 0.61601 | 0.58996 | 0.56346 | 0.52941 | 0.50061 | 0.46859 | 0.44146 | 0.42465 | 0.39963 | 0.34413 | 0.32087 | 0.2995
|  | STRONSAY | CT |  |  |  | 0.012 | 0.62817 | 0.60603 | 0.58076 | 0.5504 | 0.51892 | 0.48057 | 0.44382 | 0.41275 | 0.38888 | 0.37508 | 0.35529 | 0.28694 | 0.2566 | 0.23084 | 0.75684 | 0.74334 | 0.7309 | 0.71593 | 0.70119 | 0.68097 | 0.66653 | 0.64383 | 0.62667 | 0.61883 | 0.60271 | 0.56095 | 0.54619 | 0.52248 | 0.65888 | 0.63764 | 0.61601 | 0.58996 | 0.56346 | 0.52941 | 0.50061 | 0.46859 | 0.44424 | 0.43136 | 0.40977 | 0.347 | 0.32435 | 0.30471
|  | STRONSAY | LW |  |  |  | 0.012 | 0.63193 | 0.6136 | 0.58878 | 0.55774 | 0.5295 | 0.48756 | 0.45136 | 0.42126 | 0.38785 | 0.36938 | 0.34484 | 0.28038 | 0.24879 | 0.22125 | 0.75876 | 0.7472 | 0.73618 | 0.72051 | 0.70982 | 0.68604 | 0.67182 | 0.65088 | 0.62565 | 0.61555 | 0.59784 | 0.56444 | 0.55408 | 0.54355 | 0.66251 | 0.6442 | 0.62353 | 0.59616 | 0.57409 | 0.53542 | 0.50682 | 0.4765 | 0.44146 | 0.42465 | 0.39963 | 0.34413 | 0.32087 | 0.2995
|  | STRONSAY | ST |  |  |  | 0.012 | 0.62591 | 0.62108 | 0.59956 | 0.57839 | 0.55721 | 0.53369 | 0.50697 | 0.48833 | 0.46131 | 0.44476 | 0.41748 | 0.30781 | 0.26155 | 0.23704 | 0.75239 | 0.75435 | 0.74448 | 0.73508 | 0.72592 | 0.71429 | 0.69901 | 0.68984 | 0.67149 | 0.66594 | 0.64793 | 0.57568 | 0.55065 | 0.52678 | 0.65957 | 0.65324 | 0.63519 | 0.61763 | 0.60037 | 0.57995 | 0.55536 | 0.53952 | 0.5127 | 0.50075 | 0.47421 | 0.3689 | 0.33132 | 0.3131
|  | STRONSAY | FS |  |  |  | 0.012 | 0.63675 | 0.62674 | 0.62502 | 0.61739 | 0.61166 | 0.60511 | 0.59591 | 0.57711 | 0.56194 | 0.54181 | 0.52049 | 0.42618 | 0.31685 | 0.27891 | 0.75773 | 0.7521 | 0.75267 | 0.74766 | 0.74437 | 0.74053 | 0.73421 | 0.72224 | 0.71446 | 0.70109 | 0.68656 | 0.63157 | 0.5601 | 0.51083 | 0.66852 | 0.65599 | 0.65508 | 0.64762 | 0.64216 | 0.63608 | 0.62694 | 0.609 | 0.59608 | 0.57649 | 0.55552 | 0.47103 | 0.37257 | 0.34444
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 0.064 | -0.041731 | -0.046869 | -0.085204 | -0.13166 | -0.17885 | -0.23517 | -0.30132 | -0.34352 | -0.36867 | -0.3957 | -0.41981 | -0.48763 | -0.53497 | -0.5957 | 0.38208 | 0.36802 | 0.34268 | 0.31374 | 0.29117 | 0.25295 | 0.2114 | 0.18204 | 0.1612 | 0.13792 | 0.11676 | 0.05954 | 0.02212 | -0.030893 | 0.0015736 | -0.0091138 | -0.042249 | -0.078063 | -0.11041 | -0.1543 | -0.20558 | -0.2309 | -0.24569 | -0.26123 | -0.27485 | -0.32227 | -0.36803 | -0.41554
|  | STRONTIAN | CT |  |  |  | 0.064 | -0.027011 | -0.037374 | -0.076688 | -0.12965 | -0.17885 | -0.23517 | -0.30132 | -0.33833 | -0.34792 | -0.3643 | -0.3791 | -0.43143 | -0.4609 | -0.50035 | 0.39208 | 0.37862 | 0.35943 | 0.32752 | 0.30306 | 0.27336 | 0.2378 | 0.20997 | 0.20023 | 0.18312 | 0.16688 | 0.11712 | 0.093623 | 0.055205 | 0.014475 | -0.0012943 | -0.028781 | -0.069662 | -0.10455 | -0.14409 | -0.1923 | -0.21408 | -0.21988 | -0.22877 | -0.23632 | -0.26728 | -0.29071 | -0.31842
|  | STRONTIAN | LW |  |  |  | 0.064 | -0.027678 | -0.046869 | -0.085204 | -0.13166 | -0.17378 | -0.23353 | -0.30066 | -0.34352 | -0.36867 | -0.3957 | -0.41981 | -0.48763 | -0.53497 | -0.5957 | 0.39235 | 0.36802 | 0.34268 | 0.31374 | 0.29117 | 0.25295 | 0.2114 | 0.18204 | 0.1612 | 0.13792 | 0.11676 | 0.05954 | 0.02212 | -0.030893 | 0.016012 | -0.0091138 | -0.042249 | -0.078063 | -0.11041 | -0.1543 | -0.20558 | -0.2309 | -0.24569 | -0.26123 | -0.27485 | -0.32227 | -0.36803 | -0.41554
|  | STRONTIAN | ST |  |  |  | 0.064 | -0.041731 | -0.032354 | -0.046545 | -0.067754 | -0.088178 | -0.11006 | -0.13471 | -0.16478 | -0.19171 | -0.20931 | -0.23686 | -0.35578 | -0.41147 | -0.44433 | 0.38208 | 0.38718 | 0.37233 | 0.35928 | 0.34771 | 0.33485 | 0.32112 | 0.30208 | 0.28314 | 0.27206 | 0.25303 | 0.15266 | 0.097432 | 0.053854 | 0.0015736 | 0.0076874 | -0.011174 | -0.028194 | -0.043716 | -0.059478 | -0.076813 | -0.096334 | -0.11489 | -0.12896 | -0.14768 | -0.24363 | -0.30009 | -0.33909
|  | STRONTIAN | FS |  |  |  | 0.064 | -0.035913 | -0.025612 | -0.029246 | -0.033191 | -0.037587 | -0.043913 | -0.056688 | -0.076934 | -0.098752 | -0.12084 | -0.13371 | -0.23531 | -0.33665 | -0.37528 | 0.38831 | 0.3951 | 0.38894 | 0.38254 | 0.3758 | 0.36601 | 0.35432 | 0.34185 | 0.3258 | 0.30948 | 0.30214 | 0.23078 | 0.15686 | 0.1093 | 0.010774 | 0.019822 | 0.013379 | 0.0067705 | -0.00013716 | -0.0088533 | -0.019198 | -0.033236 | -0.049254 | -0.065437 | -0.075267 | -0.14468 | -0.21564 | -0.24773
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0 | -0.66978 | -0.69764 | -0.75716 | -0.82184 | -0.90181 | -0.98516 | -1.0943 | -1.1842 | -1.2646 | -1.355 | -1.4377 | -1.688 | -1.8488 | -1.9567 | -0.027218 | -0.050982 | -0.088513 | -0.12416 | -0.16178 | -0.21091 | -0.27523 | -0.32176 | -0.38466 | -0.43625 | -0.48733 | -0.68418 | -0.84663 | -0.93247 | -0.86692 | -0.9027 | -0.95821 | -1.0216 | -1.0974 | -1.1749 | -1.2819 | -1.3751 | -1.4571 | -1.5475 | -1.6301 | -1.8505 | -1.9677 | -2.1332
|  | SUMBURGH | CT |  |  |  | 0 | -0.66978 | -0.69437 | -0.75204 | -0.82184 | -0.90181 | -0.98516 | -1.0943 | -1.1842 | -1.2643 | -1.3368 | -1.4009 | -1.6697 | -1.8488 | -1.9567 | -0.027218 | -0.045288 | -0.077452 | -0.11621 | -0.16089 | -0.20259 | -0.26699 | -0.31507 | -0.36179 | -0.4055 | -0.44787 | -0.60483 | -0.70049 | -0.80024 | -0.86692 | -0.89873 | -0.95263 | -1.0216 | -1.0974 | -1.1749 | -1.2819 | -1.3751 | -1.4529 | -1.5259 | -1.5907 | -1.8209 | -1.9518 | -2.0296
|  | SUMBURGH | LW |  |  |  | 0 | -0.66819 | -0.69764 | -0.75716 | -0.81973 | -0.88631 | -0.96788 | -1.0657 | -1.1603 | -1.2646 | -1.355 | -1.4377 | -1.688 | -1.8205 | -1.952 | -0.026089 | -0.050982 | -0.088513 | -0.12416 | -0.16178 | -0.21091 | -0.27523 | -0.32176 | -0.38466 | -0.43625 | -0.48733 | -0.62316 | -0.68887 | -0.77139 | -0.86579 | -0.9027 | -0.95821 | -1.018 | -1.079 | -1.1612 | -1.2603 | -1.3514 | -1.4571 | -1.5475 | -1.6301 | -1.8505 | -1.9515 | -2.0521
|  | SUMBURGH | ST |  |  |  | 0 | -0.65506 | -0.66674 | -0.68598 | -0.70606 | -0.72785 | -0.75239 | -0.77366 | -0.80242 | -0.83295 | -0.87711 | -0.9587 | -1.4872 | -1.7271 | -1.869 | -0.01819 | -0.027159 | -0.042577 | -0.058471 | -0.076245 | -0.096259 | -0.11077 | -0.13517 | -0.16136 | -0.22501 | -0.28794 | -0.68418 | -0.84663 | -0.93247 | -0.85428 | -0.86959 | -0.89438 | -0.92161 | -0.95242 | -0.98831 | -1.0254 | -1.073 | -1.1306 | -1.1966 | -1.2615 | -1.7212 | -1.9677 | -2.1332
|  | SUMBURGH | FS |  |  |  | 0 | -0.65655 | -0.6675 | -0.68382 | -0.70249 | -0.71978 | -0.74141 | -0.7659 | -0.79382 | -0.83246 | -0.86632 | -0.90437 | -1.2144 | -1.5829 | -1.8623 | -0.018196 | -0.02609 | -0.037718 | -0.051827 | -0.064185 | -0.081491 | -0.10233 | -0.1195 | -0.14911 | -0.1728 | -0.20094 | -0.45013 | -0.70769 | -0.88718 | -0.85327 | -0.86479 | -0.88377 | -0.90591 | -0.92887 | -0.9571 | -0.9901 | -1.0268 | -1.0777 | -1.1252 | -1.1779 | -1.5065 | -1.8306 | -2.0943
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 1.273 | 6.4314 | 6.1567 | 5.9271 | 5.6475 | 5.2889 | 4.8633 | 4.3665 | 4.1242 | 3.9796 | 3.8305 | 3.6978 | 3.1053 | 2.7918 | 2.4728 | 8.7243 | 8.4829 | 8.3714 | 8.23 | 8.0829 | 7.8543 | 7.5556 | 7.3411 | 7.2194 | 7.0556 | 6.875 | 6.3886 | 5.926 | 5.578 | 7.6098 | 7.3364 | 7.1278 | 6.8752 | 6.5644 | 6.181 | 5.7257 | 5.4943 | 5.3581 | 5.2152 | 5.0732 | 4.5205 | 4.1778 | 3.9423
|  | TAIN | CT |  |  |  | 1.273 | 6.4864 | 6.2143 | 5.9619 | 5.6475 | 5.2889 | 4.8633 | 4.3665 | 4.1242 | 3.9796 | 3.8305 | 3.7136 | 3.2797 | 3.0282 | 2.7705 | 8.8042 | 8.5933 | 8.4667 | 8.29 | 8.0829 | 7.8543 | 7.5556 | 7.3411 | 7.2194 | 7.0662 | 6.929 | 6.5014 | 6.288 | 5.9588 | 7.6727 | 7.4072 | 7.1788 | 6.8914 | 6.5644 | 6.181 | 5.7257 | 5.4943 | 5.3581 | 5.2152 | 5.1015 | 4.696 | 4.4747 | 4.2445
|  | TAIN | LW |  |  |  | 1.273 | 6.4314 | 6.1567 | 5.9271 | 5.6507 | 5.3591 | 4.9745 | 4.5467 | 4.3225 | 4.1001 | 3.8893 | 3.6978 | 3.1053 | 2.7918 | 2.4728 | 8.7243 | 8.4829 | 8.3714 | 8.23 | 8.0882 | 7.8919 | 7.6331 | 7.4447 | 7.2509 | 7.0556 | 6.875 | 6.4242 | 6.2747 | 6.0607 | 7.6098 | 7.3364 | 7.1278 | 6.8752 | 6.6108 | 6.2653 | 5.876 | 5.6657 | 5.4558 | 5.2554 | 5.0732 | 4.5205 | 4.2369 | 3.9423
|  | TAIN | ST |  |  |  | 1.273 | 6.5382 | 6.329 | 6.1826 | 6.0358 | 5.8704 | 5.6493 | 5.4298 | 5.2306 | 5.032 | 4.8107 | 4.5713 | 3.5406 | 3.1294 | 2.9429 | 8.8391 | 8.6632 | 8.5822 | 8.503 | 8.4045 | 8.2646 | 8.12 | 7.9834 | 7.841 | 7.6736 | 7.4893 | 6.3886 | 5.926 | 5.7528 | 7.7201 | 7.5147 | 7.3798 | 7.2457 | 7.0932 | 6.8905 | 6.6862 | 6.4989 | 6.3139 | 6.107 | 5.8826 | 4.7717 | 4.1778 | 3.9482
|  | TAIN | FS |  |  |  | 1.273 | 6.7123 | 6.5621 | 6.5234 | 6.4707 | 6.4047 | 6.3199 | 6.2309 | 6.0901 | 5.9371 | 5.7912 | 5.61 | 4.639 | 3.6331 | 3.0858 | 8.9489 | 8.8355 | 8.7981 | 8.7476 | 8.6833 | 8.6092 | 8.5216 | 8.4184 | 8.2989 | 8.1905 | 8.0465 | 7.2198 | 6.3278 | 5.578 | 7.8889 | 7.7396 | 7.7017 | 7.6501 | 7.5859 | 7.5063 | 7.4209 | 7.2896 | 7.1468 | 7.0111 | 6.8399 | 5.9179 | 4.8464 | 4.0936
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0.182 | -0.17786 | -0.24478 | -0.33724 | -0.45058 | -0.59229 | -0.7484 | -0.9143 | -1.076 | -1.2559 | -1.4172 | -1.5259 | -1.9335 | -2.1317 | -2.373 | 0.12167 | 0.084324 | 0.043466 | -0.023035 | -0.11931 | -0.2128 | -0.31079 | -0.40104 | -0.5092 | -0.60978 | -0.66538 | -0.89486 | -1.0094 | -1.1671 | -0.070817 | -0.14449 | -0.22992 | -0.33109 | -0.46317 | -0.61166 | -0.75851 | -0.90618 | -1.0752 | -1.2268 | -1.3271 | -1.7088 | -1.898 | -2.1327
|  | TARBERT | CT |  |  |  | 0.182 | -0.17372 | -0.23217 | -0.31174 | -0.42995 | -0.58054 | -0.72925 | -0.89803 | -1.0555 | -1.1885 | -1.3185 | -1.4 | -1.8498 | -2.1218 | -2.304 | 0.13383 | 0.11091 | 0.080427 | 0.011586 | -0.087263 | -0.16622 | -0.25788 | -0.34937 | -0.42719 | -0.50796 | -0.55486 | -0.81005 | -0.9514 | -1.1021 | -0.063473 | -0.12612 | -0.19711 | -0.29988 | -0.44256 | -0.57007 | -0.71884 | -0.86632 | -0.99047 | -1.1131 | -1.1888 | -1.6027 | -1.8427 | -2.012
|  | TARBERT | LW |  |  |  | 0.182 | -0.17786 | -0.24478 | -0.33724 | -0.45058 | -0.59229 | -0.7484 | -0.9143 | -1.076 | -1.2559 | -1.4172 | -1.5259 | -1.9335 | -2.1317 | -2.373 | 0.12167 | 0.084324 | 0.043466 | -0.023035 | -0.11931 | -0.2128 | -0.31079 | -0.40104 | -0.5092 | -0.60978 | -0.66538 | -0.89486 | -1.0094 | -1.1671 | -0.070817 | -0.14449 | -0.22992 | -0.33109 | -0.46317 | -0.61166 | -0.75851 | -0.90618 | -1.0752 | -1.2268 | -1.3271 | -1.7088 | -1.898 | -2.1327
|  | TARBERT | ST |  |  |  | 0.182 | -0.15235 | -0.18147 | -0.22453 | -0.27006 | -0.33148 | -0.37812 | -0.42596 | -0.48597 | -0.53589 | -0.60577 | -0.67333 | -1.1382 | -1.463 | -1.7389 | 0.13944 | 0.12866 | 0.10806 | 0.088346 | 0.036836 | 0.0034861 | -0.027144 | -0.065083 | -0.098358 | -0.14892 | -0.1983 | -0.52519 | -0.73501 | -0.92933 | -0.043552 | -0.0716 | -0.1125 | -0.16121 | -0.22501 | -0.27671 | -0.32322 | -0.38243 | -0.43098 | -0.49923 | -0.5647 | -1.0156 | -1.3086 | -1.5316
|  | TARBERT | FS |  |  |  | 0.182 | -0.13586 | -0.15771 | -0.18462 | -0.2102 | -0.26375 | -0.29132 | -0.33691 | -0.3835 | -0.44847 | -0.51372 | -0.55866 | -0.9637 | -1.3332 | -1.6433 | 0.15088 | 0.14407 | 0.13286 | 0.12256 | 0.081413 | 0.064601 | 0.030883 | -0.00046478 | -0.042638 | -0.086163 | -0.11732 | -0.39311 | -0.65132 | -0.91414 | -0.033559 | -0.047357 | -0.075794 | -0.10172 | -0.16157 | -0.18915 | -0.23543 | -0.28016 | -0.34328 | -0.40645 | -0.44747 | -0.82415 | -1.1373 | -1.4141
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0 | 0.15426 | 0.15228 | 0.15032 | 0.14799 | 0.14513 | 0.1423 | 0.13833 | 0.13395 | 0.12933 | 0.12486 | 0.12072 | 0.11847 | 0.11507 | 0.11459 | 0.12468 | 0.12299 | 0.12147 | 0.11983 | 0.11762 | 0.11546 | 0.11228 | 0.10859 | 0.10512 | 0.10091 | 0.097178 | 0.095673 | 0.093072 | 0.09289 | 0.15139 | 0.14957 | 0.14765 | 0.14547 | 0.14274 | 0.14003 | 0.13621 | 0.13206 | 0.12734 | 0.12275 | 0.11866 | 0.11652 | 0.11325 | 0.11282
|  | TARBERT JURA | CT |  |  |  | 0 | 0.15426 | 0.15228 | 0.15032 | 0.14799 | 0.14513 | 0.1423 | 0.13833 | 0.13395 | 0.13069 | 0.12704 | 0.12372 | 0.12718 | 0.12651 | 0.12583 | 0.12468 | 0.12299 | 0.12147 | 0.11983 | 0.11762 | 0.11546 | 0.11228 | 0.10859 | 0.10585 | 0.10268 | 0.099766 | 0.10746 | 0.10713 | 0.10666 | 0.15139 | 0.14957 | 0.14765 | 0.14547 | 0.14274 | 0.14003 | 0.13621 | 0.13206 | 0.12891 | 0.1252 | 0.12182 | 0.12393 | 0.12333 | 0.1227
|  | TARBERT JURA | LW |  |  |  | 0 | 0.15429 | 0.15247 | 0.15089 | 0.14857 | 0.14646 | 0.14286 | 0.1387 | 0.13454 | 0.12933 | 0.12486 | 0.12072 | 0.12702 | 0.12637 | 0.12554 | 0.12477 | 0.12325 | 0.12198 | 0.12025 | 0.11877 | 0.11602 | 0.11284 | 0.10947 | 0.10512 | 0.10091 | 0.097178 | 0.10729 | 0.10702 | 0.10651 | 0.15151 | 0.14989 | 0.14822 | 0.146 | 0.144 | 0.14058 | 0.13665 | 0.13269 | 0.12734 | 0.12275 | 0.11866 | 0.12377 | 0.12319 | 0.12243
|  | TARBERT JURA | ST |  |  |  | 0 | 0.15491 | 0.15423 | 0.15323 | 0.15189 | 0.15043 | 0.14873 | 0.14676 | 0.14451 | 0.14161 | 0.13854 | 0.13517 | 0.11847 | 0.11507 | 0.11459 | 0.12526 | 0.12467 | 0.12392 | 0.12298 | 0.12195 | 0.12073 | 0.11929 | 0.11759 | 0.11536 | 0.113 | 0.11041 | 0.095673 | 0.093072 | 0.09289 | 0.15201 | 0.15132 | 0.15042 | 0.14915 | 0.14777 | 0.14617 | 0.14432 | 0.14222 | 0.13951 | 0.13664 | 0.13322 | 0.11652 | 0.11325 | 0.11282
|  | TARBERT JURA | FS |  |  |  | 0 | 0.15507 | 0.15453 | 0.15392 | 0.15315 | 0.15233 | 0.15135 | 0.15021 | 0.14878 | 0.14694 | 0.145 | 0.14283 | 0.13003 | 0.11894 | 0.11639 | 0.1254 | 0.12494 | 0.12444 | 0.12381 | 0.12315 | 0.12236 | 0.12144 | 0.12027 | 0.11876 | 0.11722 | 0.11553 | 0.10513 | 0.095811 | 0.094142 | 0.15221 | 0.15172 | 0.15118 | 0.15052 | 0.14982 | 0.14893 | 0.14787 | 0.1464 | 0.14449 | 0.14254 | 0.14039 | 0.12776 | 0.11695 | 0.11453
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 1.585 | 0.15339 | 0.074516 | -0.037485 | -0.18026 | -0.32704 | -0.4825 | -0.65424 | -0.76348 | -0.84627 | -0.94424 | -1.0238 | -1.2834 | -1.3441 | -1.4988 | 1.0742 | 1.0483 | 1.0142 | 0.93843 | 0.86189 | 0.78085 | 0.68945 | 0.63494 | 0.59308 | 0.54898 | 0.50978 | 0.38439 | 0.33879 | 0.20439 | 0.26514 | 0.19037 | 0.087955 | -0.044082 | -0.17929 | -0.32373 | -0.48333 | -0.59177 | -0.67454 | -0.78028 | -0.85964 | -1.1161 | -1.1712 | -1.3206
|  | TARBERT LOCH FYNE | CT |  |  |  | 1.585 | 0.15339 | 0.074516 | -0.037485 | -0.18026 | -0.32704 | -0.4825 | -0.65424 | -0.76348 | -0.84627 | -0.93474 | -1.0134 | -1.1771 | -1.2317 | -1.3481 | 1.0742 | 1.0483 | 1.0142 | 0.93843 | 0.86189 | 0.78085 | 0.68945 | 0.63494 | 0.59308 | 0.54898 | 0.50978 | 0.40511 | 0.33879 | 0.20439 | 0.26514 | 0.19037 | 0.087955 | -0.044082 | -0.17929 | -0.32373 | -0.48333 | -0.59177 | -0.67454 | -0.76372 | -0.84372 | -1.0093 | -1.0596 | -1.1704
|  | TARBERT LOCH FYNE | LW |  |  |  | 1.585 | 0.16212 | 0.09093 | 0.00093512 | -0.12148 | -0.23546 | -0.3949 | -0.55147 | -0.66539 | -0.81359 | -0.94424 | -1.0238 | -1.2834 | -1.3441 | -1.4988 | 1.0769 | 1.0546 | 1.0299 | 0.97674 | 0.91861 | 0.83928 | 0.75976 | 0.70464 | 0.63273 | 0.56899 | 0.52673 | 0.38439 | 0.3485 | 0.24329 | 0.27306 | 0.20569 | 0.12383 | 0.010585 | -0.093578 | -0.24405 | -0.39106 | -0.50347 | -0.6504 | -0.78028 | -0.85964 | -1.1161 | -1.1712 | -1.3206
|  | TARBERT LOCH FYNE | ST |  |  |  | 1.585 | 0.17932 | 0.1373 | 0.091778 | 0.045476 | 0.0007865 | -0.054232 | -0.10705 | -0.17682 | -0.26511 | -0.33172 | -0.42832 | -0.787 | -0.86385 | -0.85135 | 1.0812 | 1.0674 | 1.0543 | 1.0407 | 1.0279 | 1.0018 | 0.97334 | 0.93607 | 0.8892 | 0.85086 | 0.79833 | 0.58271 | 0.50024 | 0.43646 | 0.29006 | 0.25145 | 0.20933 | 0.16643 | 0.12514 | 0.072367 | 0.021882 | -0.045396 | -0.13107 | -0.19518 | -0.28908 | -0.64367 | -0.72043 | -0.71002
|  | TARBERT LOCH FYNE | FS |  |  |  | 1.585 | 0.193 | 0.16832 | 0.1466 | 0.12511 | 0.095493 | 0.078937 | 0.045887 | 0.0038374 | -0.05888 | -0.12254 | -0.16988 | -0.54611 | -0.85897 | -0.99919 | 1.085 | 1.0768 | 1.0703 | 1.0636 | 1.0541 | 1.0495 | 1.0385 | 1.0246 | 0.98928 | 0.95302 | 0.92293 | 0.69611 | 0.44512 | 0.21497 | 0.30187 | 0.27939 | 0.25866 | 0.23816 | 0.20956 | 0.19311 | 0.16037 | 0.12052 | 0.060227 | -0.0011239 | -0.046133 | -0.41286 | -0.71321 | -0.84859
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0.015 | 2.199 | 2.1688 | 2.1057 | 2.05 | 1.9742 | 1.9078 | 1.8145 | 1.7916 | 1.764 | 1.7332 | 1.7068 | 1.6242 | 1.5946 | 1.5475 | 2.753 | 2.7342 | 2.6992 | 2.6697 | 2.6272 | 2.5918 | 2.5384 | 2.5193 | 2.4971 | 2.4719 | 2.4494 | 2.3884 | 2.3575 | 2.2896 | 2.5096 | 2.4809 | 2.4229 | 2.3727 | 2.3028 | 2.2426 | 2.1559 | 2.1326 | 2.1043 | 2.0725 | 2.0417 | 1.9601 | 1.9333 | 1.8889
|  | TAYNUILT | CT |  |  |  | 0.015 | 2.199 | 2.1688 | 2.1057 | 2.05 | 1.9742 | 1.9078 | 1.8145 | 1.7916 | 1.764 | 1.7332 | 1.7132 | 1.6454 | 1.619 | 1.5807 | 2.753 | 2.7342 | 2.6992 | 2.6697 | 2.6272 | 2.5918 | 2.5384 | 2.5193 | 2.4971 | 2.4719 | 2.4542 | 2.3893 | 2.3575 | 2.3063 | 2.5096 | 2.4809 | 2.4229 | 2.3727 | 2.3028 | 2.2426 | 2.1559 | 2.1326 | 2.1043 | 2.0725 | 2.0512 | 1.9817 | 1.9575 | 1.922
|  | TAYNUILT | LW |  |  |  | 0.015 | 2.2029 | 2.1701 | 2.1257 | 2.0781 | 2.0215 | 1.9552 | 1.8714 | 1.8223 | 1.7884 | 1.7476 | 1.7068 | 1.6242 | 1.5946 | 1.5475 | 2.7552 | 2.7349 | 2.7112 | 2.6859 | 2.655 | 2.6176 | 2.5688 | 2.5345 | 2.5088 | 2.4796 | 2.4494 | 2.3884 | 2.3714 | 2.3423 | 2.5131 | 2.4817 | 2.4412 | 2.3979 | 2.346 | 2.2845 | 2.206 | 2.1572 | 2.1235 | 2.0827 | 2.0417 | 1.9601 | 1.9333 | 1.8889
|  | TAYNUILT | ST |  |  |  | 0.015 | 2.2081 | 2.1934 | 2.1728 | 2.1481 | 2.1268 | 2.0963 | 2.0763 | 2.0425 | 2.0119 | 1.9697 | 1.9237 | 1.7646 | 1.7222 | 1.719 | 2.7586 | 2.7504 | 2.7382 | 2.7231 | 2.7101 | 2.6907 | 2.6784 | 2.6563 | 2.636 | 2.6077 | 2.5764 | 2.4557 | 2.4101 | 2.3786 | 2.5182 | 2.5048 | 2.4857 | 2.4625 | 2.4427 | 2.4138 | 2.3952 | 2.3628 | 2.3335 | 2.2927 | 2.2481 | 2.0928 | 2.0522 | 2.0494
|  | TAYNUILT | FS |  |  |  | 0.015 | 2.2182 | 2.2092 | 2.2006 | 2.1891 | 2.1808 | 2.1656 | 2.1479 | 2.1344 | 2.1043 | 2.0841 | 2.0528 | 1.8956 | 1.7385 | 1.6766 | 2.7636 | 2.7581 | 2.7519 | 2.7434 | 2.7371 | 2.7259 | 2.7126 | 2.7034 | 2.6826 | 2.6685 | 2.6466 | 2.5282 | 2.3946 | 2.2896 | 2.5273 | 2.519 | 2.5107 | 2.4995 | 2.4915 | 2.4766 | 2.4592 | 2.4467 | 2.4179 | 2.3988 | 2.3686 | 2.2171 | 2.0672 | 2.0086
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 1.131 | 9.0069 | 8.7807 | 8.2101 | 7.4905 | 6.7034 | 5.6449 | 4.3966 | 3.1336 | 1.7406 | 0.44571 | -0.74083 | -4.2016 | -4.3851 | -5.6948 | 14.7507 | 14.5773 | 14.4076 | 13.995 | 13.5082 | 13.0008 | 12.2128 | 11.3481 | 10.2415 | 9.1911 | 8.2116 | 5.8544 | 5.318 | 1.7642 | 12.4554 | 12.2582 | 12.0584 | 11.7602 | 11.2014 | 10.2142 | 9.0277 | 7.7571 | 6.2873 | 4.8523 | 3.5252 | 0.12898 | -0.045261 | -1.336
|  | THIMBLEROW | CT |  |  |  | 1.131 | 9.0125 | 8.8053 | 8.3358 | 7.6558 | 6.894 | 6.1059 | 5.0555 | 3.7979 | 2.7578 | 1.7417 | 0.848 | -2.6332 | -3.6612 | -4.5876 | 14.7507 | 14.5773 | 14.4076 | 13.995 | 13.5082 | 13.018 | 12.308 | 11.4511 | 10.7163 | 9.9201 | 9.1808 | 6.5276 | 5.318 | 3.2171 | 12.4596 | 12.2582 | 12.0584 | 11.7602 | 11.3447 | 10.6136 | 9.6049 | 8.3659 | 7.3435 | 6.2739 | 5.3061 | 1.8471 | 0.95663 | -0.091633
|  | THIMBLEROW | LW |  |  |  | 1.131 | 9.0069 | 8.7807 | 8.2101 | 7.4905 | 6.7034 | 5.6449 | 4.3966 | 3.1336 | 1.7406 | 0.44571 | -0.74083 | -4.2016 | -4.3851 | -5.6948 | 14.7537 | 14.5929 | 14.4679 | 14.0638 | 13.6297 | 13.0008 | 12.2128 | 11.3481 | 10.2415 | 9.1911 | 8.2116 | 5.8544 | 5.6942 | 4.6292 | 12.4554 | 12.2649 | 12.1196 | 11.9191 | 11.2014 | 10.2142 | 9.0277 | 7.7571 | 6.2873 | 4.8523 | 3.5252 | 0.12898 | -0.045261 | -1.336
|  | THIMBLEROW | ST |  |  |  | 1.131 | 9.0688 | 8.9914 | 8.894 | 8.7687 | 8.622 | 8.4358 | 8.2153 | 7.9089 | 7.4701 | 6.9724 | 6.4166 | 2.9172 | 1.5327 | 1.1116 | 14.7941 | 14.7238 | 14.6418 | 14.5348 | 14.4111 | 14.2535 | 14.0659 | 13.7989 | 13.4107 | 12.9513 | 12.3888 | 9.2542 | 7.7044 | 6.0216 | 12.5146 | 12.4401 | 12.3451 | 12.2238 | 12.0827 | 11.9029 | 11.6892 | 11.4225 | 11.0773 | 10.5716 | 9.9109 | 6.2435 | 4.9075 | 4.5095
|  | THIMBLEROW | FS |  |  |  | 1.131 | 9.0939 | 9.0393 | 8.9683 | 8.8798 | 8.7725 | 8.6524 | 8.4926 | 8.1834 | 7.7976 | 7.4307 | 7.0085 | 3.6646 | 0.37672 | -2.0269 | 14.8099 | 14.7561 | 14.6931 | 14.6141 | 14.5183 | 14.4092 | 14.2729 | 14.0001 | 13.6491 | 13.3118 | 12.9248 | 9.9385 | 6.1662 | 1.7642 | 12.5375 | 12.485 | 12.4162 | 12.3312 | 12.228 | 12.1126 | 11.9731 | 11.8126 | 11.5959 | 11.3824 | 11.1335 | 8.0724 | 4.7676 | 2.4947
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.19485 | 0.19143 | 0.18764 | 0.18331 | 0.17769 | 0.1719 | 0.16424 | 0.15764 | 0.15114 | 0.15204 | 0.14679 | 0.14664 | 0.14432 | 0.13923 | 0.18714 | 0.18438 | 0.1816 | 0.1785 | 0.17453 | 0.17057 | 0.16481 | 0.15873 | 0.15264 | 0.16026 | 0.15663 | 0.15654 | 0.15546 | 0.15222 | 0.17976 | 0.17646 | 0.17288 | 0.16882 | 0.16377 | 0.15866 | 0.15154 | 0.14477 | 0.13814 | 0.13856 | 0.13337 | 0.13349 | 0.13144 | 0.12658
|  | TIRORAN BRIDGE | CT |  |  |  | 0 | 0.19485 | 0.19143 | 0.18764 | 0.18331 | 0.17769 | 0.1719 | 0.16424 | 0.15764 | 0.15246 | 0.15421 | 0.14968 | 0.14853 | 0.14597 | 0.14205 | 0.18714 | 0.18438 | 0.1816 | 0.1785 | 0.17453 | 0.17057 | 0.16481 | 0.15873 | 0.15416 | 0.16186 | 0.1587 | 0.15782 | 0.15629 | 0.15352 | 0.17976 | 0.17646 | 0.17288 | 0.16882 | 0.16377 | 0.15866 | 0.15154 | 0.14477 | 0.13967 | 0.14075 | 0.13627 | 0.13538 | 0.13307 | 0.12937
|  | TIRORAN BRIDGE | LW |  |  |  | 0 | 0.19517 | 0.19206 | 0.18867 | 0.18427 | 0.17971 | 0.1731 | 0.1656 | 0.15925 | 0.15114 | 0.15204 | 0.14679 | 0.14664 | 0.14432 | 0.13923 | 0.18731 | 0.18478 | 0.18237 | 0.17919 | 0.17626 | 0.17128 | 0.1655 | 0.15982 | 0.15264 | 0.16026 | 0.15663 | 0.15654 | 0.15546 | 0.15222 | 0.18005 | 0.17705 | 0.17385 | 0.16977 | 0.16585 | 0.15968 | 0.15256 | 0.14614 | 0.13814 | 0.13856 | 0.13337 | 0.13349 | 0.13144 | 0.12658
|  | TIRORAN BRIDGE | ST |  |  |  | 0 | 0.19591 | 0.19431 | 0.19218 | 0.18952 | 0.18662 | 0.18344 | 0.17992 | 0.17627 | 0.17178 | 0.16708 | 0.16196 | 0.15617 | 0.15169 | 0.15033 | 0.188 | 0.18688 | 0.18542 | 0.18367 | 0.18174 | 0.17949 | 0.17687 | 0.1739 | 0.17003 | 0.16592 | 0.16142 | 0.16292 | 0.15998 | 0.15892 | 0.18079 | 0.17929 | 0.1773 | 0.17501 | 0.17251 | 0.16968 | 0.16645 | 0.16294 | 0.15846 | 0.15375 | 0.14861 | 0.14281 | 0.13859 | 0.13739
|  | TIRORAN BRIDGE | FS |  |  |  | 0 | 0.19666 | 0.19552 | 0.19441 | 0.19307 | 0.19164 | 0.19 | 0.18809 | 0.18546 | 0.18221 | 0.17889 | 0.17527 | 0.15971 | 0.1538 | 0.1492 | 0.18838 | 0.18753 | 0.18664 | 0.18554 | 0.18436 | 0.18296 | 0.18132 | 0.17921 | 0.17652 | 0.17376 | 0.17073 | 0.16453 | 0.16072 | 0.15699 | 0.18146 | 0.18038 | 0.17931 | 0.17802 | 0.17663 | 0.17503 | 0.17316 | 0.17063 | 0.16748 | 0.16426 | 0.16074 | 0.14577 | 0.14047 | 0.13614
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0.441 | -0.2813 | -0.3037 | -0.33858 | -0.37599 | -0.42375 | -0.47232 | -0.53712 | -0.55751 | -0.59158 | -0.62922 | -0.64024 | -0.72461 | -0.80994 | -0.85566 | -0.026433 | -0.045796 | -0.066396 | -0.087745 | -0.10698 | -0.13378 | -0.17013 | -0.18837 | -0.21394 | -0.23627 | -0.25133 | -0.30474 | -0.3691 | -0.40689 | -0.18543 | -0.2112 | -0.24568 | -0.2822 | -0.31813 | -0.36339 | -0.42623 | -0.4493 | -0.486 | -0.51998 | -0.53661 | -0.61356 | -0.70071 | -0.74977
|  | TOMATIN | CT |  |  |  | 0.441 | -0.28103 | -0.30074 | -0.33187 | -0.37373 | -0.42375 | -0.47045 | -0.53427 | -0.55285 | -0.57064 | -0.59092 | -0.6175 | -0.66528 | -0.69873 | -0.73696 | -0.026433 | -0.037679 | -0.050528 | -0.074073 | -0.093229 | -0.10992 | -0.13908 | -0.15823 | -0.17397 | -0.19054 | -0.20532 | -0.2386 | -0.26491 | -0.30901 | -0.18543 | -0.2059 | -0.2343 | -0.27469 | -0.31325 | -0.35085 | -0.41337 | -0.43532 | -0.45395 | -0.47395 | -0.50071 | -0.5472 | -0.57881 | -0.61618
|  | TOMATIN | LW |  |  |  | 0.441 | -0.2813 | -0.3037 | -0.33858 | -0.37599 | -0.4207 | -0.47232 | -0.53712 | -0.55751 | -0.59158 | -0.62922 | -0.64024 | -0.71696 | -0.76704 | -0.82554 | -0.026319 | -0.045796 | -0.066396 | -0.087745 | -0.10698 | -0.13378 | -0.17013 | -0.18837 | -0.21394 | -0.23627 | -0.25133 | -0.30364 | -0.33611 | -0.37191 | -0.18363 | -0.2112 | -0.24568 | -0.2822 | -0.31813 | -0.36339 | -0.42623 | -0.4493 | -0.486 | -0.51998 | -0.53661 | -0.61079 | -0.65867 | -0.72041
|  | TOMATIN | ST |  |  |  | 0.441 | -0.28069 | -0.2854 | -0.30813 | -0.33085 | -0.3541 | -0.37747 | -0.40549 | -0.43423 | -0.46373 | -0.49955 | -0.53421 | -0.72461 | -0.80994 | -0.85566 | -0.025001 | -0.028736 | -0.041953 | -0.054275 | -0.066159 | -0.077894 | -0.092844 | -0.10967 | -0.12755 | -0.14968 | -0.17029 | -0.30474 | -0.3691 | -0.40689 | -0.18209 | -0.19141 | -0.21372 | -0.23556 | -0.25745 | -0.27919 | -0.30549 | -0.33275 | -0.36058 | -0.39467 | -0.4273 | -0.61356 | -0.70071 | -0.74977
|  | TOMATIN | FS |  |  |  | 0.441 | -0.27947 | -0.28079 | -0.2854 | -0.29347 | -0.30419 | -0.3169 | -0.33051 | -0.35146 | -0.37712 | -0.39817 | -0.42277 | -0.56735 | -0.69712 | -0.76969 | -0.022525 | -0.025311 | -0.031608 | -0.038309 | -0.045564 | -0.054262 | -0.064232 | -0.076554 | -0.092746 | -0.10601 | -0.12023 | -0.20649 | -0.28058 | -0.32746 | -0.17498 | -0.18133 | -0.19072 | -0.2005 | -0.21105 | -0.22353 | -0.23709 | -0.25716 | -0.28203 | -0.3023 | -0.32543 | -0.46173 | -0.58265 | -0.65159
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0 | 0.11074 | 0.1023 | 0.093237 | 0.084662 | 0.078731 | 0.069265 | 0.056063 | 0.053213 | 0.049588 | 0.0465 | 0.043753 | 0.027875 | 0.0055208 | -0.019224 | 0.1042 | 0.094001 | 0.083016 | 0.072742 | 0.065666 | 0.054481 | 0.03888 | 0.036228 | 0.032829 | 0.029944 | 0.027386 | 0.0089261 | -0.018734 | -0.049434 | 0.10737 | 0.097128 | 0.086007 | 0.075537 | 0.06833 | 0.057033 | 0.041229 | 0.038411 | 0.034821 | 0.031765 | 0.029048 | 0.010193 | -0.017631 | -0.048466
|  | TORBOLL | CT |  |  |  | 0 | 0.11074 | 0.10961 | 0.10859 | 0.10016 | 0.09703 | 0.092985 | 0.084924 | 0.081257 | 0.078328 | 0.075108 | 0.072101 | 0.062525 | 0.056519 | 0.048073 | 0.10421 | 0.10316 | 0.10225 | 0.092124 | 0.088622 | 0.084159 | 0.0749 | 0.071212 | 0.068218 | 0.064922 | 0.061811 | 0.051115 | 0.043861 | 0.033545 | 0.10738 | 0.10628 | 0.10525 | 0.094845 | 0.091252 | 0.086689 | 0.077235 | 0.073394 | 0.070283 | 0.06688 | 0.063684 | 0.052734 | 0.045337 | 0.034886
|  | TORBOLL | LW |  |  |  | 0 | 0.11074 | 0.1023 | 0.093237 | 0.084662 | 0.078731 | 0.069265 | 0.056063 | 0.053213 | 0.049588 | 0.0465 | 0.043753 | 0.027875 | 0.0055208 | -0.019224 | 0.1042 | 0.094001 | 0.083016 | 0.072742 | 0.065666 | 0.054481 | 0.03888 | 0.036228 | 0.032829 | 0.029944 | 0.027386 | 0.0089261 | -0.018734 | -0.049434 | 0.10737 | 0.097128 | 0.086007 | 0.075537 | 0.06833 | 0.057033 | 0.041229 | 0.038411 | 0.034821 | 0.031765 | 0.029048 | 0.010193 | -0.017631 | -0.048466
|  | TORBOLL | ST |  |  |  | 0 | 0.11112 | 0.11071 | 0.10534 | 0.10148 | 0.099186 | 0.097569 | 0.095802 | 0.093583 | 0.090916 | 0.088132 | 0.085964 | 0.055886 | 0.029611 | 0.0066314 | 0.10455 | 0.10421 | 0.097667 | 0.093041 | 0.090395 | 0.088634 | 0.086643 | 0.08434 | 0.081615 | 0.078781 | 0.076783 | 0.042563 | 0.010403 | -0.018261 | 0.10773 | 0.10736 | 0.10079 | 0.096148 | 0.093374 | 0.091437 | 0.089316 | 0.086944 | 0.084134 | 0.08121 | 0.079101 | 0.044248 | 0.011898 | -0.016781
|  | TORBOLL | FS |  |  |  | 0 | 0.11122 | 0.11091 | 0.10897 | 0.10695 | 0.10489 | 0.10276 | 0.099699 | 0.097261 | 0.093627 | 0.089962 | 0.088628 | 0.0811 | 0.074643 | 0.070245 | 0.10461 | 0.10433 | 0.10198 | 0.099547 | 0.097085 | 0.094538 | 0.090886 | 0.088066 | 0.083917 | 0.079739 | 0.078511 | 0.071572 | 0.065705 | 0.060809 | 0.10782 | 0.10753 | 0.10519 | 0.10275 | 0.10019 | 0.097534 | 0.093752 | 0.090834 | 0.086628 | 0.082393 | 0.081103 | 0.073803 | 0.067486 | 0.062332
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 1.678 | 11.5337 | 11.3764 | 11.0156 | 10.4356 | 9.826 | 8.9315 | 7.8423 | 6.7703 | 5.088 | 3.848 | 2.8028 | 0.8622 | -0.18839 | -0.89976 | 12.9863 | 12.9089 | 12.7254 | 12.3299 | 11.9808 | 11.5768 | 10.886 | 10.2913 | 8.9341 | 8.0905 | 7.4153 | 6.4497 | 6.1784 | 5.9786 | 12.6409 | 12.5503 | 12.2996 | 11.8001 | 11.1265 | 10.2857 | 9.2687 | 8.3569 | 6.8417 | 5.7553 | 4.8463 | 3.147 | 2.2809 | 1.6593
|  | TORRYBURN | CT |  |  |  | 1.678 | 11.5337 | 11.3764 | 11.0156 | 10.4356 | 9.826 | 8.9315 | 7.8423 | 6.7703 | 5.2965 | 4.0918 | 3.175 | 0.90445 | -0.18839 | -0.89976 | 12.9868 | 12.9165 | 12.7254 | 12.3299 | 11.9808 | 11.5768 | 10.886 | 10.2913 | 9.1929 | 8.3537 | 7.7552 | 6.9286 | 6.6654 | 6.176 | 12.6422 | 12.5572 | 12.2996 | 11.8001 | 11.1265 | 10.2857 | 9.2687 | 8.3569 | 7.014 | 5.9488 | 5.1482 | 3.239 | 2.2809 | 1.6593
|  | TORRYBURN | LW |  |  |  | 1.678 | 11.5357 | 11.3816 | 11.0658 | 10.5942 | 10.0155 | 8.994 | 7.943 | 6.8228 | 5.088 | 3.848 | 2.8028 | 0.8622 | 0.15732 | -0.52438 | 12.9863 | 12.9089 | 12.7406 | 12.426 | 12.0907 | 11.6607 | 10.9146 | 10.2954 | 8.9341 | 8.0905 | 7.4153 | 6.4497 | 6.1784 | 5.9786 | 12.6409 | 12.5503 | 12.34 | 11.9177 | 11.2029 | 10.3808 | 9.3873 | 8.4259 | 6.8417 | 5.7553 | 4.8463 | 3.147 | 2.4716 | 1.8711
|  | TORRYBURN | ST |  |  |  | 1.678 | 11.6017 | 11.5469 | 11.3591 | 11.1344 | 10.9069 | 10.632 | 10.0474 | 9.5629 | 8.4769 | 7.5929 | 7.0355 | 4.9894 | 3.9033 | 2.7771 | 13.0157 | 13.0003 | 12.9004 | 12.7799 | 12.6225 | 12.4104 | 11.8712 | 11.441 | 10.4005 | 9.5903 | 9.088 | 7.6363 | 7.0509 | 6.7394 | 12.6786 | 12.662 | 12.5323 | 12.3739 | 12.2121 | 11.9647 | 11.4162 | 10.962 | 9.9177 | 9.0635 | 8.5343 | 6.6017 | 5.694 | 4.6144
|  | TORRYBURN | FS |  |  |  | 1.678 | 11.6189 | 11.5844 | 11.464 | 11.3154 | 11.1641 | 10.9857 | 10.5853 | 10.2571 | 9.5183 | 8.9663 | 8.393 | 6.2019 | 4.3062 | 2.9531 | 13.0212 | 13.0135 | 12.9473 | 12.8621 | 12.7768 | 12.6716 | 12.3054 | 12.0193 | 11.3143 | 10.8085 | 10.3287 | 8.6895 | 7.4994 | 6.7809 | 12.6863 | 12.6798 | 12.5925 | 12.48 | 12.3677 | 12.23 | 11.8707 | 11.6084 | 10.9104 | 10.3919 | 9.8702 | 7.8741 | 6.1993 | 5.0232
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0.007 | 0.22553 | 0.20309 | 0.57826 | 0.53734 | 0.50189 | 0.44712 | 0.39376 | 0.35919 | 0.32763 | 0.29394 | 0.26379 | 0.17867 | 0.12905 | 0.065983 | 0.50511 | 0.48849 | 0.92071 | 0.89357 | 0.87452 | 0.83695 | 0.80326 | 0.77684 | 0.7533 | 0.72646 | 0.7021 | 0.63957 | 0.60312 | 0.55144 | 0.25986 | 0.233 | 0.63277 | 0.59364 | 0.56308 | 0.50945 | 0.46187 | 0.42651 | 0.39616 | 0.36155 | 0.33061 | 0.25002 | 0.20266 | 0.14087
|  | TRESSADY | CT |  |  |  | 0.007 | 0.22784 | 0.20528 | 0.58637 | 0.54489 | 0.50698 | 0.46156 | 0.41324 | 0.37981 | 0.35456 | 0.33818 | 0.31671 | 0.24319 | 0.20936 | 0.16818 | 0.50997 | 0.49552 | 0.93594 | 0.90925 | 0.88923 | 0.863 | 0.83652 | 0.8093 | 0.78853 | 0.77551 | 0.75561 | 0.69735 | 0.67371 | 0.63599 | 0.25986 | 0.238 | 0.6455 | 0.60681 | 0.57384 | 0.53223 | 0.49129 | 0.45606 | 0.42951 | 0.41418 | 0.39037 | 0.31895 | 0.29119 | 0.25542
|  | TRESSADY | LW |  |  |  | 0.007 | 0.23075 | 0.20309 | 0.57826 | 0.53734 | 0.50189 | 0.44712 | 0.39376 | 0.35919 | 0.32763 | 0.29394 | 0.26379 | 0.17867 | 0.12905 | 0.065983 | 0.51079 | 0.48849 | 0.92071 | 0.89357 | 0.87452 | 0.83695 | 0.80326 | 0.77684 | 0.7533 | 0.72646 | 0.7021 | 0.63957 | 0.60312 | 0.55144 | 0.26194 | 0.233 | 0.63277 | 0.59364 | 0.56308 | 0.50945 | 0.46187 | 0.42651 | 0.39616 | 0.36155 | 0.33061 | 0.25002 | 0.20266 | 0.14087
|  | TRESSADY | ST |  |  |  | 0.007 | 0.22553 | 0.22163 | 0.60879 | 0.58762 | 0.56768 | 0.54565 | 0.51997 | 0.5007 | 0.4722 | 0.45356 | 0.42521 | 0.29372 | 0.23121 | 0.19412 | 0.50511 | 0.50792 | 0.94781 | 0.93494 | 0.92407 | 0.91137 | 0.89476 | 0.88334 | 0.86239 | 0.85282 | 0.83262 | 0.724 | 0.66713 | 0.62227 | 0.2617 | 0.25521 | 0.66603 | 0.64667 | 0.62933 | 0.60949 | 0.5848 | 0.56772 | 0.53872 | 0.52483 | 0.49686 | 0.36424 | 0.30261 | 0.2645
|  | TRESSADY | FS |  |  |  | 0.007 | 0.23514 | 0.22586 | 0.63361 | 0.62435 | 0.61691 | 0.60797 | 0.59573 | 0.57569 | 0.55774 | 0.53482 | 0.51235 | 0.41698 | 0.30852 | 0.26572 | 0.50991 | 0.50508 | 0.9585 | 0.95125 | 0.9455 | 0.93881 | 0.92833 | 0.91387 | 0.90171 | 0.8842 | 0.8685 | 0.80383 | 0.72482 | 0.67432 | 0.26934 | 0.256 | 0.68617 | 0.67686 | 0.66944 | 0.661 | 0.64843 | 0.62845 | 0.61191 | 0.58858 | 0.56689 | 0.4816 | 0.38212 | 0.34751
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0.308 | 4.548 | 4.5048 | 4.4259 | 4.3217 | 4.204 | 4.0816 | 3.9255 | 3.7756 | 3.6396 | 3.5017 | 3.365 | 2.9586 | 2.6747 | 2.5032 | 4.9442 | 4.9109 | 4.8681 | 4.8182 | 4.7659 | 4.7016 | 4.6184 | 4.5358 | 4.443 | 4.3723 | 4.2983 | 4.102 | 4.0168 | 3.9267 | 4.5212 | 4.4805 | 4.4047 | 4.3127 | 4.2002 | 4.0857 | 3.9357 | 3.7994 | 3.6819 | 3.5719 | 3.4538 | 3.1043 | 2.8275 | 2.674
|  | TUMBLIN | CT |  |  |  | 0.308 | 4.549 | 4.5122 | 4.4306 | 4.3217 | 4.204 | 4.0816 | 3.9255 | 3.7756 | 3.6493 | 3.542 | 3.4389 | 2.9868 | 2.6747 | 2.5032 | 4.9453 | 4.9207 | 4.8821 | 4.8237 | 4.7659 | 4.7094 | 4.6298 | 4.5524 | 4.4883 | 4.4385 | 4.3861 | 4.1944 | 4.0878 | 3.9268 | 4.5212 | 4.4881 | 4.4131 | 4.3127 | 4.2002 | 4.0857 | 3.9357 | 3.7994 | 3.6819 | 3.5922 | 3.5018 | 3.1048 | 2.8275 | 2.674
|  | TUMBLIN | LW |  |  |  | 0.308 | 4.548 | 4.5048 | 4.4259 | 4.3338 | 4.2361 | 4.1161 | 3.9728 | 3.8101 | 3.6396 | 3.5017 | 3.365 | 2.9586 | 2.7565 | 2.559 | 4.9442 | 4.9109 | 4.8681 | 4.8182 | 4.7677 | 4.7016 | 4.6184 | 4.5358 | 4.443 | 4.3723 | 4.2983 | 4.102 | 4.0168 | 3.9267 | 4.5213 | 4.4805 | 4.4047 | 4.317 | 4.224 | 4.1149 | 3.9818 | 3.8372 | 3.6868 | 3.5719 | 3.4538 | 3.1043 | 2.927 | 2.7464
|  | TUMBLIN | ST |  |  |  | 0.308 | 4.5711 | 4.56 | 4.5398 | 4.5159 | 4.4965 | 4.4692 | 4.4423 | 4.4067 | 4.3686 | 4.3208 | 4.2711 | 3.8348 | 3.4951 | 3.2238 | 4.9564 | 4.9489 | 4.9325 | 4.9139 | 4.8997 | 4.8796 | 4.8598 | 4.8326 | 4.8036 | 4.7668 | 4.7289 | 4.4546 | 4.2832 | 4.1625 | 4.5426 | 4.5331 | 4.5144 | 4.492 | 4.4779 | 4.4554 | 4.4366 | 4.4088 | 4.3847 | 4.3495 | 4.3167 | 3.9613 | 3.6302 | 3.3467
|  | TUMBLIN | FS |  |  |  | 0.308 | 4.5632 | 4.5485 | 4.5255 | 4.5021 | 4.4754 | 4.4514 | 4.4196 | 4.3793 | 4.328 | 4.2759 | 4.232 | 3.9 | 3.5682 | 3.2149 | 4.9541 | 4.9457 | 4.9319 | 4.9177 | 4.9009 | 4.8863 | 4.8651 | 4.8422 | 4.8103 | 4.7776 | 4.7527 | 4.554 | 4.3753 | 4.1405 | 4.5344 | 4.5206 | 4.4983 | 4.4769 | 4.4518 | 4.4322 | 4.4033 | 4.3684 | 4.3223 | 4.2755 | 4.2418 | 3.9624 | 3.6827 | 3.3638
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.888 | -0.77099 | -0.77823 | -0.80459 | -0.84642 | -0.89246 | -0.94438 | -1.0032 | -1.0386 | -1.0659 | -1.1053 | -1.1456 | -1.251 | -1.3044 | -1.3456 | -0.51132 | -0.52144 | -0.5473 | -0.5739 | -0.5997 | -0.63785 | -0.67499 | -0.70051 | -0.72394 | -0.75203 | -0.77966 | -0.83546 | -0.87855 | -0.92901 | -0.64054 | -0.66289 | -0.70083 | -0.74094 | -0.78377 | -0.83938 | -0.89409 | -0.93158 | -0.96584 | -1.0037 | -1.0377 | -1.1176 | -1.1771 | -1.2421
|  | TUMMEL BRIDGE | CT |  |  |  | 0.888 | -0.75826 | -0.7724 | -0.79657 | -0.84642 | -0.89246 | -0.94438 | -1.0032 | -1.0386 | -1.0561 | -1.081 | -1.1016 | -1.1694 | -1.2002 | -1.2411 | -0.501 | -0.51348 | -0.53354 | -0.56533 | -0.59458 | -0.62657 | -0.66247 | -0.68906 | -0.70225 | -0.72248 | -0.74047 | -0.80268 | -0.83284 | -0.8866 | -0.63667 | -0.65662 | -0.69014 | -0.7368 | -0.78377 | -0.83486 | -0.89004 | -0.92701 | -0.94491 | -0.97179 | -0.9948 | -1.0639 | -1.093 | -1.1325
|  | TUMMEL BRIDGE | LW |  |  |  | 0.888 | -0.75914 | -0.77823 | -0.80459 | -0.84263 | -0.88416 | -0.93906 | -0.99592 | -1.0326 | -1.0659 | -1.1053 | -1.1456 | -1.251 | -1.3044 | -1.3456 | -0.50209 | -0.52144 | -0.5473 | -0.5739 | -0.5997 | -0.63785 | -0.67499 | -0.70051 | -0.72394 | -0.75203 | -0.77966 | -0.83546 | -0.87855 | -0.92901 | -0.63688 | -0.66289 | -0.70083 | -0.74094 | -0.78183 | -0.83938 | -0.89409 | -0.93158 | -0.96584 | -1.0037 | -1.0377 | -1.1176 | -1.1771 | -1.2421
|  | TUMMEL BRIDGE | ST |  |  |  | 0.888 | -0.77099 | -0.76222 | -0.77718 | -0.79138 | -0.8117 | -0.83354 | -0.85469 | -0.87747 | -0.9053 | -0.93954 | -0.97679 | -1.1742 | -1.257 | -1.2915 | -0.51132 | -0.5038 | -0.51945 | -0.53362 | -0.5468 | -0.56181 | -0.5754 | -0.59291 | -0.60723 | -0.62841 | -0.65054 | -0.77391 | -0.84454 | -0.90626 | -0.64054 | -0.64167 | -0.66413 | -0.68498 | -0.70505 | -0.72774 | -0.74857 | -0.77417 | -0.79479 | -0.825 | -0.8566 | -1.0093 | -1.079 | -1.118
|  | TUMMEL BRIDGE | FS |  |  |  | 0.888 | -0.7612 | -0.75096 | -0.75629 | -0.76249 | -0.7684 | -0.77729 | -0.7886 | -0.80496 | -0.82759 | -0.85157 | -0.87044 | -1.0075 | -1.1509 | -1.2334 | -0.50307 | -0.49471 | -0.50154 | -0.50922 | -0.51654 | -0.52759 | -0.53895 | -0.55028 | -0.5682 | -0.58724 | -0.59718 | -0.6864 | -0.795 | -0.89055 | -0.62846 | -0.6263 | -0.63505 | -0.64448 | -0.65352 | -0.66744 | -0.68086 | -0.69614 | -0.71989 | -0.74493 | -0.75789 | -0.87219 | -0.99078 | -1.0431
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 0.607 | 2.7414 | 2.466 | 1.9605 | 1.3278 | 0.65551 | -0.11458 | -1.208 | -2.0016 | -2.813 | -3.4154 | -3.8832 | -5.3204 | -6.1164 | -6.8586 | -0.46103 | -0.63146 | -0.88977 | -1.2272 | -1.5742 | -1.9712 | -2.6669 | -3.1268 | -3.6946 | -4.0852 | -4.3604 | -5.1785 | -5.7463 | -6.426 | 2.7036 | 2.4364 | 1.9813 | 1.4003 | 0.77995 | 0.070023 | -0.9689 | -1.6386 | -2.4131 | -2.9936 | -3.4467 | -4.7752 | -5.4656 | -6.1201
|  | TURRIFF | CT |  |  |  | 0.607 | 2.7414 | 2.466 | 1.9605 | 1.3278 | 0.65551 | -0.11458 | -1.208 | -2.0016 | -2.7582 | -3.3268 | -3.7078 | -5.1777 | -6.1164 | -6.8586 | -0.46103 | -0.63146 | -0.88977 | -1.2272 | -1.5742 | -1.9712 | -2.6669 | -3.1268 | -3.6673 | -4.0686 | -4.3203 | -5.1785 | -5.7463 | -6.426 | 2.7036 | 2.4364 | 1.9813 | 1.4003 | 0.77995 | 0.070023 | -0.9689 | -1.6386 | -2.3554 | -2.9024 | -3.2755 | -4.6483 | -5.4656 | -6.1201
|  | TURRIFF | LW |  |  |  | 0.607 | 2.7633 | 2.512 | 2.0151 | 1.4003 | 0.76565 | 0.0037851 | -1.0992 | -1.9465 | -2.813 | -3.4154 | -3.8832 | -5.3204 | -6.0588 | -6.7219 | -0.45182 | -0.60426 | -0.84148 | -1.1558 | -1.4616 | -1.8637 | -2.5865 | -3.0738 | -3.6946 | -4.0852 | -4.3604 | -5.1074 | -5.4168 | -5.736 | 2.7252 | 2.4828 | 2.0407 | 1.4778 | 0.9026 | 0.18863 | -0.86449 | -1.5792 | -2.4131 | -2.9936 | -3.4467 | -4.7752 | -5.3993 | -5.9927
|  | TURRIFF | ST |  |  |  | 0.607 | 2.848 | 2.6694 | 2.3931 | 2.0918 | 1.7856 | 1.4523 | 0.87633 | 0.29582 | -0.29107 | -0.7485 | -1.1033 | -2.6369 | -3.8087 | -4.8437 | -0.40263 | -0.50356 | -0.64908 | -0.81889 | -0.98452 | -1.1807 | -1.6159 | -2.0741 | -2.5597 | -2.9265 | -3.1909 | -4.1192 | -4.8338 | -5.59 | 2.8076 | 2.6437 | 2.3992 | 2.1252 | 1.8572 | 1.5516 | 1.0038 | 0.45168 | -0.12039 | -0.57108 | -0.92857 | -2.273 | -3.2723 | -4.1436
|  | TURRIFF | FS |  |  |  | 0.607 | 2.9536 | 2.8337 | 2.6864 | 2.5202 | 2.3395 | 2.172 | 1.8263 | 1.3621 | 0.92465 | 0.54049 | 0.17713 | -1.5474 | -3.27 | -4.5188 | -0.35613 | -0.43106 | -0.52141 | -0.6314 | -0.75423 | -0.86009 | -1.1454 | -1.498 | -1.8432 | -2.1347 | -2.4052 | -3.5975 | -4.9391 | -6.2974 | 2.8992 | 2.7878 | 2.6571 | 2.504 | 2.3366 | 2.1907 | 1.8597 | 1.4232 | 1.0054 | 0.63653 | 0.28437 | -1.293 | -2.9044 | -4.0309
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0.521 | 0.09759 | 0.097151 | 0.093436 | 0.086266 | 0.07466 | 0.064686 | 0.048609 | 0.026358 | 0.018435 | -0.0013086 | -0.019271 | -0.22302 | -0.33608 | -0.40099 | 0.41604 | 0.41413 | 0.40589 | 0.39319 | 0.37538 | 0.3605 | 0.33447 | 0.30821 | 0.29659 | 0.27208 | 0.24954 | 0.12642 | 0.041203 | -0.01072 | 0.14445 | 0.13762 | 0.11946 | 0.098686 | 0.070578 | 0.045226 | 0.0054463 | -0.030143 | -0.047875 | -0.081398 | -0.1122 | -0.27228 | -0.379 | -0.44123
|  | TYNDRUM | CT |  |  |  | 0.521 | 0.09759 | 0.10019 | 0.093436 | 0.086266 | 0.07466 | 0.066781 | 0.048609 | 0.026358 | 0.021359 | 0.0036042 | -0.013791 | -0.0443 | -0.053966 | -0.096437 | 0.41604 | 0.41723 | 0.40589 | 0.39319 | 0.37538 | 0.3605 | 0.33447 | 0.30821 | 0.29896 | 0.27806 | 0.258 | 0.20911 | 0.18234 | 0.15061 | 0.14445 | 0.13762 | 0.11946 | 0.098686 | 0.070578 | 0.045226 | 0.0054463 | -0.030143 | -0.044464 | -0.072606 | -0.099235 | -0.17072 | -0.21415 | -0.25986
|  | TYNDRUM | LW |  |  |  | 0.521 | 0.098971 | 0.10208 | 0.09688 | 0.088978 | 0.081458 | 0.064686 | 0.051696 | 0.031872 | 0.018435 | -0.0013086 | -0.019271 | -0.04511 | -0.063431 | -0.12101 | 0.41807 | 0.42009 | 0.41057 | 0.39776 | 0.38434 | 0.36055 | 0.33988 | 0.31557 | 0.29659 | 0.27208 | 0.24954 | 0.20319 | 0.17872 | 0.14783 | 0.14714 | 0.14186 | 0.12577 | 0.10479 | 0.082131 | 0.045862 | 0.012942 | -0.020777 | -0.047875 | -0.081398 | -0.1122 | -0.18499 | -0.23071 | -0.2832
|  | TYNDRUM | ST |  |  |  | 0.521 | 0.10881 | 0.097151 | 0.10464 | 0.098883 | 0.094134 | 0.087851 | 0.077368 | 0.067255 | 0.056512 | 0.040662 | 0.023118 | -0.22302 | -0.33608 | -0.37702 | 0.42843 | 0.41413 | 0.42048 | 0.41218 | 0.40418 | 0.39468 | 0.38084 | 0.36741 | 0.35276 | 0.33275 | 0.31069 | 0.12642 | 0.041203 | 0.011567 | 0.15797 | 0.14065 | 0.14048 | 0.12786 | 0.1155 | 0.10128 | 0.081799 | 0.062946 | 0.042484 | 0.015438 | -0.01415 | -0.27228 | -0.379 | -0.41658
|  | TYNDRUM | FS |  |  |  | 0.521 | 0.11042 | 0.10101 | 0.09979 | 0.10093 | 0.096836 | 0.093345 | 0.088604 | 0.079859 | 0.070664 | 0.059331 | 0.052554 | -0.011354 | -0.23912 | -0.40099 | 0.43153 | 0.42046 | 0.42051 | 0.42016 | 0.41506 | 0.41007 | 0.40396 | 0.39257 | 0.3804 | 0.36604 | 0.35615 | 0.27371 | 0.11192 | -0.01072 | 0.16304 | 0.15014 | 0.14492 | 0.14416 | 0.13744 | 0.13086 | 0.12305 | 0.10739 | 0.090724 | 0.071373 | 0.057569 | -0.059178 | -0.28756 | -0.44123
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 0.35 | 1.0748 | 1.0119 | 0.9187 | 0.79978 | 0.67665 | 0.53657 | 0.3772 | 0.28933 | 0.20806 | 0.11543 | 0.02653 | -0.1836 | -0.29685 | -0.45819 | 1.3199 | 1.2747 | 1.2287 | 1.1645 | 1.1068 | 1.0237 | 0.93645 | 0.86091 | 0.77357 | 0.69242 | 0.61859 | 0.47987 | 0.42049 | 0.30913 | 1.2392 | 1.1737 | 1.098 | 0.99129 | 0.88711 | 0.76627 | 0.63657 | 0.53917 | 0.43311 | 0.33378 | 0.24458 | 0.068865 | -0.028907 | -0.17111
|  | UIG | CT |  |  |  | 0.35 | 1.0748 | 1.0119 | 0.9187 | 0.79978 | 0.67665 | 0.53657 | 0.3772 | 0.28933 | 0.22983 | 0.16604 | 0.11312 | -0.055555 | -0.15503 | -0.27607 | 1.3199 | 1.2768 | 1.2345 | 1.168 | 1.1068 | 1.0353 | 0.95609 | 0.88025 | 0.82867 | 0.76633 | 0.70913 | 0.57273 | 0.50855 | 0.39955 | 1.2392 | 1.1737 | 1.098 | 0.99129 | 0.88711 | 0.76627 | 0.63657 | 0.54244 | 0.48223 | 0.40956 | 0.34579 | 0.19415 | 0.11598 | 0.013139
|  | UIG | LW |  |  |  | 0.35 | 1.0857 | 1.0225 | 0.92934 | 0.81831 | 0.70885 | 0.56238 | 0.40461 | 0.31077 | 0.20806 | 0.11543 | 0.02653 | -0.1836 | -0.29685 | -0.45819 | 1.3231 | 1.2747 | 1.2287 | 1.1645 | 1.1135 | 1.0237 | 0.93645 | 0.86091 | 0.77357 | 0.69242 | 0.61859 | 0.47987 | 0.42049 | 0.30913 | 1.2467 | 1.1781 | 1.1007 | 0.9974 | 0.9085 | 0.77057 | 0.63678 | 0.53917 | 0.43311 | 0.33378 | 0.24458 | 0.068865 | -0.028907 | -0.17111
|  | UIG | ST |  |  |  | 0.35 | 1.0919 | 1.0507 | 0.99209 | 0.93446 | 0.87327 | 0.81671 | 0.75035 | 0.69383 | 0.61837 | 0.55353 | 0.47084 | 0.10875 | -0.0035772 | -0.066801 | 1.3307 | 1.3129 | 1.2803 | 1.2496 | 1.213 | 1.1847 | 1.1415 | 1.105 | 1.049 | 1.0095 | 0.9507 | 0.65411 | 0.5683 | 0.48723 | 1.257 | 1.225 | 1.1712 | 1.1199 | 1.0608 | 1.0138 | 0.94745 | 0.89439 | 0.81739 | 0.76282 | 0.68356 | 0.32135 | 0.23308 | 0.17032
|  | UIG | FS |  |  |  | 0.35 | 1.1221 | 1.0971 | 1.0787 | 1.0601 | 1.0378 | 1.0192 | 0.99267 | 0.94359 | 0.89084 | 0.82919 | 0.76696 | 0.45582 | 0.11809 | -0.016902 | 1.3402 | 1.3282 | 1.3117 | 1.2956 | 1.2737 | 1.2584 | 1.2306 | 1.1948 | 1.16 | 1.1166 | 1.0729 | 0.8509 | 0.60483 | 0.4451 | 1.2781 | 1.2578 | 1.2351 | 1.2134 | 1.1846 | 1.1654 | 1.1308 | 1.08 | 1.0324 | 0.97351 | 0.91411 | 0.63197 | 0.33538 | 0.2279
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | YES | 0.047 | 0.18532 | 0.12787 | 0.03516 | 2.6224 | 2.4965 | 2.3602 | 2.2091 | 2.1546 | 2.1161 | 2.0367 | 1.9906 | 1.7944 | 1.6866 | 1.5482 | 0.78346 | 0.74261 | 0.69541 | 3.3325 | 3.266 | 3.1922 | 3.111 | 3.0532 | 2.9832 | 2.92 | 2.886 | 2.7495 | 2.6861 | 2.5823 | 0.54186 | 0.47197 | 0.39617 | 2.9986 | 2.8798 | 2.7548 | 2.6257 | 2.54 | 2.4451 | 2.3471 | 2.3087 | 2.1085 | 2.0143 | 1.8762
|  | ULLAPOOL | CT |  |  |  | 0.047 | 0.18532 | 0.12787 | 0.03516 | 2.6224 | 2.4965 | 2.3602 | 2.2091 | 2.1546 | 2.1161 | 2.0611 | 2.0411 | 1.8883 | 1.8009 | 1.6925 | 0.78346 | 0.74261 | 0.69726 | 3.3358 | 3.266 | 3.1922 | 3.111 | 3.0532 | 3.0075 | 2.9582 | 2.9355 | 2.7966 | 2.7155 | 2.5863 | 0.54186 | 0.47197 | 0.39617 | 2.9986 | 2.8798 | 2.7548 | 2.6257 | 2.54 | 2.4723 | 2.3992 | 2.3813 | 2.2157 | 2.1429 | 2.043
|  | ULLAPOOL | LW |  |  |  | 0.047 | 0.19544 | 0.13746 | 0.048539 | 2.6427 | 2.5395 | 2.4055 | 2.2653 | 2.2056 | 2.1213 | 2.0367 | 1.9906 | 1.7944 | 1.6866 | 1.5482 | 0.78824 | 0.74301 | 0.69541 | 3.3325 | 3.2805 | 3.1959 | 3.1124 | 3.056 | 2.9832 | 2.92 | 2.886 | 2.7495 | 2.6861 | 2.5911 | 0.5495 | 0.47751 | 0.4034 | 2.9996 | 2.914 | 2.7748 | 2.6463 | 2.5593 | 2.4451 | 2.3471 | 2.3087 | 2.1085 | 2.0143 | 1.8762
|  | ULLAPOOL | ST |  |  |  | 0.047 | 0.20247 | 0.16544 | 0.11911 | 2.7698 | 2.7255 | 2.6743 | 2.625 | 2.5719 | 2.5198 | 2.4584 | 2.3968 | 2.1199 | 1.9892 | 1.9255 | 0.79551 | 0.77585 | 0.74732 | 3.4145 | 3.3891 | 3.3545 | 3.3228 | 3.2825 | 3.2459 | 3.1964 | 3.1473 | 2.9 | 2.7785 | 2.6732 | 0.56231 | 0.52975 | 0.48678 | 3.1347 | 3.0983 | 3.0436 | 2.9959 | 2.9335 | 2.8834 | 2.809 | 2.7389 | 2.4224 | 2.3102 | 2.2661
|  | ULLAPOOL | FS |  |  |  | 0.047 | 0.22882 | 0.2053 | 0.19225 | 2.8794 | 2.863 | 2.8503 | 2.8299 | 2.7924 | 2.7449 | 2.6968 | 2.6584 | 2.3692 | 2.1125 | 1.9747 | 0.8057 | 0.79092 | 0.77661 | 3.4629 | 3.4442 | 3.4308 | 3.4064 | 3.3793 | 3.3395 | 3.2987 | 3.272 | 3.04 | 2.8015 | 2.5823 | 0.58138 | 0.55723 | 0.53786 | 3.2201 | 3.1939 | 3.181 | 3.1489 | 3.1125 | 3.0557 | 2.9975 | 2.9667 | 2.6583 | 2.4127 | 2.3021
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0.544 | -1.2043 | -1.2278 | -1.2742 | -1.3301 | -1.3846 | -1.4555 | -1.5358 | -1.612 | -1.6713 | -1.7538 | -1.8259 | -2.0565 | -2.1869 | -2.3074 | -0.53516 | -0.55863 | -0.58488 | -0.6165 | -0.64061 | -0.68248 | -0.73024 | -0.77276 | -0.81416 | -0.85688 | -0.89398 | -0.99499 | -1.0424 | -1.1073 | -0.99205 | -1.0158 | -1.0546 | -1.102 | -1.1373 | -1.1948 | -1.2616 | -1.3381 | -1.4107 | -1.4826 | -1.5428 | -1.7366 | -1.8417 | -1.9468
|  | UNST | CT |  |  |  | 0.544 | -1.2043 | -1.2234 | -1.2663 | -1.3279 | -1.3846 | -1.4555 | -1.5358 | -1.612 | -1.6629 | -1.7251 | -1.7808 | -2.0223 | -2.1869 | -2.2879 | -0.53471 | -0.54958 | -0.56899 | -0.60498 | -0.63051 | -0.66189 | -0.70239 | -0.7438 | -0.76896 | -0.80035 | -0.8282 | -0.92239 | -1.005 | -1.0836 | -0.99205 | -1.0094 | -1.0419 | -1.0926 | -1.1342 | -1.1891 | -1.2616 | -1.3369 | -1.3898 | -1.4464 | -1.495 | -1.6952 | -1.8316 | -1.9117
|  | UNST | LW |  |  |  | 0.544 | -1.2029 | -1.2278 | -1.2742 | -1.3301 | -1.3776 | -1.4462 | -1.5179 | -1.5967 | -1.6713 | -1.7538 | -1.8259 | -2.0565 | -2.1797 | -2.3074 | -0.53516 | -0.55863 | -0.58488 | -0.6165 | -0.64061 | -0.68248 | -0.73024 | -0.77276 | -0.81416 | -0.85688 | -0.89398 | -0.99499 | -1.0424 | -1.1073 | -0.99087 | -1.0158 | -1.0546 | -1.102 | -1.1373 | -1.1948 | -1.2586 | -1.3381 | -1.4107 | -1.4826 | -1.5428 | -1.7366 | -1.8417 | -1.9468
|  | UNST | ST |  |  |  | 0.544 | -1.1935 | -1.1993 | -1.2138 | -1.2288 | -1.24 | -1.2552 | -1.265 | -1.2811 | -1.2954 | -1.3151 | -1.3356 | -1.5593 | -1.7967 | -1.9886 | -0.52986 | -0.53441 | -0.54764 | -0.56094 | -0.57205 | -0.58627 | -0.59898 | -0.61762 | -0.63933 | -0.66484 | -0.69222 | -0.86179 | -0.95552 | -1.0161 | -0.98386 | -0.98846 | -1.0027 | -1.0171 | -1.0273 | -1.0416 | -1.0491 | -1.0646 | -1.0775 | -1.0966 | -1.1162 | -1.3473 | -1.5192 | -1.6661
|  | UNST | FS |  |  |  | 0.544 | -1.1961 | -1.2052 | -1.217 | -1.2283 | -1.2429 | -1.2548 | -1.2718 | -1.2896 | -1.316 | -1.3428 | -1.362 | -1.5034 | -1.6738 | -1.8617 | -0.52965 | -0.53481 | -0.54276 | -0.55098 | -0.56157 | -0.5715 | -0.58559 | -0.59811 | -0.61809 | -0.63849 | -0.6547 | -0.76658 | -0.87306 | -0.95361 | -0.98524 | -0.99302 | -1.0033 | -1.0125 | -1.0257 | -1.0361 | -1.0519 | -1.0651 | -1.0883 | -1.1118 | -1.1264 | -1.2691 | -1.4391 | -1.6018
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0.199 | 5.5222 | 5.4539 | 5.3253 | 5.1487 | 4.9644 | 4.7359 | 4.4598 | 4.2208 | 4.0028 | 3.7555 | 3.5307 | 2.9355 | 2.5138 | 2.2395 | 6.1499 | 6.1089 | 6.0514 | 5.9793 | 5.9152 | 5.8206 | 5.7083 | 5.6023 | 5.4764 | 5.3626 | 5.2628 | 5.0157 | 4.9082 | 4.7002 | 5.8688 | 5.8199 | 5.7161 | 5.5873 | 5.4446 | 5.2702 | 5.0605 | 4.8917 | 4.7333 | 4.5874 | 4.4248 | 3.9106 | 3.5348 | 3.2853
|  | VOE | CT |  |  |  | 0.199 | 5.5283 | 5.4624 | 5.3272 | 5.1487 | 4.9644 | 4.7359 | 4.4598 | 4.2208 | 4.0028 | 3.7951 | 3.6215 | 2.9534 | 2.5138 | 2.2395 | 6.1621 | 6.1292 | 6.0748 | 5.9921 | 5.9152 | 5.8234 | 5.7095 | 5.6113 | 5.5226 | 5.4376 | 5.3663 | 5.1182 | 4.9155 | 4.7002 | 5.8745 | 5.8315 | 5.7272 | 5.5873 | 5.4446 | 5.2702 | 5.0605 | 4.8917 | 4.7333 | 4.5874 | 4.4672 | 3.9399 | 3.5348 | 3.2853
|  | VOE | LW |  |  |  | 0.199 | 5.5222 | 5.4539 | 5.3253 | 5.1642 | 5.0202 | 4.8039 | 4.5603 | 4.3031 | 4.015 | 3.7555 | 3.5307 | 2.9355 | 2.6521 | 2.3302 | 6.1499 | 6.1089 | 6.0514 | 5.9793 | 5.9176 | 5.8206 | 5.7083 | 5.6023 | 5.4764 | 5.3626 | 5.2628 | 5.0157 | 4.9082 | 4.7975 | 5.8688 | 5.8199 | 5.7161 | 5.5902 | 5.477 | 5.3189 | 5.1402 | 4.9614 | 4.7664 | 4.5916 | 4.4248 | 3.9106 | 3.6387 | 3.3467
|  | VOE | ST |  |  |  | 0.199 | 5.5673 | 5.5438 | 5.5025 | 5.4665 | 5.4271 | 5.3664 | 5.3194 | 5.2574 | 5.1846 | 5.1039 | 5.0492 | 4.3501 | 3.845 | 3.4032 | 6.1774 | 6.1654 | 6.1417 | 6.1191 | 6.0934 | 6.058 | 6.026 | 5.9879 | 5.9406 | 5.8885 | 5.8462 | 5.4703 | 5.2603 | 5.1056 | 5.9037 | 5.8881 | 5.8572 | 5.832 | 5.805 | 5.767 | 5.7393 | 5.7028 | 5.6625 | 5.616 | 5.5918 | 5.0719 | 4.6329 | 4.1954
|  | VOE | FS |  |  |  | 0.199 | 5.5723 | 5.5453 | 5.5049 | 5.4665 | 5.4219 | 5.3746 | 5.3189 | 5.239 | 5.1686 | 5.0821 | 4.9924 | 4.472 | 3.9695 | 3.4637 | 6.1903 | 6.1773 | 6.1586 | 6.1373 | 6.1144 | 6.0881 | 6.0583 | 6.0203 | 5.9827 | 5.9369 | 5.8895 | 5.6194 | 5.3699 | 5.015 | 5.9066 | 5.887 | 5.8567 | 5.8281 | 5.7955 | 5.7631 | 5.7247 | 5.6676 | 5.6187 | 5.5593 | 5.4973 | 5.1455 | 4.7473 | 4.2956
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 3.319 | 13.3947 | 10.53 | 7.8936 | 5.2806 | 3.3789 | 0.6117 | -3.202 | -4.295 | -5.4832 | -6.6097 | -7.6941 | -13.5122 | -19.6375 | -27.2094 | 14.073 | 10.8098 | 7.9452 | 5.2243 | 3.4307 | 0.51491 | -3.7117 | -4.4964 | -5.3344 | -6.163 | -6.9707 | -12.6568 | -20.2257 | -29.2526 | 14.0275 | 10.7239 | 7.6787 | 4.7085 | 2.4919 | -0.83942 | -5.3568 | -6.4305 | -7.5816 | -8.6908 | -9.7614 | -16.2337 | -23.8361 | -33.0467
|  | WALTON | CT |  |  |  | 3.319 | 13.6408 | 12.8375 | 12.3953 | 9.888 | 8.9894 | 7.7607 | 5.3019 | 4.1393 | 3.0001 | 1.9503 | 0.91025 | -3.2108 | -5.8169 | -8.8421 | 14.3019 | 13.5618 | 13.3336 | 10.6218 | 9.9699 | 8.7278 | 6.0926 | 5.1675 | 4.1473 | 3.1823 | 2.1717 | -2.4794 | -6.9934 | -13.6054 | 14.2751 | 13.5139 | 13.1785 | 10.3153 | 9.2816 | 7.878 | 5.0794 | 3.9424 | 2.7713 | 1.689 | 0.60066 | -3.7287 | -6.703 | -10.212
|  | WALTON | LW |  |  |  | 3.319 | 13.3947 | 10.53 | 7.8936 | 5.2806 | 3.3789 | 0.6117 | -3.202 | -4.295 | -5.4832 | -6.6097 | -7.6941 | -13.5122 | -19.6375 | -27.2094 | 14.073 | 10.8098 | 7.9452 | 5.2243 | 3.4307 | 0.51491 | -3.7117 | -4.4964 | -5.3344 | -6.163 | -6.9707 | -12.6568 | -20.2257 | -29.2526 | 14.0275 | 10.7239 | 7.6787 | 4.7085 | 2.4919 | -0.83942 | -5.3568 | -6.4305 | -7.5816 | -8.6908 | -9.7614 | -16.2337 | -23.8361 | -33.0467
|  | WALTON | ST |  |  |  | 3.319 | 13.7241 | 13.0411 | 11.5675 | 10.474 | 9.7602 | 9.3046 | 8.7951 | 8.1844 | 7.546 | 6.8702 | 6.3623 | -1.0048 | -8.5204 | -15.5677 | 14.3288 | 13.6426 | 11.8826 | 10.6357 | 9.8565 | 9.4291 | 8.9516 | 8.3594 | 7.6675 | 6.9091 | 6.3629 | -2.9007 | -13.5576 | -25.038 | 14.3284 | 13.6445 | 11.8781 | 10.6129 | 9.8159 | 9.3691 | 8.8723 | 8.1944 | 7.4129 | 6.6802 | 6.1679 | -2.4021 | -11.4892 | -19.9945
|  | WALTON | FS |  |  |  | 3.319 | 14.0329 | 13.5714 | 13.0321 | 12.4354 | 11.8081 | 11.1445 | 10.2072 | 9.4603 | 8.6303 | 7.7879 | 7.4182 | 4.3932 | 1.8336 | -0.90866 | 14.6 | 14.1251 | 13.5355 | 12.9004 | 12.2236 | 11.5068 | 10.4501 | 9.597 | 8.4736 | 7.3362 | 6.8096 | 3.0614 | -2.4855 | -12.0573 | 14.6278 | 14.1735 | 13.5732 | 12.9216 | 12.2258 | 11.4966 | 10.4354 | 9.6369 | 8.6697 | 7.6436 | 7.2411 | 4.3652 | 1.9414 | -0.9063
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 5.743 | 7.1847 | 6.9745 | 6.6801 | 6.3356 | 5.9459 | 5.5098 | 5.0216 | 4.4699 | 4.0899 | 3.7436 | 3.4738 | 2.6786 | 2.4917 | 2.3588 | 8.9766 | 8.8475 | 8.6857 | 8.4593 | 8.2391 | 8.0101 | 7.7334 | 7.4436 | 7.2308 | 6.9948 | 6.7614 | 5.7492 | 4.6366 | 1.5426 | 8.0464 | 7.8623 | 7.67 | 7.3774 | 7.1306 | 6.8757 | 6.5438 | 6.1733 | 5.8379 | 5.5335 | 5.2936 | 4.5534 | 4.1029 | 3.8155
|  | WATERLOO PLACE | CT |  |  |  | 5.743 | 7.2437 | 7.0378 | 6.7541 | 6.3651 | 5.9459 | 5.5098 | 5.0216 | 4.4699 | 4.0899 | 3.745 | 3.5109 | 2.8264 | 2.6105 | 2.4677 | 9.0054 | 8.8711 | 8.6857 | 8.4593 | 8.2391 | 8.0101 | 7.7334 | 7.4436 | 7.2308 | 6.9948 | 6.8042 | 6.0047 | 5.1953 | 3.8379 | 8.0895 | 7.9004 | 7.67 | 7.3774 | 7.1306 | 6.8757 | 6.5438 | 6.1733 | 5.8379 | 5.5335 | 5.3218 | 4.7076 | 4.5198 | 4.3923
|  | WATERLOO PLACE | LW |  |  |  | 5.743 | 7.1847 | 6.9745 | 6.6801 | 6.3356 | 5.9707 | 5.5536 | 5.1244 | 4.5951 | 4.1598 | 3.7436 | 3.4738 | 2.6786 | 2.4917 | 2.3588 | 8.9766 | 8.8475 | 8.6941 | 8.532 | 8.3657 | 8.1616 | 7.9464 | 7.6893 | 7.4353 | 7.075 | 6.7614 | 5.9162 | 5.7423 | 5.6661 | 8.0464 | 7.8623 | 7.6851 | 7.5064 | 7.3279 | 7.0936 | 6.7751 | 6.3114 | 5.919 | 5.5442 | 5.2936 | 4.5534 | 4.3806 | 4.2555
|  | WATERLOO PLACE | ST |  |  |  | 5.743 | 7.2716 | 7.1265 | 6.9561 | 6.8063 | 6.6178 | 6.4103 | 6.2155 | 5.9577 | 5.7337 | 5.4977 | 5.2912 | 3.7964 | 3.0818 | 2.9382 | 9.0277 | 8.9413 | 8.8241 | 8.7165 | 8.592 | 8.4573 | 8.3216 | 8.1488 | 7.9771 | 7.7678 | 7.4525 | 5.7492 | 5.1557 | 4.1806 | 8.1217 | 8.004 | 7.8628 | 7.732 | 7.5773 | 7.4071 | 7.2289 | 7.0041 | 6.7669 | 6.5093 | 6.2451 | 4.7927 | 4.1029 | 3.9645
|  | WATERLOO PLACE | FS |  |  |  | 5.743 | 7.3587 | 7.2432 | 7.1151 | 6.9943 | 6.849 | 6.7079 | 6.5599 | 6.3896 | 6.2216 | 6.0542 | 5.9017 | 4.9739 | 3.8304 | 2.7791 | 9.0764 | 9.0068 | 8.9239 | 8.8425 | 8.7339 | 8.6252 | 8.5001 | 8.3506 | 8.1943 | 8.0372 | 7.886 | 6.684 | 4.6366 | 1.5426 | 8.1908 | 8.0998 | 7.9957 | 7.8946 | 7.7719 | 7.6497 | 7.5169 | 7.3645 | 7.2028 | 7.0388 | 6.8793 | 5.8744 | 4.8259 | 3.8155
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 0.609 | 13.5303 | 13.2497 | 12.6029 | 11.8907 | 10.9415 | 9.7431 | 8.7281 | 7.9996 | 6.9226 | 5.9541 | 5.0746 | 2.7868 | 1.9334 | 1.1429 | 14.7346 | 14.5407 | 14.2104 | 13.8118 | 13.1382 | 12.3969 | 11.7836 | 11.4444 | 10.9716 | 10.4179 | 9.9095 | 8.4436 | 7.4295 | 5.2185 | 14.0938 | 13.816 | 13.257 | 12.6137 | 11.74 | 10.6666 | 9.732 | 9.0837 | 8.0825 | 7.1821 | 6.3636 | 4.2565 | 3.5653 | 2.8482
|  | WEST KIRKTON | CT |  |  |  | 0.609 | 13.5984 | 13.3232 | 12.6879 | 11.973 | 10.9423 | 9.7946 | 8.7478 | 8.0261 | 7.1858 | 6.394 | 5.6839 | 3.1334 | 1.9334 | 1.1429 | 14.777 | 14.5721 | 14.2211 | 13.8118 | 13.1382 | 12.3969 | 11.7836 | 11.4444 | 10.9716 | 10.4989 | 10.0603 | 8.4436 | 7.4295 | 6.0822 | 14.1559 | 13.8807 | 13.3284 | 12.6772 | 11.74 | 10.7018 | 9.7421 | 9.101 | 8.3314 | 7.5999 | 6.9443 | 4.625 | 3.5653 | 2.8482
|  | WEST KIRKTON | LW |  |  |  | 0.609 | 13.5303 | 13.2497 | 12.6029 | 11.8907 | 10.9415 | 9.7431 | 8.7281 | 7.9996 | 6.9226 | 5.9541 | 5.0746 | 2.7868 | 2.36 | 1.7911 | 14.7346 | 14.5407 | 14.2104 | 13.8324 | 13.2507 | 12.484 | 11.9052 | 11.5912 | 10.9734 | 10.4179 | 9.9095 | 8.6716 | 8.4645 | 8.0895 | 14.0938 | 13.816 | 13.257 | 12.6137 | 11.7592 | 10.6666 | 9.732 | 9.0837 | 8.0825 | 7.1821 | 6.3636 | 4.2565 | 3.8681 | 3.3233
|  | WEST KIRKTON | ST |  |  |  | 0.609 | 13.7379 | 13.6634 | 13.4332 | 13.2479 | 12.803 | 12.2784 | 12.0434 | 11.7821 | 11.436 | 11.0676 | 10.986 | 8.5284 | 7.0726 | 5.5017 | 14.8567 | 14.7942 | 14.6271 | 14.4758 | 14.0746 | 13.6119 | 13.4097 | 13.1815 | 12.8831 | 12.5626 | 12.4734 | 10.5056 | 9.1929 | 7.5711 | 14.2856 | 14.2043 | 14.0152 | 13.8448 | 13.4359 | 12.957 | 12.7392 | 12.4847 | 12.1422 | 11.7446 | 11.6619 | 9.2623 | 7.926 | 6.5828
|  | WEST KIRKTON | FS |  |  |  | 0.609 | 13.8124 | 13.7609 | 13.5243 | 13.3236 | 12.9011 | 12.3939 | 12.1273 | 11.8291 | 11.523 | 11.1662 | 10.7692 | 8.6365 | 6.233 | 4.2526 | 14.923 | 14.868 | 14.7129 | 14.5637 | 14.2031 | 13.7653 | 13.5461 | 13.3076 | 13.0588 | 12.7666 | 12.4413 | 10.7068 | 8.2289 | 5.2185 | 14.3555 | 14.2927 | 14.1013 | 13.9197 | 13.5333 | 13.0765 | 12.8352 | 12.5569 | 12.2724 | 11.9369 | 11.5656 | 9.5688 | 7.312 | 5.5744
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.08849 | 0.078324 | 0.067361 | 0.056355 | 0.048209 | 0.035285 | 0.018252 | 0.012092 | 0.012324 | 0.019364 | 0.016242 | 0.0031452 | -0.020088 | -0.04653 | 0.085335 | 0.07358 | 0.061242 | 0.049139 | 0.040576 | 0.026719 | 0.0080264 | 0.0022075 | 0.0050291 | 0.010627 | 0.0081459 | -0.0073559 | -0.035352 | -0.067039 | 0.090596 | 0.078684 | 0.065629 | 0.052747 | 0.043334 | 0.028591 | 0.0089591 | 0.003022 | 0.0016841 | 0.0089655 | 0.0057735 | -0.0099737 | -0.038475 | -0.070689
|  | WESTER DRUMMOND | CT |  |  |  | 0 | 0.08849 | 0.085435 | 0.082251 | 0.071476 | 0.065384 | 0.05849 | 0.046368 | 0.039292 | 0.041516 | 0.046885 | 0.043722 | 0.032388 | 0.025619 | 0.016004 | 0.085347 | 0.082674 | 0.080221 | 0.068434 | 0.062842 | 0.056325 | 0.043987 | 0.036976 | 0.04066 | 0.044793 | 0.041616 | 0.030086 | 0.022317 | 0.011048 | 0.090596 | 0.087647 | 0.084431 | 0.071798 | 0.065283 | 0.05775 | 0.044349 | 0.037329 | 0.037682 | 0.043425 | 0.039717 | 0.026971 | 0.018873 | 0.0073636
|  | WESTER DRUMMOND | LW |  |  |  | 0 | 0.088575 | 0.078324 | 0.067361 | 0.056355 | 0.048209 | 0.035285 | 0.018252 | 0.012092 | 0.012324 | 0.019364 | 0.016242 | 0.0031452 | -0.020088 | -0.04653 | 0.085335 | 0.07358 | 0.061242 | 0.049139 | 0.040576 | 0.026719 | 0.0080264 | 0.0022075 | 0.0050291 | 0.010627 | 0.0081459 | -0.0073559 | -0.035352 | -0.067039 | 0.090628 | 0.078684 | 0.065629 | 0.052747 | 0.043334 | 0.028591 | 0.0089591 | 0.003022 | 0.0016841 | 0.0089655 | 0.0057735 | -0.0099737 | -0.038475 | -0.070689
|  | WESTER DRUMMOND | ST |  |  |  | 0 | 0.089456 | 0.088223 | 0.081749 | 0.076589 | 0.072896 | 0.069669 | 0.066065 | 0.062051 | 0.057107 | 0.051937 | 0.047195 | 0.029317 | 0.0024954 | -0.020777 | 0.086189 | 0.085256 | 0.077961 | 0.072391 | 0.068703 | 0.065694 | 0.062314 | 0.058449 | 0.053669 | 0.048668 | 0.044302 | 0.023724 | -0.0086168 | -0.037614 | 0.091472 | 0.090341 | 0.082638 | 0.076648 | 0.072548 | 0.069133 | 0.065358 | 0.061188 | 0.056124 | 0.050844 | 0.04621 | 0.021832 | -0.011086 | -0.040061
|  | WESTER DRUMMOND | FS |  |  |  | 0 | 0.08988 | 0.088951 | 0.086402 | 0.083629 | 0.080783 | 0.077715 | 0.073606 | 0.069747 | 0.064486 | 0.059159 | 0.056035 | 0.046627 | 0.047601 | 0.042848 | 0.086377 | 0.085627 | 0.082759 | 0.079671 | 0.076513 | 0.073137 | 0.068519 | 0.064528 | 0.05894 | 0.053288 | 0.050453 | 0.044498 | 0.045831 | 0.040276 | 0.091845 | 0.090989 | 0.08813 | 0.085056 | 0.081863 | 0.078442 | 0.07379 | 0.069557 | 0.063742 | 0.057866 | 0.054816 | 0.043172 | 0.044612 | 0.039159
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.012 | -0.92615 | -0.96777 | -1.0106 | -1.0681 | -1.1252 | -1.1971 | -1.2753 | -1.3335 | -1.3608 | -1.4134 | -1.4542 | -1.5833 | -1.6458 | -1.6982 | -0.45217 | -0.4783 | -0.50128 | -0.53318 | -0.55592 | -0.59172 | -0.62824 | -0.66942 | -0.68172 | -0.71778 | -0.74292 | -0.80613 | -0.85455 | -0.9431 | -0.64231 | -0.68365 | -0.72418 | -0.77768 | -0.82251 | -0.88447 | -0.9503 | -1.0091 | -1.0347 | -1.0865 | -1.1241 | -1.2307 | -1.2765 | -1.3165
|  | WESTRAY | CT |  |  |  | 0.012 | -0.92615 | -0.96777 | -1.0106 | -1.0681 | -1.1252 | -1.1971 | -1.2753 | -1.3335 | -1.3599 | -1.4016 | -1.4383 | -1.5603 | -1.6183 | -1.6662 | -0.45217 | -0.4783 | -0.50128 | -0.53318 | -0.55592 | -0.59172 | -0.62824 | -0.66942 | -0.67804 | -0.70841 | -0.73664 | -0.80471 | -0.84314 | -0.89181 | -0.64231 | -0.68365 | -0.72418 | -0.77768 | -0.82251 | -0.88447 | -0.9503 | -1.0091 | -1.0277 | -1.0703 | -1.1087 | -1.2142 | -1.2574 | -1.2937
|  | WESTRAY | LW |  |  |  | 0.012 | -0.92009 | -0.95672 | -0.99803 | -1.0546 | -1.1052 | -1.1831 | -1.2591 | -1.3165 | -1.3608 | -1.4134 | -1.4542 | -1.5833 | -1.6458 | -1.6982 | -0.44963 | -0.47283 | -0.49351 | -0.52615 | -0.54222 | -0.58426 | -0.61983 | -0.65886 | -0.68172 | -0.71778 | -0.74292 | -0.80613 | -0.8311 | -0.85429 | -0.63672 | -0.67331 | -0.71239 | -0.76752 | -0.80503 | -0.87511 | -0.93978 | -0.99683 | -1.0347 | -1.0865 | -1.1241 | -1.2307 | -1.2765 | -1.3165
|  | WESTRAY | ST |  |  |  | 0.012 | -0.91612 | -0.9378 | -0.97221 | -1.0109 | -1.0512 | -1.0983 | -1.1373 | -1.1806 | -1.2214 | -1.271 | -1.3241 | -1.5338 | -1.6296 | -1.6802 | -0.4466 | -0.45692 | -0.47405 | -0.4944 | -0.51169 | -0.53638 | -0.55063 | -0.57615 | -0.59773 | -0.62857 | -0.66224 | -0.79106 | -0.85455 | -0.90382 | -0.63263 | -0.65305 | -0.68555 | -0.72214 | -0.7549 | -0.79649 | -0.82608 | -0.86601 | -0.90186 | -0.9485 | -0.99869 | -1.1831 | -1.2583 | -1.2956
|  | WESTRAY | FS |  |  |  | 0.012 | -0.89964 | -0.91705 | -0.92951 | -0.94053 | -0.95831 | -0.9707 | -0.99077 | -1.0237 | -1.0462 | -1.0817 | -1.1082 | -1.3085 | -1.5208 | -1.61 | -0.43931 | -0.4499 | -0.45761 | -0.46358 | -0.47614 | -0.48369 | -0.49851 | -0.51995 | -0.53004 | -0.55323 | -0.56787 | -0.68777 | -0.835 | -0.9431 | -0.61725 | -0.63447 | -0.64663 | -0.65693 | -0.67483 | -0.68669 | -0.70705 | -0.73964 | -0.75918 | -0.79398 | -0.81903 | -0.99819 | -1.178 | -1.2418
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 1.686 | 1.4549 | 1.2265 | 0.92087 | 0.55072 | 0.16476 | -0.27669 | -0.7652 | -1.049 | -1.2885 | -1.4744 | -1.6836 | -2.0094 | -2.3801 | -2.7314 | 3.2965 | 3.1745 | 3.0258 | 2.8409 | 2.663 | 2.4503 | 2.2104 | 1.9982 | 1.8191 | 1.6524 | 1.4795 | 1.3479 | 1.093 | 0.76083 | 2.4303 | 2.2248 | 1.9579 | 1.6327 | 1.3027 | 0.9178 | 0.48817 | 0.19597 | -0.044524 | -0.28555 | -0.52446 | -0.76715 | -1.0683 | -1.3762
|  | WHITEHOUSE | CT |  |  |  | 1.686 | 1.4549 | 1.2265 | 0.92087 | 0.55072 | 0.16476 | -0.27669 | -0.7652 | -1.049 | -1.2885 | -1.4744 | -1.6281 | -1.8973 | -2.2152 | -2.5437 | 3.2965 | 3.1745 | 3.0258 | 2.8409 | 2.663 | 2.4503 | 2.2104 | 1.9982 | 1.8191 | 1.6634 | 1.5234 | 1.393 | 1.1762 | 0.85576 | 2.4303 | 2.2248 | 1.9579 | 1.6327 | 1.3027 | 0.9178 | 0.48817 | 0.19597 | -0.044524 | -0.25013 | -0.42706 | -0.62862 | -0.88584 | -1.1664
|  | WHITEHOUSE | LW |  |  |  | 1.686 | 1.4883 | 1.2869 | 0.99509 | 0.65039 | 0.31171 | -0.12824 | -0.58181 | -0.87936 | -1.2188 | -1.4663 | -1.6836 | -2.0094 | -2.3801 | -2.7314 | 3.3074 | 3.2003 | 3.0694 | 2.9033 | 2.7649 | 2.5404 | 2.3187 | 2.1049 | 1.8447 | 1.6524 | 1.4795 | 1.3831 | 1.2358 | 1.0673 | 2.4566 | 2.2746 | 2.0245 | 1.7204 | 1.4398 | 1.0428 | 0.63971 | 0.33746 | -0.016116 | -0.28555 | -0.52446 | -0.76715 | -1.0683 | -1.3762
|  | WHITEHOUSE | ST |  |  |  | 1.686 | 1.5217 | 1.3561 | 1.1571 | 0.95451 | 0.73472 | 0.505 | 0.29406 | 0.055738 | -0.22677 | -0.44666 | -0.7046 | -1.7201 | -1.8342 | -2.0261 | 3.3331 | 3.2583 | 3.1704 | 3.0794 | 2.9741 | 2.8562 | 2.7555 | 2.6082 | 2.4236 | 2.2914 | 2.1221 | 1.3479 | 1.3152 | 1.059 | 2.4931 | 2.3554 | 2.1869 | 2.0147 | 1.8252 | 1.6206 | 1.4383 | 1.2174 | 0.95123 | 0.74625 | 0.49563 | -0.54647 | -0.56453 | -0.72627
|  | WHITEHOUSE | FS |  |  |  | 1.686 | 1.6428 | 1.5389 | 1.4827 | 1.4092 | 1.3472 | 1.2705 | 1.189 | 1.0057 | 0.8248 | 0.64153 | 0.44597 | -0.54326 | -1.625 | -1.787 | 3.3777 | 3.3264 | 3.289 | 3.236 | 3.1945 | 3.139 | 3.0732 | 2.958 | 2.8498 | 2.7319 | 2.6028 | 1.9055 | 1.093 | 0.76083 | 2.5882 | 2.5004 | 2.4456 | 2.3717 | 2.3127 | 2.2368 | 2.1513 | 1.9824 | 1.8235 | 1.6501 | 1.464 | 0.51111 | -0.49296 | -0.54339
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | YES | 0.578 | 6.3543 | 5.9778 | 5.3018 | 4.4309 | 3.9114 | 2.9308 | 1.6545 | 0.37517 | -0.92549 | -2.1302 | -3.2727 | -7.085 | -10.4874 | -13.828 | 8.1295 | 7.8893 | 7.52 | 7.009 | 6.8024 | 6.2426 | 5.5463 | 4.8716 | 4.177 | 3.5372 | 2.9348 | 0.99398 | -0.87731 | -2.9586 | 7.4252 | 7.0946 | 6.5089 | 5.7439 | 5.3153 | 4.4312 | 3.3126 | 2.1821 | 1.0403 | -0.012275 | -1.0032 | -4.219 | -6.9299 | -9.6488
|  | WHITESTRIPES | CT |  |  |  | 0.578 | 6.4895 | 6.1535 | 5.5041 | 4.6522 | 3.9927 | 2.9631 | 1.6545 | 0.43756 | -0.65493 | -1.6871 | -2.6461 | -6.8874 | -10.4874 | -13.828 | 8.1955 | 7.9781 | 7.6251 | 7.1277 | 6.8385 | 6.2818 | 5.5693 | 4.9217 | 4.3447 | 3.7822 | 3.2527 | 0.99398 | -0.87731 | -2.9586 | 7.5258 | 7.2323 | 6.6716 | 5.9253 | 5.3727 | 4.4683 | 3.3126 | 2.2492 | 1.3018 | 0.40413 | -0.4257 | -4.007 | -6.9299 | -9.6488
|  | WHITESTRIPES | LW |  |  |  | 0.578 | 6.3543 | 5.9778 | 5.3018 | 4.4309 | 3.9114 | 2.9308 | 1.6899 | 0.37517 | -0.92549 | -2.1302 | -3.2727 | -7.085 | -9.8189 | -12.6242 | 8.1295 | 7.8893 | 7.52 | 7.009 | 6.8024 | 6.2426 | 5.5463 | 4.8716 | 4.177 | 3.5372 | 2.9348 | 1.0341 | -0.2677 | -1.6409 | 7.4252 | 7.0946 | 6.5089 | 5.7439 | 5.3153 | 4.4312 | 3.3261 | 2.1821 | 1.0403 | -0.012275 | -1.0032 | -4.219 | -6.4373 | -8.6952
|  | WHITESTRIPES | ST |  |  |  | 0.578 | 6.5931 | 6.3552 | 6.1138 | 5.7912 | 5.4534 | 5.0405 | 4.5349 | 4.4154 | 3.9065 | 3.3868 | 2.8402 | -0.51345 | -3.3855 | -6.4135 | 8.2519 | 8.0985 | 7.9347 | 7.725 | 7.5037 | 7.2311 | 6.9025 | 6.8502 | 6.5088 | 6.1626 | 5.7977 | 3.6071 | 1.7441 | -0.35974 | 7.6215 | 7.4216 | 7.2193 | 6.9601 | 6.6932 | 6.3518 | 5.9373 | 5.863 | 5.4329 | 4.9997 | 4.5447 | 1.5655 | -0.86605 | -3.3391
|  | WHITESTRIPES | FS |  |  |  | 0.578 | 6.7584 | 6.5816 | 6.3663 | 6.0666 | 5.7427 | 5.372 | 4.9218 | 4.3909 | 4.2172 | 3.7194 | 3.2057 | 0.20373 | -2.995 | -6.4647 | 8.3353 | 8.2191 | 8.0806 | 7.8873 | 7.6895 | 7.4432 | 7.1425 | 6.7956 | 6.7197 | 6.3892 | 6.0473 | 4.0152 | 1.5932 | -1.3611 | 7.7423 | 7.5968 | 7.4164 | 7.1686 | 6.9159 | 6.6155 | 6.2391 | 5.7935 | 5.6878 | 5.2683 | 4.8358 | 2.2645 | -0.51443 | -3.3368
| CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0.383 | 6.8451 | 6.7817 | 6.6756 | 6.5692 | 6.4321 | 6.3146 | 6.1488 | 6.0467 | 5.9731 | 5.922 | 5.8318 | 5.6404 | 5.5797 | 5.4627 | 7.0337 | 6.9948 | 6.9349 | 6.876 | 6.798 | 6.7341 | 6.6398 | 6.5679 | 6.5144 | 6.4698 | 6.4008 | 6.2644 | 6.2197 | 6.1125 | 6.7752 | 6.7153 | 6.6174 | 6.5202 | 6.3933 | 6.2868 | 6.1241 | 6.0324 | 5.9595 | 5.9031 | 5.8137 | 5.6276 | 5.5739 | 5.4633
|  | WHITING BAY | CT |  |  |  | 0.383 | 6.8451 | 6.7817 | 6.6756 | 6.5692 | 6.4321 | 6.3146 | 6.1488 | 6.0467 | 5.9731 | 5.9346 | 5.8707 | 5.6942 | 5.6342 | 5.5391 | 7.0337 | 6.9948 | 6.9349 | 6.876 | 6.798 | 6.7341 | 6.6398 | 6.5679 | 6.5144 | 6.4849 | 6.4301 | 6.2782 | 6.2197 | 6.1125 | 6.7752 | 6.7153 | 6.6174 | 6.5202 | 6.3933 | 6.2868 | 6.1241 | 6.0324 | 5.9595 | 5.9207 | 5.8559 | 5.6816 | 5.6277 | 5.5393
|  | WHITING BAY | LW |  |  |  | 0.383 | 6.8538 | 6.7977 | 6.7071 | 6.6095 | 6.5017 | 6.3765 | 6.2204 | 6.1151 | 6.0246 | 5.922 | 5.8318 | 5.6404 | 5.5797 | 5.4627 | 7.0386 | 7.0047 | 6.9547 | 6.9011 | 6.8416 | 6.77 | 6.6796 | 6.6081 | 6.5466 | 6.4698 | 6.4008 | 6.2644 | 6.2367 | 6.1636 | 6.7829 | 6.7299 | 6.6464 | 6.5568 | 6.4576 | 6.342 | 6.1962 | 6.0931 | 6.0043 | 5.9031 | 5.8137 | 5.6276 | 5.5739 | 5.4633
|  | WHITING BAY | ST |  |  |  | 0.383 | 6.8683 | 6.8316 | 6.7893 | 6.7476 | 6.6936 | 6.6439 | 6.5792 | 6.5102 | 6.4523 | 6.3765 | 6.2889 | 5.9712 | 5.8955 | 5.8905 | 7.0482 | 7.0273 | 7.0025 | 6.978 | 6.9448 | 6.9143 | 6.8732 | 6.8285 | 6.7897 | 6.7401 | 6.6812 | 6.4336 | 6.3517 | 6.2952 | 6.7972 | 6.7635 | 6.7245 | 6.6862 | 6.6356 | 6.5893 | 6.528 | 6.4621 | 6.4072 | 6.3345 | 6.2501 | 5.94 | 5.8674 | 5.8631
|  | WHITING BAY | FS |  |  |  | 0.383 | 6.8903 | 6.8661 | 6.8504 | 6.8256 | 6.812 | 6.784 | 6.7623 | 6.7115 | 6.6507 | 6.6125 | 6.5504 | 6.2454 | 5.9341 | 5.8375 | 7.0586 | 7.0439 | 7.032 | 7.0138 | 7.003 | 6.9821 | 6.9647 | 6.9306 | 6.8891 | 6.8621 | 6.819 | 6.59 | 6.3323 | 6.1625 | 6.8168 | 6.7944 | 6.7792 | 6.7549 | 6.7419 | 6.7145 | 6.6933 | 6.6451 | 6.5869 | 6.5514 | 6.4919 | 6.1993 | 5.9038 | 5.8131
| MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 1.213 | 5.0658 | 4.7729 | 3.8755 | 3.0591 | 2.1834 | 1.4204 | 0.51564 | -0.13599 | -0.63679 | -0.90822 | -1.3911 | -2.9348 | -3.5668 | -4.1938 | 7.7585 | 7.5932 | 6.9345 | 6.3909 | 5.8252 | 5.4317 | 4.9514 | 4.5693 | 4.2838 | 4.2325 | 3.9518 | 3.0991 | 2.5892 | 1.8858 | 6.5454 | 6.2697 | 5.4649 | 4.7296 | 3.9283 | 3.2514 | 2.4208 | 1.7924 | 1.3117 | 1.0566 | 0.58203 | -0.85695 | -1.4036 | -2.0039
|  | WICK | CT |  |  |  | 1.213 | 5.1711 | 4.8306 | 4.032 | 3.1489 | 2.1834 | 1.4204 | 0.51564 | -0.13599 | -0.63679 | -0.78986 | -1.1442 | -2.6541 | -3.5158 | -4.1931 | 7.8713 | 7.6723 | 7.0974 | 6.4801 | 5.8252 | 5.4317 | 4.9514 | 4.5693 | 4.2838 | 4.252 | 4.0315 | 3.1359 | 2.5892 | 1.8858 | 6.6433 | 6.325 | 5.6065 | 4.8049 | 3.9283 | 3.2514 | 2.4208 | 1.7924 | 1.3117 | 1.2022 | 0.85117 | -0.5437 | -1.2763 | -1.8887
|  | WICK | LW |  |  |  | 1.213 | 5.0658 | 4.7729 | 3.8755 | 3.0591 | 2.1883 | 1.465 | 0.63099 | 0.0045766 | -0.3762 | -0.90822 | -1.3911 | -2.9348 | -3.5668 | -4.1938 | 7.7585 | 7.5932 | 6.9345 | 6.3909 | 5.8261 | 5.4741 | 5.0517 | 4.7042 | 4.5378 | 4.2325 | 3.9518 | 3.0991 | 2.8205 | 2.4508 | 6.5454 | 6.2697 | 5.4649 | 4.7296 | 3.9488 | 3.2933 | 2.5225 | 1.9202 | 1.5778 | 1.0566 | 0.58203 | -0.85695 | -1.4036 | -2.0039
|  | WICK | ST |  |  |  | 1.213 | 5.2798 | 5.0487 | 4.4733 | 3.9109 | 3.3198 | 2.9781 | 2.6256 | 2.3204 | 2.0304 | 1.7013 | 1.351 | -0.022606 | -0.96121 | -1.7385 | 7.9299 | 7.8049 | 7.3321 | 6.8751 | 6.3963 | 6.1885 | 5.9754 | 5.7838 | 5.6056 | 5.3945 | 5.1653 | 4.2456 | 3.5763 | 2.8955 | 6.7471 | 6.5426 | 6.0271 | 5.5178 | 4.9803 | 4.6679 | 4.3386 | 4.0445 | 3.7663 | 3.4411 | 3.0928 | 1.7684 | 0.9259 | 0.26364
|  | WICK | FS |  |  |  | 1.213 | 5.571 | 5.4175 | 5.0591 | 4.734 | 4.3422 | 4.1539 | 3.9711 | 3.6897 | 3.3672 | 3.077 | 2.7303 | 1.0755 | -0.65903 | -1.7193 | 8.1252 | 8.0352 | 7.7022 | 7.4015 | 7.0359 | 6.8919 | 6.7449 | 6.5634 | 6.341 | 6.1477 | 5.9078 | 4.7614 | 3.4269 | 2.1174 | 7.0047 | 6.8677 | 6.5393 | 6.2414 | 5.8803 | 5.7008 | 5.5254 | 5.2631 | 4.9573 | 4.6898 | 4.3604 | 2.8147 | 1.2128 | 0.26627
| #N/A | WOODHILL | MINIMUM HEADROOM | #N/A | NO | #N/A | 4.963 | 6.6372 | 6.0689 | 5.1556 | 4.0541 | 2.8606 | 1.232 | -0.45485 | -2.4109 | -4.5583 | -6.5055 | -8.2965 | -12.8286 | -13.2989 | -14.4056 | 7.9544 | 7.5689 | 7.0481 | 6.3815 | 5.6331 | 4.8325 | 3.9409 | 2.7034 | 1.3341 | 0.053566 | -1.3417 | -4.4286 | -5.9063 | -12.3815 | 7.7881 | 7.2702 | 6.4387 | 5.4301 | 4.3403 | 2.8529 | 1.3229 | -0.45631 | -2.4083 | -4.1786 | -5.8053 | -9.9333 | -10.3682 | -11.304
|  | WOODHILL | CT |  |  |  | 4.963 | 6.7065 | 6.17 | 5.3133 | 4.2496 | 3.0438 | 1.7871 | 0.36738 | -1.6553 | -3.3259 | -4.9326 | -6.3542 | -11.151 | -13.0474 | -14.3967 | 7.9625 | 7.5726 | 7.0481 | 6.3815 | 5.6331 | 4.8325 | 3.9719 | 2.7034 | 1.6669 | 0.60614 | -0.37217 | -3.8703 | -5.9063 | -8.9879 | 7.8454 | 7.3631 | 6.5848 | 5.6048 | 4.512 | 3.3672 | 2.0847 | 0.24246 | -1.2783 | -2.7368 | -4.0246 | -8.3726 | -10.1011 | -11.2995
|  | WOODHILL | LW |  |  |  | 4.963 | 6.6372 | 6.0689 | 5.1556 | 4.0541 | 2.8606 | 1.232 | -0.45485 | -2.4109 | -4.5583 | -6.5055 | -8.2965 | -12.8286 | -13.2989 | -14.4056 | 7.9544 | 7.5689 | 7.0909 | 6.496 | 5.8616 | 4.9058 | 3.9409 | 2.744 | 1.3341 | 0.053566 | -1.3417 | -4.4286 | -4.6253 | -5.1482 | 7.7881 | 7.2702 | 6.4387 | 5.4301 | 4.3403 | 2.8529 | 1.3229 | -0.45631 | -2.4083 | -4.1786 | -5.8053 | -9.9333 | -10.3682 | -11.304
|  | WOODHILL | ST |  |  |  | 4.963 | 6.9191 | 6.7043 | 6.4357 | 6.1284 | 5.7391 | 5.2957 | 4.7256 | 4.1178 | 3.3251 | 2.4397 | 0.87015 | -7.6131 | -10.9105 | -12.5696 | 8.0916 | 7.9221 | 7.704 | 7.4573 | 7.1456 | 6.784 | 6.3347 | 5.811 | 5.102 | 4.5217 | 3.2987 | -3.2182 | -5.4832 | -6.9105 | 8.0386 | 7.8465 | 7.6024 | 7.3271 | 6.9772 | 6.5734 | 6.0671 | 5.5106 | 4.3529 | 3.1108 | 1.5995 | -6.4446 | -9.222 | -10.2862
|  | WOODHILL | FS |  |  |  | 4.963 | 7.0487 | 6.8918 | 6.6379 | 6.3224 | 5.9962 | 5.6068 | 5.1298 | 4.6166 | 3.9658 | 3.304 | 2.5933 | -2.8795 | -9.237 | -13.5523 | 8.1518 | 8.0049 | 7.8114 | 7.569 | 7.3132 | 6.9975 | 6.594 | 6.1539 | 5.5784 | 4.9883 | 4.3494 | 0.15164 | -5.4603 | -12.3815 | 8.1474 | 8.0086 | 7.7791 | 7.4981 | 7.2085 | 6.8589 | 6.4383 | 5.9691 | 5.376 | 4.7719 | 4.1237 | -1.334 | -7.0047 | -11.0365

## Primary Headroom Gen
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [13 empty] | Generation Headroom Summer (MVA) | [13 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.21785 | 0.21745 | 0.21728 | 0.21703 | 0.21676 | 0.21646 | 0.21563 | 0.21448 | 0.21333 | 0.21218 | 0.21105 | 0.20519 | 0.19796 | 0.18764 | 0.2172 | 0.21679 | 0.2166 | 0.21627 | 0.21591 | 0.21552 | 0.21512 | 0.21406 | 0.21254 | 0.21102 | 0.20952 | 0.20102 | 0.19163 | 0.18023 | 0.21694 | 0.21654 | 0.21637 | 0.21612 | 0.21584 | 0.21554 | 0.21523 | 0.21498 | 0.21374 | 0.21209 | 0.21046 | 0.20884 | 0.20718 | 0.20551
|  | ABERCHALDER | CT |  |  |  | 0 | 0.21785 | 0.21772 | 0.21761 | 0.21746 | 0.21727 | 0.21706 | 0.21683 | 0.21668 | 0.21652 | 0.21637 | 0.21621 | 0.21521 | 0.21287 | 0.20947 | 0.21721 | 0.21706 | 0.21694 | 0.21676 | 0.21656 | 0.21632 | 0.21607 | 0.2159 | 0.21572 | 0.21555 | 0.21537 | 0.21427 | 0.21261 | 0.20889 | 0.21694 | 0.2168 | 0.21669 | 0.21654 | 0.21636 | 0.21614 | 0.21591 | 0.21576 | 0.21561 | 0.21546 | 0.2153 | 0.21514 | 0.21494 | 0.21474
|  | ABERCHALDER | LW |  |  |  | 0 | 0.21785 | 0.21745 | 0.21728 | 0.21703 | 0.21676 | 0.21646 | 0.21563 | 0.21448 | 0.21333 | 0.21218 | 0.21105 | 0.20519 | 0.19796 | 0.18764 | 0.2172 | 0.21679 | 0.2166 | 0.21627 | 0.21591 | 0.21552 | 0.21512 | 0.21406 | 0.21254 | 0.21102 | 0.20952 | 0.20102 | 0.19163 | 0.18023 | 0.21694 | 0.21654 | 0.21637 | 0.21612 | 0.21584 | 0.21554 | 0.21523 | 0.21498 | 0.21374 | 0.21209 | 0.21046 | 0.20884 | 0.20718 | 0.20551
|  | ABERCHALDER | ST |  |  |  | 0 | 0.21785 | 0.2178 | 0.21778 | 0.21772 | 0.21764 | 0.21755 | 0.21745 | 0.21742 | 0.21738 | 0.21735 | 0.21731 | 0.21716 | 0.21642 | 0.21604 | 0.21723 | 0.21718 | 0.21715 | 0.21708 | 0.21699 | 0.21688 | 0.21677 | 0.21672 | 0.21667 | 0.21662 | 0.21657 | 0.21635 | 0.21556 | 0.21513 | 0.21694 | 0.21689 | 0.21687 | 0.2168 | 0.21673 | 0.21664 | 0.21654 | 0.21651 | 0.21647 | 0.21643 | 0.2164 | 0.21625 | 0.21551 | 0.21513
|  | ABERCHALDER | FS |  |  |  | 0 | 0.21785 | 0.21781 | 0.2178 | 0.2178 | 0.2178 | 0.21779 | 0.21779 | 0.21777 | 0.21775 | 0.21773 | 0.2177 | 0.21764 | 0.2173 | 0.21658 | 0.21723 | 0.21718 | 0.21718 | 0.21718 | 0.21717 | 0.21716 | 0.21714 | 0.21711 | 0.21708 | 0.21705 | 0.21701 | 0.21689 | 0.2165 | 0.21573 | 0.21694 | 0.21689 | 0.21689 | 0.21689 | 0.21689 | 0.21688 | 0.21688 | 0.21686 | 0.21684 | 0.21682 | 0.21679 | 0.21673 | 0.21639 | 0.21567
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0.025263 | 8.1758 | 8.1535 | 8.1327 | 8.1098 | 8.0845 | 8.0568 | 8.028 | 8.0042 | 7.98 | 7.9557 | 7.9314 | 7.6755 | 7.0844 | 6.3183 | 8.0982 | 8.0759 | 8.0551 | 8.0322 | 8.0069 | 7.9792 | 7.9319 | 7.8218 | 7.7123 | 7.6023 | 7.4936 | 6.9286 | 6.2751 | 5.4467 | 8.3576 | 8.3353 | 8.3145 | 8.2916 | 8.2663 | 8.2386 | 8.2098 | 8.186 | 8.1262 | 8.0176 | 7.9101 | 7.8036 | 7.6914 | 7.5787
|  | ABERFELDY | CT |  |  |  | 0.025263 | 8.1758 | 8.1535 | 8.1327 | 8.1098 | 8.0845 | 8.0568 | 8.028 | 8.0042 | 7.98 | 7.9557 | 7.9314 | 7.7837 | 7.5209 | 6.987 | 8.0982 | 8.0759 | 8.0551 | 8.0322 | 8.0069 | 7.9792 | 7.9504 | 7.9266 | 7.8821 | 7.7991 | 7.7166 | 7.2837 | 6.7839 | 6.2068 | 8.3576 | 8.3353 | 8.3145 | 8.2916 | 8.2663 | 8.2386 | 8.2098 | 8.186 | 8.1618 | 8.1375 | 8.1132 | 8.0479 | 7.9622 | 7.8761
|  | ABERFELDY | LW |  |  |  | 0.025263 | 8.1977 | 8.166 | 8.1492 | 8.1267 | 8.1017 | 8.0741 | 8.0445 | 8.0197 | 7.9947 | 7.9686 | 7.9428 | 7.6755 | 7.0844 | 6.3183 | 8.1201 | 8.0884 | 8.0716 | 8.0491 | 8.0241 | 7.9965 | 7.9319 | 7.8218 | 7.7123 | 7.6023 | 7.4936 | 6.9286 | 6.2751 | 5.4467 | 8.3795 | 8.3478 | 8.331 | 8.3085 | 8.2835 | 8.2559 | 8.2263 | 8.2015 | 8.1262 | 8.0176 | 7.9101 | 7.8036 | 7.6914 | 7.5787
|  | ABERFELDY | ST |  |  |  | 0.025263 | 8.2019 | 8.1948 | 8.1897 | 8.1825 | 8.1733 | 8.1632 | 8.1523 | 8.1461 | 8.1399 | 8.1338 | 8.1279 | 8.0992 | 8.0232 | 7.9725 | 8.1243 | 8.1172 | 8.1121 | 8.1049 | 8.0957 | 8.0856 | 8.0747 | 8.0685 | 8.0623 | 8.0562 | 8.0503 | 7.9428 | 7.6839 | 7.4538 | 8.3837 | 8.3766 | 8.3715 | 8.3643 | 8.3551 | 8.345 | 8.3341 | 8.3279 | 8.3217 | 8.3156 | 8.3097 | 8.281 | 8.0988 | 7.8715
|  | ABERFELDY | FS |  |  |  | 0.025263 | 8.2036 | 8.1984 | 8.1957 | 8.193 | 8.1902 | 8.1873 | 8.1844 | 8.1804 | 8.1771 | 8.1735 | 8.1698 | 8.1527 | 8.1124 | 8.0391 | 8.126 | 8.1208 | 8.1181 | 8.1154 | 8.1126 | 8.1097 | 8.1068 | 8.1028 | 8.0995 | 8.0959 | 8.0922 | 8.0751 | 7.9799 | 7.7672 | 8.3854 | 8.3802 | 8.3775 | 8.3748 | 8.372 | 8.3691 | 8.3662 | 8.3622 | 8.3588 | 8.3553 | 8.3516 | 8.3345 | 8.2942 | 8.181
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.031579 | 5.5334 | 5.5211 | 5.5148 | 5.5062 | 5.4963 | 5.4856 | 5.4734 | 5.4637 | 5.4538 | 5.4438 | 5.4339 | 5.3737 | 5.2815 | 5.1088 | 5.305 | 5.2779 | 5.2558 | 5.2182 | 5.18 | 5.1422 | 5.1038 | 5.0668 | 5.03 | 4.9934 | 4.9574 | 4.7684 | 4.5451 | 4.2424 | 5.4049 | 5.3926 | 5.3864 | 5.3777 | 5.3679 | 5.3571 | 5.3449 | 5.3352 | 5.3253 | 5.3073 | 5.282 | 5.2571 | 5.2299 | 5.2023
|  | ABERFOYLE | CT |  |  |  | 0.031579 | 5.5334 | 5.5277 | 5.5228 | 5.5164 | 5.5088 | 5.5001 | 5.4907 | 5.4843 | 5.4777 | 5.4711 | 5.4644 | 5.422 | 5.3566 | 5.2538 | 5.3075 | 5.2921 | 5.2764 | 5.25 | 5.2228 | 5.1954 | 5.168 | 5.1427 | 5.1176 | 5.0926 | 5.0678 | 4.9365 | 4.7811 | 4.5899 | 5.4049 | 5.3993 | 5.3943 | 5.388 | 5.3804 | 5.3716 | 5.3623 | 5.3559 | 5.3493 | 5.3426 | 5.3359 | 5.329 | 5.3205 | 5.304
|  | ABERFOYLE | LW |  |  |  | 0.031579 | 5.5351 | 5.5211 | 5.5148 | 5.5062 | 5.4963 | 5.4856 | 5.4734 | 5.4637 | 5.4538 | 5.4438 | 5.4339 | 5.3737 | 5.2815 | 5.1088 | 5.305 | 5.2779 | 5.2558 | 5.2182 | 5.18 | 5.1422 | 5.1038 | 5.0668 | 5.03 | 4.9934 | 4.9574 | 4.7684 | 4.5451 | 4.2424 | 5.4066 | 5.3926 | 5.3864 | 5.3777 | 5.3679 | 5.3571 | 5.3449 | 5.3352 | 5.3253 | 5.3073 | 5.282 | 5.2571 | 5.2299 | 5.2023
|  | ABERFOYLE | ST |  |  |  | 0.031579 | 5.5359 | 5.5341 | 5.5332 | 5.5309 | 5.528 | 5.5246 | 5.5209 | 5.5195 | 5.5181 | 5.5167 | 5.5154 | 5.5096 | 5.4803 | 5.4652 | 5.3249 | 5.3217 | 5.3195 | 5.3041 | 5.2884 | 5.2727 | 5.257 | 5.2428 | 5.2289 | 5.2153 | 5.202 | 5.1389 | 5.0547 | 4.9863 | 5.4075 | 5.4056 | 5.4048 | 5.4024 | 5.3995 | 5.3962 | 5.3924 | 5.391 | 5.3896 | 5.3883 | 5.387 | 5.3811 | 5.3518 | 5.3119
|  | ABERFOYLE | FS |  |  |  | 0.031579 | 5.5359 | 5.5342 | 5.5341 | 5.534 | 5.5339 | 5.5337 | 5.5335 | 5.5328 | 5.532 | 5.5311 | 5.5301 | 5.5274 | 5.5138 | 5.4839 | 5.3257 | 5.3236 | 5.3222 | 5.3203 | 5.3165 | 5.3074 | 5.2985 | 5.288 | 5.2774 | 5.2667 | 5.256 | 5.2058 | 5.1471 | 5.074 | 5.4075 | 5.4057 | 5.4057 | 5.4056 | 5.4054 | 5.4053 | 5.4051 | 5.4043 | 5.4035 | 5.4026 | 5.4016 | 5.399 | 5.3853 | 5.3554
| KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 0.078947 | 6.2489 | 6.2315 | 6.215 | 6.1975 | 6.1783 | 6.1576 | 6.1361 | 6.1178 | 6.0992 | 6.0805 | 6.0618 | 5.95 | 5.7954 | 5.4745 | 6.0256 | 6.0082 | 5.9918 | 5.9742 | 5.955 | 5.9343 | 5.9129 | 5.8872 | 5.8307 | 5.7738 | 5.7177 | 5.4216 | 5.0692 | 4.6033 | 6.053 | 6.0356 | 6.0192 | 6.0017 | 5.9825 | 5.9618 | 5.9403 | 5.9219 | 5.8988 | 5.8449 | 5.7918 | 5.7393 | 5.6832 | 5.6265
|  | ABERLOUR | CT |  |  |  | 0.078947 | 6.2489 | 6.2315 | 6.215 | 6.1975 | 6.1783 | 6.1576 | 6.1361 | 6.1178 | 6.0992 | 6.0805 | 6.0618 | 5.95 | 5.7954 | 5.588 | 6.0256 | 6.0082 | 5.9918 | 5.9742 | 5.955 | 5.9343 | 5.9129 | 5.8945 | 5.8759 | 5.8455 | 5.8004 | 5.562 | 5.277 | 4.9423 | 6.053 | 6.0356 | 6.0192 | 6.0017 | 5.9825 | 5.9618 | 5.9403 | 5.9219 | 5.9033 | 5.8847 | 5.866 | 5.823 | 5.778 | 5.7318
|  | ABERLOUR | LW |  |  |  | 0.078947 | 6.2674 | 6.2449 | 6.2331 | 6.217 | 6.1994 | 6.1797 | 6.1584 | 6.1405 | 6.1223 | 6.1032 | 6.0843 | 5.9706 | 5.8024 | 5.4745 | 6.0441 | 6.0217 | 6.0098 | 5.9938 | 5.9761 | 5.9564 | 5.9352 | 5.8872 | 5.8307 | 5.7738 | 5.7177 | 5.4216 | 5.0692 | 4.6033 | 6.0716 | 6.0491 | 6.0372 | 6.0212 | 6.0036 | 5.9839 | 5.9626 | 5.9446 | 5.8988 | 5.8449 | 5.7918 | 5.7393 | 5.6832 | 5.6265
|  | ABERLOUR | ST |  |  |  | 0.078947 | 6.2716 | 6.2667 | 6.263 | 6.2574 | 6.2502 | 6.2424 | 6.235 | 6.2306 | 6.2262 | 6.2219 | 6.2177 | 6.1956 | 6.1417 | 6.1053 | 6.0484 | 6.0434 | 6.0397 | 6.0341 | 6.027 | 6.0192 | 6.0117 | 6.0073 | 6.0029 | 5.9986 | 5.9944 | 5.9719 | 5.839 | 5.7265 | 6.0758 | 6.0708 | 6.0672 | 6.0615 | 6.0544 | 6.0466 | 6.0391 | 6.0348 | 6.0304 | 6.0261 | 6.0218 | 5.9998 | 5.908 | 5.8016
|  | ABERLOUR | FS |  |  |  | 0.078947 | 6.2725 | 6.2686 | 6.2668 | 6.265 | 6.2631 | 6.2612 | 6.2593 | 6.2567 | 6.2539 | 6.2511 | 6.2481 | 6.2329 | 6.207 | 6.1605 | 6.0492 | 6.0453 | 6.0435 | 6.0417 | 6.0399 | 6.0379 | 6.036 | 6.0334 | 6.0306 | 6.0278 | 6.0248 | 6.0097 | 5.9838 | 5.8869 | 6.0766 | 6.0727 | 6.071 | 6.0692 | 6.0673 | 6.0654 | 6.0634 | 6.0608 | 6.0581 | 6.0552 | 6.0523 | 6.0371 | 6.0112 | 5.9535
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0 | 1.6674 | 1.6595 | 1.6531 | 1.6451 | 1.6349 | 1.624 | 1.6127 | 1.6034 | 1.594 | 1.5846 | 1.5753 | 1.5173 | 1.4299 | 1.2742 | 1.627 | 1.6185 | 1.6117 | 1.6023 | 1.5911 | 1.5792 | 1.5669 | 1.5566 | 1.5462 | 1.5357 | 1.5253 | 1.4528 | 1.2668 | 1.0115 | 1.4373 | 1.416 | 1.3976 | 1.3682 | 1.3376 | 1.3072 | 1.2773 | 1.2476 | 1.2182 | 1.189 | 1.1604 | 1.1322 | 1.1022 | 1.0711
|  | ABERNETHY | CT |  |  |  | 0 | 1.6674 | 1.6599 | 1.6531 | 1.6451 | 1.6368 | 1.6276 | 1.6179 | 1.6099 | 1.6017 | 1.5935 | 1.5853 | 1.5369 | 1.4661 | 1.3653 | 1.627 | 1.6192 | 1.6119 | 1.6031 | 1.5941 | 1.5842 | 1.5738 | 1.5651 | 1.5562 | 1.5473 | 1.5384 | 1.4867 | 1.4126 | 1.2619 | 1.4373 | 1.4222 | 1.4069 | 1.3839 | 1.3611 | 1.3382 | 1.3153 | 1.2934 | 1.2716 | 1.2501 | 1.2287 | 1.2074 | 1.1849 | 1.1622
|  | ABERNETHY | LW |  |  |  | 0 | 1.6724 | 1.6595 | 1.6533 | 1.6451 | 1.6349 | 1.624 | 1.6127 | 1.6034 | 1.594 | 1.5846 | 1.5753 | 1.5173 | 1.4299 | 1.2742 | 1.6319 | 1.6185 | 1.6117 | 1.6023 | 1.5911 | 1.5792 | 1.5669 | 1.5566 | 1.5462 | 1.5357 | 1.5253 | 1.4528 | 1.2668 | 1.0115 | 1.4386 | 1.416 | 1.3976 | 1.3682 | 1.3376 | 1.3072 | 1.2773 | 1.2476 | 1.2182 | 1.189 | 1.1604 | 1.1322 | 1.1022 | 1.0711
|  | ABERNETHY | ST |  |  |  | 0 | 1.6732 | 1.6709 | 1.6693 | 1.6665 | 1.6633 | 1.6597 | 1.6558 | 1.6538 | 1.6518 | 1.6498 | 1.6479 | 1.6389 | 1.611 | 1.5946 | 1.6335 | 1.6311 | 1.6295 | 1.6263 | 1.6226 | 1.6185 | 1.6141 | 1.6116 | 1.6091 | 1.6067 | 1.6043 | 1.5932 | 1.5632 | 1.545 | 1.4545 | 1.4517 | 1.4498 | 1.4373 | 1.4245 | 1.4118 | 1.3991 | 1.3877 | 1.3765 | 1.3656 | 1.355 | 1.305 | 1.2383 | 1.1851
|  | ABERNETHY | FS |  |  |  | 0 | 1.6749 | 1.6735 | 1.6726 | 1.6717 | 1.6708 | 1.6698 | 1.6688 | 1.6673 | 1.6658 | 1.6642 | 1.6626 | 1.6562 | 1.6409 | 1.6126 | 1.6352 | 1.6338 | 1.6329 | 1.6319 | 1.6308 | 1.6295 | 1.6282 | 1.6263 | 1.6244 | 1.6224 | 1.6204 | 1.612 | 1.5949 | 1.5649 | 1.4566 | 1.455 | 1.4537 | 1.452 | 1.4478 | 1.4407 | 1.4336 | 1.4243 | 1.4151 | 1.4057 | 1.3964 | 1.3522 | 1.3019 | 1.2407
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 0.052632 | 16.298 | 16.2575 | 16.2282 | 16.189 | 16.1442 | 15.9771 | 15.7582 | 15.5383 | 15.3265 | 15.1221 | 14.9336 | 14.0218 | 13.0388 | 11.7744 | 14.6023 | 14.352 | 14.1155 | 13.8079 | 13.5093 | 13.2255 | 12.9636 | 12.6962 | 12.4394 | 12.1921 | 11.9648 | 10.8801 | 9.7409 | 8.3301 | 15.1364 | 14.9127 | 14.7052 | 14.4352 | 14.1592 | 13.8917 | 13.6443 | 13.3941 | 13.1536 | 12.9218 | 12.7085 | 12.5083 | 12.3018 | 12.0965
|  | ABOYNE | CT |  |  |  | 0.052632 | 16.298 | 16.2672 | 16.2402 | 16.2074 | 16.1697 | 16.1276 | 16.0832 | 16.0497 | 15.8981 | 15.7531 | 15.6155 | 14.9271 | 14.2022 | 13.3643 | 14.667 | 14.5194 | 14.3599 | 14.1528 | 13.9372 | 13.7175 | 13.5221 | 13.3324 | 13.1469 | 12.9734 | 12.8089 | 11.9939 | 11.1586 | 10.2163 | 15.1893 | 15.0581 | 14.9171 | 14.7343 | 14.5436 | 14.3488 | 14.1668 | 13.988 | 13.8129 | 13.6491 | 13.4939 | 13.3391 | 13.1811 | 13.0276
|  | ABOYNE | LW |  |  |  | 0.052632 | 16.3174 | 16.2575 | 16.2282 | 16.189 | 16.1442 | 15.9771 | 15.7582 | 15.5383 | 15.3265 | 15.1221 | 14.9336 | 14.0218 | 13.0388 | 11.7744 | 14.6023 | 14.352 | 14.1155 | 13.8079 | 13.5093 | 13.2255 | 12.9636 | 12.6962 | 12.4394 | 12.1921 | 11.9648 | 10.8801 | 9.7409 | 8.3301 | 15.1364 | 14.9127 | 14.7052 | 14.4352 | 14.1592 | 13.8917 | 13.6443 | 13.3941 | 13.1536 | 12.9218 | 12.7085 | 12.5083 | 12.3018 | 12.0965
|  | ABOYNE | ST |  |  |  | 0.052632 | 16.3224 | 16.3129 | 16.307 | 16.2954 | 16.281 | 16.2648 | 16.247 | 16.2382 | 16.2294 | 16.2209 | 16.2125 | 16.0995 | 15.6936 | 15.3561 | 14.7917 | 14.7473 | 14.7005 | 14.5938 | 14.4806 | 14.3652 | 14.2563 | 14.1459 | 14.0348 | 13.9278 | 13.825 | 13.359 | 12.8806 | 12.4737 | 15.3 | 15.2605 | 15.2194 | 15.126 | 15.0266 | 14.9251 | 14.8289 | 14.7328 | 14.636 | 14.5428 | 14.4532 | 14.0214 | 13.5679 | 13.1862
|  | ABOYNE | FS |  |  |  | 0.052632 | 16.3241 | 16.3161 | 16.3141 | 16.3121 | 16.3099 | 16.3075 | 16.3051 | 16.3007 | 16.296 | 16.2909 | 16.2855 | 16.264 | 16.1737 | 15.8376 | 14.8092 | 14.7733 | 14.7404 | 14.7018 | 14.6487 | 14.5777 | 14.5079 | 14.4273 | 14.3428 | 14.2599 | 14.1778 | 13.7965 | 13.4454 | 13.0533 | 15.3153 | 15.2833 | 15.2547 | 15.2213 | 15.1752 | 15.1139 | 15.0535 | 14.9835 | 14.9102 | 14.8382 | 14.7668 | 14.4348 | 14.1037 | 13.7306
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | YES | 0 | 1.4013 | 1.3942 | 1.3897 | 1.3829 | 1.3756 | 1.3682 | 1.3607 | 1.3537 | 1.3468 | 1.3399 | 1.3331 | 1.2958 | 1.2469 | 1.1696 | 1.1782 | 1.1729 | 1.1705 | 1.1547 | 1.1372 | 1.1199 | 1.1027 | 1.0852 | 1.0678 | 1.0506 | 1.0336 | 0.94698 | 0.84802 | 0.72164 | 1.1237 | 1.1118 | 1.1013 | 1.0844 | 1.0672 | 1.0503 | 1.0335 | 1.0164 | 0.9994 | 0.98253 | 0.96591 | 0.9495 | 0.93237 | 0.91513
|  | ACHILTIBUIE | CT |  |  |  | 0 | 1.4015 | 1.3985 | 1.3955 | 1.391 | 1.3861 | 1.3809 | 1.3755 | 1.371 | 1.3664 | 1.3618 | 1.3573 | 1.3317 | 1.2983 | 1.2539 | 1.1782 | 1.1764 | 1.1749 | 1.17 | 1.1581 | 1.1461 | 1.1341 | 1.1221 | 1.1101 | 1.0982 | 1.0865 | 1.0256 | 0.95697 | 0.8782 | 1.1246 | 1.1182 | 1.1109 | 1.0994 | 1.0877 | 1.076 | 1.0643 | 1.0525 | 1.0408 | 1.0292 | 1.0178 | 1.0063 | 0.99439 | 0.98239
|  | ACHILTIBUIE | LW |  |  |  | 0 | 1.4013 | 1.3942 | 1.3897 | 1.3829 | 1.3756 | 1.3682 | 1.3607 | 1.3537 | 1.3468 | 1.3399 | 1.3331 | 1.2958 | 1.2469 | 1.1696 | 1.1782 | 1.1729 | 1.1705 | 1.1547 | 1.1372 | 1.1199 | 1.1027 | 1.0852 | 1.0678 | 1.0506 | 1.0336 | 0.94698 | 0.84802 | 0.72164 | 1.1237 | 1.1118 | 1.1013 | 1.0844 | 1.0672 | 1.0503 | 1.0335 | 1.0164 | 0.9994 | 0.98253 | 0.96591 | 0.9495 | 0.93237 | 0.91513
|  | ACHILTIBUIE | ST |  |  |  | 0 | 1.4036 | 1.4029 | 1.4023 | 1.3998 | 1.3971 | 1.3943 | 1.3914 | 1.3893 | 1.3872 | 1.3852 | 1.3832 | 1.3738 | 1.3565 | 1.3445 | 1.1782 | 1.1776 | 1.1773 | 1.1764 | 1.1754 | 1.1742 | 1.1718 | 1.1649 | 1.158 | 1.1513 | 1.1448 | 1.1135 | 1.0753 | 1.0431 | 1.1327 | 1.1318 | 1.1304 | 1.1232 | 1.1158 | 1.1085 | 1.1012 | 1.0944 | 1.0877 | 1.0812 | 1.0748 | 1.0444 | 1.007 | 0.97556
|  | ACHILTIBUIE | FS |  |  |  | 0 | 1.4037 | 1.4031 | 1.403 | 1.4027 | 1.4021 | 1.401 | 1.3998 | 1.3984 | 1.397 | 1.3955 | 1.394 | 1.3874 | 1.3774 | 1.3622 | 1.1782 | 1.1777 | 1.1776 | 1.1776 | 1.1776 | 1.1775 | 1.1774 | 1.1772 | 1.1769 | 1.1766 | 1.1719 | 1.1483 | 1.1223 | 1.0919 | 1.1331 | 1.1324 | 1.1322 | 1.1309 | 1.1289 | 1.1247 | 1.1205 | 1.1157 | 1.1109 | 1.1061 | 1.1013 | 1.0784 | 1.053 | 1.0231
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0 | 0.52322 | 0.51941 | 0.51567 | 0.51179 | 0.50781 | 0.50372 | 0.49958 | 0.49571 | 0.49182 | 0.48794 | 0.48405 | 0.45818 | 0.4236 | 0.3832 | 0.51458 | 0.51006 | 0.50551 | 0.50017 | 0.49476 | 0.48935 | 0.48396 | 0.47876 | 0.47359 | 0.46844 | 0.46332 | 0.43387 | 0.39841 | 0.3546 | 0.51537 | 0.51101 | 0.50666 | 0.50167 | 0.4966 | 0.4915 | 0.4864 | 0.48152 | 0.47665 | 0.4718 | 0.46698 | 0.46216 | 0.45638 | 0.45058
|  | AIGAS | CT |  |  |  | 0 | 0.52322 | 0.51941 | 0.51567 | 0.51179 | 0.50781 | 0.50372 | 0.49958 | 0.49571 | 0.49182 | 0.48794 | 0.48405 | 0.45818 | 0.4236 | 0.3832 | 0.51458 | 0.51006 | 0.50551 | 0.50017 | 0.49476 | 0.48935 | 0.48396 | 0.47876 | 0.47359 | 0.46844 | 0.46332 | 0.43387 | 0.39841 | 0.35719 | 0.51537 | 0.51101 | 0.50666 | 0.50167 | 0.4966 | 0.4915 | 0.4864 | 0.48152 | 0.47665 | 0.4718 | 0.46698 | 0.46216 | 0.45638 | 0.45058
|  | AIGAS | LW |  |  |  | 0 | 0.52912 | 0.52694 | 0.52551 | 0.52299 | 0.52037 | 0.51767 | 0.51492 | 0.51126 | 0.50638 | 0.50154 | 0.49591 | 0.46714 | 0.43143 | 0.38571 | 0.52023 | 0.5171 | 0.51451 | 0.509 | 0.50344 | 0.49794 | 0.49248 | 0.48716 | 0.48187 | 0.47661 | 0.47058 | 0.43986 | 0.40221 | 0.3546 | 0.52108 | 0.51817 | 0.51586 | 0.51106 | 0.5062 | 0.50136 | 0.49654 | 0.49188 | 0.48716 | 0.4823 | 0.47666 | 0.47106 | 0.46498 | 0.45881
|  | AIGAS | ST |  |  |  | 0 | 0.52996 | 0.52896 | 0.52804 | 0.52699 | 0.5259 | 0.52476 | 0.52359 | 0.52263 | 0.52166 | 0.5207 | 0.51974 | 0.51503 | 0.50835 | 0.50197 | 0.52245 | 0.5214 | 0.52044 | 0.51844 | 0.51642 | 0.51441 | 0.51241 | 0.51054 | 0.5087 | 0.50689 | 0.50512 | 0.49665 | 0.48655 | 0.47791 | 0.52297 | 0.52193 | 0.52098 | 0.51921 | 0.5174 | 0.5156 | 0.5138 | 0.51215 | 0.51051 | 0.50891 | 0.50733 | 0.49975 | 0.49046 | 0.48257
|  | AIGAS | FS |  |  |  | 0 | 0.5308 | 0.52982 | 0.52897 | 0.52812 | 0.52727 | 0.52641 | 0.52555 | 0.52465 | 0.52374 | 0.52282 | 0.5219 | 0.51747 | 0.51215 | 0.50554 | 0.52341 | 0.52239 | 0.5215 | 0.52056 | 0.51944 | 0.51799 | 0.51655 | 0.51496 | 0.51337 | 0.51178 | 0.51018 | 0.50248 | 0.49422 | 0.48494 | 0.5239 | 0.52289 | 0.52201 | 0.52109 | 0.52003 | 0.51872 | 0.51742 | 0.516 | 0.51457 | 0.51314 | 0.5117 | 0.50478 | 0.49722 | 0.48856
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0 | 8.2376 | 8.223 | 8.2165 | 8.2074 | 8.1972 | 8.1859 | 8.1741 | 8.1648 | 8.1553 | 8.1457 | 8.1363 | 7.9872 | 7.7511 | 7.4316 | 7.96 | 7.9453 | 7.9388 | 7.9298 | 7.9195 | 7.9082 | 7.8964 | 7.8871 | 7.8777 | 7.868 | 7.8586 | 7.7368 | 7.48 | 7.1386 | 7.8771 | 7.8615 | 7.8538 | 7.8426 | 7.8129 | 7.7689 | 7.7253 | 7.682 | 7.6391 | 7.5964 | 7.5543 | 7.5127 | 7.4687 | 7.4252
|  | AIRD | CT |  |  |  | 0 | 8.2376 | 8.2325 | 8.2282 | 8.2223 | 8.2151 | 8.2067 | 8.1976 | 8.1917 | 8.1856 | 8.1795 | 8.1733 | 8.1326 | 7.999 | 7.7993 | 7.96 | 7.9548 | 7.9505 | 7.9446 | 7.9374 | 7.929 | 7.92 | 7.9141 | 7.9079 | 7.9018 | 7.8956 | 7.8549 | 7.7518 | 7.5377 | 7.8773 | 7.8715 | 7.8663 | 7.8589 | 7.8502 | 7.8332 | 7.802 | 7.7722 | 7.7425 | 7.713 | 7.6837 | 7.6545 | 7.6235 | 7.5933
|  | AIRD | LW |  |  |  | 0 | 8.2376 | 8.223 | 8.2165 | 8.2074 | 8.1972 | 8.1859 | 8.1741 | 8.1648 | 8.1553 | 8.1457 | 8.1363 | 7.9872 | 7.7511 | 7.4316 | 7.96 | 7.9453 | 7.9388 | 7.9298 | 7.9195 | 7.9082 | 7.8964 | 7.8871 | 7.8777 | 7.868 | 7.8586 | 7.7368 | 7.48 | 7.1386 | 7.8771 | 7.8615 | 7.8538 | 7.8426 | 7.8129 | 7.7689 | 7.7253 | 7.682 | 7.6391 | 7.5964 | 7.5543 | 7.5127 | 7.4687 | 7.4252
|  | AIRD | ST |  |  |  | 0 | 8.2376 | 8.2357 | 8.2348 | 8.2323 | 8.2292 | 8.2257 | 8.2217 | 8.2202 | 8.2187 | 8.2172 | 8.2159 | 8.2096 | 8.1786 | 8.1626 | 7.96 | 7.958 | 7.9571 | 7.9546 | 7.9515 | 7.948 | 7.944 | 7.9425 | 7.941 | 7.9396 | 7.9382 | 7.9319 | 7.9009 | 7.885 | 7.8784 | 7.8764 | 7.8754 | 7.8719 | 7.8679 | 7.8634 | 7.8585 | 7.8559 | 7.8534 | 7.8448 | 7.8279 | 7.7492 | 7.6501 | 7.5678
|  | AIRD | FS |  |  |  | 0 | 8.2376 | 8.2358 | 8.2357 | 8.2356 | 8.2355 | 8.2353 | 8.2351 | 8.2343 | 8.2334 | 8.2325 | 8.2314 | 8.2286 | 8.214 | 8.1822 | 7.96 | 7.9581 | 7.9581 | 7.958 | 7.9578 | 7.9576 | 7.9574 | 7.9566 | 7.9557 | 7.9548 | 7.9537 | 7.9509 | 7.9364 | 7.9045 | 7.8785 | 7.8766 | 7.8764 | 7.8762 | 7.8757 | 7.8749 | 7.874 | 7.8725 | 7.8708 | 7.8691 | 7.8673 | 7.8294 | 7.7572 | 7.6698
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.34061 | 0.33798 | 0.33538 | 0.33274 | 0.33008 | 0.32739 | 0.3247 | 0.32206 | 0.31942 | 0.31678 | 0.31413 | 0.30073 | 0.28265 | 0.26239 | 0.32627 | 0.32365 | 0.32104 | 0.3184 | 0.31574 | 0.31306 | 0.31036 | 0.30772 | 0.30508 | 0.30244 | 0.2998 | 0.28639 | 0.26831 | 0.24871 | 0.32763 | 0.325 | 0.3224 | 0.31976 | 0.3171 | 0.31441 | 0.31172 | 0.30908 | 0.30644 | 0.3038 | 0.30115 | 0.2985 | 0.29582 | 0.29314
|  | AIRIGH-NA-BRODAIG | CT |  |  |  | 0 | 0.34061 | 0.33798 | 0.33538 | 0.33274 | 0.33008 | 0.32739 | 0.3247 | 0.32206 | 0.31942 | 0.31678 | 0.31413 | 0.30073 | 0.28265 | 0.26239 | 0.32627 | 0.32365 | 0.32104 | 0.3184 | 0.31574 | 0.31306 | 0.31036 | 0.30772 | 0.30508 | 0.30244 | 0.2998 | 0.28639 | 0.26831 | 0.24871 | 0.32763 | 0.325 | 0.3224 | 0.31976 | 0.3171 | 0.31441 | 0.31172 | 0.30908 | 0.30644 | 0.3038 | 0.30115 | 0.2985 | 0.29582 | 0.29314
|  | AIRIGH-NA-BRODAIG | LW |  |  |  | 0 | 0.34397 | 0.34286 | 0.3419 | 0.34089 | 0.33986 | 0.33881 | 0.33775 | 0.33673 | 0.33487 | 0.33301 | 0.33115 | 0.32163 | 0.30743 | 0.28975 | 0.32964 | 0.32853 | 0.32756 | 0.32655 | 0.32552 | 0.32447 | 0.32341 | 0.3224 | 0.32054 | 0.31867 | 0.31681 | 0.3073 | 0.29462 | 0.27865 | 0.33099 | 0.32988 | 0.32892 | 0.32791 | 0.32688 | 0.32583 | 0.32477 | 0.32375 | 0.32189 | 0.32003 | 0.31817 | 0.31631 | 0.31441 | 0.3125
|  | AIRIGH-NA-BRODAIG | ST |  |  |  | 0 | 0.34566 | 0.34478 | 0.34392 | 0.34303 | 0.34213 | 0.34122 | 0.3403 | 0.33943 | 0.33856 | 0.33769 | 0.33683 | 0.3325 | 0.32769 | 0.32318 | 0.33132 | 0.33044 | 0.32958 | 0.32869 | 0.32779 | 0.32689 | 0.32597 | 0.3251 | 0.32423 | 0.32336 | 0.32249 | 0.31816 | 0.31336 | 0.30884 | 0.33268 | 0.3318 | 0.33094 | 0.33005 | 0.32915 | 0.32824 | 0.32732 | 0.32645 | 0.32558 | 0.32471 | 0.32384 | 0.31952 | 0.31471 | 0.3102
|  | AIRIGH-NA-BRODAIG | FS |  |  |  | 0 | 0.34566 | 0.34562 | 0.34562 | 0.34562 | 0.34562 | 0.34561 | 0.34561 | 0.34559 | 0.34558 | 0.34556 | 0.34554 | 0.34212 | 0.33847 | 0.33785 | 0.33132 | 0.33129 | 0.33129 | 0.33128 | 0.33128 | 0.33128 | 0.33127 | 0.33126 | 0.33124 | 0.33122 | 0.3312 | 0.32778 | 0.32413 | 0.32351 | 0.33268 | 0.33264 | 0.33264 | 0.33264 | 0.33264 | 0.33263 | 0.33263 | 0.33261 | 0.3326 | 0.33258 | 0.33256 | 0.32914 | 0.32548 | 0.32487
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 0.51263 | 6.3473 | 6.3217 | 6.2987 | 6.2732 | 6.2447 | 6.2135 | 6.181 | 6.1537 | 6.1258 | 6.0979 | 6.0698 | 5.5987 | 5.0291 | 4.2571 | 6.2934 | 6.2667 | 6.207 | 6.1071 | 6.0051 | 5.9032 | 5.8022 | 5.7022 | 5.6028 | 5.5031 | 5.4046 | 4.8846 | 4.2659 | 3.4453 | 6.1468 | 6.1213 | 6.0983 | 6.0727 | 6.0443 | 6.0131 | 5.9805 | 5.9532 | 5.9254 | 5.8974 | 5.82 | 5.7228 | 5.619 | 5.5136
|  | ALYTH | CT |  |  |  | 0.51263 | 6.3473 | 6.3217 | 6.2987 | 6.2732 | 6.2447 | 6.2135 | 6.181 | 6.1537 | 6.1258 | 6.0979 | 6.0698 | 5.8579 | 5.4109 | 4.8754 | 6.2934 | 6.2667 | 6.2197 | 6.1418 | 6.062 | 5.9817 | 5.9016 | 5.8238 | 5.7461 | 5.6689 | 5.5922 | 5.1862 | 4.7048 | 4.1357 | 6.1468 | 6.1213 | 6.0983 | 6.0727 | 6.0443 | 6.0131 | 5.9805 | 5.9532 | 5.9254 | 5.8974 | 5.8694 | 5.8408 | 5.8076 | 5.7675
|  | ALYTH | LW |  |  |  | 0.51263 | 6.3717 | 6.3347 | 6.3159 | 6.2905 | 6.2616 | 6.2296 | 6.1954 | 6.1669 | 6.1381 | 6.1081 | 6.0705 | 5.5987 | 5.0291 | 4.2571 | 6.3174 | 6.2673 | 6.207 | 6.1071 | 6.0051 | 5.9032 | 5.8022 | 5.7022 | 5.6028 | 5.5031 | 5.4046 | 4.8846 | 4.2659 | 3.4453 | 6.1712 | 6.1342 | 6.1154 | 6.0901 | 6.0611 | 6.0292 | 5.995 | 5.9665 | 5.9377 | 5.9076 | 5.82 | 5.7228 | 5.619 | 5.5136
|  | ALYTH | ST |  |  |  | 0.51263 | 6.3767 | 6.3691 | 6.3636 | 6.3547 | 6.3438 | 6.3316 | 6.3194 | 6.3128 | 6.3061 | 6.2995 | 6.2931 | 6.2607 | 6.1708 | 6.0898 | 6.3246 | 6.3169 | 6.3113 | 6.3009 | 6.2869 | 6.2427 | 6.1992 | 6.1584 | 6.1182 | 6.0788 | 6.0401 | 5.8553 | 5.62 | 5.4213 | 6.1763 | 6.1686 | 6.1632 | 6.1543 | 6.1433 | 6.1312 | 6.119 | 6.1123 | 6.1056 | 6.0991 | 6.0926 | 6.0602 | 5.9704 | 5.8367
|  | ALYTH | FS |  |  |  | 0.51263 | 6.3784 | 6.3727 | 6.3699 | 6.3672 | 6.3644 | 6.3614 | 6.3584 | 6.3541 | 6.3496 | 6.3449 | 6.34 | 6.3177 | 6.2715 | 6.1871 | 6.3264 | 6.3206 | 6.3178 | 6.3148 | 6.3115 | 6.3076 | 6.3036 | 6.2847 | 6.2539 | 6.2239 | 6.1938 | 6.0479 | 5.8837 | 5.686 | 6.178 | 6.1722 | 6.1695 | 6.1668 | 6.1639 | 6.1609 | 6.1579 | 6.1537 | 6.1492 | 6.1445 | 6.1396 | 6.1173 | 6.071 | 5.9867
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 0.031579 | 8.0852 | 8.0659 | 8.0566 | 8.0436 | 8.0281 | 8.0112 | 7.9934 | 7.9792 | 7.9649 | 7.9503 | 7.936 | 7.8048 | 7.5081 | 7.0931 | 7.984 | 7.9648 | 7.9555 | 7.9425 | 7.927 | 7.9101 | 7.8923 | 7.8652 | 7.8121 | 7.7594 | 7.7076 | 7.4355 | 7.112 | 6.6704 | 8.0515 | 8.0322 | 8.0229 | 8.0099 | 7.9944 | 7.9775 | 7.9597 | 7.9455 | 7.9312 | 7.8864 | 7.8355 | 7.7853 | 7.7317 | 7.6776
|  | ANNAT | CT |  |  |  | 0.031579 | 8.0852 | 8.0771 | 8.0701 | 8.061 | 8.05 | 8.0373 | 8.0237 | 8.0146 | 8.0051 | 7.9956 | 7.986 | 7.9246 | 7.8051 | 7.5432 | 7.984 | 7.976 | 7.969 | 7.9599 | 7.9489 | 7.9362 | 7.9226 | 7.9135 | 7.904 | 7.8945 | 7.8653 | 7.6734 | 7.4397 | 7.1591 | 8.0515 | 8.0434 | 8.0364 | 8.0273 | 8.0163 | 8.0036 | 7.99 | 7.9809 | 7.9714 | 7.9619 | 7.9523 | 7.9424 | 7.9165 | 7.8781
|  | ANNAT | LW |  |  |  | 0.031579 | 8.0868 | 8.0659 | 8.0566 | 8.0436 | 8.0281 | 8.0112 | 7.9934 | 7.9792 | 7.9649 | 7.9503 | 7.936 | 7.8048 | 7.5081 | 7.0931 | 7.9857 | 7.9648 | 7.9555 | 7.9425 | 7.927 | 7.9101 | 7.8923 | 7.8652 | 7.8121 | 7.7594 | 7.7076 | 7.4355 | 7.112 | 6.6704 | 8.0531 | 8.0322 | 8.0229 | 8.0099 | 7.9944 | 7.9775 | 7.9597 | 7.9455 | 7.9312 | 7.8864 | 7.8355 | 7.7853 | 7.7317 | 7.6776
|  | ANNAT | ST |  |  |  | 0.031579 | 8.0868 | 8.0841 | 8.0828 | 8.0793 | 8.075 | 8.07 | 8.0644 | 8.0623 | 8.0602 | 8.0581 | 8.0562 | 8.0474 | 8.0037 | 7.9812 | 7.9857 | 7.983 | 7.9817 | 7.9782 | 7.9739 | 7.9689 | 7.9633 | 7.9612 | 7.959 | 7.957 | 7.9551 | 7.9463 | 7.8424 | 7.7443 | 8.0531 | 8.0504 | 8.0491 | 8.0456 | 8.0413 | 8.0363 | 8.0307 | 8.0286 | 8.0264 | 8.0244 | 8.0225 | 8.0137 | 7.9686 | 7.8725
|  | ANNAT | FS |  |  |  | 0.031579 | 8.0877 | 8.0851 | 8.085 | 8.0848 | 8.0846 | 8.0843 | 8.0841 | 8.0829 | 8.0817 | 8.0803 | 8.0788 | 8.0748 | 8.0541 | 8.0089 | 7.9866 | 7.984 | 7.9839 | 7.9837 | 7.9835 | 7.9832 | 7.9829 | 7.9818 | 7.9806 | 7.9792 | 7.9777 | 7.9737 | 7.953 | 7.8705 | 8.054 | 8.0514 | 8.0513 | 8.0511 | 8.0509 | 8.0506 | 8.0504 | 8.0492 | 8.048 | 8.0466 | 8.0451 | 8.0411 | 8.0204 | 7.9752
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.099909 | 0.099808 | 0.099734 | 0.099611 | 0.099486 | 0.099362 | 0.099239 | 0.099123 | 0.099009 | 0.098895 | 0.098785 | 0.0982 | 0.097483 | 0.096447 | 0.099893 | 0.099786 | 0.099703 | 0.099565 | 0.099425 | 0.099287 | 0.099152 | 0.099022 | 0.098894 | 0.098768 | 0.098645 | 0.097999 | 0.097221 | 0.096125 | 0.099894 | 0.099786 | 0.099704 | 0.099566 | 0.099426 | 0.099289 | 0.099154 | 0.099024 | 0.098897 | 0.098771 | 0.098648 | 0.098527 | 0.098398 | 0.098268
|  | ARDCHYLE | CT |  |  |  | 0 | 0.099919 | 0.09987 | 0.099819 | 0.099736 | 0.09965 | 0.099562 | 0.099475 | 0.099398 | 0.099321 | 0.099245 | 0.09917 | 0.09877 | 0.098281 | 0.097672 | 0.099905 | 0.09985 | 0.099794 | 0.099701 | 0.099604 | 0.099507 | 0.099411 | 0.099324 | 0.099237 | 0.099152 | 0.099069 | 0.098626 | 0.098094 | 0.097444 | 0.099905 | 0.099851 | 0.099795 | 0.099701 | 0.099605 | 0.099508 | 0.099412 | 0.099325 | 0.099239 | 0.099154 | 0.099071 | 0.098988 | 0.098899 | 0.09881
|  | ARDCHYLE | LW |  |  |  | 0 | 0.099909 | 0.099808 | 0.099734 | 0.099611 | 0.099486 | 0.099362 | 0.099239 | 0.099123 | 0.099009 | 0.098895 | 0.098785 | 0.0982 | 0.097483 | 0.096447 | 0.099893 | 0.099786 | 0.099703 | 0.099565 | 0.099425 | 0.099287 | 0.099152 | 0.099022 | 0.098894 | 0.098768 | 0.098645 | 0.097999 | 0.097221 | 0.096125 | 0.099894 | 0.099786 | 0.099704 | 0.099566 | 0.099426 | 0.099289 | 0.099154 | 0.099024 | 0.098897 | 0.098771 | 0.098648 | 0.098527 | 0.098398 | 0.098268
|  | ARDCHYLE | ST |  |  |  | 0 | 0.099965 | 0.099955 | 0.09995 | 0.099902 | 0.099852 | 0.099803 | 0.099754 | 0.099712 | 0.09967 | 0.09963 | 0.099592 | 0.099414 | 0.099155 | 0.098964 | 0.099959 | 0.099949 | 0.099943 | 0.099888 | 0.099832 | 0.099777 | 0.099721 | 0.099672 | 0.099625 | 0.099579 | 0.099534 | 0.09933 | 0.099046 | 0.098831 | 0.099959 | 0.099949 | 0.099943 | 0.099888 | 0.099832 | 0.099777 | 0.099722 | 0.099673 | 0.099626 | 0.09958 | 0.099535 | 0.099332 | 0.099048 | 0.098833
|  | ARDCHYLE | FS |  |  |  | 0 | 0.099971 | 0.099963 | 0.099961 | 0.099957 | 0.099946 | 0.099922 | 0.099898 | 0.099869 | 0.099839 | 0.099809 | 0.099779 | 0.09964 | 0.099471 | 0.099248 | 0.099965 | 0.099957 | 0.099955 | 0.09995 | 0.099937 | 0.099909 | 0.099882 | 0.099847 | 0.099813 | 0.099778 | 0.099743 | 0.099582 | 0.099392 | 0.09915 | 0.099965 | 0.099957 | 0.099955 | 0.09995 | 0.099937 | 0.09991 | 0.099882 | 0.099848 | 0.099813 | 0.099779 | 0.099744 | 0.099583 | 0.099393 | 0.099152
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.063158 | 5.7337 | 5.7197 | 5.7066 | 5.6918 | 5.6764 | 5.6596 | 5.6422 | 5.6274 | 5.6124 | 5.5973 | 5.5821 | 5.4473 | 5.1865 | 4.8269 | 5.5163 | 5.5023 | 5.4892 | 5.4744 | 5.459 | 5.4423 | 5.4249 | 5.41 | 5.395 | 5.351 | 5.3076 | 5.0756 | 4.7954 | 4.4167 | 5.4987 | 5.4847 | 5.4716 | 5.4568 | 5.4414 | 5.4246 | 5.4072 | 5.3924 | 5.3773 | 5.3622 | 5.3471 | 5.3317 | 5.3136 | 5.2953
|  | ARDERSIER | CT |  |  |  | 0.063158 | 5.7337 | 5.7197 | 5.7066 | 5.6918 | 5.6764 | 5.6596 | 5.6422 | 5.6274 | 5.6124 | 5.5973 | 5.5821 | 5.491 | 5.3342 | 5.0794 | 5.5163 | 5.5023 | 5.4892 | 5.4744 | 5.459 | 5.4423 | 5.4249 | 5.41 | 5.395 | 5.3799 | 5.3647 | 5.1904 | 4.9666 | 4.6988 | 5.4987 | 5.4847 | 5.4716 | 5.4568 | 5.4414 | 5.4246 | 5.4072 | 5.3924 | 5.3773 | 5.3622 | 5.3471 | 5.3317 | 5.3136 | 5.2953
|  | ARDERSIER | LW |  |  |  | 0.063158 | 5.748 | 5.7294 | 5.7197 | 5.7063 | 5.6916 | 5.675 | 5.6577 | 5.6433 | 5.6278 | 5.6122 | 5.5968 | 5.4473 | 5.1865 | 4.8269 | 5.5306 | 5.512 | 5.5023 | 5.4889 | 5.4742 | 5.4576 | 5.4403 | 5.4259 | 5.3951 | 5.351 | 5.3076 | 5.0756 | 4.7954 | 4.4167 | 5.513 | 5.4943 | 5.4846 | 5.4713 | 5.4566 | 5.44 | 5.4227 | 5.4082 | 5.3928 | 5.3772 | 5.3618 | 5.3464 | 5.3278 | 5.3087
|  | ARDERSIER | ST |  |  |  | 0.063158 | 5.7514 | 5.7476 | 5.7449 | 5.7405 | 5.7347 | 5.7283 | 5.7215 | 5.7174 | 5.7132 | 5.7091 | 5.7051 | 5.6857 | 5.6405 | 5.6106 | 5.534 | 5.5302 | 5.5275 | 5.5231 | 5.5173 | 5.5109 | 5.5041 | 5.5 | 5.4958 | 5.4917 | 5.4877 | 5.4684 | 5.4034 | 5.3161 | 5.5164 | 5.5126 | 5.5099 | 5.5055 | 5.4997 | 5.4933 | 5.4865 | 5.4823 | 5.4782 | 5.4741 | 5.4701 | 5.4507 | 5.4055 | 5.3756
|  | ARDERSIER | FS |  |  |  | 0.063158 | 5.7531 | 5.7503 | 5.7485 | 5.7467 | 5.7449 | 5.743 | 5.7411 | 5.7386 | 5.7359 | 5.7332 | 5.7304 | 5.7189 | 5.6948 | 5.6522 | 5.5357 | 5.5329 | 5.5311 | 5.5293 | 5.5275 | 5.5256 | 5.5237 | 5.5212 | 5.5185 | 5.5158 | 5.513 | 5.5015 | 5.4774 | 5.4345 | 5.5181 | 5.5153 | 5.5135 | 5.5117 | 5.5099 | 5.508 | 5.5061 | 5.5035 | 5.5009 | 5.4982 | 5.4954 | 5.4839 | 5.4598 | 5.4172
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.10908 | 0.10815 | 0.10723 | 0.10629 | 0.10532 | 0.10434 | 0.10335 | 0.10241 | 0.10146 | 0.10052 | 0.099573 | 0.092178 | 0.082177 | 0.071525 | 0.10866 | 0.10772 | 0.1068 | 0.10584 | 0.10486 | 0.10386 | 0.10285 | 0.1019 | 0.10094 | 0.09998 | 0.099022 | 0.091562 | 0.082051 | 0.071129 | 0.10848 | 0.10755 | 0.10664 | 0.1057 | 0.10473 | 0.10375 | 0.10275 | 0.10181 | 0.10087 | 0.099925 | 0.09898 | 0.098032 | 0.097059 | 0.09524
|  | ARDOCHY | CT |  |  |  | 0 | 0.10908 | 0.10815 | 0.10723 | 0.10629 | 0.10532 | 0.10434 | 0.10335 | 0.10241 | 0.10146 | 0.10052 | 0.099573 | 0.092178 | 0.082177 | 0.071525 | 0.10866 | 0.10772 | 0.1068 | 0.10584 | 0.10486 | 0.10386 | 0.10285 | 0.1019 | 0.10094 | 0.09998 | 0.099022 | 0.091562 | 0.082051 | 0.071129 | 0.10848 | 0.10755 | 0.10664 | 0.1057 | 0.10473 | 0.10375 | 0.10275 | 0.10181 | 0.10087 | 0.099925 | 0.09898 | 0.098032 | 0.097059 | 0.09524
|  | ARDOCHY | LW |  |  |  | 0 | 0.11076 | 0.1105 | 0.11038 | 0.10938 | 0.10835 | 0.10731 | 0.10626 | 0.10525 | 0.10424 | 0.10323 | 0.10222 | 0.09621 | 0.089437 | 0.078811 | 0.11034 | 0.11007 | 0.10994 | 0.10891 | 0.10786 | 0.1068 | 0.10573 | 0.1047 | 0.10367 | 0.10264 | 0.10161 | 0.095989 | 0.088792 | 0.077736 | 0.11017 | 0.1099 | 0.10979 | 0.10878 | 0.10776 | 0.10671 | 0.10566 | 0.10466 | 0.10365 | 0.10264 | 0.10163 | 0.10063 | 0.099587 | 0.098539
|  | ARDOCHY | ST |  |  |  | 0 | 0.11076 | 0.11073 | 0.11071 | 0.11067 | 0.11062 | 0.11056 | 0.1105 | 0.11048 | 0.11045 | 0.11043 | 0.11041 | 0.11031 | 0.10982 | 0.10957 | 0.11035 | 0.11032 | 0.11031 | 0.11026 | 0.1102 | 0.11013 | 0.11005 | 0.11002 | 0.10999 | 0.10995 | 0.10992 | 0.10978 | 0.10926 | 0.10897 | 0.11017 | 0.11013 | 0.11012 | 0.11008 | 0.11003 | 0.10997 | 0.10991 | 0.10988 | 0.10986 | 0.10983 | 0.10981 | 0.10971 | 0.10923 | 0.10898
|  | ARDOCHY | FS |  |  |  | 0 | 0.1116 | 0.11157 | 0.11157 | 0.11157 | 0.11157 | 0.11156 | 0.11156 | 0.11155 | 0.11154 | 0.11152 | 0.1115 | 0.11146 | 0.11124 | 0.11076 | 0.1112 | 0.11117 | 0.11117 | 0.11116 | 0.11116 | 0.11115 | 0.11114 | 0.11112 | 0.1111 | 0.11108 | 0.11105 | 0.11097 | 0.11071 | 0.1102 | 0.11101 | 0.11098 | 0.11098 | 0.11098 | 0.11097 | 0.11097 | 0.11097 | 0.11096 | 0.11094 | 0.11093 | 0.11091 | 0.11087 | 0.11064 | 0.11016
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 0 | 2.6756 | 2.6689 | 2.6659 | 2.6618 | 2.651 | 2.6358 | 2.6207 | 2.6058 | 2.5909 | 2.5762 | 2.5617 | 2.4871 | 2.3971 | 2.2729 | 2.6609 | 2.6542 | 2.6512 | 2.6471 | 2.6424 | 2.6249 | 2.6059 | 2.5866 | 2.5676 | 2.5487 | 2.5301 | 2.4359 | 2.3257 | 2.1818 | 2.6366 | 2.63 | 2.627 | 2.6102 | 2.5913 | 2.5726 | 2.5542 | 2.5355 | 2.517 | 2.4986 | 2.4806 | 2.4628 | 2.4441 | 2.4253
|  | ARISAIG | CT |  |  |  | 0 | 2.6756 | 2.6733 | 2.6715 | 2.6689 | 2.6658 | 2.6593 | 2.6482 | 2.6383 | 2.6284 | 2.6186 | 2.6089 | 2.5574 | 2.4964 | 2.4224 | 2.6609 | 2.6587 | 2.6568 | 2.6542 | 2.6511 | 2.6474 | 2.6398 | 2.6269 | 2.6141 | 2.6014 | 2.5889 | 2.5235 | 2.4487 | 2.3614 | 2.6366 | 2.6344 | 2.6325 | 2.6279 | 2.6143 | 2.6007 | 2.5872 | 2.5747 | 2.5623 | 2.55 | 2.5379 | 2.5258 | 2.513 | 2.5002
|  | ARISAIG | LW |  |  |  | 0 | 2.6756 | 2.6689 | 2.6659 | 2.6618 | 2.651 | 2.6358 | 2.6207 | 2.6058 | 2.5909 | 2.5762 | 2.5617 | 2.4871 | 2.3971 | 2.2729 | 2.6609 | 2.6542 | 2.6512 | 2.6471 | 2.6424 | 2.6249 | 2.6059 | 2.5866 | 2.5676 | 2.5487 | 2.5301 | 2.4359 | 2.3257 | 2.1818 | 2.6366 | 2.63 | 2.627 | 2.6102 | 2.5913 | 2.5726 | 2.5542 | 2.5355 | 2.517 | 2.4986 | 2.4806 | 2.4628 | 2.4441 | 2.4253
|  | ARISAIG | ST |  |  |  | 0 | 2.6756 | 2.6748 | 2.6744 | 2.6733 | 2.672 | 2.6705 | 2.6689 | 2.6683 | 2.6676 | 2.6668 | 2.6613 | 2.6353 | 2.6003 | 2.5724 | 2.6609 | 2.6601 | 2.6597 | 2.6586 | 2.6573 | 2.6559 | 2.6542 | 2.6536 | 2.6529 | 2.6523 | 2.6518 | 2.6194 | 2.5755 | 2.539 | 2.6366 | 2.6358 | 2.6354 | 2.6344 | 2.6331 | 2.6316 | 2.6299 | 2.6241 | 2.6165 | 2.6092 | 2.602 | 2.5678 | 2.5251 | 2.4897
|  | ARISAIG | FS |  |  |  | 0 | 2.6756 | 2.6748 | 2.6748 | 2.6748 | 2.6747 | 2.6746 | 2.6746 | 2.6743 | 2.6739 | 2.6735 | 2.6731 | 2.6635 | 2.6405 | 2.6117 | 2.6609 | 2.6602 | 2.6601 | 2.6601 | 2.66 | 2.6599 | 2.6599 | 2.6596 | 2.6592 | 2.6588 | 2.6584 | 2.6557 | 2.6258 | 2.5905 | 2.6366 | 2.6359 | 2.6359 | 2.6358 | 2.6358 | 2.6357 | 2.6356 | 2.6353 | 2.635 | 2.6343 | 2.6288 | 2.603 | 2.574 | 2.5396
| STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | YES | 0 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983
|  | ARNISH | CT |  |  |  | 0 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988
|  | ARNISH | LW |  |  |  | 0 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983
|  | ARNISH | ST |  |  |  | 0 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9994 | 11.9993 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744
|  | ARNISH | FS |  |  |  | 0 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 0.012632 | 11.9155 | 25.127 | 25.0915 | 25.0427 | 24.9867 | 24.9256 | 24.8613 | 24.8102 | 24.7584 | 24.7048 | 24.6522 | 24.3264 | 23.6397 | 22.0683 | 11.4342 | 23.4457 | 23.4102 | 23.3614 | 23.3054 | 23.2443 | 23.18 | 23.1289 | 22.9899 | 22.7934 | 22.5998 | 21.5821 | 20.3612 | 18.6918 | 11.7872 | 24.3986 | 24.3631 | 24.3143 | 24.2583 | 24.1972 | 24.133 | 24.0819 | 24.03 | 23.9075 | 23.7459 | 23.5864 | 23.4138 | 23.24
|  | ASHGROVE | CT |  |  |  | 0.012632 | 11.9155 | 25.1641 | 25.1368 | 25.1015 | 25.0593 | 25.0109 | 24.9592 | 24.9236 | 24.8869 | 24.85 | 24.8127 | 24.5719 | 24.1968 | 23.6298 | 11.4342 | 23.4828 | 23.4555 | 23.4201 | 23.378 | 23.3296 | 23.2778 | 23.2423 | 23.2056 | 23.1686 | 23.1314 | 22.4438 | 21.5745 | 20.521 | 11.7872 | 24.4358 | 24.4084 | 24.3731 | 24.331 | 24.2825 | 24.2308 | 24.1953 | 24.1585 | 24.1216 | 24.0844 | 24.0458 | 23.9854 | 23.8606
|  | ASHGROVE | LW |  |  |  | 0.012632 | 11.9248 | 25.127 | 25.0915 | 25.0427 | 24.9867 | 24.9256 | 24.8613 | 24.8102 | 24.7584 | 24.7048 | 24.6522 | 24.3264 | 23.6397 | 22.0683 | 11.4435 | 23.4457 | 23.4102 | 23.3614 | 23.3054 | 23.2443 | 23.18 | 23.1289 | 22.9899 | 22.7934 | 22.5998 | 21.5821 | 20.3612 | 18.6918 | 11.7965 | 24.3986 | 24.3631 | 24.3143 | 24.2583 | 24.1972 | 24.133 | 24.0819 | 24.03 | 23.9075 | 23.7459 | 23.5864 | 23.4138 | 23.24
|  | ASHGROVE | ST |  |  |  | 0.012632 | 11.9265 | 25.1956 | 25.1899 | 25.176 | 25.1585 | 25.1383 | 25.1159 | 25.1065 | 25.097 | 25.0879 | 25.0791 | 25.0381 | 24.8676 | 24.775 | 11.4452 | 23.5142 | 23.5086 | 23.4947 | 23.4772 | 23.457 | 23.4346 | 23.4252 | 23.4157 | 23.4066 | 23.3977 | 23.3568 | 23.0611 | 22.6759 | 11.7981 | 24.4672 | 24.4615 | 24.4477 | 24.4302 | 24.41 | 24.3876 | 24.3782 | 24.3687 | 24.3595 | 24.3507 | 24.3098 | 24.1392 | 23.8326
|  | ASHGROVE | FS |  |  |  | 0.012632 | 11.9273 | 25.1969 | 25.1956 | 25.1943 | 25.1927 | 25.1908 | 25.1889 | 25.1839 | 25.1784 | 25.1725 | 25.1661 | 25.1471 | 25.066 | 24.8935 | 11.446 | 23.5156 | 23.5143 | 23.513 | 23.5114 | 23.5095 | 23.5076 | 23.5026 | 23.4971 | 23.4912 | 23.4848 | 23.4658 | 23.3847 | 23.17 | 11.799 | 24.4685 | 24.4673 | 24.4659 | 24.4643 | 24.4624 | 24.4605 | 24.4556 | 24.4501 | 24.4441 | 24.4377 | 24.4188 | 24.3377 | 24.1651
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 0.33789 | 13.2989 | 13.2188 | 32.2701 | 32.203 | 32.1275 | 32.0449 | 31.9574 | 31.8865 | 31.8149 | 31.7415 | 31.6646 | 31.168 | 29.9425 | 28.0646 | 12.6822 | 12.5964 | 30.1425 | 30.0667 | 29.971 | 29.7095 | 29.4532 | 29.2025 | 28.9558 | 28.7114 | 28.474 | 27.2412 | 25.7744 | 23.7653 | 12.6025 | 12.5224 | 30.8237 | 30.7566 | 30.633 | 30.3903 | 30.1463 | 29.9087 | 29.6748 | 29.4428 | 29.2176 | 28.9967 | 28.762 | 28.5241
|  | ASHLUDIE | CT |  |  |  | 0.33789 | 13.2989 | 13.2519 | 32.31 | 32.259 | 32.1992 | 32.1316 | 32.0601 | 32.0083 | 31.9551 | 31.9018 | 31.8482 | 31.5044 | 30.9637 | 30.0382 | 12.6822 | 12.6321 | 30.1867 | 30.1296 | 30.0639 | 29.9908 | 29.8717 | 29.6936 | 29.5172 | 29.3437 | 29.1739 | 28.2771 | 27.2195 | 25.9477 | 12.6025 | 12.5555 | 30.8636 | 30.8125 | 30.7528 | 30.6852 | 30.5383 | 30.3729 | 30.2054 | 30.0407 | 29.8794 | 29.7178 | 29.5457 | 29.3734
|  | ASHLUDIE | LW |  |  |  | 0.33789 | 13.3225 | 13.2188 | 32.2701 | 32.203 | 32.1275 | 32.0449 | 31.9574 | 31.8865 | 31.8149 | 31.7415 | 31.6646 | 31.168 | 29.9425 | 28.0646 | 12.7044 | 12.5964 | 30.1425 | 30.0667 | 29.971 | 29.7095 | 29.4532 | 29.2025 | 28.9558 | 28.7114 | 28.474 | 27.2412 | 25.7744 | 23.7653 | 12.626 | 12.5224 | 30.8237 | 30.7566 | 30.633 | 30.3903 | 30.1463 | 29.9087 | 29.6748 | 29.4428 | 29.2176 | 28.9967 | 28.762 | 28.5241
|  | ASHLUDIE | ST |  |  |  | 0.33789 | 13.3275 | 13.3117 | 32.4023 | 32.3837 | 32.3608 | 32.3346 | 32.3057 | 32.2927 | 32.2797 | 32.2671 | 32.255 | 32.1982 | 31.9846 | 31.8634 | 12.7152 | 12.699 | 30.2892 | 30.2668 | 30.2401 | 30.2103 | 30.1779 | 30.1612 | 30.1445 | 30.1284 | 30.1128 | 29.7354 | 29.1867 | 28.7486 | 12.6311 | 12.6153 | 30.9559 | 30.9373 | 30.9144 | 30.8882 | 30.8593 | 30.8463 | 30.8333 | 30.8207 | 30.8086 | 30.4255 | 29.9012 | 29.4863
|  | ASHLUDIE | FS |  |  |  | 0.33789 | 13.3292 | 13.316 | 32.4129 | 32.4098 | 32.4064 | 32.4025 | 32.3988 | 32.3913 | 32.384 | 32.3762 | 32.3679 | 32.3384 | 32.2342 | 32.0226 | 12.7172 | 12.7037 | 30.3003 | 30.2966 | 30.2918 | 30.2855 | 30.2791 | 30.2687 | 30.2585 | 30.2478 | 30.2365 | 30.1666 | 29.7743 | 29.293 | 12.6328 | 12.6196 | 30.9665 | 30.9634 | 30.9599 | 30.9561 | 30.9524 | 30.9449 | 30.9376 | 30.9298 | 30.9215 | 30.8308 | 30.4642 | 30.0026
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | YES | 0.0052632 | 1.5779 | 1.5623 | 1.5554 | 1.5458 | 1.5349 | 1.523 | 1.5068 | 1.4663 | 1.4261 | 1.3862 | 1.3469 | 1.1441 | 0.90612 | 0.58743 | 1.3863 | 1.37 | 1.3622 | 1.3509 | 1.3384 | 1.325 | 1.311 | 1.2996 | 1.2594 | 1.2142 | 1.1697 | 0.94171 | 0.67813 | 0.33437 | 1.4311 | 1.4156 | 1.4087 | 1.3991 | 1.3882 | 1.3763 | 1.3353 | 1.2921 | 1.2492 | 1.2066 | 1.1648 | 1.1235 | 1.08 | 1.0362
|  | AULTBEA | CT |  |  |  | 0.0052632 | 1.5779 | 1.5727 | 1.5683 | 1.5623 | 1.555 | 1.5464 | 1.5373 | 1.5314 | 1.5253 | 1.501 | 1.4746 | 1.3356 | 1.1739 | 0.98162 | 1.3865 | 1.3807 | 1.3757 | 1.3685 | 1.3601 | 1.3505 | 1.3403 | 1.3332 | 1.326 | 1.3188 | 1.3116 | 1.156 | 0.97683 | 0.7676 | 1.4311 | 1.4259 | 1.4215 | 1.4156 | 1.4082 | 1.3997 | 1.3906 | 1.3847 | 1.3567 | 1.3282 | 1.3 | 1.2719 | 1.2423 | 1.2125
|  | AULTBEA | LW |  |  |  | 0.0052632 | 1.5779 | 1.5623 | 1.5554 | 1.5458 | 1.5349 | 1.523 | 1.5068 | 1.4663 | 1.4261 | 1.3862 | 1.3469 | 1.1441 | 0.90612 | 0.58743 | 1.3863 | 1.37 | 1.3622 | 1.3509 | 1.3384 | 1.325 | 1.311 | 1.2996 | 1.2594 | 1.2142 | 1.1697 | 0.94171 | 0.67813 | 0.33437 | 1.4311 | 1.4156 | 1.4087 | 1.3991 | 1.3882 | 1.3763 | 1.3353 | 1.2921 | 1.2492 | 1.2066 | 1.1648 | 1.1235 | 1.08 | 1.0362
|  | AULTBEA | ST |  |  |  | 0.0052632 | 1.5779 | 1.576 | 1.575 | 1.5726 | 1.5696 | 1.5661 | 1.5621 | 1.5607 | 1.5592 | 1.5578 | 1.5564 | 1.5382 | 1.4459 | 1.3704 | 1.3874 | 1.3854 | 1.3844 | 1.3812 | 1.3774 | 1.3731 | 1.3685 | 1.3663 | 1.364 | 1.3619 | 1.3598 | 1.3503 | 1.2774 | 1.1913 | 1.4311 | 1.4292 | 1.4283 | 1.4258 | 1.4228 | 1.4193 | 1.4154 | 1.4139 | 1.4125 | 1.411 | 1.4097 | 1.366 | 1.2681 | 1.1873
|  | AULTBEA | FS |  |  |  | 0.0052632 | 1.5779 | 1.5762 | 1.5761 | 1.576 | 1.5759 | 1.5757 | 1.5755 | 1.5748 | 1.5739 | 1.573 | 1.572 | 1.5694 | 1.5555 | 1.4789 | 1.3874 | 1.3856 | 1.3855 | 1.3853 | 1.385 | 1.3843 | 1.3837 | 1.3824 | 1.381 | 1.3795 | 1.378 | 1.3726 | 1.3564 | 1.3153 | 1.4311 | 1.4294 | 1.4294 | 1.4293 | 1.4291 | 1.4289 | 1.4288 | 1.428 | 1.4272 | 1.4263 | 1.4253 | 1.4227 | 1.3843 | 1.3035
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 0.04 | 18.1768 | 18.1314 | 18.1113 | 18.0832 | 18.0513 | 18.0164 | 17.9796 | 17.9507 | 17.9214 | 17.8916 | 17.8623 | 17.3681 | 16.5868 | 15.5449 | 17.628 | 17.5826 | 17.5624 | 17.5343 | 17.5025 | 17.4676 | 17.4308 | 17.4019 | 17.3374 | 17.1874 | 17.0392 | 16.2727 | 15.3887 | 14.2447 | 17.6322 | 17.5868 | 17.5666 | 17.5385 | 17.5066 | 17.4718 | 17.435 | 17.4061 | 17.3768 | 17.3469 | 17.3013 | 17.1635 | 17.018 | 16.8723
|  | AVIEMORE | CT |  |  |  | 0.04 | 18.1768 | 18.1612 | 18.1479 | 18.1299 | 18.1079 | 18.0821 | 18.0545 | 18.0364 | 18.0176 | 17.9987 | 17.9797 | 17.8548 | 17.427 | 16.7785 | 17.628 | 17.6123 | 17.5991 | 17.5811 | 17.5591 | 17.5333 | 17.5056 | 17.4876 | 17.4688 | 17.4499 | 17.4308 | 16.9641 | 16.3491 | 15.6302 | 17.6322 | 17.6165 | 17.6033 | 17.5853 | 17.5633 | 17.5375 | 17.5098 | 17.4918 | 17.473 | 17.4541 | 17.435 | 17.4152 | 17.3903 | 17.3646
|  | AVIEMORE | LW |  |  |  | 0.04 | 18.1768 | 18.1314 | 18.1113 | 18.0832 | 18.0513 | 18.0164 | 17.9796 | 17.9507 | 17.9214 | 17.8916 | 17.8623 | 17.3681 | 16.5868 | 15.5449 | 17.628 | 17.5826 | 17.5624 | 17.5343 | 17.5025 | 17.4676 | 17.4308 | 17.4019 | 17.3374 | 17.1874 | 17.0392 | 16.2727 | 15.3887 | 14.2447 | 17.6322 | 17.5868 | 17.5666 | 17.5385 | 17.5066 | 17.4718 | 17.435 | 17.4061 | 17.3768 | 17.3469 | 17.3013 | 17.1635 | 17.018 | 16.8723
|  | AVIEMORE | ST |  |  |  | 0.04 | 18.1768 | 18.1709 | 18.168 | 18.1603 | 18.151 | 18.14 | 18.1278 | 18.1232 | 18.1186 | 18.1142 | 18.11 | 18.0908 | 17.9949 | 17.9454 | 17.628 | 17.622 | 17.6192 | 17.6115 | 17.6021 | 17.5912 | 17.579 | 17.5744 | 17.5698 | 17.5654 | 17.5611 | 17.5419 | 17.3501 | 17.0489 | 17.6322 | 17.6262 | 17.6234 | 17.6157 | 17.6063 | 17.5954 | 17.5831 | 17.5786 | 17.574 | 17.5695 | 17.5653 | 17.5461 | 17.4502 | 17.3165
|  | AVIEMORE | FS |  |  |  | 0.04 | 18.1768 | 18.1712 | 18.1709 | 18.1706 | 18.1702 | 18.1696 | 18.1689 | 18.1665 | 18.1638 | 18.1608 | 18.1575 | 18.1489 | 18.1038 | 18.0051 | 17.628 | 17.6224 | 17.6221 | 17.6218 | 17.6214 | 17.6207 | 17.6201 | 17.6177 | 17.615 | 17.612 | 17.6087 | 17.6001 | 17.5549 | 17.4445 | 17.6322 | 17.6265 | 17.6263 | 17.626 | 17.6256 | 17.6249 | 17.6243 | 17.6219 | 17.6192 | 17.6162 | 17.6129 | 17.6042 | 17.5591 | 17.4605
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 0.054737 | 1.7774 | 1.7527 | 1.7417 | 1.7264 | 1.7091 | 1.6901 | 1.6701 | 1.6543 | 1.6384 | 1.6222 | 1.6063 | 1.4418 | 1.1055 | 0.62901 | 1.5072 | 1.4604 | 1.4226 | 1.3585 | 1.2934 | 1.2292 | 1.1657 | 1.1043 | 1.0434 | 0.98297 | 0.92355 | 0.6111 | 0.23767 | -0.27561 | 1.5052 | 1.4805 | 1.4695 | 1.4542 | 1.4368 | 1.4178 | 1.3978 | 1.3821 | 1.3495 | 1.2965 | 1.2433 | 1.1908 | 1.1341 | 1.0709
|  | BALALDIE | CT |  |  |  | 0.054737 | 1.7774 | 1.7689 | 1.7616 | 1.7518 | 1.7398 | 1.7257 | 1.7106 | 1.7008 | 1.6905 | 1.6802 | 1.6699 | 1.602 | 1.4585 | 1.1652 | 1.5138 | 1.4887 | 1.4631 | 1.4194 | 1.3743 | 1.3288 | 1.2836 | 1.2411 | 1.1987 | 1.1568 | 1.1154 | 0.89742 | 0.63403 | 0.31488 | 1.5052 | 1.4966 | 1.4894 | 1.4796 | 1.4676 | 1.4535 | 1.4384 | 1.4285 | 1.4183 | 1.408 | 1.3976 | 1.3767 | 1.3398 | 1.3004
|  | BALALDIE | LW |  |  |  | 0.054737 | 1.7774 | 1.7527 | 1.7417 | 1.7264 | 1.7091 | 1.6901 | 1.6701 | 1.6543 | 1.6384 | 1.6222 | 1.6063 | 1.4418 | 1.1055 | 0.62901 | 1.5072 | 1.4604 | 1.4226 | 1.3585 | 1.2934 | 1.2292 | 1.1657 | 1.1043 | 1.0434 | 0.98297 | 0.92355 | 0.6111 | 0.23767 | -0.27561 | 1.5052 | 1.4805 | 1.4695 | 1.4542 | 1.4368 | 1.4178 | 1.3978 | 1.3821 | 1.3495 | 1.2965 | 1.2433 | 1.1908 | 1.1341 | 1.0709
|  | BALALDIE | ST |  |  |  | 0.054737 | 1.7774 | 1.7742 | 1.7726 | 1.7685 | 1.7634 | 1.7574 | 1.7508 | 1.7483 | 1.7458 | 1.7434 | 1.7411 | 1.7307 | 1.6788 | 1.6521 | 1.5394 | 1.5342 | 1.5309 | 1.5047 | 1.4778 | 1.4512 | 1.4246 | 1.3997 | 1.3752 | 1.3514 | 1.3282 | 1.2218 | 1.0794 | 0.96527 | 1.5052 | 1.502 | 1.5004 | 1.4962 | 1.4911 | 1.4852 | 1.4785 | 1.476 | 1.4735 | 1.4711 | 1.4688 | 1.4584 | 1.3869 | 1.2856
|  | BALALDIE | FS |  |  |  | 0.054737 | 1.7774 | 1.7744 | 1.7742 | 1.7741 | 1.7738 | 1.7735 | 1.7732 | 1.7719 | 1.7704 | 1.7688 | 1.767 | 1.7623 | 1.7379 | 1.6846 | 1.5407 | 1.5369 | 1.535 | 1.5321 | 1.5253 | 1.5102 | 1.4951 | 1.4771 | 1.4589 | 1.4407 | 1.4224 | 1.3369 | 1.2365 | 1.1112 | 1.5052 | 1.5021 | 1.502 | 1.5018 | 1.5016 | 1.5013 | 1.5009 | 1.4996 | 1.4981 | 1.4965 | 1.4948 | 1.4901 | 1.4657 | 1.4099
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.31053 | 6.9655 | 9.4324 | 9.4009 | 9.3662 | 9.3293 | 9.2898 | 9.249 | 9.2143 | 9.1783 | 9.1422 | 9.106 | 8.8909 | 8.6009 | 8.0387 | 6.2616 | 8.7284 | 8.697 | 8.6622 | 8.6254 | 8.5859 | 8.5451 | 8.5104 | 8.4743 | 8.4383 | 8.4021 | 8.0206 | 7.4314 | 6.642 | 6.276 | 8.7371 | 8.6816 | 8.6039 | 8.5136 | 8.4211 | 8.3287 | 8.2377 | 8.1466 | 8.0554 | 7.9656 | 7.8762 | 7.782 | 7.6863
|  | BALBEGGIE | CT |  |  |  | 0.31053 | 6.9655 | 9.4324 | 9.4009 | 9.3662 | 9.3293 | 9.2898 | 9.249 | 9.2143 | 9.1783 | 9.1422 | 9.106 | 8.8909 | 8.6009 | 8.213 | 6.2616 | 8.7284 | 8.697 | 8.6622 | 8.6254 | 8.5859 | 8.5451 | 8.5104 | 8.4743 | 8.4383 | 8.4021 | 8.1869 | 7.7165 | 7.1387 | 6.276 | 8.7371 | 8.6816 | 8.6039 | 8.5252 | 8.4461 | 8.3673 | 8.2918 | 8.2158 | 8.1404 | 8.0656 | 7.9902 | 7.9105 | 7.8296
|  | BALBEGGIE | LW |  |  |  | 0.31053 | 7.0034 | 9.4635 | 9.4412 | 9.4123 | 9.3798 | 9.3443 | 9.3067 | 9.274 | 9.2403 | 9.2053 | 9.1708 | 8.9605 | 8.6538 | 8.0387 | 6.2995 | 8.7596 | 8.7373 | 8.7084 | 8.6759 | 8.6404 | 8.6028 | 8.5701 | 8.5363 | 8.5014 | 8.4669 | 8.0206 | 7.4314 | 6.642 | 6.3139 | 8.7538 | 8.6971 | 8.6064 | 8.5136 | 8.4211 | 8.3287 | 8.2377 | 8.1466 | 8.0554 | 7.9656 | 7.8762 | 7.782 | 7.6863
|  | BALBEGGIE | ST |  |  |  | 0.31053 | 7.0118 | 9.5026 | 9.4955 | 9.4851 | 9.4718 | 9.4583 | 9.4438 | 9.4347 | 9.4256 | 9.4166 | 9.4078 | 9.3642 | 9.2667 | 9.196 | 6.3079 | 8.7986 | 8.7916 | 8.7812 | 8.7679 | 8.7543 | 8.7399 | 8.7308 | 8.7217 | 8.7127 | 8.7039 | 8.6602 | 8.5628 | 8.4921 | 6.3223 | 8.8131 | 8.806 | 8.7956 | 8.7681 | 8.7279 | 8.6877 | 8.651 | 8.6149 | 8.5796 | 8.5451 | 8.3805 | 8.1688 | 7.9891
|  | BALBEGGIE | FS |  |  |  | 0.31053 | 7.016 | 9.5097 | 9.5053 | 9.5009 | 9.4964 | 9.4917 | 9.4871 | 9.4821 | 9.4769 | 9.4715 | 9.4659 | 9.4398 | 9.3884 | 9.3013 | 6.3121 | 8.8057 | 8.8013 | 8.7969 | 8.7924 | 8.7878 | 8.7832 | 8.7781 | 8.7729 | 8.7675 | 8.7619 | 8.7359 | 8.6844 | 8.5974 | 6.3265 | 8.8202 | 8.8158 | 8.8114 | 8.8069 | 8.8022 | 8.7953 | 8.7694 | 8.7433 | 8.7172 | 8.6909 | 8.5638 | 8.4187 | 8.2438
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 0.011579 | 24.8635 | 24.7868 | 24.752 | 24.7036 | 24.6477 | 24.5864 | 24.5218 | 24.4707 | 24.4187 | 24.3657 | 24.3136 | 23.9878 | 23.3971 | 22.1684 | 23.9355 | 23.8589 | 23.8241 | 23.7756 | 23.7197 | 23.6584 | 23.5938 | 23.5427 | 23.4907 | 23.4378 | 23.3856 | 23.0599 | 22.0078 | 20.3586 | 23.8429 | 23.7031 | 23.594 | 23.4104 | 23.2223 | 23.0355 | 22.8502 | 22.67 | 22.4906 | 22.3121 | 22.1362 | 21.9624 | 21.7737 | 21.5831
|  | BALDOVIE | CT |  |  |  | 0.011579 | 24.8635 | 24.8361 | 24.8128 | 24.7814 | 24.7432 | 24.6985 | 24.6504 | 24.6186 | 24.5855 | 24.5521 | 24.5183 | 24.2956 | 23.9331 | 23.3738 | 23.9355 | 23.9081 | 23.8848 | 23.8535 | 23.8153 | 23.7705 | 23.7224 | 23.6906 | 23.6575 | 23.6241 | 23.5903 | 23.3677 | 23.0051 | 22.2133 | 23.8566 | 23.7835 | 23.7077 | 23.5816 | 23.4506 | 23.3177 | 23.1849 | 23.0628 | 22.9406 | 22.8193 | 22.699 | 22.5785 | 22.4474 | 22.3153
|  | BALDOVIE | LW |  |  |  | 0.011579 | 24.8652 | 24.7868 | 24.752 | 24.7036 | 24.6477 | 24.5864 | 24.5218 | 24.4707 | 24.4187 | 24.3657 | 24.3136 | 23.9878 | 23.3971 | 22.1684 | 23.9372 | 23.8589 | 23.8241 | 23.7756 | 23.7197 | 23.6584 | 23.5938 | 23.5427 | 23.4907 | 23.4378 | 23.3856 | 23.0599 | 22.0078 | 20.3586 | 23.8429 | 23.7031 | 23.594 | 23.4104 | 23.2223 | 23.0355 | 22.8502 | 22.67 | 22.4906 | 22.3121 | 22.1362 | 21.9624 | 21.7737 | 21.5831
|  | BALDOVIE | ST |  |  |  | 0.011579 | 24.8652 | 24.8548 | 24.8498 | 24.8364 | 24.8202 | 24.8011 | 24.7798 | 24.7718 | 24.7638 | 24.7561 | 24.7488 | 24.7151 | 24.5434 | 24.4544 | 23.9372 | 23.9268 | 23.9218 | 23.9085 | 23.8922 | 23.8731 | 23.8518 | 23.8439 | 23.8358 | 23.8282 | 23.8208 | 23.7871 | 23.6155 | 23.5264 | 23.9298 | 23.915 | 23.9057 | 23.8307 | 23.7536 | 23.6766 | 23.5993 | 23.5298 | 23.4616 | 23.395 | 23.33 | 23.0201 | 22.5813 | 22.2306
|  | BALDOVIE | FS |  |  |  | 0.011579 | 24.866 | 24.8558 | 24.8553 | 24.8548 | 24.854 | 24.8528 | 24.8517 | 24.8473 | 24.8424 | 24.8369 | 24.831 | 24.8153 | 24.733 | 24.5524 | 23.938 | 23.9278 | 23.9273 | 23.9268 | 23.926 | 23.9249 | 23.9237 | 23.9194 | 23.9144 | 23.909 | 23.9031 | 23.8873 | 23.805 | 23.6244 | 23.9324 | 23.9192 | 23.9143 | 23.9067 | 23.8856 | 23.8422 | 23.799 | 23.7458 | 23.6922 | 23.6383 | 23.584 | 23.3325 | 23.0255 | 22.6292
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 0.042105 | 10.9713 | 10.9221 | 10.8936 | 10.8541 | 10.8121 | 10.7683 | 10.724 | 10.6857 | 10.6477 | 10.6097 | 10.4987 | 9.6943 | 8.8397 | 7.7907 | 12.3296 | 12.2903 | 12.2728 | 12.2485 | 12.2209 | 12.1908 | 12.0678 | 11.8562 | 11.6516 | 11.4531 | 11.2669 | 10.3708 | 9.4313 | 8.3005 | 12.398 | 12.3587 | 12.3413 | 12.3169 | 12.1174 | 11.8965 | 11.6902 | 11.4768 | 11.2666 | 11.0626 | 10.8713 | 10.6897 | 10.5041 | 10.3184
|  | BALLATER | CT |  |  |  | 0.042105 | 10.9754 | 10.9558 | 10.9374 | 10.9121 | 10.8832 | 10.8513 | 10.819 | 10.7944 | 10.7695 | 10.745 | 10.7209 | 10.5599 | 9.9668 | 9.299 | 12.3296 | 12.3163 | 12.305 | 12.2897 | 12.271 | 12.2491 | 12.2257 | 12.2104 | 12.1946 | 12.1057 | 11.9761 | 11.3368 | 10.6824 | 9.9571 | 12.398 | 12.3847 | 12.3734 | 12.3581 | 12.3394 | 12.2993 | 12.1518 | 12.0066 | 11.8635 | 11.7282 | 11.5981 | 11.4667 | 11.3323 | 11.2012
|  | BALLATER | LW |  |  |  | 0.042105 | 10.9713 | 10.9221 | 10.8936 | 10.8541 | 10.8121 | 10.7683 | 10.724 | 10.6857 | 10.6477 | 10.6097 | 10.4987 | 9.6943 | 8.8397 | 7.7907 | 12.3296 | 12.2903 | 12.2728 | 12.2485 | 12.2209 | 12.1908 | 12.0678 | 11.8562 | 11.6516 | 11.4531 | 11.2669 | 10.3708 | 9.4313 | 8.3005 | 12.398 | 12.3587 | 12.3413 | 12.3169 | 12.1174 | 11.8965 | 11.6902 | 11.4768 | 11.2666 | 11.0626 | 10.8713 | 10.6897 | 10.5041 | 10.3184
|  | BALLATER | ST |  |  |  | 0.042105 | 10.9814 | 10.9747 | 10.9703 | 10.9581 | 10.9444 | 10.9293 | 10.9136 | 10.9036 | 10.8935 | 10.8838 | 10.8745 | 10.8312 | 10.7291 | 10.6661 | 12.3296 | 12.3246 | 12.3223 | 12.3159 | 12.3081 | 12.2989 | 12.2888 | 12.2849 | 12.2811 | 12.2774 | 12.2739 | 12.258 | 11.8739 | 11.5182 | 12.398 | 12.3931 | 12.3907 | 12.3843 | 12.3765 | 12.3674 | 12.3572 | 12.3534 | 12.3495 | 12.3459 | 12.3014 | 11.9045 | 11.4937 | 11.128
|  | BALLATER | FS |  |  |  | 0.042105 | 10.9823 | 10.9763 | 10.9745 | 10.9724 | 10.9692 | 10.9646 | 10.96 | 10.9534 | 10.9464 | 10.9393 | 10.932 | 10.9031 | 10.8482 | 10.7515 | 12.3296 | 12.3251 | 12.3249 | 12.3246 | 12.3243 | 12.3238 | 12.3233 | 12.3213 | 12.3191 | 12.3167 | 12.3141 | 12.3071 | 12.271 | 12.0228 | 12.398 | 12.3935 | 12.3933 | 12.393 | 12.3927 | 12.3922 | 12.3917 | 12.3897 | 12.3875 | 12.3851 | 12.3825 | 12.2712 | 11.973 | 11.645
| CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.0063158 | 1.0386 | 1.0344 | 1.0311 | 1.0211 | 1.0109 | 1.0009 | 0.99091 | 0.98141 | 0.972 | 0.96266 | 0.9535 | 0.90552 | 0.84827 | 0.7688 | 1.101 | 1.0927 | 1.0861 | 1.0748 | 1.0634 | 1.0521 | 1.041 | 1.0303 | 1.0197 | 1.0091 | 0.99882 | 0.94519 | 0.88228 | 0.79728 | 1.0955 | 1.0878 | 1.0819 | 1.072 | 1.0618 | 1.0517 | 1.0417 | 1.0322 | 1.0228 | 1.0134 | 1.0043 | 0.99524 | 0.98563 | 0.97592
|  | BALLIEKINE | CT |  |  |  | 0.0063158 | 1.0386 | 1.0372 | 1.036 | 1.0304 | 1.0237 | 1.0169 | 1.0101 | 1.0032 | 0.9964 | 0.98964 | 0.98294 | 0.94758 | 0.90595 | 0.85589 | 1.1018 | 1.0971 | 1.0924 | 1.085 | 1.0775 | 1.0699 | 1.0623 | 1.0545 | 1.0468 | 1.0391 | 1.0315 | 0.99176 | 0.94577 | 0.89148 | 1.0962 | 1.092 | 1.0878 | 1.0813 | 1.0746 | 1.0678 | 1.061 | 1.0541 | 1.0472 | 1.0405 | 1.0337 | 1.0271 | 1.02 | 1.0128
|  | BALLIEKINE | LW |  |  |  | 0.0063158 | 1.0386 | 1.0344 | 1.0311 | 1.0211 | 1.0109 | 1.0009 | 0.99091 | 0.98141 | 0.972 | 0.96266 | 0.9535 | 0.90552 | 0.84827 | 0.7688 | 1.101 | 1.0927 | 1.0861 | 1.0748 | 1.0634 | 1.0521 | 1.041 | 1.0303 | 1.0197 | 1.0091 | 0.99882 | 0.94519 | 0.88228 | 0.79728 | 1.0955 | 1.0878 | 1.0819 | 1.072 | 1.0618 | 1.0517 | 1.0417 | 1.0322 | 1.0228 | 1.0134 | 1.0043 | 0.99524 | 0.98563 | 0.97592
|  | BALLIEKINE | ST |  |  |  | 0.0063158 | 1.0386 | 1.0381 | 1.0379 | 1.0372 | 1.0363 | 1.0354 | 1.0323 | 1.0287 | 1.025 | 1.0215 | 1.0181 | 1.002 | 0.98017 | 0.963 | 1.1073 | 1.1066 | 1.1062 | 1.1015 | 1.0968 | 1.092 | 1.0873 | 1.083 | 1.0788 | 1.0748 | 1.0708 | 1.0521 | 1.0278 | 1.0083 | 1.1009 | 1.1002 | 1.0998 | 1.0958 | 1.0916 | 1.0874 | 1.0832 | 1.0795 | 1.0759 | 1.0724 | 1.0689 | 1.0528 | 1.031 | 1.0138
|  | BALLIEKINE | FS |  |  |  | 0.0063158 | 1.0386 | 1.0382 | 1.0382 | 1.0381 | 1.0381 | 1.038 | 1.038 | 1.0378 | 1.0376 | 1.0351 | 1.0323 | 1.0188 | 1.003 | 0.98357 | 1.1077 | 1.1071 | 1.107 | 1.1067 | 1.1058 | 1.1029 | 1.1 | 1.0967 | 1.0934 | 1.0901 | 1.0867 | 1.0709 | 1.053 | 1.0315 | 1.1012 | 1.1007 | 1.1005 | 1.1003 | 1.0995 | 1.097 | 1.0946 | 1.0918 | 1.0889 | 1.086 | 1.0832 | 1.0696 | 1.0539 | 1.0344
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 0.11684 | 14.7454 | 14.7249 | 14.7053 | 14.6838 | 14.6607 | 14.6371 | 14.6127 | 14.5663 | 14.5086 | 14.447 | 14.3854 | 14.0624 | 13.6811 | 13.1888 | 12.3857 | 12.3651 | 12.3455 | 12.3231 | 12.2552 | 12.1872 | 12.1189 | 12.0507 | 11.982 | 11.9138 | 11.8456 | 11.4908 | 11.0773 | 10.5534 | 13.7424 | 13.7218 | 13.7023 | 13.6808 | 13.6577 | 13.634 | 13.6096 | 13.5882 | 13.5657 | 13.5363 | 13.4692 | 13.4029 | 13.3333 | 13.2632
|  | BALLINDALLOCH | CT |  |  |  | 0.11684 | 14.7454 | 14.7249 | 14.7053 | 14.6838 | 14.6607 | 14.6371 | 14.6127 | 14.5761 | 14.5332 | 14.4904 | 14.4479 | 14.1772 | 13.8588 | 13.4907 | 12.3857 | 12.3651 | 12.3455 | 12.3235 | 12.2663 | 12.2097 | 12.1534 | 12.0972 | 12.0403 | 11.9839 | 11.9278 | 11.633 | 11.2919 | 10.9016 | 13.7424 | 13.7218 | 13.7023 | 13.6808 | 13.6577 | 13.634 | 13.6096 | 13.5882 | 13.5657 | 13.5432 | 13.5207 | 13.4931 | 13.4354 | 13.3774
|  | BALLINDALLOCH | LW |  |  |  | 0.11684 | 14.7707 | 14.7479 | 14.7346 | 14.7172 | 14.6983 | 14.6645 | 14.6148 | 14.5663 | 14.5086 | 14.447 | 14.3854 | 14.0624 | 13.6811 | 13.1888 | 12.4109 | 12.3882 | 12.3749 | 12.3231 | 12.2552 | 12.1872 | 12.1189 | 12.0507 | 11.982 | 11.9138 | 11.8456 | 11.4908 | 11.0773 | 10.5534 | 13.7677 | 13.7449 | 13.7316 | 13.7142 | 13.6952 | 13.6743 | 13.6518 | 13.6326 | 13.6033 | 13.5363 | 13.4692 | 13.4029 | 13.3333 | 13.2632
|  | BALLINDALLOCH | ST |  |  |  | 0.11684 | 14.7766 | 14.7709 | 14.7665 | 14.7601 | 14.7523 | 14.7439 | 14.735 | 14.7291 | 14.7231 | 14.7172 | 14.7114 | 14.6318 | 14.4996 | 14.3745 | 12.4168 | 12.4112 | 12.4067 | 12.4004 | 12.3926 | 12.3842 | 12.3753 | 12.3496 | 12.3205 | 12.2919 | 12.2638 | 12.1284 | 11.9696 | 11.8307 | 13.7736 | 13.7679 | 13.7634 | 13.7571 | 13.7493 | 13.7409 | 13.732 | 13.726 | 13.7201 | 13.7142 | 13.7083 | 13.68 | 13.5915 | 13.4551
|  | BALLINDALLOCH | FS |  |  |  | 0.11684 | 14.7791 | 14.7754 | 14.7728 | 14.7701 | 14.7674 | 14.7647 | 14.7619 | 14.7585 | 14.755 | 14.7514 | 14.7477 | 14.7302 | 14.6559 | 14.5549 | 12.4194 | 12.4156 | 12.413 | 12.4104 | 12.4077 | 12.4049 | 12.4022 | 12.3988 | 12.3953 | 12.3917 | 12.3717 | 12.2676 | 12.1563 | 12.0295 | 13.7761 | 13.7723 | 13.7697 | 13.7671 | 13.7644 | 13.7617 | 13.7589 | 13.7555 | 13.752 | 13.7484 | 13.7447 | 13.7272 | 13.6984 | 13.6505
| CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0 | 2.2444 | 2.2342 | 2.2244 | 2.2147 | 2.2042 | 2.1932 | 2.1818 | 2.1713 | 2.1606 | 2.1499 | 2.1392 | 2.0767 | 1.96 | 1.7663 | 2.1845 | 2.1687 | 2.1527 | 2.1323 | 2.1115 | 2.0905 | 2.0696 | 2.0462 | 2.0225 | 1.9989 | 1.9756 | 1.8501 | 1.6988 | 1.4979 | 2.1103 | 2.0941 | 2.0778 | 2.0568 | 2.0353 | 2.0138 | 1.9915 | 1.9667 | 1.9421 | 1.9176 | 1.8935 | 1.8697 | 1.8439 | 1.818
|  | BALLURE | CT |  |  |  | 0 | 2.2444 | 2.2342 | 2.2244 | 2.2147 | 2.2042 | 2.1932 | 2.1818 | 2.1713 | 2.1606 | 2.1499 | 2.1392 | 2.0767 | 1.994 | 1.8547 | 2.1845 | 2.1687 | 2.1527 | 2.1323 | 2.1115 | 2.0905 | 2.0696 | 2.0491 | 2.0286 | 2.0082 | 1.988 | 1.8792 | 1.75 | 1.5974 | 2.1103 | 2.0941 | 2.0778 | 2.0568 | 2.0353 | 2.0138 | 1.9923 | 1.9712 | 1.9501 | 1.9292 | 1.9084 | 1.8877 | 1.8654 | 1.8429
|  | BALLURE | LW |  |  |  | 0 | 2.257 | 2.2468 | 2.2409 | 2.2336 | 2.2248 | 2.2155 | 2.2059 | 2.1968 | 2.1877 | 2.1785 | 2.1694 | 2.1051 | 1.96 | 1.7663 | 2.1941 | 2.1769 | 2.162 | 2.1397 | 2.1163 | 2.0931 | 2.0702 | 2.0462 | 2.0225 | 1.9989 | 1.9756 | 1.8501 | 1.6988 | 1.4979 | 2.1197 | 2.1021 | 2.0867 | 2.0635 | 2.0392 | 2.0152 | 1.9915 | 1.9667 | 1.9421 | 1.9176 | 1.8935 | 1.8697 | 1.8439 | 1.818
|  | BALLURE | ST |  |  |  | 0 | 2.2587 | 2.2561 | 2.2539 | 2.251 | 2.2478 | 2.2443 | 2.2406 | 2.2382 | 2.2357 | 2.2333 | 2.231 | 2.2186 | 2.1932 | 2.1727 | 2.2068 | 2.2039 | 2.2015 | 2.1916 | 2.1815 | 2.1715 | 2.1615 | 2.1523 | 2.1433 | 2.1344 | 2.1257 | 2.0835 | 2.0298 | 1.9821 | 2.1331 | 2.1301 | 2.1277 | 2.1174 | 2.1069 | 2.0965 | 2.0861 | 2.0766 | 2.0671 | 2.0579 | 2.0488 | 2.0048 | 1.9494 | 1.9002
|  | BALLURE | FS |  |  |  | 0 | 2.2604 | 2.2587 | 2.257 | 2.2552 | 2.2535 | 2.2517 | 2.2508 | 2.2495 | 2.2483 | 2.247 | 2.2456 | 2.2367 | 2.2213 | 2.1976 | 2.209 | 2.2071 | 2.2052 | 2.2029 | 2.1988 | 2.1928 | 2.1878 | 2.181 | 2.1742 | 2.1674 | 2.1606 | 2.1248 | 2.084 | 2.0362 | 2.1353 | 2.1334 | 2.1314 | 2.1292 | 2.1249 | 2.1187 | 2.1134 | 2.1063 | 2.0992 | 2.0921 | 2.0849 | 2.0475 | 2.0052 | 1.956
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 0.028421 | 8.282 | 8.2554 | 8.2309 | 8.203 | 8.1705 | 8.0048 | 7.7468 | 7.4816 | 7.2327 | 6.9969 | 6.7908 | 5.8677 | 4.9771 | 3.9118 | 7.8718 | 7.8374 | 7.7835 | 7.4005 | 7.0396 | 6.7024 | 6.4059 | 6.0996 | 5.8127 | 5.5414 | 5.3048 | 4.2552 | 3.2621 | 2.1054 | 8.1097 | 8.083 | 8.0585 | 8.0181 | 7.9069 | 7.578 | 7.2887 | 6.9901 | 6.7103 | 6.4456 | 6.2148 | 6.0096 | 5.8004 | 5.5939
|  | BALMEDIE | CT |  |  |  | 0.028421 | 8.282 | 8.2554 | 8.2309 | 8.203 | 8.1714 | 8.1367 | 8.1003 | 8.0717 | 8.018 | 7.8527 | 7.7014 | 6.9813 | 6.3131 | 5.5772 | 7.8718 | 7.8451 | 7.8131 | 7.7747 | 7.6493 | 7.3825 | 7.161 | 6.944 | 6.7337 | 6.5445 | 6.3716 | 5.556 | 4.8148 | 4.0121 | 8.1097 | 8.083 | 8.0585 | 8.0306 | 7.9991 | 7.9527 | 7.9059 | 7.8111 | 7.606 | 7.4212 | 7.2523 | 7.083 | 6.9175 | 6.7597
|  | BALMEDIE | LW |  |  |  | 0.028421 | 8.3039 | 8.2587 | 8.2359 | 8.2049 | 8.1705 | 8.0048 | 7.7468 | 7.4816 | 7.2327 | 6.9969 | 6.7908 | 5.8677 | 4.9771 | 3.9118 | 7.8937 | 7.8374 | 7.7835 | 7.4005 | 7.0396 | 6.7024 | 6.4059 | 6.0996 | 5.8127 | 5.5414 | 5.3048 | 4.2552 | 3.2621 | 2.1054 | 8.1316 | 8.0864 | 8.0636 | 8.0181 | 7.9069 | 7.578 | 7.2887 | 6.9901 | 6.7103 | 6.4456 | 6.2148 | 6.0096 | 5.8004 | 5.5939
|  | BALMEDIE | ST |  |  |  | 0.028421 | 8.3081 | 8.2996 | 8.2938 | 8.2846 | 8.2731 | 8.2603 | 8.2464 | 8.239 | 8.2317 | 8.2245 | 8.2175 | 8.1842 | 7.8987 | 7.563 | 7.8979 | 7.8893 | 7.8835 | 7.8743 | 7.8607 | 7.8422 | 7.8232 | 7.8102 | 7.7969 | 7.6772 | 7.56 | 7.0385 | 6.5856 | 6.2014 | 8.1358 | 8.1273 | 8.1214 | 8.1123 | 8.1008 | 8.088 | 8.074 | 8.0667 | 8.0593 | 8.0522 | 8.039 | 7.9061 | 7.4632 | 7.0881
|  | BALMEDIE | FS |  |  |  | 0.028421 | 8.3098 | 8.3034 | 8.3007 | 8.2979 | 8.295 | 8.2919 | 8.2889 | 8.2844 | 8.2804 | 8.2762 | 8.2718 | 8.2527 | 8.2028 | 8.0321 | 7.8996 | 7.8931 | 7.8904 | 7.8876 | 7.8847 | 7.8817 | 7.8752 | 7.8663 | 7.8577 | 7.849 | 7.8401 | 7.4639 | 7.1128 | 6.7385 | 8.1375 | 8.1311 | 8.1283 | 8.1256 | 8.1227 | 8.1196 | 8.1166 | 8.112 | 8.108 | 8.1038 | 8.0994 | 8.0668 | 7.9789 | 7.6125
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 0.99789 | 13.1339 | 13.1118 | 13.0995 | 13.0826 | 13.0644 | 13.0447 | 13.0244 | 13.0069 | 12.989 | 12.945 | 12.8893 | 12.5955 | 12.2367 | 11.7111 | 13.072 | 13.0537 | 13.0456 | 13.0343 | 13.0215 | 13.0069 | 12.9913 | 12.9788 | 12.9657 | 12.8895 | 12.817 | 12.4426 | 12.0033 | 11.3937 | 13.2195 | 13.1981 | 13.1867 | 13.1709 | 13.1538 | 13.085 | 13.0075 | 12.9299 | 12.8533 | 12.7787 | 12.7083 | 12.6411 | 12.5666 | 12.4924
|  | BALNAGASK | CT |  |  |  | 0.99789 | 13.1357 | 13.1275 | 13.12 | 13.1097 | 13.0979 | 13.0841 | 13.0699 | 13.0591 | 13.0478 | 13.0364 | 13.025 | 12.9004 | 12.6485 | 12.3232 | 13.072 | 13.0662 | 13.0613 | 13.0547 | 13.0466 | 13.0367 | 13.0258 | 13.0185 | 13.0105 | 13.0023 | 12.9939 | 12.8343 | 12.5254 | 12.1407 | 13.2209 | 13.2132 | 13.2062 | 13.1967 | 13.1856 | 13.1726 | 13.1591 | 13.1355 | 13.0823 | 13.0322 | 12.9835 | 12.9341 | 12.8805 | 12.8283
|  | BALNAGASK | LW |  |  |  | 0.99789 | 13.1339 | 13.1118 | 13.0995 | 13.0826 | 13.0644 | 13.0447 | 13.0244 | 13.0069 | 12.989 | 12.945 | 12.8893 | 12.5955 | 12.2367 | 11.7111 | 13.072 | 13.0537 | 13.0456 | 13.0343 | 13.0215 | 13.0069 | 12.9913 | 12.9788 | 12.9657 | 12.8895 | 12.817 | 12.4426 | 12.0033 | 11.3937 | 13.2195 | 13.1981 | 13.1867 | 13.1709 | 13.1538 | 13.085 | 13.0075 | 12.9299 | 12.8533 | 12.7787 | 12.7083 | 12.6411 | 12.5666 | 12.4924
|  | BALNAGASK | ST |  |  |  | 0.99789 | 13.1377 | 13.1342 | 13.132 | 13.1264 | 13.1198 | 13.1125 | 13.1047 | 13.1002 | 13.0957 | 13.0914 | 13.0872 | 13.0671 | 13.0017 | 12.925 | 13.072 | 13.0691 | 13.0678 | 13.0641 | 13.0597 | 13.0545 | 13.0487 | 13.0466 | 13.0444 | 13.0423 | 13.0403 | 13.0305 | 12.9745 | 12.8646 | 13.2225 | 13.2191 | 13.2171 | 13.2119 | 13.2057 | 13.1988 | 13.1914 | 13.1875 | 13.1834 | 13.1795 | 13.1758 | 13.0932 | 12.912 | 12.7544
|  | BALNAGASK | FS |  |  |  | 0.99789 | 13.1379 | 13.1339 | 13.1331 | 13.1321 | 13.1307 | 13.1287 | 13.1267 | 13.1234 | 13.1199 | 13.1162 | 13.1124 | 13.0985 | 13.0618 | 12.989 | 13.072 | 13.0685 | 13.0684 | 13.0682 | 13.0679 | 13.0675 | 13.0671 | 13.0657 | 13.064 | 13.0622 | 13.0602 | 13.0549 | 13.0261 | 12.9611 | 13.2226 | 13.2187 | 13.2181 | 13.2173 | 13.2161 | 13.2144 | 13.2128 | 13.2098 | 13.2067 | 13.2033 | 13.1999 | 13.1877 | 13.0777 | 12.9083
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 0.12211 | 16.861 | 16.784 | 16.7327 | 16.6627 | 16.5833 | 16.4966 | 16.3633 | 15.8873 | 15.4332 | 14.9979 | 14.6029 | 12.742 | 10.81 | 8.3892 | 14.5388 | 14.0007 | 13.4839 | 12.8336 | 12.2096 | 11.6184 | 11.0835 | 10.5353 | 10.0131 | 9.5133 | 9.0608 | 6.9486 | 4.7955 | 2.1696 | 15.3638 | 14.8874 | 14.4373 | 13.851 | 13.2411 | 12.6631 | 12.1397 | 11.6038 | 11.0932 | 10.6043 | 10.1617 | 9.753 | 9.3341 | 8.9173
|  | BANCHORY | CT |  |  |  | 0.12211 | 16.861 | 16.8099 | 16.764 | 16.7078 | 16.6427 | 16.5705 | 16.4943 | 16.4382 | 16.3799 | 16.3215 | 16.1831 | 14.7895 | 13.3818 | 11.7869 | 14.707 | 14.3965 | 14.0559 | 13.6283 | 13.1816 | 12.7256 | 12.3301 | 11.9461 | 11.5702 | 11.222 | 10.8967 | 9.3178 | 7.7536 | 6.0123 | 15.5036 | 15.2302 | 14.9318 | 14.5574 | 14.1653 | 13.7435 | 13.3562 | 12.9807 | 12.6131 | 12.2724 | 11.954 | 11.6363 | 11.317 | 11.01
|  | BANCHORY | LW |  |  |  | 0.12211 | 16.8914 | 16.784 | 16.7327 | 16.6627 | 16.5833 | 16.4966 | 16.3633 | 15.8873 | 15.4332 | 14.9979 | 14.6029 | 12.742 | 10.81 | 8.3892 | 14.5388 | 14.0007 | 13.4839 | 12.8336 | 12.2096 | 11.6184 | 11.0835 | 10.5353 | 10.0131 | 9.5133 | 9.0608 | 6.9486 | 4.7955 | 2.1696 | 15.3638 | 14.8874 | 14.4373 | 13.851 | 13.2411 | 12.6631 | 12.1397 | 11.6038 | 11.0932 | 10.6043 | 10.1617 | 9.753 | 9.3341 | 8.9173
|  | BANCHORY | ST |  |  |  | 0.12211 | 16.8964 | 16.8795 | 16.8692 | 16.8486 | 16.8236 | 16.7951 | 16.764 | 16.7501 | 16.736 | 16.7224 | 16.7092 | 16.6458 | 16.3447 | 15.6566 | 14.9451 | 14.8468 | 14.7401 | 14.522 | 14.2908 | 14.0534 | 13.8308 | 13.6049 | 13.3754 | 13.1558 | 12.946 | 11.9913 | 11.0588 | 10.2707 | 15.7126 | 15.626 | 15.533 | 15.3433 | 15.1416 | 14.9341 | 14.7389 | 14.5434 | 14.3448 | 14.1547 | 13.9617 | 13.0301 | 12.116 | 11.3449
|  | BANCHORY | FS |  |  |  | 0.12211 | 16.8998 | 16.8855 | 16.8816 | 16.8776 | 16.8733 | 16.8686 | 16.864 | 16.8564 | 16.8482 | 16.8394 | 16.8301 | 16.796 | 16.6859 | 16.4664 | 14.9849 | 14.9022 | 14.8247 | 14.7342 | 14.6156 | 14.4634 | 14.3143 | 14.1444 | 13.9659 | 13.7907 | 13.6179 | 12.8278 | 12.1255 | 11.3533 | 15.7472 | 15.6743 | 15.6073 | 15.5292 | 15.427 | 15.2959 | 15.1675 | 15.0209 | 14.8668 | 14.7154 | 14.566 | 13.8489 | 13.1619 | 12.4041
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 0.33684 | 1.9462 | 1.925 | 1.9155 | 1.9024 | 1.8875 | 1.8712 | 1.8542 | 1.8409 | 1.8274 | 1.8138 | 1.8004 | 1.7187 | 1.4985 | 1.0798 | 2.1937 | 2.1725 | 2.1631 | 2.1499 | 2.135 | 2.1188 | 2.1018 | 2.0884 | 2.0202 | 1.9491 | 1.8817 | 1.55 | 1.1844 | 0.71787 | 2.0122 | 1.9885 | 1.9765 | 1.9513 | 1.888 | 1.8264 | 1.7578 | 1.688 | 1.6204 | 1.5541 | 1.4913 | 1.431 | 1.3687 | 1.3059
|  | BARCALDINE | CT |  |  |  | 0.33684 | 1.9462 | 1.9391 | 1.9331 | 1.925 | 1.915 | 1.9034 | 1.891 | 1.8829 | 1.8746 | 1.8663 | 1.8579 | 1.8038 | 1.7193 | 1.5902 | 2.1937 | 2.1866 | 2.1806 | 2.1725 | 2.1625 | 2.1509 | 2.1385 | 2.1305 | 2.1222 | 2.1138 | 2.1054 | 1.8931 | 1.643 | 1.355 | 2.013 | 2.0044 | 1.9966 | 1.9858 | 1.9731 | 1.9323 | 1.8895 | 1.8501 | 1.8071 | 1.7625 | 1.7191 | 1.6768 | 1.6324 | 1.5887
|  | BARCALDINE | LW |  |  |  | 0.33684 | 1.9462 | 1.925 | 1.9155 | 1.9024 | 1.8875 | 1.8712 | 1.8542 | 1.8409 | 1.8274 | 1.8138 | 1.8004 | 1.7187 | 1.4985 | 1.0798 | 2.1937 | 2.1725 | 2.1631 | 2.1499 | 2.135 | 2.1188 | 2.1018 | 2.0884 | 2.0202 | 1.9491 | 1.8817 | 1.55 | 1.1844 | 0.71787 | 2.0122 | 1.9885 | 1.9765 | 1.9513 | 1.888 | 1.8264 | 1.7578 | 1.688 | 1.6204 | 1.5541 | 1.4913 | 1.431 | 1.3687 | 1.3059
|  | BARCALDINE | ST |  |  |  | 0.33684 | 1.9462 | 1.9436 | 1.9424 | 1.939 | 1.935 | 1.9302 | 1.9249 | 1.9229 | 1.9209 | 1.919 | 1.9172 | 1.9089 | 1.8688 | 1.8483 | 2.1937 | 2.1911 | 2.1899 | 2.1866 | 2.1825 | 2.1778 | 2.1724 | 2.1705 | 2.1685 | 2.1665 | 2.1647 | 2.1565 | 2.1157 | 1.9975 | 2.0148 | 2.0118 | 2.0102 | 2.0053 | 1.9997 | 1.9934 | 1.9866 | 1.9831 | 1.9795 | 1.9679 | 1.9468 | 1.8472 | 1.7114 | 1.6014
|  | BARCALDINE | FS |  |  |  | 0.33684 | 1.9462 | 1.9439 | 1.9438 | 1.9437 | 1.9435 | 1.9432 | 1.943 | 1.942 | 1.9409 | 1.9397 | 1.9383 | 1.9348 | 1.9166 | 1.8771 | 2.1937 | 2.1914 | 2.1913 | 2.1912 | 2.191 | 2.1908 | 2.1905 | 2.1895 | 2.1884 | 2.1872 | 2.1859 | 2.1823 | 2.1641 | 2.1247 | 2.015 | 2.0124 | 2.012 | 2.0115 | 2.0106 | 2.0093 | 2.008 | 2.0058 | 2.0034 | 2.001 | 1.9984 | 1.946 | 1.8605 | 1.7474
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.0010526 | 2.9697 | 2.9414 | 2.9287 | 2.9112 | 2.8913 | 2.8695 | 2.8465 | 2.8285 | 2.8102 | 2.7916 | 2.7734 | 2.6601 | 2.4501 | 1.909 | 2.8794 | 2.851 | 2.8384 | 2.8208 | 2.8009 | 2.7791 | 2.7562 | 2.7381 | 2.7198 | 2.7013 | 2.683 | 2.349 | 1.9257 | 1.3429 | 2.8485 | 2.8201 | 2.8075 | 2.79 | 2.77 | 2.7483 | 2.7253 | 2.7073 | 2.689 | 2.6704 | 2.6522 | 2.6092 | 2.5384 | 2.4669
|  | BARVAS | CT |  |  |  | 0.0010526 | 2.9697 | 2.9598 | 2.9515 | 2.9401 | 2.9262 | 2.91 | 2.8925 | 2.8811 | 2.8693 | 2.8574 | 2.8455 | 2.7672 | 2.6423 | 2.4495 | 2.8794 | 2.8695 | 2.8611 | 2.8498 | 2.8359 | 2.8196 | 2.8021 | 2.7908 | 2.779 | 2.7671 | 2.7551 | 2.6725 | 2.3783 | 2.0203 | 2.8485 | 2.8386 | 2.8303 | 2.8189 | 2.805 | 2.7887 | 2.7713 | 2.7599 | 2.7481 | 2.7362 | 2.7242 | 2.7118 | 2.6962 | 2.6801
|  | BARVAS | LW |  |  |  | 0.0010526 | 2.9697 | 2.9414 | 2.9287 | 2.9112 | 2.8913 | 2.8695 | 2.8465 | 2.8285 | 2.8102 | 2.7916 | 2.7734 | 2.6601 | 2.4501 | 1.909 | 2.8794 | 2.851 | 2.8384 | 2.8208 | 2.8009 | 2.7791 | 2.7562 | 2.7381 | 2.7198 | 2.7013 | 2.683 | 2.349 | 1.9257 | 1.3429 | 2.8485 | 2.8201 | 2.8075 | 2.79 | 2.77 | 2.7483 | 2.7253 | 2.7073 | 2.689 | 2.6704 | 2.6522 | 2.6092 | 2.5384 | 2.4669
|  | BARVAS | ST |  |  |  | 0.0010526 | 2.9697 | 2.966 | 2.9642 | 2.9594 | 2.9535 | 2.9466 | 2.939 | 2.9361 | 2.9332 | 2.9305 | 2.9278 | 2.9158 | 2.8562 | 2.8255 | 2.8794 | 2.8756 | 2.8738 | 2.869 | 2.8632 | 2.8563 | 2.8486 | 2.8458 | 2.8429 | 2.8401 | 2.8374 | 2.8254 | 2.7658 | 2.7352 | 2.8485 | 2.8448 | 2.843 | 2.8382 | 2.8323 | 2.8254 | 2.8178 | 2.8149 | 2.812 | 2.8092 | 2.8066 | 2.7946 | 2.735 | 2.7043
|  | BARVAS | FS |  |  |  | 0.0010526 | 2.9697 | 2.9662 | 2.9661 | 2.9659 | 2.9656 | 2.9652 | 2.9648 | 2.9633 | 2.9616 | 2.9598 | 2.9578 | 2.9524 | 2.9244 | 2.8634 | 2.8794 | 2.8759 | 2.8757 | 2.8755 | 2.8753 | 2.8749 | 2.8745 | 2.873 | 2.8713 | 2.8694 | 2.8674 | 2.862 | 2.8341 | 2.773 | 2.8485 | 2.845 | 2.8449 | 2.8447 | 2.8444 | 2.844 | 2.8436 | 2.8421 | 2.8404 | 2.8386 | 2.8366 | 2.8312 | 2.8032 | 2.7422
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 0 | 19.7273 | 19.6372 | 33.1725 | 33.1108 | 33.0411 | 32.965 | 32.8849 | 32.8208 | 32.7558 | 32.6898 | 32.6248 | 32.223 | 31.5949 | 30.4053 | 17.4004 | 17.3103 | 30.1456 | 30.0839 | 30.0142 | 29.9381 | 29.858 | 29.7939 | 29.7289 | 29.6629 | 29.5979 | 28.558 | 26.9945 | 24.8778 | 18.1436 | 18.0534 | 31.2387 | 31.1771 | 31.1074 | 31.0313 | 30.9512 | 30.8871 | 30.8221 | 30.756 | 30.6911 | 30.6268 | 30.5474 | 30.2926
|  | BATTERY POINT | CT |  |  |  | 0 | 19.7273 | 19.6892 | 33.2364 | 33.1933 | 33.1415 | 33.0824 | 33.0193 | 32.9761 | 32.9314 | 32.8864 | 32.8412 | 32.5499 | 32.0928 | 31.3981 | 17.4004 | 17.3623 | 30.2095 | 30.1664 | 30.1146 | 30.0555 | 29.9924 | 29.9492 | 29.9045 | 29.8596 | 29.8143 | 29.523 | 28.5924 | 27.2573 | 18.1436 | 18.1055 | 31.3026 | 31.2596 | 31.2077 | 31.1487 | 31.0856 | 31.0423 | 30.9976 | 30.9527 | 30.9074 | 30.8605 | 30.8027 | 30.7432
|  | BATTERY POINT | LW |  |  |  | 0 | 19.7349 | 19.6372 | 33.1725 | 33.1108 | 33.0411 | 32.965 | 32.8849 | 32.8208 | 32.7558 | 32.6898 | 32.6248 | 32.223 | 31.5949 | 30.4053 | 17.408 | 17.3103 | 30.1456 | 30.0839 | 30.0142 | 29.9381 | 29.858 | 29.7939 | 29.7289 | 29.6629 | 29.5979 | 28.558 | 26.9945 | 24.8778 | 18.1511 | 18.0534 | 31.2387 | 31.1771 | 31.1074 | 31.0313 | 30.9512 | 30.8871 | 30.8221 | 30.756 | 30.6911 | 30.6268 | 30.5474 | 30.2926
|  | BATTERY POINT | ST |  |  |  | 0 | 19.7357 | 19.722 | 33.295 | 33.2777 | 33.2567 | 33.2323 | 33.2051 | 33.1945 | 33.1837 | 33.1734 | 33.1634 | 33.118 | 32.9089 | 32.7958 | 17.4088 | 17.3951 | 30.2681 | 30.2508 | 30.2298 | 30.2054 | 30.1783 | 30.1676 | 30.1568 | 30.1465 | 30.1365 | 30.0911 | 29.882 | 29.769 | 18.152 | 18.1383 | 31.3613 | 31.3439 | 31.323 | 31.2986 | 31.2714 | 31.2607 | 31.25 | 31.2396 | 31.2297 | 31.1843 | 30.9752 | 30.8621
|  | BATTERY POINT | FS |  |  |  | 0 | 19.7365 | 19.7237 | 33.3023 | 33.3008 | 33.299 | 33.2968 | 33.2947 | 33.2887 | 33.282 | 33.2747 | 33.2669 | 33.2442 | 33.1437 | 32.9292 | 17.4097 | 17.3968 | 30.2754 | 30.2739 | 30.2721 | 30.2699 | 30.2678 | 30.2618 | 30.2551 | 30.2478 | 30.24 | 30.2173 | 30.1168 | 29.9023 | 18.1528 | 18.1399 | 31.3685 | 31.3671 | 31.3653 | 31.3631 | 31.3609 | 31.3549 | 31.3483 | 31.341 | 31.3332 | 31.3105 | 31.21 | 30.9954
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0 | 1.1763 | 1.1666 | 1.1574 | 1.1481 | 1.1381 | 1.1274 | 1.1164 | 1.1063 | 1.0961 | 1.0855 | 1.0615 | 0.93493 | 0.78243 | 0.57868 | 1.163 | 1.1467 | 1.1303 | 1.1077 | 1.0816 | 1.0535 | 1.0256 | 0.99866 | 0.9719 | 0.94453 | 0.91758 | 0.77649 | 0.6095 | 0.39167 | 1.1447 | 1.135 | 1.1258 | 1.1165 | 1.1065 | 1.0958 | 1.0848 | 1.0747 | 1.0532 | 1.0258 | 0.99895 | 0.97241 | 0.94475 | 0.91606
|  | BETTYHILL | CT |  |  |  | 0 | 1.1763 | 1.1666 | 1.1574 | 1.1481 | 1.1381 | 1.1274 | 1.1164 | 1.1063 | 1.0961 | 1.086 | 1.0758 | 0.977 | 0.85019 | 0.69927 | 1.163 | 1.1467 | 1.1303 | 1.1077 | 1.0846 | 1.0614 | 1.0384 | 1.0159 | 0.99341 | 0.97116 | 0.9491 | 0.83207 | 0.69534 | 0.53485 | 1.1447 | 1.135 | 1.1258 | 1.1165 | 1.1065 | 1.0958 | 1.0848 | 1.0747 | 1.0645 | 1.0523 | 1.0303 | 1.0084 | 0.98565 | 0.96199
|  | BETTYHILL | LW |  |  |  | 0 | 1.188 | 1.1775 | 1.1711 | 1.1631 | 1.1544 | 1.1443 | 1.1338 | 1.1249 | 1.1099 | 1.0855 | 1.0615 | 0.93493 | 0.78243 | 0.57868 | 1.1731 | 1.1535 | 1.1367 | 1.1093 | 1.0816 | 1.0535 | 1.0256 | 0.99866 | 0.9719 | 0.94453 | 0.91758 | 0.77649 | 0.6095 | 0.39167 | 1.1565 | 1.1459 | 1.1395 | 1.1315 | 1.1228 | 1.1127 | 1.1022 | 1.0799 | 1.0532 | 1.0258 | 0.99895 | 0.97241 | 0.94475 | 0.91606
|  | BETTYHILL | ST |  |  |  | 0 | 1.1906 | 1.1878 | 1.1856 | 1.1826 | 1.1792 | 1.1756 | 1.1717 | 1.1692 | 1.1667 | 1.1642 | 1.1618 | 1.15 | 1.1159 | 1.0667 | 1.1885 | 1.1854 | 1.182 | 1.1699 | 1.1576 | 1.1454 | 1.1333 | 1.122 | 1.1109 | 1.1001 | 1.0894 | 1.0389 | 0.97728 | 0.92208 | 1.159 | 1.1562 | 1.154 | 1.151 | 1.1476 | 1.144 | 1.1401 | 1.1376 | 1.1351 | 1.1326 | 1.1302 | 1.1184 | 1.0586 | 1.0035
|  | BETTYHILL | FS |  |  |  | 0 | 1.1914 | 1.1896 | 1.1887 | 1.1879 | 1.1869 | 1.186 | 1.185 | 1.1838 | 1.1825 | 1.1812 | 1.1798 | 1.1708 | 1.1583 | 1.138 | 1.1901 | 1.1881 | 1.1869 | 1.1845 | 1.1809 | 1.1742 | 1.1675 | 1.1599 | 1.1523 | 1.1447 | 1.137 | 1.0971 | 1.0559 | 1.0086 | 1.1598 | 1.158 | 1.1572 | 1.1563 | 1.1553 | 1.1544 | 1.1535 | 1.1522 | 1.1509 | 1.1496 | 1.1482 | 1.1392 | 1.1267 | 1.0898
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | YES | 0 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.099866 | 0.099592 | 0.10068 | 0.10065 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099954 | 0.099888 | 0.099565 | 0.099239 | 0.098918 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.0997 | 0.099375 | 0.099053
|  | BIDEN CLAN RAONAILD | CT |  |  |  | 0 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10068 | 0.10066 | 0.10064 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099858 | 0.09963 | 0.099405 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.099987 | 0.099765 | 0.099541
|  | BIDEN CLAN RAONAILD | LW |  |  |  | 0 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.099866 | 0.099592 | 0.10068 | 0.10065 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099954 | 0.099888 | 0.099565 | 0.099239 | 0.098918 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.0997 | 0.099375 | 0.099053
|  | BIDEN CLAN RAONAILD | ST |  |  |  | 0 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10069 | 0.10068 | 0.10066 | 0.10065 | 0.10064 | 0.10063 | 0.10062 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.099988 | 0.099847 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115
|  | BIDEN CLAN RAONAILD | FS |  |  |  | 0 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10069 | 0.10069 | 0.10069 | 0.10068 | 0.10068 | 0.10067 | 0.10067 | 0.10066 | 0.10065 | 0.10065 | 0.10064 | 0.10062 | 0.10062 | 0.10061 | 0.10078 | 0.10078 | 0.10078 | 0.10077 | 0.10077 | 0.10077 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 0.031579 | 13.157 | 24.416 | 24.3964 | 24.3739 | 24.35 | 24.2951 | 24.232 | 24.1709 | 24.1102 | 24.0498 | 23.9895 | 23.6659 | 23.2645 | 22.7001 | 12.8515 | 22.9105 | 22.8908 | 22.8684 | 22.8444 | 22.8183 | 22.791 | 22.7685 | 22.7457 | 22.7228 | 22.699 | 22.5583 | 22.3335 | 21.7971 | 12.828 | 23.487 | 23.4673 | 23.4449 | 23.4209 | 23.3948 | 23.3675 | 23.345 | 23.3222 | 23.2993 | 23.2755 | 23.2512 | 23.224 | 23.192
|  | BILBOHALL | CT |  |  |  | 0.031579 | 13.157 | 24.416 | 24.3964 | 24.3739 | 24.35 | 24.3238 | 24.2806 | 24.2318 | 24.183 | 24.1346 | 24.0857 | 23.8224 | 23.4999 | 23.1053 | 12.8515 | 22.9105 | 22.8908 | 22.8684 | 22.8444 | 22.8183 | 22.791 | 22.7685 | 22.7457 | 22.7228 | 22.699 | 22.5584 | 22.3601 | 22.0868 | 12.828 | 23.487 | 23.4673 | 23.4449 | 23.4209 | 23.3948 | 23.3675 | 23.345 | 23.3222 | 23.2993 | 23.2755 | 23.2512 | 23.224 | 23.1954
|  | BILBOHALL | LW |  |  |  | 0.031579 | 13.1773 | 24.4269 | 24.4107 | 24.3898 | 24.3586 | 24.2951 | 24.232 | 24.1709 | 24.1102 | 24.0498 | 23.9895 | 23.6659 | 23.2645 | 22.7001 | 12.8717 | 22.9214 | 22.9052 | 22.8842 | 22.8602 | 22.8336 | 22.8059 | 22.782 | 22.7579 | 22.7335 | 22.7086 | 22.5583 | 22.3335 | 21.7971 | 12.8482 | 23.4979 | 23.4817 | 23.4607 | 23.4367 | 23.4101 | 23.3824 | 23.3585 | 23.3344 | 23.31 | 23.2851 | 23.2604 | 23.2307 | 23.192
|  | BILBOHALL | ST |  |  |  | 0.031579 | 13.1815 | 24.4554 | 24.4512 | 24.4442 | 24.4354 | 24.4256 | 24.415 | 24.409 | 24.4029 | 24.397 | 24.3875 | 24.2808 | 24.1342 | 24.0134 | 12.8759 | 22.9499 | 22.9457 | 22.9387 | 22.9298 | 22.92 | 22.9095 | 22.9035 | 22.8974 | 22.8914 | 22.8856 | 22.8575 | 22.7858 | 22.7369 | 12.8524 | 23.5264 | 23.5222 | 23.5152 | 23.5063 | 23.4965 | 23.486 | 23.48 | 23.4739 | 23.4679 | 23.4621 | 23.434 | 23.3623 | 23.3134
|  | BILBOHALL | FS |  |  |  | 0.031579 | 13.184 | 24.459 | 24.4564 | 24.4537 | 24.4517 | 24.4497 | 24.4476 | 24.4445 | 24.4413 | 24.4379 | 24.4343 | 24.4012 | 24.2998 | 24.1752 | 12.8785 | 22.9535 | 22.9508 | 22.9481 | 22.9462 | 22.9442 | 22.9421 | 22.939 | 22.9358 | 22.9323 | 22.9288 | 22.912 | 22.8733 | 22.8079 | 12.855 | 23.53 | 23.5273 | 23.5246 | 23.5227 | 23.5206 | 23.5186 | 23.5155 | 23.5123 | 23.5088 | 23.5053 | 23.4885 | 23.4497 | 23.3844
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.078379 | 0.078262 | 0.078211 | 0.078139 | 0.078057 | 0.077968 | 0.077875 | 0.077801 | 0.077727 | 0.077652 | 0.077578 | 0.077125 | 0.076419 | 0.07508 | 0.064444 | 0.064328 | 0.064276 | 0.064204 | 0.064123 | 0.064034 | 0.06394 | 0.063867 | 0.063793 | 0.063718 | 0.063637 | 0.063146 | 0.062404 | 0.061028 | 0.067907 | 0.067791 | 0.067739 | 0.067667 | 0.067586 | 0.067497 | 0.067403 | 0.06733 | 0.067256 | 0.067181 | 0.067107 | 0.067034 | 0.066944 | 0.066851
|  | BLACKMOUNT | CT |  |  |  | 0 | 0.078379 | 0.078339 | 0.078306 | 0.07826 | 0.078205 | 0.07814 | 0.078071 | 0.078026 | 0.077979 | 0.077933 | 0.077885 | 0.07758 | 0.077099 | 0.076361 | 0.064444 | 0.064405 | 0.064371 | 0.064326 | 0.064271 | 0.064206 | 0.064137 | 0.064092 | 0.064045 | 0.063998 | 0.063951 | 0.063636 | 0.063129 | 0.062366 | 0.067907 | 0.067868 | 0.067834 | 0.067789 | 0.067734 | 0.067669 | 0.0676 | 0.067555 | 0.067508 | 0.067461 | 0.067414 | 0.067365 | 0.067304 | 0.067242
|  | BLACKMOUNT | LW |  |  |  | 0 | 0.078379 | 0.078262 | 0.078211 | 0.078139 | 0.078057 | 0.077968 | 0.077875 | 0.077801 | 0.077727 | 0.077652 | 0.077578 | 0.077125 | 0.076419 | 0.07508 | 0.064444 | 0.064328 | 0.064276 | 0.064204 | 0.064123 | 0.064034 | 0.06394 | 0.063867 | 0.063793 | 0.063718 | 0.063637 | 0.063146 | 0.062404 | 0.061028 | 0.067907 | 0.067791 | 0.067739 | 0.067667 | 0.067586 | 0.067497 | 0.067403 | 0.06733 | 0.067256 | 0.067181 | 0.067107 | 0.067034 | 0.066944 | 0.066851
|  | BLACKMOUNT | ST |  |  |  | 0 | 0.078379 | 0.078364 | 0.078357 | 0.078338 | 0.078315 | 0.078288 | 0.078258 | 0.078247 | 0.078236 | 0.078225 | 0.078215 | 0.078168 | 0.077939 | 0.077822 | 0.064444 | 0.06443 | 0.064423 | 0.064404 | 0.064381 | 0.064354 | 0.064324 | 0.064313 | 0.064302 | 0.064291 | 0.06428 | 0.064234 | 0.064005 | 0.063883 | 0.067907 | 0.067893 | 0.067886 | 0.067867 | 0.067844 | 0.067817 | 0.067787 | 0.067776 | 0.067765 | 0.067754 | 0.067743 | 0.067697 | 0.067468 | 0.067351
|  | BLACKMOUNT | FS |  |  |  | 0 | 0.078379 | 0.078366 | 0.078365 | 0.078364 | 0.078363 | 0.078362 | 0.078361 | 0.078355 | 0.078349 | 0.078342 | 0.078334 | 0.078315 | 0.078212 | 0.077987 | 0.064444 | 0.064431 | 0.064431 | 0.06443 | 0.064429 | 0.064428 | 0.064426 | 0.064421 | 0.064414 | 0.064408 | 0.0644 | 0.06438 | 0.064277 | 0.064053 | 0.067907 | 0.067894 | 0.067894 | 0.067893 | 0.067892 | 0.067891 | 0.067889 | 0.067884 | 0.067877 | 0.067871 | 0.067863 | 0.067843 | 0.06774 | 0.067516
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 0 | 6.748 | 6.7198 | 6.7073 | 6.6899 | 6.67 | 6.6485 | 6.6258 | 6.5836 | 6.5253 | 6.4675 | 6.4109 | 6.1123 | 5.7513 | 5.2412 | 6.5501 | 6.5219 | 6.5094 | 6.4429 | 6.3736 | 6.3053 | 6.2379 | 6.1723 | 6.1073 | 6.0429 | 5.9798 | 5.6499 | 5.2572 | 4.7162 | 6.5762 | 6.548 | 6.5354 | 6.518 | 6.4982 | 6.4766 | 6.4539 | 6.4362 | 6.4182 | 6.3999 | 6.3821 | 6.3644 | 6.307 | 6.2431
|  | BLACKSTAND | CT |  |  |  | 0 | 6.748 | 6.7385 | 6.7305 | 6.7195 | 6.7061 | 6.6906 | 6.6738 | 6.663 | 6.6517 | 6.638 | 6.5992 | 6.3942 | 6.1444 | 5.8373 | 6.5501 | 6.5406 | 6.5325 | 6.5081 | 6.46 | 6.4116 | 6.3635 | 6.3188 | 6.2743 | 6.2303 | 6.187 | 5.9602 | 5.688 | 5.3595 | 6.5762 | 6.5667 | 6.5586 | 6.5477 | 6.5343 | 6.5187 | 6.502 | 6.4911 | 6.4799 | 6.4686 | 6.4572 | 6.4454 | 6.4308 | 6.4156
|  | BLACKSTAND | LW |  |  |  | 0 | 6.748 | 6.7198 | 6.7073 | 6.6899 | 6.67 | 6.6485 | 6.6258 | 6.5836 | 6.5253 | 6.4675 | 6.4109 | 6.1123 | 5.7513 | 5.2412 | 6.5501 | 6.5219 | 6.5094 | 6.4429 | 6.3736 | 6.3053 | 6.2379 | 6.1723 | 6.1073 | 6.0429 | 5.9798 | 5.6499 | 5.2572 | 4.7162 | 6.5762 | 6.548 | 6.5354 | 6.518 | 6.4982 | 6.4766 | 6.4539 | 6.4362 | 6.4182 | 6.3999 | 6.3821 | 6.3644 | 6.307 | 6.2431
|  | BLACKSTAND | ST |  |  |  | 0 | 6.748 | 6.7445 | 6.7428 | 6.7383 | 6.7328 | 6.7263 | 6.7191 | 6.7164 | 6.7137 | 6.7111 | 6.7086 | 6.6973 | 6.5735 | 6.4686 | 6.5501 | 6.5466 | 6.5449 | 6.5404 | 6.5348 | 6.5284 | 6.5142 | 6.4885 | 6.4633 | 6.4388 | 6.4151 | 6.3039 | 6.1548 | 6.0372 | 6.5762 | 6.5727 | 6.571 | 6.5664 | 6.5609 | 6.5544 | 6.5472 | 6.5445 | 6.5418 | 6.5392 | 6.5367 | 6.5255 | 6.4703 | 6.442
|  | BLACKSTAND | FS |  |  |  | 0 | 6.748 | 6.7448 | 6.7447 | 6.7445 | 6.7443 | 6.7439 | 6.7436 | 6.7422 | 6.7406 | 6.7389 | 6.7371 | 6.7321 | 6.7066 | 6.6064 | 6.5501 | 6.5469 | 6.5467 | 6.5466 | 6.5463 | 6.546 | 6.5456 | 6.5442 | 6.5427 | 6.5357 | 6.5163 | 6.4257 | 6.3211 | 6.1917 | 6.5762 | 6.573 | 6.5728 | 6.5726 | 6.5724 | 6.572 | 6.5717 | 6.5703 | 6.5688 | 6.567 | 6.5652 | 6.5603 | 6.5348 | 6.4794
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 0.89368 | 25.1606 | 25.0937 | 25.0499 | 24.9901 | 24.923 | 24.8493 | 24.7711 | 24.7081 | 24.6434 | 24.5777 | 24.5122 | 23.8509 | 22.5414 | 20.7178 | 23.7995 | 23.7326 | 23.6888 | 23.629 | 23.4189 | 23.1886 | 22.9509 | 22.7174 | 22.4846 | 22.2532 | 22.0244 | 20.8207 | 19.3792 | 17.4243 | 24.2373 | 24.1704 | 24.1266 | 24.0668 | 23.9356 | 23.7061 | 23.4777 | 23.2548 | 23.0325 | 22.8114 | 22.5928 | 22.3769 | 22.1455 | 21.9128
|  | BLAIRGOWRIE | CT |  |  |  | 0.89368 | 25.1606 | 25.1168 | 25.0775 | 25.0294 | 24.9744 | 24.9124 | 24.8468 | 24.7984 | 24.7487 | 24.698 | 24.6469 | 24.3289 | 23.7103 | 22.539 | 23.7995 | 23.7557 | 23.7165 | 23.6683 | 23.6133 | 23.4639 | 23.2924 | 23.1315 | 22.9643 | 22.7975 | 22.632 | 21.7527 | 20.7028 | 19.441 | 24.2373 | 24.1935 | 24.1542 | 24.1061 | 24.0511 | 23.9803 | 23.8094 | 23.649 | 23.4889 | 23.3293 | 23.1709 | 23.0126 | 22.8431 | 22.6725
|  | BLAIRGOWRIE | LW |  |  |  | 0.89368 | 25.1851 | 25.0937 | 25.0499 | 24.9901 | 24.923 | 24.8493 | 24.7711 | 24.7081 | 24.6434 | 24.5777 | 24.5122 | 23.8509 | 22.5414 | 20.7178 | 23.824 | 23.7326 | 23.6888 | 23.629 | 23.4189 | 23.1886 | 22.9509 | 22.7174 | 22.4846 | 22.2532 | 22.0244 | 20.8207 | 19.3792 | 17.4243 | 24.2617 | 24.1704 | 24.1266 | 24.0668 | 23.9356 | 23.7061 | 23.4777 | 23.2548 | 23.0325 | 22.8114 | 22.5928 | 22.3769 | 22.1455 | 21.9128
|  | BLAIRGOWRIE | ST |  |  |  | 0.89368 | 25.1901 | 25.1755 | 25.1667 | 25.1489 | 25.127 | 25.1021 | 25.0749 | 25.062 | 25.0491 | 25.0374 | 25.0261 | 24.9705 | 24.7686 | 24.6503 | 23.829 | 23.8144 | 23.8056 | 23.7878 | 23.7659 | 23.741 | 23.7138 | 23.7009 | 23.688 | 23.6078 | 23.524 | 23.1151 | 22.5645 | 22.1078 | 24.2668 | 24.2522 | 24.2434 | 24.2256 | 24.2037 | 24.1788 | 24.1516 | 24.1387 | 24.1258 | 24.1141 | 24.0407 | 23.6441 | 23.1152 | 22.6795
|  | BLAIRGOWRIE | FS |  |  |  | 0.89368 | 25.1926 | 25.1803 | 25.1773 | 25.1742 | 25.1708 | 25.1671 | 25.1634 | 25.1563 | 25.1486 | 25.1404 | 25.1317 | 25.1009 | 25.0027 | 24.8031 | 23.8315 | 23.8192 | 23.8162 | 23.8131 | 23.8097 | 23.806 | 23.8023 | 23.7952 | 23.7875 | 23.7793 | 23.7706 | 23.545 | 23.1669 | 22.6932 | 24.2693 | 24.2569 | 24.2539 | 24.2508 | 24.2475 | 24.2438 | 24.2401 | 24.233 | 24.2253 | 24.2171 | 24.2084 | 24.062 | 23.6947 | 23.238
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0 | 0.43594 | 0.43223 | 0.4293 | 0.42497 | 0.42055 | 0.41618 | 0.41186 | 0.40774 | 0.40365 | 0.39961 | 0.39564 | 0.37494 | 0.35047 | 0.3168 | 0.26756 | 0.26354 | 0.26026 | 0.25539 | 0.25046 | 0.24559 | 0.2408 | 0.23618 | 0.23161 | 0.22708 | 0.22265 | 0.19967 | 0.17292 | 0.13705 | 0.26078 | 0.25679 | 0.25355 | 0.24873 | 0.24385 | 0.23904 | 0.23429 | 0.22973 | 0.22521 | 0.22073 | 0.21634 | 0.21203 | 0.20748 | 0.2029
|  | BLAIRLINNANS | CT |  |  |  | 0 | 0.43623 | 0.43479 | 0.43256 | 0.42939 | 0.42612 | 0.42282 | 0.41952 | 0.41652 | 0.41353 | 0.41057 | 0.40765 | 0.3923 | 0.37444 | 0.35318 | 0.2679 | 0.26632 | 0.26381 | 0.26023 | 0.25655 | 0.25286 | 0.2492 | 0.24581 | 0.24244 | 0.23911 | 0.23582 | 0.21868 | 0.19905 | 0.17608 | 0.26111 | 0.25955 | 0.25707 | 0.25353 | 0.24989 | 0.24624 | 0.24262 | 0.23927 | 0.23594 | 0.23265 | 0.2294 | 0.22616 | 0.22277 | 0.21935
|  | BLAIRLINNANS | LW |  |  |  | 0 | 0.43594 | 0.43223 | 0.4293 | 0.42497 | 0.42055 | 0.41618 | 0.41186 | 0.40774 | 0.40365 | 0.39961 | 0.39564 | 0.37494 | 0.35047 | 0.3168 | 0.26756 | 0.26354 | 0.26026 | 0.25539 | 0.25046 | 0.24559 | 0.2408 | 0.23618 | 0.23161 | 0.22708 | 0.22265 | 0.19967 | 0.17292 | 0.13705 | 0.26078 | 0.25679 | 0.25355 | 0.24873 | 0.24385 | 0.23904 | 0.23429 | 0.22973 | 0.22521 | 0.22073 | 0.21634 | 0.21203 | 0.20748 | 0.2029
|  | BLAIRLINNANS | ST |  |  |  | 0 | 0.43755 | 0.43727 | 0.43711 | 0.43495 | 0.43275 | 0.43056 | 0.42837 | 0.42638 | 0.42442 | 0.42249 | 0.42061 | 0.41167 | 0.4004 | 0.39109 | 0.26944 | 0.26915 | 0.26898 | 0.26651 | 0.264 | 0.26152 | 0.25904 | 0.25674 | 0.25448 | 0.25226 | 0.2501 | 0.23979 | 0.22721 | 0.21664 | 0.26263 | 0.26234 | 0.26217 | 0.25974 | 0.25726 | 0.2548 | 0.25235 | 0.25009 | 0.24786 | 0.24567 | 0.24354 | 0.23337 | 0.22092 | 0.21049
|  | BLAIRLINNANS | FS |  |  |  | 0 | 0.43768 | 0.43744 | 0.43738 | 0.43727 | 0.43693 | 0.43622 | 0.43552 | 0.43464 | 0.43375 | 0.43286 | 0.43195 | 0.42783 | 0.42285 | 0.41638 | 0.26959 | 0.26934 | 0.26928 | 0.26915 | 0.26876 | 0.26793 | 0.26711 | 0.2661 | 0.26508 | 0.26405 | 0.26302 | 0.25826 | 0.25271 | 0.24572 | 0.26278 | 0.26254 | 0.26247 | 0.26234 | 0.26196 | 0.26114 | 0.26033 | 0.25934 | 0.25833 | 0.25732 | 0.2563 | 0.2516 | 0.24611 | 0.23917
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0.024211 | 8.7464 | 8.7263 | 8.7166 | 8.7031 | 8.6878 | 8.6462 | 8.5959 | 8.5474 | 8.4993 | 8.4486 | 8.398 | 8.1328 | 7.8195 | 7.3789 | 8.6565 | 8.6364 | 8.6267 | 8.6132 | 8.5917 | 8.5363 | 8.4813 | 8.428 | 8.375 | 8.3224 | 8.2706 | 7.959 | 7.5955 | 7.1177 | 8.659 | 8.6389 | 8.6292 | 8.6158 | 8.6005 | 8.583 | 8.5646 | 8.55 | 8.5353 | 8.5204 | 8.4936 | 8.4343 | 8.3718 | 8.3089
|  | BOAT OF GARTEN | CT |  |  |  | 0.024211 | 8.7464 | 8.7382 | 8.7311 | 8.7218 | 8.7106 | 8.6977 | 8.6822 | 8.649 | 8.6158 | 8.583 | 8.5504 | 8.3697 | 8.1484 | 7.8809 | 8.6565 | 8.6482 | 8.6412 | 8.6319 | 8.6206 | 8.6077 | 8.5756 | 8.5389 | 8.5023 | 8.466 | 8.4301 | 8.2401 | 7.9834 | 7.6816 | 8.659 | 8.6508 | 8.6437 | 8.6344 | 8.6232 | 8.6103 | 8.5965 | 8.5873 | 8.5777 | 8.5681 | 8.5585 | 8.5486 | 8.5364 | 8.5238
|  | BOAT OF GARTEN | LW |  |  |  | 0.024211 | 8.7481 | 8.7263 | 8.7166 | 8.7031 | 8.6878 | 8.6462 | 8.5959 | 8.5474 | 8.4993 | 8.4486 | 8.398 | 8.1328 | 7.8195 | 7.3789 | 8.6581 | 8.6364 | 8.6267 | 8.6132 | 8.5917 | 8.5363 | 8.4813 | 8.428 | 8.375 | 8.3224 | 8.2706 | 7.959 | 7.5955 | 7.1177 | 8.6607 | 8.6389 | 8.6292 | 8.6158 | 8.6005 | 8.583 | 8.5646 | 8.55 | 8.5353 | 8.5204 | 8.4936 | 8.4343 | 8.3718 | 8.3089
|  | BOAT OF GARTEN | ST |  |  |  | 0.024211 | 8.7489 | 8.7462 | 8.7449 | 8.7414 | 8.7371 | 8.7321 | 8.7265 | 8.7244 | 8.7223 | 8.7203 | 8.7184 | 8.6448 | 8.5347 | 8.441 | 8.659 | 8.6563 | 8.6549 | 8.6514 | 8.6472 | 8.6422 | 8.6366 | 8.6345 | 8.6324 | 8.6304 | 8.6215 | 8.529 | 8.4093 | 8.3134 | 8.6615 | 8.6588 | 8.6575 | 8.654 | 8.6497 | 8.6447 | 8.6391 | 8.637 | 8.6349 | 8.6329 | 8.631 | 8.6223 | 8.5796 | 8.5342
|  | BOAT OF GARTEN | FS |  |  |  | 0.024211 | 8.7489 | 8.7464 | 8.7463 | 8.7462 | 8.746 | 8.7457 | 8.7454 | 8.7444 | 8.7432 | 8.7418 | 8.7404 | 8.7366 | 8.6626 | 8.5673 | 8.659 | 8.6565 | 8.6564 | 8.6562 | 8.656 | 8.6558 | 8.6555 | 8.6544 | 8.6532 | 8.6519 | 8.6505 | 8.6313 | 8.5483 | 8.4454 | 8.6615 | 8.6591 | 8.6589 | 8.6588 | 8.6586 | 8.6583 | 8.6581 | 8.657 | 8.6558 | 8.6545 | 8.653 | 8.6492 | 8.6295 | 8.5866
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 0.32 | 9.8117 | 9.8021 | 9.794 | 9.7613 | 9.7069 | 9.6534 | 9.6018 | 9.5498 | 9.4989 | 9.4489 | 9.401 | 9.155 | 8.879 | 8.5261 | 9.4502 | 9.4047 | 9.3627 | 9.3005 | 9.2387 | 9.1783 | 9.1201 | 9.0612 | 9.0035 | 8.947 | 8.8928 | 8.617 | 8.312 | 7.9306 | 9.3238 | 9.2855 | 9.2515 | 9.2014 | 9.1515 | 9.1022 | 9.0545 | 9.0068 | 8.9564 | 8.9033 | 8.8525 | 8.8021 | 8.7495 | 8.6975
|  | BODDAM | CT |  |  |  | 0.32 | 9.8117 | 9.8021 | 9.794 | 9.7846 | 9.7602 | 9.7189 | 9.6799 | 9.6414 | 9.603 | 9.5655 | 9.529 | 9.34 | 9.1305 | 8.8885 | 9.4533 | 9.4237 | 9.392 | 9.3475 | 9.3013 | 9.255 | 9.2116 | 9.1683 | 9.1251 | 9.0831 | 9.0422 | 8.8318 | 8.602 | 8.3404 | 9.3245 | 9.2995 | 9.2732 | 9.2369 | 9.199 | 9.1608 | 9.1246 | 9.089 | 9.0534 | 9.0187 | 8.9849 | 8.951 | 8.9119 | 8.8725
|  | BODDAM | LW |  |  |  | 0.32 | 9.8193 | 9.8044 | 9.7969 | 9.7613 | 9.7069 | 9.6534 | 9.6018 | 9.5498 | 9.4989 | 9.4489 | 9.401 | 9.155 | 8.879 | 8.5261 | 9.4502 | 9.4047 | 9.3627 | 9.3005 | 9.2387 | 9.1783 | 9.1201 | 9.0612 | 9.0035 | 8.947 | 8.8928 | 8.617 | 8.312 | 7.9306 | 9.3238 | 9.2855 | 9.2515 | 9.2014 | 9.1515 | 9.1022 | 9.0545 | 9.0068 | 8.9564 | 8.9033 | 8.8525 | 8.8021 | 8.7495 | 8.6975
|  | BODDAM | ST |  |  |  | 0.32 | 9.821 | 9.8184 | 9.8167 | 9.8137 | 9.8093 | 9.8044 | 9.7992 | 9.7971 | 9.7766 | 9.756 | 9.7357 | 9.6383 | 9.5271 | 9.4307 | 9.4842 | 9.4775 | 9.4699 | 9.4453 | 9.4195 | 9.393 | 9.3673 | 9.3421 | 9.3171 | 9.2933 | 9.2699 | 9.158 | 9.0339 | 8.9249 | 9.3503 | 9.3445 | 9.3383 | 9.3187 | 9.2979 | 9.2764 | 9.2555 | 9.2357 | 9.216 | 9.1973 | 9.1788 | 9.0903 | 8.9856 | 8.8833
|  | BODDAM | FS |  |  |  | 0.32 | 9.821 | 9.8185 | 9.8176 | 9.8167 | 9.8157 | 9.8147 | 9.8137 | 9.8121 | 9.8105 | 9.8088 | 9.807 | 9.7328 | 9.6518 | 9.5582 | 9.4867 | 9.4803 | 9.4753 | 9.4688 | 9.4595 | 9.4439 | 9.4283 | 9.4094 | 9.3905 | 9.3715 | 9.3524 | 9.2648 | 9.1731 | 9.0691 | 9.3522 | 9.3467 | 9.3426 | 9.3375 | 9.3301 | 9.3179 | 9.3057 | 9.2909 | 9.2759 | 9.2609 | 9.2459 | 9.1772 | 9.1028 | 9.0154
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0.018947 | 2.0426 | 2.0296 | 2.0219 | 2.0115 | 1.9997 | 1.987 | 1.9737 | 1.9631 | 1.9523 | 1.9414 | 1.9307 | 1.8655 | 1.7634 | 1.5734 | 1.7355 | 1.7225 | 1.7148 | 1.7044 | 1.6927 | 1.68 | 1.6666 | 1.656 | 1.6453 | 1.6343 | 1.6236 | 1.3736 | 1.0548 | 0.65015 | 1.8075 | 1.7945 | 1.7868 | 1.7764 | 1.7647 | 1.752 | 1.7386 | 1.728 | 1.7172 | 1.7063 | 1.6956 | 1.685 | 1.6721 | 1.6587
|  | BONSKEID | CT |  |  |  | 0.018947 | 2.0426 | 2.0357 | 2.0296 | 2.0219 | 2.0129 | 2.0026 | 1.9926 | 1.985 | 1.9771 | 1.9692 | 1.9612 | 1.912 | 1.8388 | 1.7281 | 1.7355 | 1.7286 | 1.7225 | 1.7148 | 1.7058 | 1.6956 | 1.6856 | 1.6779 | 1.67 | 1.6621 | 1.6542 | 1.6049 | 1.3792 | 1.1176 | 1.8075 | 1.8006 | 1.7945 | 1.7868 | 1.7778 | 1.7676 | 1.7576 | 1.7499 | 1.742 | 1.7341 | 1.7261 | 1.718 | 1.7081 | 1.698
|  | BONSKEID | LW |  |  |  | 0.018947 | 2.0451 | 2.0296 | 2.0219 | 2.0115 | 1.9997 | 1.987 | 1.9737 | 1.9631 | 1.9523 | 1.9414 | 1.9307 | 1.8655 | 1.7634 | 1.5734 | 1.738 | 1.7225 | 1.7148 | 1.7044 | 1.6927 | 1.68 | 1.6666 | 1.656 | 1.6453 | 1.6343 | 1.6236 | 1.3736 | 1.0548 | 0.65015 | 1.81 | 1.7945 | 1.7868 | 1.7764 | 1.7647 | 1.752 | 1.7386 | 1.728 | 1.7172 | 1.7063 | 1.6956 | 1.685 | 1.6721 | 1.6587
|  | BONSKEID | ST |  |  |  | 0.018947 | 2.0451 | 2.0431 | 2.0422 | 2.0397 | 2.0366 | 2.033 | 2.029 | 2.0275 | 2.026 | 2.0246 | 2.0232 | 2.0169 | 1.986 | 1.9666 | 1.738 | 1.7361 | 1.7351 | 1.7326 | 1.7296 | 1.726 | 1.722 | 1.7205 | 1.719 | 1.7175 | 1.7161 | 1.7099 | 1.6789 | 1.6539 | 1.81 | 1.8081 | 1.8071 | 1.8046 | 1.8015 | 1.798 | 1.794 | 1.7925 | 1.791 | 1.7895 | 1.7881 | 1.7819 | 1.7509 | 1.7316
|  | BONSKEID | FS |  |  |  | 0.018947 | 2.0459 | 2.0441 | 2.044 | 2.0439 | 2.0438 | 2.0436 | 2.0434 | 2.0426 | 2.0418 | 2.0408 | 2.0398 | 2.037 | 2.0226 | 1.9913 | 1.7389 | 1.7371 | 1.737 | 1.7369 | 1.7367 | 1.7365 | 1.7363 | 1.7356 | 1.7347 | 1.7337 | 1.7327 | 1.7299 | 1.7156 | 1.6843 | 1.8109 | 1.809 | 1.809 | 1.8089 | 1.8087 | 1.8085 | 1.8083 | 1.8076 | 1.8067 | 1.8057 | 1.8047 | 1.8019 | 1.7876 | 1.7563
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | YES | 0 | 5.3609 | 5.2934 | 5.231 | 5.1418 | 5.0536 | 4.9677 | 4.8856 | 4.8029 | 4.7226 | 4.6439 | 4.5688 | 4.1944 | 3.7784 | 3.2429 | 4.6572 | 4.5976 | 4.5442 | 4.468 | 4.3922 | 4.3182 | 4.2472 | 4.1763 | 4.1073 | 4.0397 | 3.975 | 3.5702 | 3.0743 | 2.4609 | 5.1387 | 5.0583 | 4.981 | 4.8702 | 4.7613 | 4.6557 | 4.5554 | 4.4531 | 4.354 | 4.2571 | 4.1646 | 4.0756 | 3.9837 | 3.8914
|  | BOWMORE | CT |  |  |  | 0 | 5.379 | 5.3416 | 5.3012 | 5.2421 | 5.1808 | 5.1182 | 5.059 | 5.0019 | 4.9455 | 4.8915 | 4.8391 | 4.5738 | 4.2806 | 3.9393 | 4.6722 | 4.6399 | 4.6054 | 4.5549 | 4.5023 | 4.4483 | 4.397 | 4.3482 | 4.2999 | 4.2536 | 4.2086 | 3.9784 | 3.6851 | 3.2885 | 5.162 | 5.1161 | 5.0661 | 4.9926 | 4.917 | 4.84 | 4.7678 | 4.697 | 4.6272 | 4.5604 | 4.4958 | 4.4313 | 4.3658 | 4.301
|  | BOWMORE | LW |  |  |  | 0 | 5.3609 | 5.2934 | 5.231 | 5.1418 | 5.0536 | 4.9677 | 4.8856 | 4.8029 | 4.7226 | 4.6439 | 4.5688 | 4.1944 | 3.7784 | 3.2429 | 4.6572 | 4.5976 | 4.5442 | 4.468 | 4.3922 | 4.3182 | 4.2472 | 4.1763 | 4.1073 | 4.0397 | 3.975 | 3.5702 | 3.0743 | 2.4609 | 5.1387 | 5.0583 | 4.981 | 4.8702 | 4.7613 | 4.6557 | 4.5554 | 4.4531 | 4.354 | 4.2571 | 4.1646 | 4.0756 | 3.9837 | 3.8914
|  | BOWMORE | ST |  |  |  | 0 | 5.4102 | 5.4003 | 5.3898 | 5.3559 | 5.3206 | 5.2846 | 5.2491 | 5.2148 | 5.1809 | 5.1473 | 5.1149 | 4.9626 | 4.7895 | 4.6427 | 4.6981 | 4.6894 | 4.6805 | 4.6517 | 4.6217 | 4.5909 | 4.5605 | 4.5317 | 4.5032 | 4.475 | 4.4478 | 4.32 | 4.1686 | 4.0428 | 5.2021 | 5.1902 | 5.1771 | 5.1346 | 5.0906 | 5.0458 | 5.002 | 4.9586 | 4.9156 | 4.8732 | 4.8321 | 4.6393 | 4.4302 | 4.2486
|  | BOWMORE | FS |  |  |  | 0 | 5.414 | 5.4051 | 5.3987 | 5.3902 | 5.3762 | 5.3542 | 5.3329 | 5.3081 | 5.2824 | 5.2566 | 5.2314 | 5.1126 | 4.9891 | 4.8441 | 4.7012 | 4.6934 | 4.688 | 4.681 | 4.6694 | 4.651 | 4.6334 | 4.6126 | 4.591 | 4.5694 | 4.5483 | 4.4491 | 4.343 | 4.2147 | 5.2069 | 5.1962 | 5.188 | 5.1772 | 5.1593 | 5.1312 | 5.104 | 5.0724 | 5.0397 | 5.007 | 4.9752 | 4.8239 | 4.6716 | 4.4991
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0 | 1.4977 | 1.483 | 1.4761 | 1.4664 | 1.4555 | 1.4435 | 1.431 | 1.4211 | 1.4111 | 1.4009 | 1.3909 | 1.3255 | 1.2086 | 0.93062 | 1.39 | 1.3753 | 1.3684 | 1.3587 | 1.3478 | 1.3358 | 1.3131 | 1.2781 | 1.2434 | 1.209 | 1.1753 | 0.99368 | 0.77365 | 0.46665 | 1.3998 | 1.3851 | 1.3782 | 1.3685 | 1.3576 | 1.3456 | 1.333 | 1.3232 | 1.3131 | 1.3029 | 1.2918 | 1.2594 | 1.2236 | 1.1875
|  | BRAE | CT |  |  |  | 0 | 1.4977 | 1.4915 | 1.4861 | 1.479 | 1.4706 | 1.4608 | 1.4504 | 1.4434 | 1.4361 | 1.4288 | 1.4214 | 1.3745 | 1.3022 | 1.1932 | 1.39 | 1.3838 | 1.3783 | 1.3713 | 1.3628 | 1.3531 | 1.3427 | 1.3357 | 1.3251 | 1.3009 | 1.2769 | 1.1491 | 0.99479 | 0.80586 | 1.3998 | 1.3936 | 1.3881 | 1.3811 | 1.3726 | 1.3629 | 1.3525 | 1.3455 | 1.3382 | 1.3308 | 1.3235 | 1.3158 | 1.3065 | 1.2968
|  | BRAE | LW |  |  |  | 0 | 1.4986 | 1.483 | 1.4761 | 1.4664 | 1.4555 | 1.4435 | 1.431 | 1.4211 | 1.4111 | 1.4009 | 1.3909 | 1.3255 | 1.2086 | 0.93062 | 1.3909 | 1.3753 | 1.3684 | 1.3587 | 1.3478 | 1.3358 | 1.3131 | 1.2781 | 1.2434 | 1.209 | 1.1753 | 0.99368 | 0.77365 | 0.46665 | 1.4006 | 1.3851 | 1.3782 | 1.3685 | 1.3576 | 1.3456 | 1.333 | 1.3232 | 1.3131 | 1.3029 | 1.2918 | 1.2594 | 1.2236 | 1.1875
|  | BRAE | ST |  |  |  | 0 | 1.4994 | 1.4974 | 1.4964 | 1.4938 | 1.4906 | 1.4868 | 1.4826 | 1.4811 | 1.4795 | 1.478 | 1.4765 | 1.47 | 1.4376 | 1.4209 | 1.3917 | 1.3897 | 1.3887 | 1.386 | 1.3828 | 1.3791 | 1.3749 | 1.3734 | 1.3718 | 1.3703 | 1.3688 | 1.3507 | 1.2708 | 1.2087 | 1.4015 | 1.3994 | 1.3985 | 1.3958 | 1.3926 | 1.3889 | 1.3847 | 1.3831 | 1.3816 | 1.3801 | 1.3786 | 1.3721 | 1.3396 | 1.3229
|  | BRAE | FS |  |  |  | 0 | 1.4994 | 1.4975 | 1.4975 | 1.4974 | 1.4972 | 1.497 | 1.4968 | 1.496 | 1.4951 | 1.4941 | 1.493 | 1.4901 | 1.4751 | 1.4424 | 1.3917 | 1.3898 | 1.3897 | 1.3896 | 1.3895 | 1.3893 | 1.3891 | 1.3883 | 1.3874 | 1.3864 | 1.3853 | 1.3824 | 1.3638 | 1.2926 | 1.4015 | 1.3996 | 1.3995 | 1.3994 | 1.3993 | 1.3991 | 1.3989 | 1.3981 | 1.3972 | 1.3962 | 1.3951 | 1.3922 | 1.3772 | 1.3445
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 0 | 13.5785 | 13.5401 | 13.5052 | 13.4607 | 13.409 | 13.3528 | 13.293 | 13.2432 | 13.1325 | 12.8722 | 12.6334 | 11.4698 | 10.1996 | 8.5481 | 12.6874 | 12.649 | 12.6141 | 12.5696 | 12.3682 | 12.039 | 11.7371 | 11.4284 | 11.1241 | 10.8212 | 10.544 | 9.2083 | 7.7805 | 5.9782 | 13.1784 | 13.14 | 13.1051 | 12.7487 | 12.39 | 12.0483 | 11.7354 | 11.4149 | 11.1073 | 10.8109 | 10.5395 | 10.2857 | 10.0195 | 9.7554
|  | BRECHIN | CT |  |  |  | 0 | 13.5785 | 13.5402 | 13.5052 | 13.4646 | 13.4184 | 13.3668 | 13.3124 | 13.2704 | 13.2272 | 13.1829 | 13.1383 | 12.5936 | 11.6393 | 10.5205 | 12.6874 | 12.6491 | 12.6141 | 12.5734 | 12.5273 | 12.4757 | 12.3715 | 12.1502 | 11.9329 | 11.729 | 11.5357 | 10.5425 | 9.4771 | 8.2512 | 13.1784 | 13.1401 | 13.1051 | 13.0645 | 12.9005 | 12.6337 | 12.3978 | 12.1684 | 11.9431 | 11.7319 | 11.5319 | 11.3316 | 11.1264 | 10.9266
|  | BRECHIN | LW |  |  |  | 0 | 13.6079 | 13.5401 | 13.5063 | 13.4607 | 13.409 | 13.3528 | 13.293 | 13.2432 | 13.1325 | 12.8722 | 12.6334 | 11.4698 | 10.1996 | 8.5481 | 12.7168 | 12.649 | 12.6152 | 12.5696 | 12.3682 | 12.039 | 11.7371 | 11.4284 | 11.1241 | 10.8212 | 10.544 | 9.2083 | 7.7805 | 5.9782 | 13.2079 | 13.14 | 13.1062 | 12.7487 | 12.39 | 12.0483 | 11.7354 | 11.4149 | 11.1073 | 10.8109 | 10.5395 | 10.2857 | 10.0195 | 9.7554
|  | BRECHIN | ST |  |  |  | 0 | 13.613 | 13.6002 | 13.5919 | 13.5767 | 13.5582 | 13.5374 | 13.5157 | 13.5049 | 13.4941 | 13.4836 | 13.4733 | 13.4226 | 13.2543 | 13.1061 | 12.7219 | 12.7091 | 12.7008 | 12.6856 | 12.6671 | 12.6463 | 12.6246 | 12.6138 | 12.603 | 12.5925 | 12.5822 | 12.1849 | 11.6041 | 11.1009 | 13.2129 | 13.2001 | 13.1918 | 13.1766 | 13.1581 | 13.1374 | 13.1156 | 13.1048 | 13.0236 | 12.895 | 12.7711 | 12.1976 | 11.5981 | 11.0835
|  | BRECHIN | FS |  |  |  | 0 | 13.6172 | 13.607 | 13.6033 | 13.5994 | 13.5954 | 13.5911 | 13.5876 | 13.5815 | 13.5748 | 13.5678 | 13.5603 | 13.5312 | 13.4454 | 13.2766 | 12.7261 | 12.7159 | 12.7122 | 12.7083 | 12.7043 | 12.7 | 12.6965 | 12.6903 | 12.6837 | 12.6766 | 12.6692 | 12.6401 | 12.2495 | 11.7532 | 13.2171 | 13.2069 | 13.2032 | 13.1994 | 13.1953 | 13.191 | 13.1875 | 13.1814 | 13.1747 | 13.1677 | 13.1602 | 12.7063 | 12.2642 | 11.753
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | YES | 0.79895 | 18.9895 | 18.8152 | 18.6962 | 17.7559 | 16.7681 | 15.8458 | 15.043 | 14.2123 | 13.4354 | 12.7054 | 12.0766 | 9.3177 | 6.7492 | 3.7373 | 17.597 | 16.8444 | 15.8494 | 14.7064 | 13.6332 | 12.6323 | 11.7626 | 10.8474 | 9.9572 | 9.1216 | 8.4032 | 5.2576 | 2.3643 | -0.93858 | 17.5303 | 17.3689 | 16.9413 | 15.7631 | 14.6309 | 13.5759 | 12.66 | 11.7089 | 10.8204 | 9.9863 | 9.2693 | 8.6372 | 7.9962 | 7.3681
|  | BRIDGE OF DON | CT |  |  |  | 0.79895 | 19.0162 | 18.9383 | 18.8607 | 18.7662 | 18.6207 | 17.906 | 17.3214 | 16.7514 | 16.2007 | 15.7086 | 15.2635 | 13.1953 | 11.3593 | 9.3672 | 17.6115 | 17.5478 | 17.1115 | 16.3995 | 15.6481 | 14.8722 | 14.2391 | 13.6199 | 13.022 | 12.4882 | 12.0058 | 9.7091 | 7.6583 | 5.4653 | 17.5505 | 17.4801 | 17.4109 | 17.326 | 16.7543 | 15.9398 | 15.2732 | 14.6201 | 13.9896 | 13.427 | 12.9189 | 12.4108 | 11.9159 | 11.4538
|  | BRIDGE OF DON | LW |  |  |  | 0.79895 | 18.9895 | 18.8152 | 18.6962 | 17.7559 | 16.7681 | 15.8458 | 15.043 | 14.2123 | 13.4354 | 12.7054 | 12.0766 | 9.3177 | 6.7492 | 3.7373 | 17.597 | 16.8444 | 15.8494 | 14.7064 | 13.6332 | 12.6323 | 11.7626 | 10.8474 | 9.9572 | 9.1216 | 8.4032 | 5.2576 | 2.3643 | -0.93858 | 17.5303 | 17.3689 | 16.9413 | 15.7631 | 14.6309 | 13.5759 | 12.66 | 11.7089 | 10.8204 | 9.9863 | 9.2693 | 8.6372 | 7.9962 | 7.3681
|  | BRIDGE OF DON | ST |  |  |  | 0.79895 | 19.0475 | 19.0189 | 18.9949 | 18.9518 | 18.9032 | 18.8498 | 18.7962 | 18.7576 | 18.718 | 18.5864 | 18.2705 | 16.8572 | 15.6308 | 14.5998 | 17.6341 | 17.6106 | 17.5926 | 17.5585 | 17.47 | 17.0826 | 16.7295 | 16.3568 | 15.9721 | 15.6083 | 15.2637 | 13.7226 | 12.403 | 11.2869 | 17.5773 | 17.5514 | 17.5305 | 17.4921 | 17.4485 | 17.4003 | 17.3514 | 17.318 | 17.0552 | 16.7142 | 16.3498 | 14.7205 | 13.3367 | 12.1618
|  | BRIDGE OF DON | FS |  |  |  | 0.79895 | 19.055 | 19.0297 | 19.0157 | 18.9998 | 18.9806 | 18.9589 | 18.9379 | 18.9104 | 18.8806 | 18.8509 | 18.8211 | 17.9829 | 17.0351 | 16.0054 | 17.6394 | 17.6185 | 17.6091 | 17.5984 | 17.5855 | 17.5709 | 17.415 | 17.1303 | 16.8247 | 16.528 | 16.2385 | 14.9411 | 13.915 | 12.8116 | 17.5836 | 17.5606 | 17.549 | 17.5359 | 17.52 | 17.502 | 17.4846 | 17.4611 | 17.4356 | 17.41 | 17.3075 | 16.0031 | 14.923 | 13.7688
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0 | 1.2172 | 1.2087 | 1.2005 | 1.1916 | 1.182 | 1.1718 | 1.1612 | 1.1523 | 1.1424 | 1.1231 | 1.1005 | 0.98103 | 0.84046 | 0.65248 | 1.0548 | 1.0392 | 1.0235 | 1.0013 | 0.97517 | 0.94892 | 0.9221 | 0.896 | 0.87008 | 0.84434 | 0.81811 | 0.68135 | 0.52409 | 0.31992 | 1.1835 | 1.1689 | 1.1543 | 1.134 | 1.1124 | 1.0887 | 1.0643 | 1.0408 | 1.0174 | 0.99412 | 0.97034 | 0.94682 | 0.9222 | 0.89738
|  | BRIDGE OF DUN | CT |  |  |  | 0 | 1.2172 | 1.2087 | 1.2005 | 1.1916 | 1.182 | 1.1718 | 1.1612 | 1.1523 | 1.1424 | 1.1326 | 1.1176 | 1.018 | 0.8988 | 0.75864 | 1.0548 | 1.0392 | 1.0235 | 1.0013 | 0.97864 | 0.9559 | 0.93327 | 0.9118 | 0.88955 | 0.86747 | 0.84555 | 0.73442 | 0.60396 | 0.45282 | 1.1835 | 1.1689 | 1.1543 | 1.134 | 1.1132 | 1.0922 | 1.0713 | 1.0517 | 1.0312 | 1.0109 | 0.99067 | 0.9705 | 0.95032 | 0.93005
|  | BRIDGE OF DUN | LW |  |  |  | 0 | 1.2282 | 1.2186 | 1.2126 | 1.2053 | 1.1973 | 1.1887 | 1.1791 | 1.1676 | 1.1453 | 1.1231 | 1.1005 | 0.98103 | 0.84046 | 0.65248 | 1.0643 | 1.0454 | 1.0289 | 1.0017 | 0.97517 | 0.94892 | 0.9221 | 0.896 | 0.87008 | 0.84434 | 0.81811 | 0.68135 | 0.52409 | 0.31992 | 1.1932 | 1.1756 | 1.1606 | 1.1363 | 1.1124 | 1.0887 | 1.0643 | 1.0408 | 1.0174 | 0.99412 | 0.97034 | 0.94682 | 0.9222 | 0.89738
|  | BRIDGE OF DUN | ST |  |  |  | 0 | 1.2307 | 1.228 | 1.2259 | 1.2229 | 1.2197 | 1.2162 | 1.2125 | 1.2101 | 1.2077 | 1.2052 | 1.2029 | 1.1913 | 1.1536 | 1.1106 | 1.0796 | 1.0766 | 1.0733 | 1.0619 | 1.0504 | 1.039 | 1.0275 | 1.0169 | 1.0065 | 0.9962 | 0.98612 | 0.93792 | 0.8792 | 0.82926 | 1.2067 | 1.2037 | 1.2006 | 1.1904 | 1.1801 | 1.1698 | 1.1595 | 1.15 | 1.1407 | 1.1316 | 1.1226 | 1.0796 | 1.0259 | 0.98082
|  | BRIDGE OF DUN | FS |  |  |  | 0 | 1.2315 | 1.2298 | 1.2289 | 1.228 | 1.2271 | 1.2262 | 1.2252 | 1.224 | 1.2227 | 1.2214 | 1.2201 | 1.2128 | 1.2016 | 1.1807 | 1.081 | 1.079 | 1.0779 | 1.0756 | 1.0721 | 1.0657 | 1.0593 | 1.0521 | 1.0448 | 1.0375 | 1.0302 | 0.99377 | 0.95509 | 0.90957 | 1.208 | 1.2061 | 1.205 | 1.2028 | 1.1997 | 1.1941 | 1.1885 | 1.1821 | 1.1757 | 1.1693 | 1.1628 | 1.1306 | 1.0958 | 1.054
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.32316 | 15.8356 | 15.8117 | 15.7937 | 15.7696 | 15.7418 | 15.7117 | 15.6793 | 15.6531 | 15.6265 | 15.5996 | 15.5722 | 15.225 | 14.7474 | 14.0699 | 14.689 | 14.6634 | 14.637 | 14.5506 | 14.462 | 14.3746 | 14.2874 | 14.2033 | 14.12 | 14.0373 | 13.9552 | 13.5224 | 12.9984 | 12.2754 | 15.215 | 15.1911 | 15.173 | 15.149 | 15.0667 | 14.9801 | 14.8937 | 14.8103 | 14.7277 | 14.6458 | 14.5645 | 14.4844 | 14.3989 | 14.3118
|  | BRIDGE OF EARN | CT |  |  |  | 0.32316 | 15.8356 | 15.8163 | 15.7987 | 15.7776 | 15.7534 | 15.7265 | 15.6989 | 15.6778 | 15.6562 | 15.6345 | 15.6127 | 15.477 | 15.1383 | 14.6977 | 14.689 | 14.6686 | 14.6499 | 14.6011 | 14.5343 | 14.4671 | 14.4012 | 14.3395 | 14.278 | 14.2172 | 14.157 | 13.8337 | 13.4444 | 12.9723 | 15.215 | 15.1956 | 15.178 | 15.1569 | 15.1327 | 15.0716 | 15.0061 | 14.945 | 14.8841 | 14.8238 | 14.7641 | 14.7046 | 14.6404 | 14.5758
|  | BRIDGE OF EARN | LW |  |  |  | 0.32316 | 15.8491 | 15.8117 | 15.7937 | 15.7696 | 15.7418 | 15.7117 | 15.6793 | 15.6531 | 15.6265 | 15.5996 | 15.5722 | 15.225 | 14.7474 | 14.0699 | 14.7021 | 14.6634 | 14.637 | 14.5506 | 14.462 | 14.3746 | 14.2874 | 14.2033 | 14.12 | 14.0373 | 13.9552 | 13.5224 | 12.9984 | 12.2754 | 15.2284 | 15.1911 | 15.173 | 15.149 | 15.0667 | 14.9801 | 14.8937 | 14.8103 | 14.7277 | 14.6458 | 14.5645 | 14.4844 | 14.3989 | 14.3118
|  | BRIDGE OF EARN | ST |  |  |  | 0.32316 | 15.8508 | 15.8447 | 15.8409 | 15.8335 | 15.824 | 15.8133 | 15.8025 | 15.7975 | 15.7924 | 15.7874 | 15.7826 | 15.7582 | 15.6759 | 15.6269 | 14.7058 | 14.6995 | 14.6956 | 14.6869 | 14.6761 | 14.6642 | 14.6373 | 14.604 | 14.5714 | 14.5397 | 14.5088 | 14.3634 | 14.1692 | 14.0134 | 15.2301 | 15.224 | 15.2202 | 15.2128 | 15.2033 | 15.1926 | 15.1819 | 15.1768 | 15.1717 | 15.144 | 15.1135 | 14.9697 | 14.777 | 14.6226
|  | BRIDGE OF EARN | FS |  |  |  | 0.32316 | 15.8525 | 15.8475 | 15.8456 | 15.8437 | 15.8417 | 15.8396 | 15.8374 | 15.834 | 15.8303 | 15.8273 | 15.824 | 15.8101 | 15.7687 | 15.6885 | 14.7075 | 14.7025 | 14.7006 | 14.6985 | 14.6961 | 14.6931 | 14.6901 | 14.6856 | 14.6808 | 14.6591 | 14.6342 | 14.5145 | 14.3748 | 14.2065 | 15.2318 | 15.2268 | 15.225 | 15.223 | 15.221 | 15.2189 | 15.2168 | 15.2133 | 15.2096 | 15.2066 | 15.2033 | 15.1195 | 14.981 | 14.814
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.021053 | 1.2569 | 1.2554 | 1.2541 | 1.2526 | 1.2509 | 1.249 | 1.2471 | 1.2456 | 1.2441 | 1.2425 | 1.2401 | 1.2269 | 1.2109 | 1.1857 | 1.1394 | 1.138 | 1.1366 | 1.1351 | 1.1334 | 1.1316 | 1.1296 | 1.1279 | 1.1262 | 1.1244 | 1.122 | 1.1082 | 1.0892 | 1.0434 | 1.1686 | 1.1672 | 1.1658 | 1.1643 | 1.1626 | 1.1608 | 1.1589 | 1.1574 | 1.1558 | 1.1542 | 1.1518 | 1.1494 | 1.1468 | 1.1441
|  | BRIDGE OF GAUR | CT |  |  |  | 0.021053 | 1.2569 | 1.2554 | 1.2541 | 1.2526 | 1.2509 | 1.249 | 1.2471 | 1.2456 | 1.2441 | 1.2425 | 1.2401 | 1.2269 | 1.2109 | 1.1908 | 1.1394 | 1.138 | 1.1366 | 1.1351 | 1.1334 | 1.1316 | 1.1296 | 1.1279 | 1.1262 | 1.1245 | 1.122 | 1.1082 | 1.0916 | 1.069 | 1.1686 | 1.1672 | 1.1658 | 1.1643 | 1.1626 | 1.1608 | 1.1589 | 1.1574 | 1.1558 | 1.1542 | 1.1518 | 1.1494 | 1.1468 | 1.1441
|  | BRIDGE OF GAUR | LW |  |  |  | 0.021053 | 1.2594 | 1.2577 | 1.2569 | 1.255 | 1.253 | 1.2508 | 1.2486 | 1.2466 | 1.2447 | 1.2427 | 1.2408 | 1.2297 | 1.2147 | 1.1857 | 1.142 | 1.1402 | 1.1395 | 1.1376 | 1.1354 | 1.1331 | 1.1307 | 1.1286 | 1.1265 | 1.1244 | 1.1223 | 1.1104 | 1.0892 | 1.0434 | 1.1711 | 1.1694 | 1.1687 | 1.1668 | 1.1647 | 1.1625 | 1.1603 | 1.1584 | 1.1564 | 1.1545 | 1.1525 | 1.1506 | 1.1484 | 1.1461
|  | BRIDGE OF GAUR | ST |  |  |  | 0.021053 | 1.2594 | 1.2592 | 1.2591 | 1.2588 | 1.2584 | 1.258 | 1.2575 | 1.2574 | 1.2572 | 1.257 | 1.2569 | 1.2561 | 1.2525 | 1.2507 | 1.142 | 1.1417 | 1.1416 | 1.1413 | 1.141 | 1.1406 | 1.1401 | 1.1399 | 1.1397 | 1.1394 | 1.1392 | 1.138 | 1.1339 | 1.1316 | 1.1711 | 1.1709 | 1.1708 | 1.1705 | 1.1702 | 1.1697 | 1.1693 | 1.1691 | 1.1689 | 1.1688 | 1.1686 | 1.1679 | 1.1643 | 1.1624
|  | BRIDGE OF GAUR | FS |  |  |  | 0.021053 | 1.2602 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.2599 | 1.2598 | 1.2596 | 1.2595 | 1.2592 | 1.2575 | 1.2538 | 1.1428 | 1.1426 | 1.1426 | 1.1426 | 1.1425 | 1.1425 | 1.1425 | 1.1424 | 1.1423 | 1.1422 | 1.1421 | 1.1417 | 1.1399 | 1.136 | 1.172 | 1.1718 | 1.1718 | 1.1718 | 1.1717 | 1.1717 | 1.1717 | 1.1716 | 1.1715 | 1.1714 | 1.1713 | 1.1709 | 1.1692 | 1.1655
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 0.042105 | 5.7085 | 5.6945 | 5.6851 | 5.6717 | 5.6571 | 5.6416 | 5.6248 | 5.6105 | 5.5813 | 5.5438 | 5.5067 | 5.3039 | 5.045 | 4.7003 | 5.5116 | 5.4991 | 5.4913 | 5.4807 | 5.4687 | 5.4558 | 5.4375 | 5.3882 | 5.3392 | 5.2906 | 5.2427 | 4.9951 | 4.7081 | 4.3361 | 5.5259 | 5.5135 | 5.5056 | 5.495 | 5.4831 | 5.4701 | 5.4557 | 5.4192 | 5.3709 | 5.3229 | 5.2756 | 5.2289 | 5.18 | 5.1306
|  | BROADFORD | CT |  |  |  | 0.042105 | 5.7085 | 5.6997 | 5.6916 | 5.6811 | 5.6692 | 5.6561 | 5.6425 | 5.6321 | 5.6214 | 5.6108 | 5.6002 | 5.4635 | 5.2899 | 5.0708 | 5.5116 | 5.5037 | 5.4967 | 5.4881 | 5.4781 | 5.4668 | 5.455 | 5.4464 | 5.4376 | 5.4067 | 5.3726 | 5.1938 | 4.9885 | 4.7483 | 5.5259 | 5.5181 | 5.5111 | 5.5024 | 5.4924 | 5.4812 | 5.4693 | 5.4607 | 5.4519 | 5.436 | 5.4038 | 5.3703 | 5.3352 | 5.2999
|  | BROADFORD | LW |  |  |  | 0.042105 | 5.7124 | 5.6945 | 5.6851 | 5.6717 | 5.6571 | 5.6416 | 5.6248 | 5.6105 | 5.5813 | 5.5438 | 5.5067 | 5.3039 | 5.045 | 4.7003 | 5.5158 | 5.4991 | 5.4913 | 5.4807 | 5.4687 | 5.4558 | 5.4375 | 5.3882 | 5.3392 | 5.2906 | 5.2427 | 4.9951 | 4.7081 | 4.3361 | 5.5302 | 5.5135 | 5.5056 | 5.495 | 5.4831 | 5.4701 | 5.4557 | 5.4192 | 5.3709 | 5.3229 | 5.2756 | 5.2289 | 5.18 | 5.1306
|  | BROADFORD | ST |  |  |  | 0.042105 | 5.7149 | 5.712 | 5.7101 | 5.7055 | 5.7003 | 5.6947 | 5.6886 | 5.685 | 5.6814 | 5.6779 | 5.6744 | 5.6581 | 5.5915 | 5.5175 | 5.5166 | 5.5138 | 5.512 | 5.5087 | 5.5047 | 5.5003 | 5.4954 | 5.493 | 5.4907 | 5.4884 | 5.4861 | 5.4588 | 5.344 | 5.2469 | 5.531 | 5.5282 | 5.5264 | 5.523 | 5.5191 | 5.5146 | 5.5098 | 5.5074 | 5.505 | 5.5027 | 5.5005 | 5.4869 | 5.376 | 5.2802
|  | BROADFORD | FS |  |  |  | 0.042105 | 5.7158 | 5.7139 | 5.7129 | 5.7119 | 5.7104 | 5.7086 | 5.7067 | 5.705 | 5.7032 | 5.7013 | 5.6993 | 5.6885 | 5.6658 | 5.6199 | 5.5175 | 5.5157 | 5.5148 | 5.5138 | 5.5129 | 5.5118 | 5.5108 | 5.51 | 5.5092 | 5.5082 | 5.5072 | 5.5011 | 5.473 | 5.3814 | 5.5318 | 5.5301 | 5.5292 | 5.5282 | 5.5272 | 5.5262 | 5.5252 | 5.5244 | 5.5235 | 5.5226 | 5.5216 | 5.5155 | 5.4972 | 5.4129
| CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.24211 | 9.4201 | 9.3849 | 9.3692 | 9.3474 | 9.3227 | 9.2957 | 9.2673 | 9.245 | 9.2224 | 9.1994 | 9.1769 | 8.7215 | 8.1747 | 7.4351 | 9.0383 | 9.0031 | 8.9874 | 8.9656 | 8.9409 | 8.9139 | 8.8854 | 8.8631 | 8.8406 | 8.8176 | 8.7951 | 8.535 | 7.9289 | 7.1308 | 9.0791 | 9.0439 | 9.0282 | 9.0064 | 8.9817 | 8.9547 | 8.9263 | 8.904 | 8.8814 | 8.8584 | 8.8359 | 8.7825 | 8.6777 | 8.5729
|  | BRODICK | CT |  |  |  | 0.24211 | 9.4201 | 9.4081 | 9.3979 | 9.3841 | 9.3672 | 9.3475 | 9.3263 | 9.3126 | 9.2983 | 9.2839 | 9.2695 | 9.148 | 8.7705 | 8.3174 | 9.0383 | 9.0263 | 9.0161 | 9.0023 | 8.9854 | 8.9657 | 8.9445 | 8.9307 | 8.9165 | 8.9021 | 8.8876 | 8.7935 | 8.5949 | 8.1017 | 9.0791 | 9.0671 | 9.0569 | 9.0431 | 9.0262 | 9.0065 | 8.9853 | 8.9715 | 8.9573 | 8.9429 | 8.9285 | 8.9134 | 8.8947 | 8.8753
|  | BRODICK | LW |  |  |  | 0.24211 | 9.4201 | 9.3849 | 9.3692 | 9.3474 | 9.3227 | 9.2957 | 9.2673 | 9.245 | 9.2224 | 9.1994 | 9.1769 | 8.7215 | 8.1747 | 7.4351 | 9.0383 | 9.0031 | 8.9874 | 8.9656 | 8.9409 | 8.9139 | 8.8854 | 8.8631 | 8.8406 | 8.8176 | 8.7951 | 8.535 | 7.9289 | 7.1308 | 9.0791 | 9.0439 | 9.0282 | 9.0064 | 8.9817 | 8.9547 | 8.9263 | 8.904 | 8.8814 | 8.8584 | 8.8359 | 8.7825 | 8.6777 | 8.5729
|  | BRODICK | ST |  |  |  | 0.24211 | 9.4201 | 9.4156 | 9.4135 | 9.4077 | 9.4006 | 9.3923 | 9.3831 | 9.3797 | 9.3762 | 9.3729 | 9.3697 | 9.3552 | 9.284 | 9.2281 | 9.0383 | 9.0338 | 9.0317 | 9.0258 | 9.0188 | 9.0105 | 9.0013 | 8.9978 | 8.9944 | 8.991 | 8.9879 | 8.9734 | 8.9021 | 8.8655 | 9.0791 | 9.0746 | 9.0725 | 9.0667 | 9.0596 | 9.0513 | 9.0421 | 9.0387 | 9.0352 | 9.0318 | 9.0287 | 9.0142 | 8.943 | 8.9063
|  | BRODICK | FS |  |  |  | 0.24211 | 9.4201 | 9.416 | 9.4158 | 9.4156 | 9.4153 | 9.4148 | 9.4143 | 9.4126 | 9.4106 | 9.4084 | 9.406 | 9.3996 | 9.3666 | 9.2947 | 9.0383 | 9.0342 | 9.034 | 9.0338 | 9.0334 | 9.033 | 9.0325 | 9.0308 | 9.0288 | 9.0266 | 9.0242 | 9.0178 | 8.9848 | 8.9129 | 9.0791 | 9.075 | 9.0748 | 9.0746 | 9.0743 | 9.0738 | 9.0733 | 9.0716 | 9.0696 | 9.0674 | 9.065 | 9.0586 | 9.0256 | 8.9537
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 0 | 5.5267 | 5.51 | 5.4942 | 5.4764 | 5.4578 | 5.4375 | 5.4165 | 5.3988 | 5.3599 | 5.318 | 5.2767 | 5.0502 | 4.7658 | 4.3241 | 5.4552 | 5.4384 | 5.4226 | 5.4048 | 5.3862 | 5.338 | 5.2811 | 5.2251 | 5.1686 | 5.1126 | 5.0574 | 4.7628 | 4.4127 | 3.9453 | 5.3499 | 5.3331 | 5.3174 | 5.2996 | 5.2809 | 5.2472 | 5.1926 | 5.139 | 5.0849 | 5.0311 | 4.9782 | 4.9252 | 4.8691 | 4.8118
|  | BRORA | CT |  |  |  | 0 | 5.5267 | 5.51 | 5.4942 | 5.4764 | 5.4578 | 5.4375 | 5.4165 | 5.3988 | 5.3807 | 5.3609 | 5.3265 | 5.1381 | 4.9071 | 4.6226 | 5.4552 | 5.4384 | 5.4226 | 5.4048 | 5.3862 | 5.3652 | 5.3263 | 5.2812 | 5.2363 | 5.1917 | 5.1476 | 4.9113 | 4.6319 | 4.3002 | 5.3499 | 5.3331 | 5.3174 | 5.2996 | 5.2809 | 5.2607 | 5.2338 | 5.1905 | 5.1472 | 5.1043 | 5.0618 | 5.0193 | 4.9739 | 4.9273
|  | BRORA | LW |  |  |  | 0 | 5.5444 | 5.5215 | 5.5094 | 5.4931 | 5.4751 | 5.4551 | 5.4342 | 5.4021 | 5.3599 | 5.318 | 5.2767 | 5.0502 | 4.7658 | 4.3241 | 5.4728 | 5.4499 | 5.4378 | 5.4215 | 5.3955 | 5.338 | 5.2811 | 5.2251 | 5.1686 | 5.1126 | 5.0574 | 4.7628 | 4.4127 | 3.9453 | 5.3676 | 5.3446 | 5.3326 | 5.3163 | 5.2983 | 5.2472 | 5.1926 | 5.139 | 5.0849 | 5.0311 | 4.9782 | 4.9252 | 4.8691 | 4.8118
|  | BRORA | ST |  |  |  | 0 | 5.5478 | 5.5428 | 5.539 | 5.5333 | 5.5269 | 5.5197 | 5.5121 | 5.5077 | 5.5032 | 5.4988 | 5.4945 | 5.4739 | 5.3797 | 5.2974 | 5.4762 | 5.4712 | 5.4675 | 5.4617 | 5.4553 | 5.4482 | 5.4405 | 5.4361 | 5.4316 | 5.4267 | 5.4165 | 5.3152 | 5.1862 | 5.0759 | 5.3709 | 5.3659 | 5.3622 | 5.3565 | 5.35 | 5.3429 | 5.3353 | 5.3308 | 5.3264 | 5.322 | 5.3177 | 5.227 | 5.1028 | 4.9972
|  | BRORA | FS |  |  |  | 0 | 5.5495 | 5.5463 | 5.5446 | 5.5428 | 5.5409 | 5.539 | 5.537 | 5.5344 | 5.5316 | 5.5287 | 5.5257 | 5.5137 | 5.4871 | 5.4104 | 5.4779 | 5.4748 | 5.473 | 5.4712 | 5.4693 | 5.4674 | 5.4654 | 5.4628 | 5.46 | 5.4571 | 5.4541 | 5.4253 | 5.3343 | 5.2251 | 5.3726 | 5.3695 | 5.3677 | 5.3659 | 5.364 | 5.3621 | 5.3602 | 5.3575 | 5.3547 | 5.3518 | 5.3488 | 5.3327 | 5.2458 | 5.1403
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 0 | 11.8039 | 11.7332 | 11.7014 | 11.6572 | 11.6069 | 11.5517 | 11.4933 | 11.4474 | 11.4005 | 11.3528 | 11.3058 | 11.0079 | 10.5324 | 9.3616 | 11.506 | 11.4353 | 11.4035 | 11.3592 | 11.3072 | 11.2456 | 11.1811 | 11.1286 | 11.0753 | 11.0212 | 10.9679 | 10.37 | 9.2104 | 7.6056 | 11.54 | 11.4693 | 11.4376 | 11.3933 | 11.343 | 11.2878 | 11.2295 | 11.1835 | 11.1367 | 11.0889 | 11.0419 | 10.9952 | 10.9294 | 10.7867
|  | BROUGHTY FERRY | CT |  |  |  | 0 | 11.8039 | 11.7792 | 11.7581 | 11.7298 | 11.6954 | 11.655 | 11.6115 | 11.5828 | 11.5528 | 11.5225 | 11.4919 | 11.2902 | 10.963 | 10.4555 | 11.506 | 11.4812 | 11.4602 | 11.4319 | 11.3975 | 11.3571 | 11.31 | 11.2767 | 11.2422 | 11.2074 | 11.1724 | 10.9488 | 10.4339 | 9.4518 | 11.54 | 11.5153 | 11.4942 | 11.466 | 11.4315 | 11.3911 | 11.3477 | 11.3189 | 11.2889 | 11.2586 | 11.228 | 11.1961 | 11.1558 | 11.1142
|  | BROUGHTY FERRY | LW |  |  |  | 0 | 11.8047 | 11.7332 | 11.7014 | 11.6572 | 11.6069 | 11.5517 | 11.4933 | 11.4474 | 11.4005 | 11.3528 | 11.3058 | 11.0079 | 10.5324 | 9.3616 | 11.5068 | 11.4353 | 11.4035 | 11.3592 | 11.3072 | 11.2456 | 11.1811 | 11.1286 | 11.0753 | 11.0212 | 10.9679 | 10.37 | 9.2104 | 7.6056 | 11.5409 | 11.4693 | 11.4376 | 11.3933 | 11.343 | 11.2878 | 11.2295 | 11.1835 | 11.1367 | 11.0889 | 11.0419 | 10.9952 | 10.9294 | 10.7867
|  | BROUGHTY FERRY | ST |  |  |  | 0 | 11.8056 | 11.7962 | 11.7916 | 11.7795 | 11.7647 | 11.7474 | 11.7281 | 11.7209 | 11.7136 | 11.7067 | 11.7 | 11.6693 | 11.512 | 11.4302 | 11.5076 | 11.4982 | 11.4937 | 11.4816 | 11.4668 | 11.4495 | 11.4302 | 11.423 | 11.4157 | 11.4087 | 11.4005 | 11.3556 | 11.1847 | 11.0894 | 11.5417 | 11.5323 | 11.5278 | 11.5156 | 11.5009 | 11.4836 | 11.4643 | 11.457 | 11.4498 | 11.4428 | 11.4361 | 11.4054 | 11.2481 | 11.1663
|  | BROUGHTY FERRY | FS |  |  |  | 0 | 11.8056 | 11.7962 | 11.7958 | 11.7953 | 11.7945 | 11.7935 | 11.7925 | 11.7884 | 11.7839 | 11.7789 | 11.7735 | 11.759 | 11.6833 | 11.517 | 11.5076 | 11.4982 | 11.4978 | 11.4973 | 11.4966 | 11.4955 | 11.4945 | 11.4905 | 11.4859 | 11.4809 | 11.4755 | 11.4563 | 11.3692 | 11.1919 | 11.5417 | 11.5323 | 11.5319 | 11.5314 | 11.5306 | 11.5296 | 11.5286 | 11.5246 | 11.52 | 11.515 | 11.5096 | 11.4951 | 11.4195 | 11.2532
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 0 | 15.3519 | 15.3349 | 15.3249 | 15.3115 | 15.2963 | 15.2754 | 15.2239 | 15.1737 | 15.1233 | 15.0728 | 15.0194 | 14.7207 | 14.3409 | 13.8089 | 14.2987 | 14.2816 | 14.2717 | 14.2582 | 14.2307 | 14.1701 | 14.1087 | 14.0479 | 13.987 | 13.9261 | 13.8655 | 13.5391 | 13.1377 | 12.5834 | 14.6737 | 14.6566 | 14.6467 | 14.6332 | 14.618 | 14.6012 | 14.5825 | 14.5346 | 14.4704 | 14.4061 | 14.3422 | 14.2786 | 14.2094 | 14.1398
|  | BRUCHAG | CT |  |  |  | 0 | 15.3519 | 15.3424 | 15.334 | 15.3234 | 15.311 | 15.2967 | 15.2815 | 15.2635 | 15.2275 | 15.1914 | 15.1553 | 14.9495 | 14.6783 | 14.3339 | 14.2987 | 14.2892 | 14.2807 | 14.2701 | 14.2578 | 14.2435 | 14.2006 | 14.1573 | 14.1138 | 14.0704 | 14.0269 | 13.7902 | 13.4987 | 13.1388 | 14.6737 | 14.6642 | 14.6557 | 14.6451 | 14.6328 | 14.6185 | 14.6032 | 14.5923 | 14.5809 | 14.5586 | 14.5128 | 14.4668 | 14.4168 | 14.3665
|  | BRUCHAG | LW |  |  |  | 0 | 15.3561 | 15.3349 | 15.3249 | 15.3115 | 15.2963 | 15.2754 | 15.2239 | 15.1737 | 15.1233 | 15.0728 | 15.0194 | 14.7207 | 14.3409 | 13.8089 | 14.3029 | 14.2816 | 14.2717 | 14.2582 | 14.2307 | 14.1701 | 14.1087 | 14.0479 | 13.987 | 13.9261 | 13.8655 | 13.5391 | 13.1377 | 12.5834 | 14.6779 | 14.6566 | 14.6467 | 14.6332 | 14.618 | 14.6012 | 14.5825 | 14.5346 | 14.4704 | 14.4061 | 14.3422 | 14.2786 | 14.2094 | 14.1398
|  | BRUCHAG | ST |  |  |  | 0 | 15.357 | 15.3532 | 15.3509 | 15.3463 | 15.3408 | 15.3345 | 15.3276 | 15.3245 | 15.3214 | 15.3183 | 15.3154 | 15.2434 | 15.106 | 14.9843 | 14.3037 | 14.2999 | 14.2977 | 14.293 | 14.2875 | 14.2813 | 14.2744 | 14.2712 | 14.2681 | 14.2651 | 14.2411 | 14.1218 | 13.96 | 13.8217 | 14.6787 | 14.6749 | 14.6727 | 14.668 | 14.6625 | 14.6563 | 14.6494 | 14.6462 | 14.6431 | 14.6401 | 14.6372 | 14.6099 | 14.4402 | 14.2941
|  | BRUCHAG | FS |  |  |  | 0 | 15.3578 | 15.3546 | 15.3536 | 15.3526 | 15.3515 | 15.3503 | 15.3491 | 15.3477 | 15.3462 | 15.3445 | 15.3426 | 15.3343 | 15.2425 | 15.1159 | 14.3046 | 14.3014 | 14.3004 | 14.2994 | 14.2983 | 14.2971 | 14.2959 | 14.2945 | 14.2929 | 14.2912 | 14.2893 | 14.2346 | 14.1199 | 13.974 | 14.6796 | 14.6764 | 14.6754 | 14.6744 | 14.6733 | 14.6721 | 14.6709 | 14.6695 | 14.6679 | 14.6662 | 14.6643 | 14.656 | 14.6076 | 14.4556
| KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 0.074737 | 25.8667 | 25.782 | 25.7304 | 25.6596 | 25.58 | 25.4927 | 25.4003 | 25.3261 | 25.25 | 25.1729 | 25.097 | 24.603 | 23.0082 | 20.806 | 24.6902 | 24.6056 | 24.5539 | 24.4831 | 24.4035 | 24.3163 | 24.2238 | 24.1496 | 24.0736 | 23.9965 | 23.9206 | 23.2395 | 21.4913 | 19.1369 | 25.4241 | 25.3321 | 25.2732 | 25.1896 | 25.0974 | 24.9981 | 24.894 | 24.8075 | 24.7193 | 24.6302 | 24.5424 | 24.4547 | 24.3499 | 24.2418
|  | BUCKIE | CT |  |  |  | 0.074737 | 25.8667 | 25.8165 | 25.7718 | 25.7164 | 25.6525 | 25.5801 | 25.5033 | 25.4476 | 25.3905 | 25.333 | 25.2744 | 24.9083 | 24.355 | 23.0734 | 24.6902 | 24.6401 | 24.5954 | 24.5399 | 24.476 | 24.4036 | 24.3268 | 24.2712 | 24.214 | 24.1566 | 24.0979 | 23.7318 | 23.1466 | 21.6317 | 25.4241 | 25.3695 | 25.3198 | 25.2553 | 25.1826 | 25.1017 | 25.0168 | 24.9525 | 24.8868 | 24.821 | 24.754 | 24.6855 | 24.6046 | 24.5219
|  | BUCKIE | LW |  |  |  | 0.074737 | 25.8911 | 25.782 | 25.7304 | 25.6596 | 25.58 | 25.4927 | 25.4003 | 25.3261 | 25.25 | 25.1729 | 25.097 | 24.603 | 23.0082 | 20.806 | 24.7147 | 24.6056 | 24.5539 | 24.4831 | 24.4035 | 24.3163 | 24.2238 | 24.1496 | 24.0736 | 23.9965 | 23.9206 | 23.2395 | 21.4913 | 19.1369 | 25.447 | 25.3321 | 25.2732 | 25.1896 | 25.0974 | 24.9981 | 24.894 | 24.8075 | 24.7193 | 24.6302 | 24.5424 | 24.4547 | 24.3499 | 24.2418
|  | BUCKIE | ST |  |  |  | 0.074737 | 25.8961 | 25.8792 | 25.8693 | 25.8484 | 25.8229 | 25.7937 | 25.7617 | 25.747 | 25.7323 | 25.7189 | 25.7059 | 25.6428 | 25.4048 | 25.268 | 24.7197 | 24.7027 | 24.6929 | 24.672 | 24.6465 | 24.6173 | 24.5852 | 24.5706 | 24.5559 | 24.5425 | 24.5295 | 24.4664 | 24.2283 | 24.0916 | 25.4602 | 25.4428 | 25.4325 | 25.4057 | 25.3743 | 25.3396 | 25.3021 | 25.2816 | 25.2611 | 25.2421 | 25.2236 | 25.1342 | 24.8711 | 24.7102
|  | BUCKIE | FS |  |  |  | 0.074737 | 25.8987 | 25.8843 | 25.8812 | 25.878 | 25.8745 | 25.8705 | 25.8666 | 25.8587 | 25.85 | 25.8407 | 25.8308 | 25.7979 | 25.6837 | 25.4491 | 24.7222 | 24.7079 | 24.7048 | 24.7016 | 24.698 | 24.6941 | 24.6902 | 24.6822 | 24.6735 | 24.6643 | 24.6544 | 24.6214 | 24.5072 | 24.2726 | 25.4632 | 25.4485 | 25.445 | 25.4411 | 25.4357 | 25.4279 | 25.4202 | 25.4077 | 25.3946 | 25.3809 | 25.3666 | 25.3119 | 25.1772 | 24.923
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.2383 | 2.2342 | 2.2324 | 2.2299 | 2.227 | 2.2239 | 2.2206 | 2.218 | 2.2114 | 2.2018 | 2.1923 | 2.1424 | 2.083 | 2.0011 | 2.2296 | 2.2251 | 2.223 | 2.2198 | 2.2162 | 2.2125 | 2.2085 | 2.2053 | 2.2021 | 2.1988 | 2.1872 | 2.1232 | 2.0438 | 1.9414 | 2.2261 | 2.222 | 2.2202 | 2.2177 | 2.2148 | 2.2117 | 2.2084 | 2.2058 | 2.2032 | 2.2005 | 2.1979 | 2.192 | 2.1782 | 2.1643
|  | BUNOICH | CT |  |  |  | 0 | 2.2383 | 2.2369 | 2.2357 | 2.2341 | 2.2322 | 2.2299 | 2.2274 | 2.2258 | 2.2242 | 2.2225 | 2.2209 | 2.1896 | 2.1491 | 2.0996 | 2.2296 | 2.228 | 2.2266 | 2.2245 | 2.2221 | 2.2194 | 2.2165 | 2.2144 | 2.2124 | 2.2103 | 2.2082 | 2.1835 | 2.1332 | 2.072 | 2.2261 | 2.2247 | 2.2235 | 2.2219 | 2.22 | 2.2177 | 2.2153 | 2.2137 | 2.212 | 2.2103 | 2.2087 | 2.2069 | 2.2048 | 2.2025
|  | BUNOICH | LW |  |  |  | 0 | 2.2383 | 2.2342 | 2.2324 | 2.2299 | 2.227 | 2.2239 | 2.2206 | 2.218 | 2.2114 | 2.2018 | 2.1923 | 2.1424 | 2.083 | 2.0011 | 2.2296 | 2.2251 | 2.223 | 2.2198 | 2.2162 | 2.2125 | 2.2085 | 2.2053 | 2.2021 | 2.1988 | 2.1872 | 2.1232 | 2.0438 | 1.9414 | 2.2261 | 2.222 | 2.2202 | 2.2177 | 2.2148 | 2.2117 | 2.2084 | 2.2058 | 2.2032 | 2.2005 | 2.1979 | 2.192 | 2.1782 | 2.1643
|  | BUNOICH | ST |  |  |  | 0 | 2.2383 | 2.2378 | 2.2375 | 2.2368 | 2.236 | 2.2351 | 2.234 | 2.2336 | 2.2332 | 2.2328 | 2.2324 | 2.2308 | 2.2142 | 2.1948 | 2.23 | 2.2295 | 2.2292 | 2.2282 | 2.227 | 2.2258 | 2.2244 | 2.2237 | 2.223 | 2.2223 | 2.2216 | 2.2185 | 2.2088 | 2.1874 | 2.2261 | 2.2256 | 2.2253 | 2.2247 | 2.2238 | 2.2229 | 2.2218 | 2.2214 | 2.221 | 2.2206 | 2.2203 | 2.2186 | 2.2103 | 2.2045
|  | BUNOICH | FS |  |  |  | 0 | 2.2383 | 2.2378 | 2.2378 | 2.2377 | 2.2377 | 2.2377 | 2.2376 | 2.2374 | 2.2372 | 2.2369 | 2.2366 | 2.2359 | 2.232 | 2.2231 | 2.23 | 2.2295 | 2.2295 | 2.2294 | 2.2293 | 2.229 | 2.2287 | 2.2283 | 2.2278 | 2.2273 | 2.2268 | 2.225 | 2.2201 | 2.2106 | 2.2261 | 2.2256 | 2.2256 | 2.2256 | 2.2255 | 2.2255 | 2.2254 | 2.2252 | 2.225 | 2.2247 | 2.2244 | 2.2237 | 2.2198 | 2.2115
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 0.52632 | 4.5615 | 4.5371 | 4.5173 | 4.4849 | 4.4518 | 4.419 | 4.3865 | 4.3545 | 4.3228 | 4.2912 | 4.2602 | 4.0967 | 3.8971 | 3.623 | 4.5294 | 4.5025 | 4.48 | 4.4435 | 4.4064 | 4.3698 | 4.3337 | 4.2977 | 4.2619 | 4.2265 | 4.1916 | 4.0092 | 3.7904 | 3.4973 | 4.5362 | 4.5096 | 4.4874 | 4.4509 | 4.4138 | 4.3772 | 4.341 | 4.3051 | 4.2694 | 4.2341 | 4.1992 | 4.1649 | 4.1284 | 4.0917
|  | BURGARHILL | CT |  |  |  | 0.52632 | 4.5615 | 4.5474 | 4.5325 | 4.5089 | 4.4841 | 4.459 | 4.4339 | 4.4109 | 4.388 | 4.3653 | 4.3428 | 4.2231 | 4.0785 | 3.9024 | 4.5295 | 4.5139 | 4.4971 | 4.4701 | 4.4424 | 4.4145 | 4.3868 | 4.3611 | 4.3354 | 4.31 | 4.2848 | 4.1518 | 3.9937 | 3.8045 | 4.5362 | 4.5208 | 4.5043 | 4.4775 | 4.4498 | 4.4219 | 4.3942 | 4.3684 | 4.3428 | 4.3174 | 4.2922 | 4.2671 | 4.2405 | 4.2137
|  | BURGARHILL | LW |  |  |  | 0.52632 | 4.5618 | 4.5371 | 4.5173 | 4.4849 | 4.4518 | 4.419 | 4.3865 | 4.3545 | 4.3228 | 4.2912 | 4.2602 | 4.0967 | 3.8971 | 3.623 | 4.5294 | 4.5025 | 4.48 | 4.4435 | 4.4064 | 4.3698 | 4.3337 | 4.2977 | 4.2619 | 4.2265 | 4.1916 | 4.0092 | 3.7904 | 3.4973 | 4.5362 | 4.5096 | 4.4874 | 4.4509 | 4.4138 | 4.3772 | 4.341 | 4.3051 | 4.2694 | 4.2341 | 4.1992 | 4.1649 | 4.1284 | 4.0917
|  | BURGARHILL | ST |  |  |  | 0.52632 | 4.5694 | 4.5676 | 4.5668 | 4.5599 | 4.5459 | 4.532 | 4.5188 | 4.5069 | 4.4953 | 4.4839 | 4.4728 | 4.4187 | 4.343 | 4.2815 | 4.5475 | 4.5452 | 4.543 | 4.5281 | 4.512 | 4.496 | 4.4808 | 4.4671 | 4.4537 | 4.4405 | 4.4277 | 4.3655 | 4.2818 | 4.2127 | 4.5532 | 4.5512 | 4.549 | 4.5347 | 4.5189 | 4.5033 | 4.4882 | 4.4745 | 4.4611 | 4.4479 | 4.4351 | 4.3729 | 4.2894 | 4.2203
|  | BURGARHILL | FS |  |  |  | 0.52632 | 4.5694 | 4.5677 | 4.5677 | 4.5676 | 4.5675 | 4.563 | 4.5559 | 4.5475 | 4.539 | 4.5304 | 4.5216 | 4.4806 | 4.4315 | 4.3689 | 4.5478 | 4.5462 | 4.5457 | 4.5438 | 4.5397 | 4.5312 | 4.5227 | 4.5127 | 4.5026 | 4.4925 | 4.4823 | 4.4346 | 4.3792 | 4.3105 | 4.5532 | 4.5515 | 4.5515 | 4.5498 | 4.546 | 4.5378 | 4.5296 | 4.5198 | 4.51 | 4.4999 | 4.4897 | 4.442 | 4.3865 | 4.3179
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 0.050526 | 17.8067 | 17.7085 | 17.6187 | 17.4686 | 17.3167 | 17.1648 | 17.0139 | 16.8622 | 16.7113 | 16.5611 | 16.4127 | 15.6429 | 14.7588 | 13.6293 | 16.4676 | 16.437 | 16.414 | 16.324 | 16.1577 | 15.9919 | 15.8274 | 15.6611 | 15.4958 | 15.3314 | 15.1688 | 14.3299 | 13.3759 | 12.1773 | 17.1305 | 17.0999 | 17.0769 | 17.0454 | 17.0103 | 16.9715 | 16.9309 | 16.8972 | 16.7729 | 16.6038 | 16.4366 | 16.2703 | 16.0976 | 15.924
|  | BURGHEAD | CT |  |  |  | 0.050526 | 17.8067 | 17.7411 | 17.6714 | 17.5613 | 17.4486 | 17.3359 | 17.2234 | 17.1131 | 17.0031 | 16.8938 | 16.7844 | 16.2177 | 15.5694 | 14.8177 | 16.4676 | 16.4426 | 16.4198 | 16.3926 | 16.3041 | 16.1817 | 16.0597 | 15.9391 | 15.819 | 15.6996 | 15.5803 | 14.9652 | 14.2682 | 13.4682 | 17.1305 | 17.1055 | 17.0827 | 17.0555 | 17.0244 | 16.9907 | 16.9552 | 16.928 | 16.9003 | 16.8725 | 16.8437 | 16.7389 | 16.6129 | 16.4857
|  | BURGHEAD | LW |  |  |  | 0.050526 | 17.8103 | 17.7085 | 17.6187 | 17.4686 | 17.3167 | 17.1648 | 17.0139 | 16.8622 | 16.7113 | 16.5611 | 16.4127 | 15.6429 | 14.7588 | 13.6293 | 16.4845 | 16.437 | 16.414 | 16.324 | 16.1577 | 15.9919 | 15.8274 | 15.6611 | 15.4958 | 15.3314 | 15.1688 | 14.3299 | 13.3759 | 12.1773 | 17.1474 | 17.0999 | 17.0769 | 17.0454 | 17.0103 | 16.9715 | 16.9309 | 16.8972 | 16.7729 | 16.6038 | 16.4366 | 16.2703 | 16.0976 | 15.924
|  | BURGHEAD | ST |  |  |  | 0.050526 | 17.8879 | 17.8738 | 17.8619 | 17.7965 | 17.7301 | 17.6638 | 17.5974 | 17.5337 | 17.4706 | 17.4086 | 17.3475 | 17.0554 | 16.7068 | 16.4024 | 16.4887 | 16.4806 | 16.4754 | 16.4658 | 16.4546 | 16.4419 | 16.428 | 16.3923 | 16.3224 | 16.2534 | 16.1856 | 15.8614 | 15.482 | 15.1477 | 17.1516 | 17.1435 | 17.1383 | 17.1287 | 17.1175 | 17.1048 | 17.0909 | 17.0842 | 17.0773 | 17.0707 | 17.0643 | 17.0331 | 16.7561 | 16.4119
|  | BURGHEAD | FS |  |  |  | 0.050526 | 17.8927 | 17.8827 | 17.8756 | 17.8656 | 17.8454 | 17.8064 | 17.7674 | 17.7217 | 17.6758 | 17.6297 | 17.5835 | 17.3589 | 17.1136 | 16.8279 | 16.4895 | 16.4836 | 16.4817 | 16.4797 | 16.4777 | 16.4754 | 16.4732 | 16.4693 | 16.4652 | 16.4608 | 16.444 | 16.1937 | 15.9242 | 15.6152 | 17.1524 | 17.1465 | 17.1446 | 17.1426 | 17.1406 | 17.1383 | 17.1361 | 17.1322 | 17.1281 | 17.1237 | 17.1191 | 17.1021 | 17.0534 | 16.8932
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 1.3916 | 15.4684 | 15.3885 | 15.3406 | 15.2746 | 15.2004 | 15.1189 | 15.0325 | 14.9631 | 14.8919 | 14.8196 | 14.7485 | 14.3071 | 13.6242 | 12.3575 | 14.2926 | 14.208 | 14.1556 | 14.0814 | 13.9992 | 13.8085 | 13.5804 | 13.3604 | 13.141 | 12.9231 | 12.7089 | 11.5648 | 10.1592 | 8.1746 | 14.6858 | 14.6059 | 14.558 | 14.492 | 14.4178 | 14.3363 | 14.2498 | 14.1804 | 14.1093 | 14.037 | 13.9659 | 13.7904 | 13.5551 | 13.3168
|  | BURGHMUIR | CT |  |  |  | 1.3916 | 15.4684 | 15.4228 | 15.3822 | 15.3317 | 15.2734 | 15.2073 | 15.1371 | 15.0863 | 15.034 | 14.9806 | 14.9269 | 14.5894 | 14.0775 | 13.3201 | 14.2926 | 14.2442 | 14.2004 | 14.1441 | 14.0803 | 14.0088 | 13.9304 | 13.7739 | 13.6175 | 13.4619 | 13.3076 | 12.4782 | 11.4622 | 10.2103 | 14.6858 | 14.6401 | 14.5995 | 14.549 | 14.4908 | 14.4246 | 14.3544 | 14.3036 | 14.2513 | 14.198 | 14.1442 | 14.0888 | 14.0218 | 13.953
|  | BURGHMUIR | LW |  |  |  | 1.3916 | 15.4903 | 15.3885 | 15.3406 | 15.2746 | 15.2004 | 15.1189 | 15.0325 | 14.9631 | 14.8919 | 14.8196 | 14.7485 | 14.3071 | 13.6242 | 12.3575 | 14.3136 | 14.208 | 14.1556 | 14.0814 | 13.9992 | 13.8085 | 13.5804 | 13.3604 | 13.141 | 12.9231 | 12.7089 | 11.5648 | 10.1592 | 8.1746 | 14.7077 | 14.6059 | 14.558 | 14.492 | 14.4178 | 14.3363 | 14.2498 | 14.1804 | 14.1093 | 14.037 | 13.9659 | 13.7904 | 13.5551 | 13.3168
|  | BURGHMUIR | ST |  |  |  | 1.3916 | 15.4954 | 15.4794 | 15.47 | 15.4503 | 15.4272 | 15.4006 | 15.3714 | 15.3584 | 15.3452 | 15.3325 | 15.3202 | 15.2627 | 15.0414 | 14.9155 | 14.324 | 14.3077 | 14.2981 | 14.2747 | 14.2479 | 14.2178 | 14.1853 | 14.1685 | 14.1518 | 14.1356 | 14.1198 | 13.8021 | 13.2825 | 12.8689 | 14.7127 | 14.6967 | 14.6873 | 14.6677 | 14.6445 | 14.618 | 14.5888 | 14.5757 | 14.5626 | 14.5499 | 14.5376 | 14.48 | 14.2587 | 14.1328
|  | BURGHMUIR | FS |  |  |  | 1.3916 | 15.4971 | 15.4833 | 15.4803 | 15.4771 | 15.4736 | 15.4698 | 15.4659 | 15.4582 | 15.4499 | 15.4418 | 15.4332 | 15.4029 | 15.2939 | 15.0707 | 14.3258 | 14.3119 | 14.3087 | 14.3051 | 14.3004 | 14.2941 | 14.2878 | 14.2772 | 14.266 | 14.2551 | 14.2436 | 14.1995 | 13.8376 | 13.3744 | 14.7144 | 14.7007 | 14.6976 | 14.6945 | 14.691 | 14.6871 | 14.6833 | 14.6756 | 14.6672 | 14.6592 | 14.6505 | 14.6202 | 14.5113 | 14.288
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.1028 | 0.10278 | 0.10277 | 0.10276 | 0.10275 | 0.10274 | 0.10272 | 0.10271 | 0.1027 | 0.10269 | 0.10268 | 0.10261 | 0.10251 | 0.1023 | 0.10183 | 0.10182 | 0.10181 | 0.1018 | 0.10179 | 0.10178 | 0.10176 | 0.10175 | 0.10174 | 0.10173 | 0.10172 | 0.10165 | 0.10154 | 0.10134 | 0.10227 | 0.10226 | 0.10225 | 0.10224 | 0.10223 | 0.10221 | 0.1022 | 0.10219 | 0.10218 | 0.10217 | 0.10216 | 0.10215 | 0.10213 | 0.10212
|  | BUTTERBRIDGE | CT |  |  |  | 0 | 0.1028 | 0.10279 | 0.10279 | 0.10278 | 0.10277 | 0.10276 | 0.10275 | 0.10275 | 0.10274 | 0.10273 | 0.10272 | 0.10268 | 0.1026 | 0.10249 | 0.10183 | 0.10183 | 0.10182 | 0.10182 | 0.10181 | 0.1018 | 0.10179 | 0.10178 | 0.10177 | 0.10177 | 0.10176 | 0.10171 | 0.10164 | 0.10152 | 0.10227 | 0.10227 | 0.10226 | 0.10226 | 0.10225 | 0.10224 | 0.10223 | 0.10222 | 0.10221 | 0.10221 | 0.1022 | 0.10219 | 0.10218 | 0.10217
|  | BUTTERBRIDGE | LW |  |  |  | 0 | 0.1028 | 0.10278 | 0.10277 | 0.10276 | 0.10275 | 0.10274 | 0.10272 | 0.10271 | 0.1027 | 0.10269 | 0.10268 | 0.10261 | 0.10251 | 0.1023 | 0.10183 | 0.10182 | 0.10181 | 0.1018 | 0.10179 | 0.10178 | 0.10176 | 0.10175 | 0.10174 | 0.10173 | 0.10172 | 0.10165 | 0.10154 | 0.10134 | 0.10227 | 0.10226 | 0.10225 | 0.10224 | 0.10223 | 0.10221 | 0.1022 | 0.10219 | 0.10218 | 0.10217 | 0.10216 | 0.10215 | 0.10213 | 0.10212
|  | BUTTERBRIDGE | ST |  |  |  | 0 | 0.1028 | 0.1028 | 0.10279 | 0.10279 | 0.10279 | 0.10278 | 0.10278 | 0.10278 | 0.10278 | 0.10277 | 0.10277 | 0.10277 | 0.10273 | 0.10271 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10182 | 0.10182 | 0.10181 | 0.10181 | 0.10181 | 0.10181 | 0.1018 | 0.10177 | 0.10175 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10226 | 0.10226 | 0.10226 | 0.10225 | 0.10225 | 0.10225 | 0.10225 | 0.10224 | 0.10221 | 0.10219
|  | BUTTERBRIDGE | FS |  |  |  | 0 | 0.1028 | 0.1028 | 0.1028 | 0.1028 | 0.1028 | 0.1028 | 0.1028 | 0.10279 | 0.10279 | 0.10279 | 0.10279 | 0.10279 | 0.10277 | 0.10273 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10183 | 0.10182 | 0.10181 | 0.10177 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10227 | 0.10226 | 0.10225 | 0.10221
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0 | 8.9328 | 8.895 | 8.8779 | 8.854 | 8.8269 | 8.7973 | 8.766 | 8.7414 | 8.7165 | 8.6622 | 8.5768 | 8.1237 | 7.575 | 6.8032 | 8.0745 | 8.0367 | 8.0196 | 7.9957 | 7.9686 | 7.939 | 7.9077 | 7.8832 | 7.8582 | 7.8329 | 7.8079 | 7.5377 | 6.9846 | 6.2084 | 8.3685 | 8.3307 | 8.3136 | 8.2897 | 8.2626 | 8.233 | 8.1784 | 8.0802 | 7.9825 | 7.8854 | 7.7898 | 7.6954 | 7.5944 | 7.4925
|  | CALLANDER | CT |  |  |  | 0 | 8.9328 | 8.9197 | 8.9086 | 8.8935 | 8.8751 | 8.8535 | 8.8303 | 8.8152 | 8.7995 | 8.7837 | 8.7677 | 8.5377 | 8.1526 | 7.6788 | 8.0745 | 8.0614 | 8.0503 | 8.0352 | 8.0168 | 7.9953 | 7.9721 | 7.9569 | 7.9412 | 7.9254 | 7.9094 | 7.8038 | 7.5673 | 7.0905 | 8.3685 | 8.3554 | 8.3443 | 8.3293 | 8.3108 | 8.2893 | 8.2661 | 8.2509 | 8.2273 | 8.1611 | 8.0955 | 8.0299 | 7.9596 | 7.8889
|  | CALLANDER | LW |  |  |  | 0 | 8.9336 | 8.895 | 8.8779 | 8.854 | 8.8269 | 8.7973 | 8.766 | 8.7414 | 8.7165 | 8.6622 | 8.5768 | 8.1237 | 7.575 | 6.8032 | 8.0753 | 8.0367 | 8.0196 | 7.9957 | 7.9686 | 7.939 | 7.9077 | 7.8832 | 7.8582 | 7.8329 | 7.8079 | 7.5377 | 6.9846 | 6.2084 | 8.3693 | 8.3307 | 8.3136 | 8.2897 | 8.2626 | 8.233 | 8.1784 | 8.0802 | 7.9825 | 7.8854 | 7.7898 | 7.6954 | 7.5944 | 7.4925
|  | CALLANDER | ST |  |  |  | 0 | 8.9336 | 8.9286 | 8.9262 | 8.9197 | 8.9119 | 8.9027 | 8.8925 | 8.8886 | 8.8847 | 8.881 | 8.8775 | 8.8614 | 8.7805 | 8.6265 | 8.0753 | 8.0703 | 8.0679 | 8.0615 | 8.0536 | 8.0444 | 8.0342 | 8.0303 | 8.0265 | 8.0228 | 8.0192 | 8.0031 | 7.9222 | 7.8805 | 8.3693 | 8.3643 | 8.3619 | 8.3555 | 8.3476 | 8.3384 | 8.3282 | 8.3243 | 8.3205 | 8.3168 | 8.3132 | 8.2554 | 8.0239 | 7.8356
|  | CALLANDER | FS |  |  |  | 0 | 8.9336 | 8.9288 | 8.9286 | 8.9284 | 8.928 | 8.9275 | 8.927 | 8.9249 | 8.9226 | 8.9201 | 8.9174 | 8.9101 | 8.8721 | 8.789 | 8.0753 | 8.0706 | 8.0704 | 8.0701 | 8.0697 | 8.0692 | 8.0687 | 8.0667 | 8.0644 | 8.0618 | 8.0591 | 8.0518 | 8.0138 | 7.9308 | 8.3693 | 8.3646 | 8.3644 | 8.3641 | 8.3637 | 8.3632 | 8.3627 | 8.3607 | 8.3584 | 8.3559 | 8.3531 | 8.3458 | 8.2818 | 8.0808
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0 | 4.5767 | 4.5598 | 4.5515 | 4.5395 | 4.5263 | 4.5121 | 4.4973 | 4.4851 | 4.4728 | 4.4603 | 4.4481 | 4.3748 | 4.2184 | 3.9047 | 4.5855 | 4.5697 | 4.5627 | 4.5529 | 4.5418 | 4.5296 | 4.5168 | 4.5068 | 4.4966 | 4.4828 | 4.4434 | 4.2365 | 3.9905 | 3.6547 | 4.5418 | 4.5252 | 4.5171 | 4.5056 | 4.4927 | 4.4789 | 4.4476 | 4.4094 | 4.3715 | 4.3338 | 4.2968 | 4.2603 | 4.2195 | 4.1781
|  | CALLANISH | CT |  |  |  | 0 | 4.5769 | 4.5706 | 4.565 | 4.5571 | 4.5478 | 4.5373 | 4.5262 | 4.5183 | 4.5102 | 4.5021 | 4.4939 | 4.443 | 4.3656 | 4.2502 | 4.5855 | 4.58 | 4.5753 | 4.5689 | 4.5611 | 4.5521 | 4.5423 | 4.5359 | 4.5293 | 4.5226 | 4.5159 | 4.423 | 4.2504 | 4.0417 | 4.542 | 4.5359 | 4.5304 | 4.5229 | 4.5139 | 4.5036 | 4.4927 | 4.4852 | 4.4659 | 4.4401 | 4.4145 | 4.3889 | 4.3614 | 4.3338
|  | CALLANISH | LW |  |  |  | 0 | 4.5767 | 4.5598 | 4.5515 | 4.5395 | 4.5263 | 4.5121 | 4.4973 | 4.4851 | 4.4728 | 4.4603 | 4.4481 | 4.3748 | 4.2184 | 3.9047 | 4.5855 | 4.5697 | 4.5627 | 4.5529 | 4.5418 | 4.5296 | 4.5168 | 4.5068 | 4.4966 | 4.4828 | 4.4434 | 4.2365 | 3.9905 | 3.6547 | 4.5418 | 4.5252 | 4.5171 | 4.5056 | 4.4927 | 4.4789 | 4.4476 | 4.4094 | 4.3715 | 4.3338 | 4.2968 | 4.2603 | 4.2195 | 4.1781
|  | CALLANISH | ST |  |  |  | 0 | 4.5781 | 4.576 | 4.5749 | 4.5711 | 4.5668 | 4.562 | 4.5568 | 4.5542 | 4.5516 | 4.5491 | 4.5467 | 4.5355 | 4.4978 | 4.4764 | 4.5855 | 4.5834 | 4.5824 | 4.5797 | 4.5764 | 4.5725 | 4.5682 | 4.5666 | 4.565 | 4.5635 | 4.562 | 4.5552 | 4.5217 | 4.4697 | 4.543 | 4.5409 | 4.5398 | 4.5362 | 4.5321 | 4.5275 | 4.5225 | 4.52 | 4.5176 | 4.5153 | 4.5131 | 4.4834 | 4.3943 | 4.3233
|  | CALLANISH | FS |  |  |  | 0 | 4.5782 | 4.5762 | 4.576 | 4.5758 | 4.5753 | 4.5744 | 4.5736 | 4.572 | 4.5703 | 4.5685 | 4.5666 | 4.5599 | 4.5407 | 4.5031 | 4.5855 | 4.5835 | 4.5834 | 4.5833 | 4.5832 | 4.5829 | 4.5827 | 4.5819 | 4.5809 | 4.5799 | 4.5788 | 4.5757 | 4.56 | 4.5256 | 4.543 | 4.5411 | 4.5409 | 4.5407 | 4.5403 | 4.5395 | 4.5388 | 4.5373 | 4.5358 | 4.5341 | 4.5324 | 4.5264 | 4.4943 | 4.417
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.15579 | 1.3608 | 1.3578 | 1.3549 | 1.3516 | 1.348 | 1.344 | 1.3399 | 1.3366 | 1.3333 | 1.33 | 1.3266 | 1.3073 | 1.2744 | 1.2181 | 1.4372 | 1.4342 | 1.4313 | 1.428 | 1.4244 | 1.4204 | 1.4163 | 1.413 | 1.4097 | 1.4064 | 1.403 | 1.3837 | 1.3508 | 1.2945 | 1.3241 | 1.321 | 1.3182 | 1.3149 | 1.3113 | 1.3073 | 1.3032 | 1.2999 | 1.2966 | 1.2932 | 1.2899 | 1.2864 | 1.2826 | 1.2787
|  | CALVINE | CT |  |  |  | 0.15579 | 1.3608 | 1.3578 | 1.3549 | 1.3516 | 1.348 | 1.344 | 1.3399 | 1.3366 | 1.3333 | 1.33 | 1.3266 | 1.3073 | 1.2772 | 1.2377 | 1.4372 | 1.4342 | 1.4313 | 1.428 | 1.4244 | 1.4204 | 1.4163 | 1.413 | 1.4097 | 1.4064 | 1.403 | 1.3837 | 1.3536 | 1.3141 | 1.3241 | 1.321 | 1.3182 | 1.3149 | 1.3113 | 1.3073 | 1.3032 | 1.2999 | 1.2966 | 1.2932 | 1.2899 | 1.2864 | 1.2826 | 1.2787
|  | CALVINE | LW |  |  |  | 0.15579 | 1.365 | 1.3602 | 1.3576 | 1.3542 | 1.3506 | 1.3466 | 1.3426 | 1.3392 | 1.3357 | 1.3323 | 1.3289 | 1.3078 | 1.2744 | 1.2181 | 1.4414 | 1.4366 | 1.434 | 1.4306 | 1.427 | 1.423 | 1.419 | 1.4156 | 1.4121 | 1.4087 | 1.4053 | 1.3842 | 1.3508 | 1.2945 | 1.3283 | 1.3235 | 1.3208 | 1.3175 | 1.3138 | 1.3099 | 1.3058 | 1.3024 | 1.299 | 1.2955 | 1.2921 | 1.2887 | 1.2847 | 1.2806
|  | CALVINE | ST |  |  |  | 0.15579 | 1.365 | 1.3645 | 1.3643 | 1.3636 | 1.3619 | 1.3601 | 1.3582 | 1.357 | 1.3557 | 1.3545 | 1.3541 | 1.3499 | 1.3383 | 1.3298 | 1.4414 | 1.4409 | 1.4407 | 1.44 | 1.4383 | 1.4365 | 1.4346 | 1.4334 | 1.4321 | 1.4309 | 1.4305 | 1.4263 | 1.4147 | 1.4062 | 1.3283 | 1.3278 | 1.3275 | 1.3269 | 1.3252 | 1.3234 | 1.3215 | 1.3203 | 1.319 | 1.3178 | 1.3174 | 1.3132 | 1.3015 | 1.293
|  | CALVINE | FS |  |  |  | 0.15579 | 1.365 | 1.3646 | 1.3645 | 1.3645 | 1.3645 | 1.3644 | 1.3644 | 1.3642 | 1.3639 | 1.3637 | 1.3634 | 1.3627 | 1.3588 | 1.3504 | 1.4414 | 1.441 | 1.4409 | 1.4409 | 1.4409 | 1.4408 | 1.4408 | 1.4406 | 1.4403 | 1.4401 | 1.4398 | 1.4391 | 1.4352 | 1.4268 | 1.3283 | 1.3278 | 1.3278 | 1.3278 | 1.3277 | 1.3277 | 1.3276 | 1.3274 | 1.3272 | 1.3269 | 1.3267 | 1.3259 | 1.3221 | 1.3137
| CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0.036842 | 16.6441 | 16.5914 | 16.5676 | 16.5335 | 16.4125 | 16.2445 | 16.0783 | 15.9121 | 15.7468 | 15.5824 | 15.4209 | 14.5738 | 13.5731 | 12.2284 | 15.5279 | 15.4706 | 15.4424 | 15.4018 | 15.3568 | 15.3083 | 15.2576 | 15.2081 | 15.02 | 14.833 | 14.6494 | 13.6935 | 12.5813 | 11.1179 | 16.0632 | 16.0105 | 15.9867 | 15.9536 | 15.9159 | 15.8745 | 15.8306 | 15.796 | 15.7606 | 15.7246 | 15.689 | 15.6536 | 15.6089 | 15.5072
|  | CAMPBELTOWN | CT |  |  |  | 0.036842 | 16.6441 | 16.625 | 16.6088 | 16.587 | 16.5605 | 16.4967 | 16.3773 | 16.2632 | 16.1487 | 16.0354 | 15.9232 | 15.3299 | 14.6293 | 13.7873 | 15.528 | 15.5063 | 15.4871 | 15.4601 | 15.4285 | 15.3924 | 15.3541 | 15.3267 | 15.2984 | 15.2698 | 15.2165 | 14.5467 | 13.7681 | 12.8483 | 16.0632 | 16.0441 | 16.0279 | 16.0061 | 15.9797 | 15.9486 | 15.9151 | 15.8929 | 15.8696 | 15.8461 | 15.8223 | 15.7975 | 15.766 | 15.7336
|  | CAMPBELTOWN | LW |  |  |  | 0.036842 | 16.6449 | 16.5914 | 16.5676 | 16.5335 | 16.4125 | 16.2445 | 16.0783 | 15.9121 | 15.7468 | 15.5824 | 15.4209 | 14.5738 | 13.5731 | 12.2284 | 15.5279 | 15.4706 | 15.4424 | 15.4018 | 15.3568 | 15.3083 | 15.2576 | 15.2081 | 15.02 | 14.833 | 14.6494 | 13.6935 | 12.5813 | 11.1179 | 16.0641 | 16.0105 | 15.9867 | 15.9536 | 15.9159 | 15.8745 | 15.8306 | 15.796 | 15.7606 | 15.7246 | 15.689 | 15.6536 | 15.6089 | 15.5072
|  | CAMPBELTOWN | ST |  |  |  | 0.036842 | 16.6458 | 16.6385 | 16.635 | 16.6256 | 16.6142 | 16.6008 | 16.5858 | 16.5803 | 16.5724 | 16.5404 | 16.4753 | 16.1619 | 15.7595 | 15.4175 | 15.5334 | 15.5257 | 15.5216 | 15.5089 | 15.4941 | 15.4774 | 15.4593 | 15.4502 | 15.4411 | 15.4324 | 15.4238 | 15.3838 | 15.0216 | 14.6308 | 16.0649 | 16.0576 | 16.0541 | 16.0447 | 16.0333 | 16.0199 | 16.0049 | 15.9994 | 15.9937 | 15.9883 | 15.9832 | 15.9593 | 15.8363 | 15.7722
|  | CAMPBELTOWN | FS |  |  |  | 0.036842 | 16.6458 | 16.6385 | 16.6381 | 16.6378 | 16.6372 | 16.6364 | 16.6356 | 16.6324 | 16.6289 | 16.625 | 16.6208 | 16.4731 | 16.1905 | 15.8438 | 15.5336 | 15.5259 | 15.5252 | 15.5242 | 15.5224 | 15.5193 | 15.5162 | 15.5105 | 15.5042 | 15.4977 | 15.4908 | 15.4667 | 15.3949 | 15.1203 | 16.0649 | 16.0576 | 16.0573 | 16.0569 | 16.0563 | 16.0555 | 16.0547 | 16.0515 | 16.048 | 16.0441 | 16.0399 | 16.0286 | 15.9694 | 15.8388
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 0.10105 | 13.3095 | 13.2515 | 13.196 | 13.1365 | 13.0729 | 13.0064 | 12.9388 | 12.8776 | 12.8157 | 12.7529 | 12.6891 | 12.0256 | 11.0971 | 9.86 | 12.9718 | 12.9138 | 12.8583 | 12.7988 | 12.7352 | 12.6687 | 12.6011 | 12.5399 | 12.478 | 12.4151 | 12.3513 | 11.5477 | 10.5295 | 9.2029 | 13.1329 | 13.0749 | 13.0194 | 12.9599 | 12.8963 | 12.8298 | 12.7622 | 12.6436 | 12.4831 | 12.3227 | 12.1633 | 12.0047 | 11.8379 | 11.6675
|  | CAPUTH | CT |  |  |  | 0.10105 | 13.3095 | 13.2515 | 13.196 | 13.1365 | 13.0729 | 13.0064 | 12.9388 | 12.8776 | 12.8157 | 12.7529 | 12.6891 | 12.2068 | 11.4076 | 10.4611 | 12.9718 | 12.9138 | 12.8583 | 12.7988 | 12.7352 | 12.6687 | 12.6011 | 12.5399 | 12.478 | 12.4151 | 12.3513 | 11.8073 | 10.9456 | 9.9378 | 13.1329 | 13.0749 | 13.0194 | 12.9599 | 12.8963 | 12.8298 | 12.7622 | 12.6977 | 12.562 | 12.4262 | 12.2904 | 12.1548 | 12.0113 | 11.8656
|  | CAPUTH | LW |  |  |  | 0.10105 | 13.3828 | 13.3237 | 13.2888 | 13.2432 | 13.192 | 13.1361 | 13.0767 | 13.0245 | 12.9702 | 12.9146 | 12.7947 | 12.0256 | 11.0971 | 9.86 | 13.0451 | 12.986 | 12.951 | 12.9054 | 12.8543 | 12.7984 | 12.739 | 12.6868 | 12.6325 | 12.5671 | 12.405 | 11.5477 | 10.5295 | 9.2029 | 13.2062 | 13.1471 | 13.1121 | 13.0665 | 13.0154 | 12.9595 | 12.8033 | 12.6436 | 12.4831 | 12.3227 | 12.1633 | 12.0047 | 11.8379 | 11.6675
|  | CAPUTH | ST |  |  |  | 0.10105 | 13.3979 | 13.3818 | 13.3689 | 13.3511 | 13.3299 | 13.3071 | 13.283 | 13.2666 | 13.2511 | 13.2357 | 13.2205 | 13.1432 | 12.9879 | 12.7613 | 13.0602 | 13.0441 | 13.0311 | 13.0133 | 12.9921 | 12.9693 | 12.9453 | 12.9289 | 12.9133 | 12.8979 | 12.8828 | 12.8054 | 12.6501 | 12.3627 | 13.2213 | 13.2052 | 13.1922 | 13.1744 | 13.1532 | 13.1304 | 13.1064 | 13.09 | 13.0744 | 13.059 | 13.0439 | 12.836 | 12.458 | 12.1224
|  | CAPUTH | FS |  |  |  | 0.10105 | 13.4055 | 13.3949 | 13.387 | 13.3792 | 13.3711 | 13.3629 | 13.3547 | 13.3448 | 13.3353 | 13.3256 | 13.3156 | 13.2657 | 13.1805 | 13.045 | 13.0678 | 13.0571 | 13.0493 | 13.0414 | 13.0334 | 13.0252 | 13.017 | 13.007 | 12.9976 | 12.9878 | 12.9779 | 12.928 | 12.8428 | 12.7072 | 13.2289 | 13.2182 | 13.2104 | 13.2025 | 13.1945 | 13.1863 | 13.1781 | 13.1681 | 13.1587 | 13.1489 | 13.139 | 13.0891 | 12.894 | 12.5875
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 0.016842 | 16.9079 | 16.8203 | 16.7756 | 16.7131 | 16.6425 | 16.5656 | 16.4838 | 16.2169 | 15.9057 | 15.6051 | 15.3267 | 13.957 | 12.4333 | 10.3919 | 15.5056 | 15.401 | 15.3433 | 15.1997 | 14.7866 | 14.3921 | 14.0262 | 13.6576 | 13.3027 | 12.9605 | 12.6442 | 11.1036 | 9.4219 | 7.2303 | 15.9603 | 15.8726 | 15.8279 | 15.6734 | 15.3104 | 14.9623 | 14.6379 | 14.3137 | 13.9908 | 13.6696 | 13.3724 | 13.0918 | 12.7978 | 12.505
|  | CARNOUSTIE | CT |  |  |  | 0.016842 | 16.9079 | 16.8691 | 16.8353 | 16.7917 | 16.7395 | 16.6795 | 16.6155 | 16.5716 | 16.5264 | 16.4809 | 16.4127 | 15.4177 | 14.333 | 13.0448 | 15.5056 | 15.4595 | 15.4174 | 15.3625 | 15.2989 | 15.1167 | 14.8495 | 14.5948 | 14.345 | 14.1098 | 13.8854 | 12.7661 | 11.5702 | 10.1764 | 15.9603 | 15.9215 | 15.8877 | 15.844 | 15.7919 | 15.5976 | 15.3601 | 15.1362 | 14.9164 | 14.7089 | 14.5104 | 14.3129 | 14.1079 | 13.8974
|  | CARNOUSTIE | LW |  |  |  | 0.016842 | 16.9188 | 16.8203 | 16.7756 | 16.7131 | 16.6425 | 16.5656 | 16.4838 | 16.2169 | 15.9057 | 15.6051 | 15.3267 | 13.957 | 12.4333 | 10.3919 | 15.5114 | 15.401 | 15.3433 | 15.1997 | 14.7866 | 14.3921 | 14.0262 | 13.6576 | 13.3027 | 12.9605 | 12.6442 | 11.1036 | 9.4219 | 7.2303 | 15.9712 | 15.8726 | 15.8279 | 15.6734 | 15.3104 | 14.9623 | 14.6379 | 14.3137 | 13.9908 | 13.6696 | 13.3724 | 13.0918 | 12.7978 | 12.505
|  | CARNOUSTIE | ST |  |  |  | 0.016842 | 16.9214 | 16.9072 | 16.8995 | 16.8818 | 16.8605 | 16.8359 | 16.8086 | 16.7973 | 16.786 | 16.7751 | 16.7646 | 16.716 | 16.4428 | 15.945 | 15.5256 | 15.5094 | 15.4994 | 15.4754 | 15.4478 | 15.4168 | 15.3836 | 15.3658 | 15.3479 | 15.3307 | 15.2326 | 14.6014 | 13.908 | 13.3415 | 15.9737 | 15.9596 | 15.9519 | 15.9341 | 15.9129 | 15.8882 | 15.861 | 15.8497 | 15.8384 | 15.8274 | 15.709 | 15.1629 | 14.5404 | 14.0299
|  | CARNOUSTIE | FS |  |  |  | 0.016842 | 16.9222 | 16.9096 | 16.9082 | 16.9068 | 16.905 | 16.9028 | 16.9007 | 16.8948 | 16.8883 | 16.8812 | 16.8735 | 16.8504 | 16.7521 | 16.5424 | 15.5275 | 15.5132 | 15.5101 | 15.5063 | 15.5014 | 15.4947 | 15.4881 | 15.4773 | 15.4655 | 15.4533 | 15.4407 | 15.1928 | 14.6902 | 14.0985 | 15.9746 | 15.962 | 15.9606 | 15.9591 | 15.9573 | 15.9552 | 15.9531 | 15.9472 | 15.9407 | 15.9335 | 15.9259 | 15.6876 | 15.2441 | 14.7082
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0 | 1.0401 | 1.039 | 1.0383 | 1.0373 | 1.0362 | 1.035 | 1.0339 | 1.0329 | 1.0319 | 1.0308 | 1.0296 | 1.008 | 0.98411 | 0.95467 | 1.0183 | 1.0172 | 1.0165 | 1.0157 | 1.0116 | 1.0066 | 1.0016 | 0.99675 | 0.9919 | 0.98708 | 0.98231 | 0.9579 | 0.93115 | 0.8989 | 1.0376 | 1.0366 | 1.0361 | 1.0355 | 1.0323 | 1.0276 | 1.0229 | 1.0182 | 1.0133 | 1.0084 | 1.0036 | 0.99881 | 0.99388 | 0.98892
|  | CASHLIE | CT |  |  |  | 0 | 1.0401 | 1.0397 | 1.0392 | 1.0386 | 1.0379 | 1.037 | 1.0362 | 1.0356 | 1.0349 | 1.0342 | 1.0336 | 1.0284 | 1.0122 | 0.99381 | 1.0183 | 1.0179 | 1.0175 | 1.0169 | 1.0162 | 1.0138 | 1.0104 | 1.0071 | 1.0039 | 1.0006 | 0.99741 | 0.98088 | 0.96275 | 0.9425 | 1.0376 | 1.0373 | 1.037 | 1.0366 | 1.0361 | 1.0344 | 1.0312 | 1.0281 | 1.025 | 1.022 | 1.0188 | 1.0156 | 1.0123 | 1.0089
|  | CASHLIE | LW |  |  |  | 0 | 1.0401 | 1.039 | 1.0383 | 1.0373 | 1.0362 | 1.035 | 1.0339 | 1.0329 | 1.0319 | 1.0308 | 1.0296 | 1.008 | 0.98411 | 0.95467 | 1.0183 | 1.0172 | 1.0165 | 1.0157 | 1.0116 | 1.0066 | 1.0016 | 0.99675 | 0.9919 | 0.98708 | 0.98231 | 0.9579 | 0.93115 | 0.8989 | 1.0376 | 1.0366 | 1.0361 | 1.0355 | 1.0323 | 1.0276 | 1.0229 | 1.0182 | 1.0133 | 1.0084 | 1.0036 | 0.99881 | 0.99388 | 0.98892
|  | CASHLIE | ST |  |  |  | 0 | 1.0404 | 1.0402 | 1.0402 | 1.0399 | 1.0395 | 1.0391 | 1.0388 | 1.0385 | 1.0383 | 1.0381 | 1.0378 | 1.0368 | 1.0341 | 1.0325 | 1.0184 | 1.0183 | 1.0182 | 1.018 | 1.0177 | 1.0174 | 1.017 | 1.0168 | 1.0166 | 1.0164 | 1.016 | 1.008 | 0.99866 | 0.99045 | 1.0376 | 1.0375 | 1.0374 | 1.0373 | 1.0371 | 1.0368 | 1.0366 | 1.0365 | 1.0364 | 1.0363 | 1.0361 | 1.0291 | 1.0201 | 1.0118
|  | CASHLIE | FS |  |  |  | 0 | 1.0404 | 1.0403 | 1.0402 | 1.0402 | 1.0402 | 1.0401 | 1.04 | 1.0398 | 1.0396 | 1.0394 | 1.0392 | 1.0385 | 1.037 | 1.0344 | 1.0184 | 1.0183 | 1.0183 | 1.0183 | 1.0183 | 1.0182 | 1.0181 | 1.018 | 1.0179 | 1.0177 | 1.0176 | 1.0139 | 1.0061 | 0.99733 | 1.0376 | 1.0375 | 1.0375 | 1.0375 | 1.0375 | 1.0375 | 1.0375 | 1.0374 | 1.0374 | 1.0373 | 1.0372 | 1.0347 | 1.0273 | 1.0187
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | -2.0502 | -2.0507 | -2.0509 | -2.0513 | -2.0517 | -2.0521 | -2.0525 | -2.0529 | -2.0532 | -2.0536 | -2.0539 | -2.056 | -2.0592 | -2.0649 | -1.6519 | -1.6524 | -1.6526 | -1.6529 | -1.6532 | -1.6536 | -1.654 | -1.6543 | -1.6546 | -1.6549 | -1.6552 | -1.657 | -1.66 | -1.6655 | -1.9577 | -1.9585 | -1.9591 | -1.9602 | -1.9612 | -1.9622 | -1.9632 | -1.9641 | -1.9651 | -1.966 | -1.9669 | -1.9678 | -1.9688 | -1.9698
|  | CHAORACH | CT |  |  |  | 0 | -2.0502 | -2.0504 | -2.0505 | -2.0508 | -2.051 | -2.0513 | -2.0516 | -2.0519 | -2.0521 | -2.0523 | -2.0525 | -2.054 | -2.0561 | -2.0593 | -1.6519 | -1.6521 | -1.6522 | -1.6524 | -1.6526 | -1.6529 | -1.6532 | -1.6534 | -1.6535 | -1.6537 | -1.6539 | -1.6552 | -1.6572 | -1.6603 | -1.9577 | -1.9581 | -1.9585 | -1.9592 | -1.9599 | -1.9606 | -1.9613 | -1.962 | -1.9626 | -1.9632 | -1.9638 | -1.9645 | -1.9651 | -1.9658
|  | CHAORACH | LW |  |  |  | 0 | -2.0502 | -2.0507 | -2.0509 | -2.0513 | -2.0517 | -2.0521 | -2.0525 | -2.0529 | -2.0532 | -2.0536 | -2.0539 | -2.056 | -2.0592 | -2.0649 | -1.6519 | -1.6524 | -1.6526 | -1.6529 | -1.6532 | -1.6536 | -1.654 | -1.6543 | -1.6546 | -1.6549 | -1.6552 | -1.657 | -1.66 | -1.6655 | -1.9577 | -1.9585 | -1.9591 | -1.9602 | -1.9612 | -1.9622 | -1.9632 | -1.9641 | -1.9651 | -1.966 | -1.9669 | -1.9678 | -1.9688 | -1.9698
|  | CHAORACH | ST |  |  |  | 0 | -2.0502 | -2.0502 | -2.0502 | -2.0503 | -2.0505 | -2.0506 | -2.0507 | -2.0508 | -2.0509 | -2.051 | -2.051 | -2.0513 | -2.0524 | -2.0529 | -1.6519 | -1.652 | -1.652 | -1.6521 | -1.6522 | -1.6523 | -1.6524 | -1.6524 | -1.6525 | -1.6525 | -1.6526 | -1.6528 | -1.6537 | -1.6542 | -1.9573 | -1.9573 | -1.9574 | -1.9578 | -1.9582 | -1.9586 | -1.959 | -1.9594 | -1.9597 | -1.9601 | -1.9604 | -1.9619 | -1.9641 | -1.9657
|  | CHAORACH | FS |  |  |  | 0 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -2.0504 | -2.0504 | -2.0504 | -2.0506 | -2.0511 | -2.0521 | -1.6519 | -1.652 | -1.652 | -1.652 | -1.652 | -1.652 | -1.652 | -1.652 | -1.652 | -1.6521 | -1.6521 | -1.6522 | -1.6526 | -1.6535 | -1.9572 | -1.9573 | -1.9573 | -1.9573 | -1.9574 | -1.9576 | -1.9578 | -1.9581 | -1.9583 | -1.9586 | -1.9589 | -1.96 | -1.9615 | -1.9633
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0.18947 | 13.5509 | 13.4764 | 13.4417 | 13.3937 | 13.3394 | 13.2796 | 13.2164 | 13.1664 | 13.1153 | 12.9881 | 12.808 | 11.8521 | 10.6858 | 9.033 | 12.8605 | 12.7804 | 12.7406 | 12.6842 | 12.6217 | 12.5542 | 12.4836 | 12.4257 | 12.3669 | 12.3073 | 12.1772 | 11.0897 | 9.7881 | 7.9992 | 13.1162 | 13.0416 | 13.007 | 12.959 | 12.9046 | 12.8448 | 12.7816 | 12.7316 | 12.566 | 12.3659 | 12.1707 | 11.979 | 11.7714 | 11.562
|  | CHARLES AVENUE | CT |  |  |  | 0.18947 | 13.5509 | 13.5232 | 13.4994 | 13.4678 | 13.4294 | 13.3845 | 13.3361 | 13.3038 | 13.2702 | 13.2361 | 13.2017 | 12.7227 | 11.9019 | 10.8752 | 12.8605 | 12.8298 | 12.8026 | 12.7652 | 12.7211 | 12.6706 | 12.6171 | 12.5793 | 12.5402 | 12.5008 | 12.4612 | 12.0822 | 11.1674 | 10.0463 | 13.1162 | 13.0884 | 13.0646 | 13.033 | 12.9946 | 12.9497 | 12.9013 | 12.8691 | 12.8354 | 12.8014 | 12.7669 | 12.6694 | 12.5233 | 12.3762
|  | CHARLES AVENUE | LW |  |  |  | 0.18947 | 13.5535 | 13.4764 | 13.4417 | 13.3937 | 13.3394 | 13.2796 | 13.2164 | 13.1664 | 13.1153 | 12.9881 | 12.808 | 11.8521 | 10.6858 | 9.033 | 12.8617 | 12.7804 | 12.7406 | 12.6842 | 12.6217 | 12.5542 | 12.4836 | 12.4257 | 12.3669 | 12.3073 | 12.1772 | 11.0897 | 9.7881 | 7.9992 | 13.1187 | 13.0416 | 13.007 | 12.959 | 12.9046 | 12.8448 | 12.7816 | 12.7316 | 12.566 | 12.3659 | 12.1707 | 11.979 | 11.7714 | 11.562
|  | CHARLES AVENUE | ST |  |  |  | 0.18947 | 13.5551 | 13.5439 | 13.5381 | 13.5238 | 13.5067 | 13.4868 | 13.4647 | 13.4558 | 13.447 | 13.4384 | 13.4302 | 13.3921 | 13.2134 | 12.9005 | 12.8688 | 12.8571 | 12.8507 | 12.8329 | 12.8121 | 12.7886 | 12.763 | 12.7505 | 12.7379 | 12.7258 | 12.7141 | 12.6593 | 12.4648 | 12.2668 | 13.1204 | 13.1091 | 13.1033 | 13.0891 | 13.072 | 13.052 | 13.0299 | 13.0211 | 13.0122 | 13.0037 | 12.9955 | 12.9574 | 12.6582 | 12.2616
|  | CHARLES AVENUE | FS |  |  |  | 0.18947 | 13.5551 | 13.5447 | 13.5443 | 13.5437 | 13.5429 | 13.5417 | 13.5406 | 13.5362 | 13.5311 | 13.5256 | 13.5196 | 13.5036 | 13.4195 | 13.2343 | 12.869 | 12.8582 | 12.8574 | 12.8562 | 12.854 | 12.8503 | 12.8466 | 12.8392 | 12.8313 | 12.8229 | 12.814 | 12.784 | 12.6867 | 12.4887 | 13.1204 | 13.11 | 13.1095 | 13.109 | 13.1081 | 13.107 | 13.1058 | 13.1014 | 13.0964 | 13.0908 | 13.0848 | 13.0688 | 12.9848 | 12.7385
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 0.12316 | 16.6028 | 16.5821 | 16.5716 | 16.5561 | 16.539 | 16.5204 | 16.501 | 16.4847 | 16.468 | 16.451 | 16.4341 | 16.3297 | 16.1672 | 15.7344 | 15.6402 | 15.6213 | 15.6126 | 15.6004 | 15.5866 | 15.5712 | 15.5548 | 15.5418 | 15.5284 | 15.5147 | 15.5011 | 15.2869 | 14.899 | 14.3617 | 15.9438 | 15.925 | 15.9162 | 15.904 | 15.8902 | 15.8748 | 15.8584 | 15.8454 | 15.832 | 15.8183 | 15.8047 | 15.7911 | 15.7736 | 15.7553
|  | CHARLESTON | CT |  |  |  | 0.12316 | 16.6028 | 16.5949 | 16.5879 | 16.5778 | 16.566 | 16.5525 | 16.538 | 16.5275 | 16.5166 | 16.5055 | 16.4943 | 16.4219 | 16.3027 | 16.1218 | 15.6402 | 15.6334 | 15.6277 | 15.6199 | 15.6104 | 15.599 | 15.5866 | 15.5785 | 15.5699 | 15.5611 | 15.5522 | 15.4913 | 15.2826 | 14.9403 | 15.9438 | 15.937 | 15.9313 | 15.9235 | 15.914 | 15.9026 | 15.8903 | 15.8821 | 15.8735 | 15.8647 | 15.8558 | 15.8464 | 15.8342 | 15.8216
|  | CHARLESTON | LW |  |  |  | 0.12316 | 16.6033 | 16.5821 | 16.5716 | 16.5561 | 16.539 | 16.5204 | 16.501 | 16.4847 | 16.468 | 16.451 | 16.4341 | 16.3297 | 16.1672 | 15.7344 | 15.641 | 15.6213 | 15.6126 | 15.6004 | 15.5866 | 15.5712 | 15.5548 | 15.5418 | 15.5284 | 15.5147 | 15.5011 | 15.2869 | 14.899 | 14.3617 | 15.9446 | 15.925 | 15.9162 | 15.904 | 15.8902 | 15.8748 | 15.8584 | 15.8454 | 15.832 | 15.8183 | 15.8047 | 15.7911 | 15.7736 | 15.7553
|  | CHARLESTON | ST |  |  |  | 0.12316 | 16.6054 | 16.6024 | 16.6008 | 16.5956 | 16.5895 | 16.5827 | 16.5753 | 16.5715 | 16.5678 | 16.5641 | 16.5605 | 16.5435 | 16.4846 | 16.4499 | 15.641 | 15.6381 | 15.6367 | 15.633 | 15.6285 | 15.6232 | 15.6173 | 15.615 | 15.6128 | 15.6107 | 15.6086 | 15.599 | 15.5477 | 15.5206 | 15.9446 | 15.9418 | 15.9404 | 15.9366 | 15.9321 | 15.9268 | 15.9209 | 15.9187 | 15.9164 | 15.9143 | 15.9123 | 15.9027 | 15.8513 | 15.8242
|  | CHARLESTON | FS |  |  |  | 0.12316 | 16.6054 | 16.6022 | 16.6019 | 16.6016 | 16.6008 | 16.5994 | 16.598 | 16.5954 | 16.5927 | 16.5898 | 16.5868 | 16.576 | 16.5445 | 16.482 | 15.641 | 15.6379 | 15.6378 | 15.6376 | 15.6374 | 15.637 | 15.6367 | 15.6354 | 15.6339 | 15.6322 | 15.6305 | 15.6257 | 15.6004 | 15.5439 | 15.9446 | 15.9416 | 15.9414 | 15.9413 | 15.941 | 15.9407 | 15.9403 | 15.939 | 15.9375 | 15.9359 | 15.9341 | 15.9293 | 15.904 | 15.8476
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 0 | 6.5629 | 6.546 | 6.5385 | 6.528 | 6.5161 | 6.5031 | 6.4894 | 6.4786 | 6.4677 | 6.4304 | 6.3925 | 6.1917 | 5.9494 | 5.6107 | 6.5892 | 6.5723 | 6.5647 | 6.5542 | 6.5227 | 6.4771 | 6.432 | 6.3884 | 6.3451 | 6.3021 | 6.2597 | 6.0376 | 5.7735 | 5.4133 | 6.5952 | 6.5773 | 6.5687 | 6.5562 | 6.5117 | 6.4661 | 6.4211 | 6.3776 | 6.3343 | 6.2914 | 6.2491 | 6.2075 | 6.163 | 6.1181
|  | CLACHAN | CT |  |  |  | 0 | 6.5629 | 6.557 | 6.552 | 6.5452 | 6.5369 | 6.5271 | 6.5167 | 6.5098 | 6.5027 | 6.4956 | 6.4884 | 6.3744 | 6.2032 | 5.9931 | 6.5892 | 6.5833 | 6.5782 | 6.5714 | 6.5631 | 6.5479 | 6.516 | 6.4858 | 6.4557 | 6.4259 | 6.3964 | 6.2394 | 6.0529 | 5.8276 | 6.5955 | 6.5889 | 6.5831 | 6.5749 | 6.5651 | 6.5369 | 6.505 | 6.4749 | 6.4448 | 6.415 | 6.3855 | 6.3561 | 6.3247 | 6.293
|  | CLACHAN | LW |  |  |  | 0 | 6.5629 | 6.546 | 6.5385 | 6.528 | 6.5161 | 6.5031 | 6.4894 | 6.4786 | 6.4677 | 6.4304 | 6.3925 | 6.1917 | 5.9494 | 5.6107 | 6.5892 | 6.5723 | 6.5647 | 6.5542 | 6.5227 | 6.4771 | 6.432 | 6.3884 | 6.3451 | 6.3021 | 6.2597 | 6.0376 | 5.7735 | 5.4133 | 6.5952 | 6.5773 | 6.5687 | 6.5562 | 6.5117 | 6.4661 | 6.4211 | 6.3776 | 6.3343 | 6.2914 | 6.2491 | 6.2075 | 6.163 | 6.1181
|  | CLACHAN | ST |  |  |  | 0 | 6.5629 | 6.5607 | 6.5596 | 6.5567 | 6.5532 | 6.5491 | 6.5445 | 6.5427 | 6.541 | 6.5393 | 6.5377 | 6.5305 | 6.4893 | 6.4145 | 6.5892 | 6.5869 | 6.5859 | 6.583 | 6.5794 | 6.5753 | 6.5707 | 6.569 | 6.5672 | 6.5621 | 6.5457 | 6.4678 | 6.3643 | 6.2804 | 6.5966 | 6.5943 | 6.5931 | 6.5892 | 6.5848 | 6.5798 | 6.5743 | 6.5716 | 6.5678 | 6.551 | 6.5347 | 6.457 | 6.3536 | 6.2698
|  | CLACHAN | FS |  |  |  | 0 | 6.5629 | 6.5608 | 6.5607 | 6.5606 | 6.5604 | 6.5602 | 6.56 | 6.5591 | 6.558 | 6.5569 | 6.5557 | 6.5524 | 6.5354 | 6.4984 | 6.5892 | 6.5871 | 6.587 | 6.5869 | 6.5867 | 6.5865 | 6.5862 | 6.5853 | 6.5843 | 6.5832 | 6.5819 | 6.5481 | 6.4748 | 6.3841 | 6.5966 | 6.5945 | 6.5943 | 6.5941 | 6.5936 | 6.5927 | 6.5919 | 6.5902 | 6.5885 | 6.5866 | 6.5847 | 6.5371 | 6.4639 | 6.3734
| CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.32358 | 0.31903 | 0.31454 | 0.30994 | 0.30525 | 0.30049 | 0.29569 | 0.28994 | 0.28381 | 0.2777 | 0.2716 | 0.23805 | 0.19785 | 0.15131 | 0.32029 | 0.31574 | 0.31124 | 0.30665 | 0.30196 | 0.2972 | 0.29239 | 0.2878 | 0.28319 | 0.27857 | 0.27396 | 0.24177 | 0.1997 | 0.15124 | 0.319 | 0.31445 | 0.30996 | 0.30536 | 0.30067 | 0.29591 | 0.29111 | 0.28651 | 0.2819 | 0.27729 | 0.27267 | 0.26804 | 0.2633 | 0.2577
|  | CLAONAIG | CT |  |  |  | 0 | 0.32358 | 0.31903 | 0.31454 | 0.30994 | 0.30525 | 0.30049 | 0.29569 | 0.28994 | 0.28381 | 0.2777 | 0.2716 | 0.23805 | 0.19785 | 0.15131 | 0.32029 | 0.31574 | 0.31124 | 0.30665 | 0.30196 | 0.2972 | 0.29239 | 0.2878 | 0.28319 | 0.27857 | 0.27396 | 0.24177 | 0.1997 | 0.15124 | 0.319 | 0.31445 | 0.30996 | 0.30536 | 0.30067 | 0.29591 | 0.29111 | 0.28651 | 0.2819 | 0.27729 | 0.27267 | 0.26804 | 0.2633 | 0.2577
|  | CLAONAIG | LW |  |  |  | 0 | 0.33116 | 0.32934 | 0.32722 | 0.32493 | 0.32256 | 0.31825 | 0.31239 | 0.30664 | 0.3009 | 0.29518 | 0.28949 | 0.25794 | 0.21936 | 0.17001 | 0.32787 | 0.32605 | 0.32393 | 0.32164 | 0.31927 | 0.31683 | 0.31352 | 0.31036 | 0.30546 | 0.29911 | 0.29279 | 0.25797 | 0.21659 | 0.16479 | 0.32658 | 0.32476 | 0.32264 | 0.32035 | 0.31798 | 0.31555 | 0.31223 | 0.30909 | 0.30593 | 0.30277 | 0.29696 | 0.2911 | 0.28509 | 0.27821
|  | CLAONAIG | ST |  |  |  | 0 | 0.332 | 0.33103 | 0.33013 | 0.32912 | 0.32808 | 0.32701 | 0.32591 | 0.32497 | 0.32403 | 0.3231 | 0.32216 | 0.31253 | 0.3005 | 0.28619 | 0.32871 | 0.32774 | 0.32684 | 0.32583 | 0.32479 | 0.32372 | 0.32262 | 0.32168 | 0.32074 | 0.3198 | 0.31887 | 0.31425 | 0.30476 | 0.28904 | 0.32742 | 0.32645 | 0.32555 | 0.32454 | 0.3235 | 0.32243 | 0.32133 | 0.32039 | 0.31945 | 0.31851 | 0.31758 | 0.31297 | 0.30676 | 0.29351
|  | CLAONAIG | FS |  |  |  | 0 | 0.332 | 0.33104 | 0.33019 | 0.32935 | 0.3285 | 0.32764 | 0.32679 | 0.32589 | 0.32499 | 0.32409 | 0.32318 | 0.31722 | 0.30658 | 0.29497 | 0.32871 | 0.32775 | 0.3269 | 0.32605 | 0.3252 | 0.32435 | 0.32349 | 0.3226 | 0.3217 | 0.3208 | 0.31989 | 0.3155 | 0.31035 | 0.29883 | 0.32742 | 0.32646 | 0.32561 | 0.32477 | 0.32391 | 0.32306 | 0.32221 | 0.32131 | 0.32041 | 0.31951 | 0.3186 | 0.31421 | 0.30907 | 0.30262
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 0.0063158 | 27.7626 | 27.6818 | 27.6456 | 27.5951 | 27.5378 | 27.4731 | 27.404 | 27.3489 | 27.2915 | 27.2322 | 27.1733 | 26.7835 | 25.3175 | 22.8967 | 26.1046 | 26.0155 | 25.9707 | 25.9073 | 25.8374 | 25.7606 | 25.6801 | 25.6127 | 25.5432 | 25.3848 | 25.0902 | 23.5259 | 21.6402 | 19.0428 | 26.6161 | 26.5354 | 26.4992 | 26.4487 | 26.3914 | 26.3267 | 26.2576 | 26.2025 | 26.145 | 26.0858 | 26.0269 | 25.9676 | 25.8897 | 25.8086
|  | CLAYHILLS | CT |  |  |  | 0.0063158 | 27.7626 | 27.7354 | 27.7131 | 27.6829 | 27.6459 | 27.6009 | 27.5517 | 27.5182 | 27.4821 | 27.4452 | 27.4074 | 27.1441 | 26.6808 | 25.6415 | 26.1066 | 26.0744 | 26.0465 | 26.0076 | 25.9617 | 25.908 | 25.8508 | 25.8087 | 25.7641 | 25.719 | 25.673 | 24.9976 | 23.6785 | 22.0461 | 26.6161 | 26.589 | 26.5667 | 26.5365 | 26.4995 | 26.4545 | 26.4053 | 26.3718 | 26.3357 | 26.2988 | 26.261 | 26.2209 | 26.1679 | 26.1133
|  | CLAYHILLS | LW |  |  |  | 0.0063158 | 27.7634 | 27.6818 | 27.6456 | 27.5951 | 27.5378 | 27.4731 | 27.404 | 27.3489 | 27.2915 | 27.2322 | 27.1733 | 26.7835 | 25.3175 | 22.8967 | 26.1046 | 26.0155 | 25.9707 | 25.9073 | 25.8374 | 25.7606 | 25.6801 | 25.6127 | 25.5432 | 25.3848 | 25.0902 | 23.5259 | 21.6402 | 19.0428 | 26.617 | 26.5354 | 26.4992 | 26.4487 | 26.3914 | 26.3267 | 26.2576 | 26.2025 | 26.145 | 26.0858 | 26.0269 | 25.9676 | 25.8897 | 25.8086
|  | CLAYHILLS | ST |  |  |  | 0.0063158 | 27.7634 | 27.7511 | 27.7453 | 27.7295 | 27.7103 | 27.6878 | 27.6626 | 27.6532 | 27.6438 | 27.6347 | 27.626 | 27.5843 | 27.3501 | 27.2249 | 26.113 | 26.0996 | 26.0924 | 26.0714 | 26.0468 | 26.0189 | 25.9886 | 25.9735 | 25.9583 | 25.9436 | 25.9294 | 25.8604 | 25.6 | 25.0333 | 26.617 | 26.6047 | 26.5989 | 26.5831 | 26.5639 | 26.5413 | 26.5162 | 26.5068 | 26.4973 | 26.4883 | 26.4796 | 26.4379 | 26.2036 | 26.0785
|  | CLAYHILLS | FS |  |  |  | 0.0063158 | 27.7634 | 27.7485 | 27.7479 | 27.7471 | 27.7459 | 27.7442 | 27.7426 | 27.7363 | 27.7291 | 27.7212 | 27.7126 | 27.6897 | 27.567 | 27.2926 | 26.1128 | 26.097 | 26.0953 | 26.0931 | 26.0895 | 26.0836 | 26.0778 | 26.0667 | 26.0546 | 26.0419 | 26.0285 | 25.9827 | 25.8381 | 25.542 | 26.617 | 26.6021 | 26.6014 | 26.6007 | 26.5995 | 26.5978 | 26.5962 | 26.5898 | 26.5826 | 26.5747 | 26.5661 | 26.5433 | 26.4206 | 26.1462
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0 | 1.1427 | 1.1374 | 1.1342 | 1.1299 | 1.1249 | 1.1195 | 1.113 | 1.1077 | 1.1024 | 1.0867 | 1.0683 | 0.97333 | 0.86365 | 0.71834 | 1.1539 | 1.1485 | 1.1453 | 1.1265 | 1.1053 | 1.0844 | 1.0629 | 1.0412 | 1.0197 | 0.99838 | 0.97738 | 0.8693 | 0.74655 | 0.58847 | 1.1336 | 1.1282 | 1.125 | 1.1207 | 1.1157 | 1.1063 | 1.0853 | 1.064 | 1.0427 | 1.0214 | 1.0004 | 0.97967 | 0.95805 | 0.93628
|  | COLDBACKIE | CT |  |  |  | 0 | 1.1427 | 1.1396 | 1.1367 | 1.1332 | 1.129 | 1.1244 | 1.1194 | 1.1159 | 1.1123 | 1.1087 | 1.1051 | 1.0518 | 0.97502 | 0.88159 | 1.1539 | 1.1507 | 1.1478 | 1.1412 | 1.1259 | 1.1105 | 1.0953 | 1.0802 | 1.0651 | 1.0503 | 1.0356 | 0.95928 | 0.87328 | 0.77094 | 1.1336 | 1.1304 | 1.1275 | 1.124 | 1.1198 | 1.1152 | 1.1102 | 1.1021 | 1.0874 | 1.0728 | 1.0584 | 1.0439 | 1.0287 | 1.0133
|  | COLDBACKIE | LW |  |  |  | 0 | 1.1444 | 1.1374 | 1.1342 | 1.1299 | 1.1249 | 1.1195 | 1.113 | 1.1077 | 1.1024 | 1.0867 | 1.0683 | 0.97333 | 0.86365 | 0.71834 | 1.1555 | 1.1485 | 1.1453 | 1.1265 | 1.1053 | 1.0844 | 1.0629 | 1.0412 | 1.0197 | 0.99838 | 0.97738 | 0.8693 | 0.74655 | 0.58847 | 1.1352 | 1.1282 | 1.125 | 1.1207 | 1.1157 | 1.1063 | 1.0853 | 1.064 | 1.0427 | 1.0214 | 1.0004 | 0.97967 | 0.95805 | 0.93628
|  | COLDBACKIE | ST |  |  |  | 0 | 1.1453 | 1.1444 | 1.144 | 1.1429 | 1.1416 | 1.14 | 1.1382 | 1.1376 | 1.1369 | 1.1363 | 1.1357 | 1.133 | 1.1198 | 1.0889 | 1.1564 | 1.1555 | 1.1551 | 1.154 | 1.1527 | 1.1511 | 1.1486 | 1.1404 | 1.1323 | 1.1245 | 1.1168 | 1.0804 | 1.0352 | 0.99781 | 1.1361 | 1.1352 | 1.1348 | 1.1337 | 1.1324 | 1.1308 | 1.1291 | 1.1284 | 1.1277 | 1.1271 | 1.1265 | 1.1028 | 1.0582 | 1.0208
|  | COLDBACKIE | FS |  |  |  | 0 | 1.1453 | 1.1445 | 1.1445 | 1.1444 | 1.1444 | 1.1443 | 1.1442 | 1.1439 | 1.1435 | 1.1431 | 1.1427 | 1.1415 | 1.1356 | 1.1227 | 1.1564 | 1.1556 | 1.1556 | 1.1556 | 1.1555 | 1.1554 | 1.1553 | 1.155 | 1.1546 | 1.1542 | 1.1494 | 1.1218 | 1.0911 | 1.0548 | 1.1361 | 1.1353 | 1.1353 | 1.1353 | 1.1352 | 1.1351 | 1.135 | 1.1347 | 1.1343 | 1.1339 | 1.1335 | 1.1324 | 1.1133 | 1.0776
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.56228 | 0.56057 | 0.5598 | 0.55874 | 0.55754 | 0.55623 | 0.55485 | 0.55293 | 0.54905 | 0.54519 | 0.54141 | 0.52167 | 0.4983 | 0.4662 | 0.5317 | 0.52999 | 0.52922 | 0.52816 | 0.52696 | 0.52404 | 0.51967 | 0.51546 | 0.5113 | 0.5071 | 0.50293 | 0.48106 | 0.45533 | 0.42092 | 0.5393 | 0.53759 | 0.53682 | 0.53576 | 0.53374 | 0.52908 | 0.52448 | 0.52005 | 0.51566 | 0.51131 | 0.50704 | 0.50284 | 0.49842 | 0.49396
|  | COLINTRAIVE | CT |  |  |  | 0 | 0.56228 | 0.56171 | 0.56123 | 0.56058 | 0.55977 | 0.55884 | 0.55785 | 0.5572 | 0.55653 | 0.55586 | 0.55519 | 0.54728 | 0.53402 | 0.5175 | 0.5317 | 0.53113 | 0.53065 | 0.52999 | 0.52919 | 0.52826 | 0.52726 | 0.52662 | 0.52539 | 0.52319 | 0.52104 | 0.50954 | 0.49539 | 0.47798 | 0.5393 | 0.53873 | 0.53825 | 0.53759 | 0.53679 | 0.53586 | 0.53486 | 0.53285 | 0.5305 | 0.5282 | 0.52593 | 0.52368 | 0.52127 | 0.51884
|  | COLINTRAIVE | LW |  |  |  | 0 | 0.56228 | 0.56057 | 0.5598 | 0.55874 | 0.55754 | 0.55623 | 0.55485 | 0.55293 | 0.54905 | 0.54519 | 0.54141 | 0.52167 | 0.4983 | 0.4662 | 0.5317 | 0.52999 | 0.52922 | 0.52816 | 0.52696 | 0.52404 | 0.51967 | 0.51546 | 0.5113 | 0.5071 | 0.50293 | 0.48106 | 0.45533 | 0.42092 | 0.5393 | 0.53759 | 0.53682 | 0.53576 | 0.53374 | 0.52908 | 0.52448 | 0.52005 | 0.51566 | 0.51131 | 0.50704 | 0.50284 | 0.49842 | 0.49396
|  | COLINTRAIVE | ST |  |  |  | 0 | 0.56228 | 0.56207 | 0.56198 | 0.56171 | 0.56138 | 0.561 | 0.56057 | 0.56041 | 0.56025 | 0.5601 | 0.55995 | 0.55929 | 0.55606 | 0.55256 | 0.5317 | 0.53149 | 0.53139 | 0.53112 | 0.5308 | 0.53042 | 0.52999 | 0.52983 | 0.52967 | 0.52951 | 0.52937 | 0.52793 | 0.52052 | 0.51499 | 0.5393 | 0.53909 | 0.53899 | 0.53873 | 0.5384 | 0.53802 | 0.53759 | 0.53743 | 0.53727 | 0.53712 | 0.53697 | 0.53303 | 0.52532 | 0.5195
|  | COLINTRAIVE | FS |  |  |  | 0 | 0.56228 | 0.5621 | 0.56209 | 0.56208 | 0.56207 | 0.56205 | 0.56202 | 0.56195 | 0.56186 | 0.56176 | 0.56165 | 0.56137 | 0.55991 | 0.55673 | 0.5317 | 0.53152 | 0.53151 | 0.5315 | 0.53148 | 0.53146 | 0.53144 | 0.53136 | 0.53127 | 0.53118 | 0.53107 | 0.53079 | 0.52904 | 0.52259 | 0.5393 | 0.53912 | 0.53911 | 0.5391 | 0.53908 | 0.53906 | 0.53904 | 0.53896 | 0.53887 | 0.53878 | 0.53867 | 0.53839 | 0.53417 | 0.52749
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0.0052632 | 2.7927 | 2.759 | 2.7357 | 2.6979 | 2.6589 | 2.6197 | 2.5805 | 2.5435 | 2.5067 | 2.47 | 2.434 | 2.2384 | 1.9884 | 1.5758 | 2.572 | 2.5502 | 2.5401 | 2.5261 | 2.5102 | 2.4928 | 2.4745 | 2.4601 | 2.4455 | 2.3972 | 2.3463 | 2.0775 | 1.7525 | 1.2956 | 2.5107 | 2.4707 | 2.44 | 2.3889 | 2.3369 | 2.2854 | 2.2346 | 2.1849 | 2.1357 | 2.0868 | 2.0388 | 1.9915 | 1.9405 | 1.8889
|  | COLL | CT |  |  |  | 0.0052632 | 2.7945 | 2.7785 | 2.7627 | 2.7371 | 2.7098 | 2.6815 | 2.653 | 2.628 | 2.6028 | 2.5779 | 2.5532 | 2.4149 | 2.2349 | 2.002 | 2.572 | 2.5641 | 2.5574 | 2.5483 | 2.5371 | 2.5241 | 2.5101 | 2.501 | 2.4915 | 2.482 | 2.4724 | 2.3201 | 2.0877 | 1.8035 | 2.5139 | 2.4934 | 2.4726 | 2.4376 | 2.4013 | 2.3645 | 2.3278 | 2.2938 | 2.2599 | 2.2264 | 2.1932 | 2.1601 | 2.1243 | 2.0873
|  | COLL | LW |  |  |  | 0.0052632 | 2.7927 | 2.759 | 2.7357 | 2.6979 | 2.6589 | 2.6197 | 2.5805 | 2.5435 | 2.5067 | 2.47 | 2.434 | 2.2384 | 1.9884 | 1.5758 | 2.5728 | 2.5502 | 2.5401 | 2.5261 | 2.5102 | 2.4928 | 2.4745 | 2.4601 | 2.4455 | 2.3972 | 2.3463 | 2.0775 | 1.7525 | 1.2956 | 2.5107 | 2.4707 | 2.44 | 2.3889 | 2.3369 | 2.2854 | 2.2346 | 2.1849 | 2.1357 | 2.0868 | 2.0388 | 1.9915 | 1.9405 | 1.8889
|  | COLL | ST |  |  |  | 0.0052632 | 2.8083 | 2.8048 | 2.8029 | 2.7879 | 2.7722 | 2.7564 | 2.7402 | 2.7271 | 2.7142 | 2.7017 | 2.6896 | 2.6327 | 2.5398 | 2.472 | 2.5728 | 2.5698 | 2.5684 | 2.5645 | 2.5598 | 2.5543 | 2.5481 | 2.5458 | 2.5435 | 2.5413 | 2.5392 | 2.5295 | 2.4802 | 2.3823 | 2.5351 | 2.5313 | 2.529 | 2.5078 | 2.486 | 2.4644 | 2.4426 | 2.4234 | 2.4046 | 2.3864 | 2.3686 | 2.2852 | 2.1672 | 2.0751
|  | COLL | FS |  |  |  | 0.0052632 | 2.809 | 2.8058 | 2.8052 | 2.804 | 2.8002 | 2.7927 | 2.7853 | 2.7759 | 2.7663 | 2.7567 | 2.7469 | 2.7031 | 2.6437 | 2.5595 | 2.5728 | 2.57 | 2.5699 | 2.5697 | 2.5695 | 2.5692 | 2.5689 | 2.5677 | 2.5663 | 2.5648 | 2.5631 | 2.5588 | 2.5361 | 2.4866 | 2.5361 | 2.5327 | 2.5318 | 2.5301 | 2.5242 | 2.5127 | 2.5013 | 2.4873 | 2.4732 | 2.459 | 2.4447 | 2.3787 | 2.2987 | 2.1951
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 0.18421 | 26.8953 | 26.8814 | 26.8749 | 26.8657 | 26.8554 | 26.8437 | 26.8313 | 26.8214 | 26.8111 | 26.8005 | 26.7899 | 26.7203 | 26.603 | 26.369 | 25.32 | 25.3061 | 25.2995 | 25.2871 | 25.2715 | 25.2548 | 25.2375 | 25.2225 | 25.2072 | 25.1916 | 25.1763 | 25.084 | 24.9441 | 24.6873 | 25.8099 | 25.796 | 25.7895 | 25.7804 | 25.77 | 25.7584 | 25.7459 | 25.736 | 25.7257 | 25.7151 | 25.7045 | 25.6939 | 25.68 | 25.6655
|  | COMMERCE STREET | CT |  |  |  | 0.18421 | 26.8953 | 26.8904 | 26.8863 | 26.8808 | 26.874 | 26.8657 | 26.8567 | 26.8507 | 26.8443 | 26.8377 | 26.831 | 26.7841 | 26.7016 | 26.5692 | 25.32 | 25.3151 | 25.311 | 25.3055 | 25.297 | 25.2851 | 25.2727 | 25.2631 | 25.2532 | 25.2432 | 25.2331 | 25.17 | 25.0717 | 24.9233 | 25.8099 | 25.8051 | 25.801 | 25.7954 | 25.7886 | 25.7803 | 25.7713 | 25.7653 | 25.7589 | 25.7524 | 25.7456 | 25.7385 | 25.7291 | 25.7193
|  | COMMERCE STREET | LW |  |  |  | 0.18421 | 26.8961 | 26.8814 | 26.8749 | 26.8657 | 26.8554 | 26.8437 | 26.8313 | 26.8214 | 26.8111 | 26.8005 | 26.7899 | 26.7203 | 26.603 | 26.369 | 25.3208 | 25.3061 | 25.2995 | 25.2871 | 25.2715 | 25.2548 | 25.2375 | 25.2225 | 25.2072 | 25.1916 | 25.1763 | 25.084 | 24.9441 | 24.6873 | 25.8108 | 25.796 | 25.7895 | 25.7804 | 25.77 | 25.7584 | 25.7459 | 25.736 | 25.7257 | 25.7151 | 25.7045 | 25.6939 | 25.68 | 25.6655
|  | COMMERCE STREET | ST |  |  |  | 0.18421 | 26.8961 | 26.8939 | 26.8928 | 26.89 | 26.8865 | 26.8824 | 26.8779 | 26.8762 | 26.8745 | 26.8728 | 26.8712 | 26.8637 | 26.8219 | 26.7996 | 25.3208 | 25.3186 | 25.3175 | 25.3147 | 25.3112 | 25.3071 | 25.3026 | 25.3007 | 25.2966 | 25.2926 | 25.2887 | 25.2699 | 25.2175 | 25.1848 | 25.8108 | 25.8085 | 25.8075 | 25.8046 | 25.8011 | 25.7971 | 25.7925 | 25.7908 | 25.7891 | 25.7875 | 25.7859 | 25.7784 | 25.7365 | 25.7142
|  | COMMERCE STREET | FS |  |  |  | 0.18421 | 26.8961 | 26.8935 | 26.8934 | 26.8933 | 26.8931 | 26.8928 | 26.8925 | 26.8914 | 26.8902 | 26.8888 | 26.8873 | 26.8833 | 26.862 | 26.8142 | 25.3208 | 25.3182 | 25.3181 | 25.318 | 25.3178 | 25.3175 | 25.3172 | 25.3161 | 25.3149 | 25.3135 | 25.3114 | 25.2986 | 25.269 | 25.213 | 25.8108 | 25.8082 | 25.8081 | 25.8079 | 25.8077 | 25.8074 | 25.8072 | 25.806 | 25.8048 | 25.8034 | 25.8019 | 25.798 | 25.7766 | 25.7289
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | NO | 0 | 0.053866 | 0.053804 | 0.053752 | 0.05368 | 0.053593 | 0.053492 | 0.053383 | 0.053313 | 0.05324 | 0.053167 | 0.053093 | 0.049817 | 0.04415 | 0.038125 | 0.052623 | 0.052461 | 0.052295 | 0.052018 | 0.051732 | 0.051444 | 0.051159 | 0.050854 | 0.050476 | 0.050101 | 0.049736 | 0.046304 | 0.040512 | 0.034367 | 0.052735 | 0.052596 | 0.052458 | 0.05223 | 0.051991 | 0.051747 | 0.051504 | 0.051291 | 0.051052 | 0.050738 | 0.050432 | 0.050128 | 0.049781 | 0.049165
|  | COMRIE | CT |  |  |  | 0 | 0.053866 | 0.053804 | 0.053752 | 0.05368 | 0.053593 | 0.053492 | 0.053383 | 0.053313 | 0.05324 | 0.053167 | 0.053093 | 0.049817 | 0.04415 | 0.038125 | 0.052623 | 0.052461 | 0.052295 | 0.052018 | 0.051732 | 0.051444 | 0.051159 | 0.050901 | 0.050646 | 0.050394 | 0.050146 | 0.046304 | 0.040512 | 0.034367 | 0.052735 | 0.052596 | 0.052458 | 0.05223 | 0.051991 | 0.051747 | 0.051504 | 0.051291 | 0.051078 | 0.050869 | 0.050662 | 0.050457 | 0.050233 | 0.049165
|  | COMRIE | LW |  |  |  | 0 | 0.054708 | 0.054523 | 0.054441 | 0.054327 | 0.054197 | 0.054056 | 0.053908 | 0.053791 | 0.053674 | 0.053555 | 0.053235 | 0.051502 | 0.049372 | 0.042922 | 0.05343 | 0.053112 | 0.052868 | 0.05246 | 0.052046 | 0.051638 | 0.051238 | 0.050854 | 0.050476 | 0.050101 | 0.049736 | 0.047822 | 0.045511 | 0.038886 | 0.053551 | 0.053264 | 0.053058 | 0.05272 | 0.052373 | 0.052029 | 0.051688 | 0.051368 | 0.051052 | 0.050738 | 0.050432 | 0.050128 | 0.049781 | 0.049428
|  | COMRIE | ST |  |  |  | 0 | 0.054708 | 0.054685 | 0.054675 | 0.054645 | 0.05461 | 0.054568 | 0.054521 | 0.054504 | 0.054486 | 0.054469 | 0.054453 | 0.054381 | 0.054028 | 0.053754 | 0.053624 | 0.053595 | 0.053577 | 0.053415 | 0.053248 | 0.053084 | 0.052921 | 0.052776 | 0.052634 | 0.052498 | 0.052366 | 0.051759 | 0.050913 | 0.050274 | 0.053698 | 0.05367 | 0.053654 | 0.053524 | 0.053388 | 0.053253 | 0.053117 | 0.053003 | 0.052891 | 0.052783 | 0.052678 | 0.052198 | 0.05147 | 0.050939
|  | COMRIE | FS |  |  |  | 0 | 0.054708 | 0.054688 | 0.054687 | 0.054686 | 0.054684 | 0.054682 | 0.05468 | 0.054671 | 0.054661 | 0.054651 | 0.054639 | 0.054608 | 0.054447 | 0.054099 | 0.053639 | 0.053614 | 0.053607 | 0.053593 | 0.053553 | 0.053467 | 0.053382 | 0.053277 | 0.05317 | 0.053064 | 0.052957 | 0.052461 | 0.05188 | 0.051144 | 0.05371 | 0.053686 | 0.05368 | 0.053669 | 0.053638 | 0.053572 | 0.053507 | 0.053424 | 0.053341 | 0.053257 | 0.053173 | 0.052788 | 0.052306 | 0.051663
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0.027368 | 1.4033 | 1.3778 | 1.3583 | 1.3257 | 1.2925 | 1.2596 | 1.227 | 1.1947 | 1.1625 | 1.1305 | 1.0999 | 0.94126 | 0.74902 | 0.48229 | 1.1907 | 1.1628 | 1.1405 | 1.103 | 1.065 | 1.0275 | 0.99043 | 0.95375 | 0.9174 | 0.88136 | 0.84687 | 0.66992 | 0.45875 | 0.17348 | 1.2703 | 1.2487 | 1.2337 | 1.2092 | 1.1755 | 1.14 | 1.1049 | 1.0703 | 1.036 | 1.002 | 0.96942 | 0.93736 | 0.90327 | 0.86971
|  | CONNEL | CT |  |  |  | 0.027368 | 1.4062 | 1.3936 | 1.3802 | 1.3579 | 1.3349 | 1.3115 | 1.289 | 1.2679 | 1.2468 | 1.226 | 1.2051 | 1.0952 | 0.9624 | 0.80095 | 1.1942 | 1.18 | 1.1646 | 1.1389 | 1.1124 | 1.0858 | 1.0603 | 1.0359 | 1.0117 | 0.98776 | 0.96409 | 0.84127 | 0.69522 | 0.52093 | 1.2722 | 1.2623 | 1.2521 | 1.2355 | 1.218 | 1.1955 | 1.1713 | 1.1484 | 1.1255 | 1.103 | 1.0807 | 1.0584 | 1.0347 | 1.0109
|  | CONNEL | LW |  |  |  | 0.027368 | 1.4033 | 1.3778 | 1.3583 | 1.3257 | 1.2925 | 1.2596 | 1.227 | 1.1947 | 1.1625 | 1.1305 | 1.0999 | 0.94126 | 0.74902 | 0.48229 | 1.1907 | 1.1628 | 1.1405 | 1.103 | 1.065 | 1.0275 | 0.99043 | 0.95375 | 0.9174 | 0.88136 | 0.84687 | 0.66992 | 0.45875 | 0.17348 | 1.2703 | 1.2487 | 1.2337 | 1.2092 | 1.1755 | 1.14 | 1.1049 | 1.0703 | 1.036 | 1.002 | 0.96942 | 0.93736 | 0.90327 | 0.86971
|  | CONNEL | ST |  |  |  | 0.027368 | 1.4193 | 1.4171 | 1.4151 | 1.4021 | 1.3888 | 1.3756 | 1.3623 | 1.3505 | 1.339 | 1.3279 | 1.317 | 1.2657 | 1.1942 | 1.1377 | 1.21 | 1.2078 | 1.2055 | 1.1903 | 1.1748 | 1.1595 | 1.1442 | 1.1303 | 1.1167 | 1.1034 | 1.0905 | 1.0298 | 0.95015 | 0.88619 | 1.2809 | 1.2788 | 1.2772 | 1.2679 | 1.2582 | 1.2483 | 1.2383 | 1.2301 | 1.222 | 1.2126 | 1.2006 | 1.144 | 1.0682 | 1.008
|  | CONNEL | FS |  |  |  | 0.027368 | 1.4201 | 1.4182 | 1.4177 | 1.4161 | 1.4127 | 1.4057 | 1.3986 | 1.3902 | 1.3817 | 1.3732 | 1.3646 | 1.3248 | 1.2773 | 1.2165 | 1.211 | 1.2091 | 1.2085 | 1.2065 | 1.2025 | 1.194 | 1.1855 | 1.1755 | 1.1655 | 1.1553 | 1.1452 | 1.0975 | 1.0428 | 0.97561 | 1.2814 | 1.2796 | 1.2793 | 1.2782 | 1.2759 | 1.2712 | 1.2665 | 1.2607 | 1.2548 | 1.2489 | 1.2429 | 1.2079 | 1.1563 | 1.0921
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 0.0042105 | 7.1808 | 7.1416 | 7.1129 | 7.0745 | 7.0307 | 6.9835 | 6.9332 | 6.8522 | 6.7431 | 6.6349 | 6.5289 | 5.9615 | 5.2619 | 4.2426 | 6.2621 | 6.1678 | 6.0869 | 5.9538 | 5.8179 | 5.684 | 5.5512 | 5.4235 | 5.2963 | 5.1705 | 5.0471 | 4.3959 | 3.612 | 2.5308 | 6.5503 | 6.4634 | 6.3894 | 6.2622 | 6.1321 | 6.0036 | 5.8751 | 5.7476 | 5.6206 | 5.4949 | 5.3717 | 5.2498 | 5.1204 | 4.9888
|  | CONON BRIDGE | CT |  |  |  | 0.0042105 | 7.1808 | 7.1513 | 7.1247 | 7.0925 | 7.0555 | 7.0142 | 6.9708 | 6.9387 | 6.9051 | 6.8714 | 6.796 | 6.3711 | 5.8518 | 5.2117 | 6.2621 | 6.2003 | 6.1376 | 6.0393 | 5.9381 | 5.8365 | 5.7355 | 5.6428 | 5.5497 | 5.4578 | 5.367 | 4.8837 | 4.306 | 3.61 | 6.5503 | 6.4929 | 6.435 | 6.3436 | 6.2464 | 6.1485 | 6.0511 | 5.9621 | 5.8727 | 5.7818 | 5.6911 | 5.6009 | 5.5044 | 5.4074
|  | CONON BRIDGE | LW |  |  |  | 0.0042105 | 7.2002 | 7.1416 | 7.1129 | 7.0745 | 7.0307 | 6.9835 | 6.9332 | 6.8522 | 6.7431 | 6.6349 | 6.5289 | 5.9615 | 5.2619 | 4.2426 | 6.2694 | 6.1678 | 6.0869 | 5.9538 | 5.8179 | 5.684 | 5.5512 | 5.4235 | 5.2963 | 5.1705 | 5.0471 | 4.3959 | 3.612 | 2.5308 | 6.5593 | 6.4634 | 6.3894 | 6.2622 | 6.1321 | 6.0036 | 5.8751 | 5.7476 | 5.6206 | 5.4949 | 5.3717 | 5.2498 | 5.1204 | 4.9888
|  | CONON BRIDGE | ST |  |  |  | 0.0042105 | 7.2035 | 7.1942 | 7.1884 | 7.1771 | 7.163 | 7.1471 | 7.1298 | 7.1212 | 7.1126 | 7.1041 | 7.0968 | 7.0599 | 6.8447 | 6.6514 | 6.3353 | 6.323 | 6.3144 | 6.2603 | 6.204 | 6.1484 | 6.0929 | 6.043 | 5.9942 | 5.9468 | 5.9016 | 5.6884 | 5.4019 | 5.1759 | 6.6169 | 6.605 | 6.5967 | 6.5483 | 6.4977 | 6.4473 | 6.3961 | 6.3488 | 6.3025 | 6.2575 | 6.2147 | 6.0124 | 5.7261 | 5.5004
|  | CONON BRIDGE | FS |  |  |  | 0.0042105 | 7.2052 | 7.1974 | 7.1954 | 7.1934 | 7.1912 | 7.1889 | 7.1865 | 7.1822 | 7.1775 | 7.1726 | 7.1673 | 7.1461 | 7.0864 | 6.9171 | 6.341 | 6.3317 | 6.3269 | 6.3203 | 6.3057 | 6.2756 | 6.2457 | 6.2097 | 6.1736 | 6.1373 | 6.1008 | 5.9272 | 5.728 | 5.4845 | 6.622 | 6.6128 | 6.6085 | 6.6025 | 6.5895 | 6.5631 | 6.5369 | 6.5052 | 6.4732 | 6.4404 | 6.4058 | 6.2417 | 6.0512 | 5.8086
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0 | 0.55784 | 0.5555 | 0.55326 | 0.55082 | 0.54821 | 0.5463 | 0.54431 | 0.54188 | 0.53861 | 0.53267 | 0.52681 | 0.49654 | 0.46046 | 0.41184 | 0.54053 | 0.53622 | 0.53187 | 0.52634 | 0.52001 | 0.51303 | 0.50612 | 0.4994 | 0.49273 | 0.4861 | 0.47957 | 0.44604 | 0.40668 | 0.35487 | 0.54226 | 0.53841 | 0.53456 | 0.52977 | 0.52486 | 0.51944 | 0.5136 | 0.50798 | 0.50239 | 0.49644 | 0.49056 | 0.48474 | 0.47867 | 0.47194
|  | CONON FALLS | CT |  |  |  | 0 | 0.55784 | 0.5555 | 0.55326 | 0.55082 | 0.54821 | 0.5463 | 0.54431 | 0.54188 | 0.53943 | 0.53697 | 0.53191 | 0.50321 | 0.47174 | 0.43484 | 0.54053 | 0.53622 | 0.53187 | 0.52634 | 0.52072 | 0.51592 | 0.51115 | 0.50492 | 0.49871 | 0.49254 | 0.48642 | 0.45502 | 0.42086 | 0.38134 | 0.54226 | 0.53841 | 0.53456 | 0.52977 | 0.52486 | 0.52075 | 0.51664 | 0.51131 | 0.50599 | 0.50071 | 0.49546 | 0.49013 | 0.48437 | 0.47859
|  | CONON FALLS | LW |  |  |  | 0 | 0.56036 | 0.5584 | 0.55668 | 0.55462 | 0.5524 | 0.55006 | 0.54764 | 0.5446 | 0.53861 | 0.53267 | 0.52681 | 0.49654 | 0.46046 | 0.41184 | 0.54269 | 0.5384 | 0.53406 | 0.52707 | 0.52001 | 0.51303 | 0.50612 | 0.4994 | 0.49273 | 0.4861 | 0.47957 | 0.44604 | 0.40668 | 0.35487 | 0.5445 | 0.54076 | 0.53705 | 0.53123 | 0.52532 | 0.51944 | 0.5136 | 0.50798 | 0.50239 | 0.49644 | 0.49056 | 0.48474 | 0.47867 | 0.47194
|  | CONON FALLS | ST |  |  |  | 0 | 0.56036 | 0.56012 | 0.56001 | 0.5597 | 0.55933 | 0.55889 | 0.55839 | 0.55821 | 0.55803 | 0.55785 | 0.55768 | 0.55692 | 0.5476 | 0.53438 | 0.54657 | 0.54625 | 0.54607 | 0.54344 | 0.54077 | 0.53812 | 0.53548 | 0.53304 | 0.53064 | 0.52828 | 0.52598 | 0.51503 | 0.50158 | 0.48695 | 0.54746 | 0.54717 | 0.547 | 0.54492 | 0.54279 | 0.54067 | 0.53854 | 0.53663 | 0.53476 | 0.53292 | 0.53112 | 0.52259 | 0.51139 | 0.49812
|  | CONON FALLS | FS |  |  |  | 0 | 0.56121 | 0.56099 | 0.56098 | 0.56097 | 0.56096 | 0.56093 | 0.56091 | 0.56082 | 0.56072 | 0.5606 | 0.56048 | 0.56015 | 0.55847 | 0.5484 | 0.54757 | 0.54731 | 0.54724 | 0.54709 | 0.54667 | 0.54485 | 0.54304 | 0.54102 | 0.53899 | 0.53696 | 0.53492 | 0.52515 | 0.51449 | 0.50224 | 0.54843 | 0.54818 | 0.54812 | 0.54801 | 0.54768 | 0.54629 | 0.5449 | 0.54334 | 0.54177 | 0.54019 | 0.53861 | 0.53108 | 0.52255 | 0.51219
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 0.052632 | 33.6518 | 33.5892 | 33.561 | 33.5217 | 33.4771 | 33.4265 | 33.3723 | 33.3289 | 33.2836 | 33.2367 | 33.19 | 32.8232 | 32.2257 | 30.4803 | 31.2711 | 31.2049 | 31.1733 | 31.1276 | 31.0767 | 31.0199 | 30.9595 | 30.9096 | 30.8576 | 30.804 | 30.7506 | 30.4036 | 29.1525 | 27.1351 | 32.3309 | 32.2637 | 32.231 | 32.1834 | 32.1305 | 32.0718 | 32.0095 | 31.9575 | 31.9035 | 31.8479 | 31.7923 | 31.7364 | 31.6646 | 31.5903
|  | CONSTABLE STREET | CT |  |  |  | 0.052632 | 33.6518 | 33.6311 | 33.6134 | 33.5898 | 33.561 | 33.5259 | 33.4874 | 33.4615 | 33.4334 | 33.4046 | 33.375 | 33.1569 | 32.7426 | 32.0975 | 31.2711 | 31.2483 | 31.2282 | 31.2001 | 31.1669 | 31.1274 | 31.0847 | 31.0541 | 31.0214 | 30.9879 | 30.9535 | 30.7208 | 30.3221 | 29.2676 | 32.331 | 32.3076 | 32.2867 | 32.2572 | 32.2226 | 32.1818 | 32.1378 | 32.1058 | 32.0716 | 32.0366 | 32.0009 | 31.9633 | 31.9148 | 31.8649
|  | CONSTABLE STREET | LW |  |  |  | 0.052632 | 33.6527 | 33.5892 | 33.561 | 33.5217 | 33.4771 | 33.4265 | 33.3723 | 33.3289 | 33.2836 | 33.2367 | 33.19 | 32.8232 | 32.2257 | 30.4803 | 31.2712 | 31.2049 | 31.1733 | 31.1276 | 31.0767 | 31.0199 | 30.9595 | 30.9096 | 30.8576 | 30.804 | 30.7506 | 30.4036 | 29.1525 | 27.1351 | 32.3309 | 32.2637 | 32.231 | 32.1834 | 32.1305 | 32.0718 | 32.0095 | 31.9575 | 31.9035 | 31.8479 | 31.7923 | 31.7364 | 31.6646 | 31.5903
|  | CONSTABLE STREET | ST |  |  |  | 0.052632 | 33.6527 | 33.643 | 33.6384 | 33.626 | 33.6109 | 33.5932 | 33.5734 | 33.566 | 33.5586 | 33.5515 | 33.5446 | 33.5115 | 33.3217 | 33.2005 | 31.2751 | 31.2652 | 31.2603 | 31.2449 | 31.2269 | 31.2063 | 31.1837 | 31.1732 | 31.1626 | 31.1524 | 31.1424 | 31.0934 | 30.8872 | 30.7679 | 32.336 | 32.326 | 32.321 | 32.3048 | 32.2858 | 32.2644 | 32.2409 | 32.2294 | 32.2178 | 32.2066 | 32.1957 | 32.1418 | 31.9304 | 31.8058
|  | CONSTABLE STREET | FS |  |  |  | 0.052632 | 33.6527 | 33.6409 | 33.6404 | 33.6397 | 33.6388 | 33.6375 | 33.6362 | 33.6311 | 33.6254 | 33.6192 | 33.6124 | 33.5942 | 33.496 | 33.2751 | 31.2748 | 31.2628 | 31.262 | 31.2609 | 31.2588 | 31.2552 | 31.2517 | 31.244 | 31.2356 | 31.2268 | 31.2173 | 31.1861 | 31.0745 | 30.8397 | 32.3356 | 32.3235 | 32.3226 | 32.3214 | 32.319 | 32.3147 | 32.3104 | 32.3019 | 32.2927 | 32.283 | 32.2727 | 32.2376 | 32.1218 | 31.8827
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0 | 0.10895 | 0.10868 | 0.10856 | 0.10839 | 0.1082 | 0.10799 | 0.10777 | 0.1076 | 0.10743 | 0.10726 | 0.10709 | 0.10586 | 0.10287 | 0.09841 | 0.10677 | 0.10649 | 0.10636 | 0.10617 | 0.10596 | 0.10574 | 0.1055 | 0.10531 | 0.10512 | 0.10481 | 0.1043 | 0.10152 | 0.098164 | 0.09343 | 0.10695 | 0.10667 | 0.10655 | 0.10638 | 0.10619 | 0.10598 | 0.10577 | 0.10559 | 0.10542 | 0.10525 | 0.10504 | 0.10455 | 0.10401 | 0.10347
|  | CONTULLICH | CT |  |  |  | 0 | 0.10895 | 0.10886 | 0.10879 | 0.10868 | 0.10855 | 0.1084 | 0.10825 | 0.10814 | 0.10804 | 0.10793 | 0.10782 | 0.10713 | 0.10604 | 0.10362 | 0.10677 | 0.10667 | 0.10659 | 0.10647 | 0.10633 | 0.10617 | 0.106 | 0.10588 | 0.10577 | 0.10565 | 0.10553 | 0.10422 | 0.10193 | 0.099125 | 0.10695 | 0.10685 | 0.10678 | 0.10667 | 0.10654 | 0.1064 | 0.10624 | 0.10613 | 0.10603 | 0.10592 | 0.10581 | 0.1057 | 0.10556 | 0.10542
|  | CONTULLICH | LW |  |  |  | 0 | 0.10895 | 0.10868 | 0.10856 | 0.10839 | 0.1082 | 0.10799 | 0.10777 | 0.1076 | 0.10743 | 0.10726 | 0.10709 | 0.10586 | 0.10287 | 0.09841 | 0.10677 | 0.10649 | 0.10636 | 0.10617 | 0.10596 | 0.10574 | 0.1055 | 0.10531 | 0.10512 | 0.10481 | 0.1043 | 0.10152 | 0.098164 | 0.09343 | 0.10695 | 0.10667 | 0.10655 | 0.10638 | 0.10619 | 0.10598 | 0.10577 | 0.10559 | 0.10542 | 0.10525 | 0.10504 | 0.10455 | 0.10401 | 0.10347
|  | CONTULLICH | ST |  |  |  | 0 | 0.10895 | 0.10892 | 0.1089 | 0.10886 | 0.10881 | 0.10875 | 0.10868 | 0.10866 | 0.10863 | 0.1086 | 0.10858 | 0.10848 | 0.10796 | 0.1077 | 0.10678 | 0.10675 | 0.10673 | 0.10668 | 0.10662 | 0.10655 | 0.10648 | 0.10644 | 0.10641 | 0.10638 | 0.10634 | 0.1062 | 0.10566 | 0.10509 | 0.10695 | 0.10691 | 0.1069 | 0.10685 | 0.1068 | 0.10674 | 0.10667 | 0.10665 | 0.10662 | 0.1066 | 0.10657 | 0.10647 | 0.10595 | 0.10569
|  | CONTULLICH | FS |  |  |  | 0 | 0.10895 | 0.10892 | 0.10892 | 0.10892 | 0.10892 | 0.10892 | 0.10891 | 0.1089 | 0.10889 | 0.10887 | 0.10885 | 0.10881 | 0.10858 | 0.10808 | 0.10678 | 0.10675 | 0.10675 | 0.10675 | 0.10675 | 0.10674 | 0.10673 | 0.10671 | 0.10669 | 0.10667 | 0.10665 | 0.10657 | 0.10631 | 0.10579 | 0.10695 | 0.10692 | 0.10691 | 0.10691 | 0.10691 | 0.10691 | 0.1069 | 0.10689 | 0.10688 | 0.10686 | 0.10685 | 0.1068 | 0.10657 | 0.10607
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | 0.042105 | 1.3384 | 1.3306 | 1.3256 | 1.3184 | 1.3104 | 1.3019 | 1.2931 | 1.2858 | 1.2776 | 1.2694 | 1.2613 | 1.19 | 1.0419 | 0.84667 | 1.3034 | 1.2953 | 1.2905 | 1.2835 | 1.2759 | 1.2677 | 1.2591 | 1.2522 | 1.2298 | 1.2021 | 1.1747 | 1.0336 | 0.87274 | 0.66485 | 1.4242 | 1.4053 | 1.3884 | 1.36 | 1.3313 | 1.303 | 1.2749 | 1.2477 | 1.2199 | 1.1923 | 1.165 | 1.1382 | 1.1101 | 1.0818
|  | CORRAN | CT |  |  |  | 0.042105 | 1.3384 | 1.3344 | 1.3303 | 1.3248 | 1.3185 | 1.3116 | 1.3043 | 1.2989 | 1.2934 | 1.2879 | 1.2824 | 1.2495 | 1.1941 | 1.072 | 1.3034 | 1.299 | 1.2951 | 1.2898 | 1.2837 | 1.277 | 1.27 | 1.2647 | 1.2594 | 1.2541 | 1.2488 | 1.1525 | 1.0402 | 0.90937 | 1.4242 | 1.4129 | 1.4006 | 1.3804 | 1.3596 | 1.3388 | 1.318 | 1.2987 | 1.2794 | 1.2603 | 1.2414 | 1.2225 | 1.2028 | 1.1829
|  | CORRAN | LW |  |  |  | 0.042105 | 1.34 | 1.3306 | 1.3256 | 1.3184 | 1.3104 | 1.3019 | 1.2931 | 1.2858 | 1.2776 | 1.2694 | 1.2613 | 1.19 | 1.0419 | 0.84667 | 1.3049 | 1.2953 | 1.2905 | 1.2835 | 1.2759 | 1.2677 | 1.2591 | 1.2522 | 1.2298 | 1.2021 | 1.1747 | 1.0336 | 0.87274 | 0.66485 | 1.4243 | 1.4053 | 1.3884 | 1.36 | 1.3313 | 1.303 | 1.2749 | 1.2477 | 1.2199 | 1.1923 | 1.165 | 1.1382 | 1.1101 | 1.0818
|  | CORRAN | ST |  |  |  | 0.042105 | 1.3409 | 1.3398 | 1.3392 | 1.3378 | 1.3356 | 1.3328 | 1.3297 | 1.3281 | 1.3265 | 1.3249 | 1.3234 | 1.3164 | 1.2956 | 1.2834 | 1.3061 | 1.3049 | 1.3044 | 1.3027 | 1.3003 | 1.2976 | 1.2947 | 1.2932 | 1.2918 | 1.2904 | 1.289 | 1.2826 | 1.2365 | 1.1834 | 1.4316 | 1.4302 | 1.4293 | 1.4216 | 1.4093 | 1.397 | 1.3847 | 1.3734 | 1.3623 | 1.3514 | 1.3407 | 1.2897 | 1.2267 | 1.1738
|  | CORRAN | FS |  |  |  | 0.042105 | 1.3409 | 1.3399 | 1.3398 | 1.3398 | 1.3397 | 1.3396 | 1.3394 | 1.3384 | 1.3373 | 1.3362 | 1.335 | 1.3306 | 1.3199 | 1.3002 | 1.3061 | 1.305 | 1.305 | 1.3049 | 1.3049 | 1.3046 | 1.3041 | 1.3031 | 1.3022 | 1.3012 | 1.3001 | 1.2962 | 1.2861 | 1.2583 | 1.4322 | 1.4309 | 1.4306 | 1.4301 | 1.4292 | 1.4249 | 1.4182 | 1.4096 | 1.401 | 1.3924 | 1.3837 | 1.3423 | 1.2974 | 1.2483
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 0.010526 | 2.5999 | 2.5821 | 2.5659 | 2.5483 | 2.5297 | 2.51 | 2.4898 | 2.4715 | 2.4529 | 2.4303 | 2.3711 | 2.061 | 1.7042 | 1.2654 | 2.716 | 2.6983 | 2.682 | 2.6645 | 2.6 | 2.5356 | 2.4703 | 2.4032 | 2.3354 | 2.2679 | 2.201 | 1.8527 | 1.4573 | 0.98008 | 2.6153 | 2.5975 | 2.5813 | 2.563 | 2.5423 | 2.5206 | 2.492 | 2.4374 | 2.382 | 2.3269 | 2.2716 | 2.2112 | 2.1459 | 2.0794
|  | COSHIEVILLE | CT |  |  |  | 0.010526 | 2.5999 | 2.5821 | 2.5659 | 2.5483 | 2.5297 | 2.51 | 2.4898 | 2.4715 | 2.4529 | 2.4343 | 2.4157 | 2.1773 | 1.8838 | 1.5474 | 2.716 | 2.6983 | 2.682 | 2.6645 | 2.6133 | 2.5593 | 2.5054 | 2.4507 | 2.3957 | 2.3408 | 2.2862 | 2.002 | 1.6814 | 1.3183 | 2.6153 | 2.5975 | 2.5813 | 2.563 | 2.5423 | 2.5206 | 2.4984 | 2.4622 | 2.4158 | 2.3696 | 2.3235 | 2.2774 | 2.2292 | 2.1799
|  | COSHIEVILLE | LW |  |  |  | 0.010526 | 2.6218 | 2.605 | 2.5944 | 2.5815 | 2.5668 | 2.5513 | 2.5344 | 2.5197 | 2.49 | 2.4303 | 2.3711 | 2.061 | 1.7042 | 1.2654 | 2.7379 | 2.7212 | 2.7105 | 2.6648 | 2.6 | 2.5356 | 2.4703 | 2.4032 | 2.3354 | 2.2679 | 2.201 | 1.8527 | 1.4573 | 0.98008 | 2.6372 | 2.6204 | 2.6098 | 2.5941 | 2.5764 | 2.546 | 2.492 | 2.4374 | 2.382 | 2.3269 | 2.2716 | 2.2112 | 2.1459 | 2.0794
|  | COSHIEVILLE | ST |  |  |  | 0.010526 | 2.626 | 2.6219 | 2.6186 | 2.614 | 2.6081 | 2.6018 | 2.5951 | 2.5905 | 2.5859 | 2.5814 | 2.5769 | 2.5549 | 2.4615 | 2.3305 | 2.7421 | 2.738 | 2.7347 | 2.7301 | 2.7243 | 2.7179 | 2.7109 | 2.6813 | 2.652 | 2.6229 | 2.5942 | 2.4546 | 2.3002 | 2.1524 | 2.6414 | 2.6373 | 2.634 | 2.6294 | 2.6235 | 2.6172 | 2.6096 | 2.6036 | 2.5975 | 2.5915 | 2.5856 | 2.485 | 2.3575 | 2.2301
|  | COSHIEVILLE | FS |  |  |  | 0.010526 | 2.6285 | 2.6253 | 2.6227 | 2.621 | 2.6192 | 2.6173 | 2.6155 | 2.6132 | 2.6108 | 2.6083 | 2.6058 | 2.5917 | 2.5681 | 2.5226 | 2.7447 | 2.7415 | 2.7389 | 2.7371 | 2.7353 | 2.7335 | 2.7317 | 2.7293 | 2.7269 | 2.7245 | 2.7043 | 2.5989 | 2.4859 | 2.3685 | 2.6439 | 2.6408 | 2.6382 | 2.6364 | 2.6346 | 2.6328 | 2.6309 | 2.6286 | 2.6262 | 2.6229 | 2.6192 | 2.5998 | 2.5119 | 2.4144
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 0.13158 | 10.2318 | 10.2014 | 10.1738 | 10.1423 | 10.1076 | 10.0698 | 10.0313 | 9.9981 | 9.9643 | 9.9304 | 9.8963 | 9.54 | 8.9202 | 8.0676 | 9.4091 | 9.376 | 9.3453 | 9.3088 | 9.2691 | 9.2265 | 9.1834 | 9.1111 | 9.0018 | 8.8938 | 8.788 | 8.2315 | 7.5481 | 6.617 | 9.6612 | 9.6288 | 9.581 | 9.4631 | 9.3437 | 9.2253 | 9.1105 | 8.9955 | 8.8812 | 8.7683 | 8.6577 | 8.5485 | 8.432 | 8.3146
|  | COUPAR ANGUS | CT |  |  |  | 0.13158 | 10.2318 | 10.2014 | 10.1738 | 10.1423 | 10.1076 | 10.0698 | 10.0313 | 9.9981 | 9.9643 | 9.9304 | 9.8963 | 9.6936 | 9.314 | 8.7147 | 9.4091 | 9.376 | 9.3453 | 9.3088 | 9.2691 | 9.2265 | 9.1834 | 9.1454 | 9.107 | 9.0686 | 8.9866 | 8.5408 | 8.0154 | 7.3866 | 9.6612 | 9.6288 | 9.599 | 9.5134 | 9.4179 | 9.3218 | 9.2285 | 9.1373 | 9.0471 | 8.9584 | 8.8712 | 8.784 | 8.6914 | 8.5984
|  | COUPAR ANGUS | LW |  |  |  | 0.13158 | 10.2613 | 10.2181 | 10.1957 | 10.1659 | 10.1321 | 10.0951 | 10.0565 | 10.0235 | 9.9893 | 9.9547 | 9.9197 | 9.54 | 8.9202 | 8.0676 | 9.4373 | 9.3903 | 9.3634 | 9.3263 | 9.2855 | 9.2417 | 9.1968 | 9.1111 | 9.0018 | 8.8938 | 8.788 | 8.2315 | 7.5481 | 6.617 | 9.6898 | 9.6438 | 9.581 | 9.4631 | 9.3437 | 9.2253 | 9.1105 | 8.9955 | 8.8812 | 8.7683 | 8.6577 | 8.5485 | 8.432 | 8.3146
|  | COUPAR ANGUS | ST |  |  |  | 0.13158 | 10.2688 | 10.2589 | 10.2524 | 10.2419 | 10.2292 | 10.2153 | 10.2003 | 10.1915 | 10.1827 | 10.174 | 10.1655 | 10.1246 | 10.0209 | 9.9517 | 9.4495 | 9.4392 | 9.4321 | 9.4184 | 9.4026 | 9.3855 | 9.3676 | 9.3555 | 9.3435 | 9.3317 | 9.3201 | 9.265 | 9.0367 | 8.8235 | 9.7007 | 9.6905 | 9.6836 | 9.6708 | 9.6558 | 9.6317 | 9.5809 | 9.5324 | 9.4845 | 9.4375 | 9.3923 | 9.1797 | 8.9163 | 8.6935
|  | COUPAR ANGUS | FS |  |  |  | 0.13158 | 10.2714 | 10.2651 | 10.2624 | 10.2596 | 10.2567 | 10.2537 | 10.2506 | 10.2461 | 10.2414 | 10.2364 | 10.2312 | 10.2048 | 10.1528 | 10.0596 | 9.4523 | 9.4457 | 9.4425 | 9.4392 | 9.4352 | 9.4301 | 9.425 | 9.418 | 9.4108 | 9.4034 | 9.3958 | 9.3578 | 9.2951 | 9.1295 | 9.7035 | 9.6969 | 9.6939 | 9.6907 | 9.687 | 9.6824 | 9.6779 | 9.6716 | 9.6482 | 9.6137 | 9.579 | 9.4125 | 9.2302 | 9.0127
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 1.9305 | 25.9318 | 25.859 | 25.8263 | 25.7765 | 25.5487 | 25.3291 | 25.1236 | 24.9217 | 24.7266 | 24.5376 | 24.3628 | 23.4922 | 22.5044 | 21.1204 | 24.8595 | 24.6251 | 24.4151 | 24.1332 | 23.8586 | 23.5955 | 23.3511 | 23.1078 | 22.8734 | 22.6469 | 22.4381 | 21.4138 | 20.2848 | 18.7823 | 25.4477 | 25.218 | 25.0131 | 24.7382 | 24.4701 | 24.213 | 23.974 | 23.7365 | 23.5076 | 23.2863 | 23.0822 | 22.8905 | 22.6875 | 22.4846
|  | CRAIGIEBUCKLER | CT |  |  |  | 1.9305 | 25.9318 | 25.9064 | 25.8848 | 25.8558 | 25.8205 | 25.7453 | 25.5964 | 25.4591 | 25.3242 | 25.1968 | 25.0761 | 24.4594 | 23.7764 | 22.9487 | 24.9272 | 24.8019 | 24.6659 | 24.4822 | 24.2899 | 24.0941 | 23.9173 | 23.7511 | 23.5883 | 23.435 | 23.2903 | 22.5617 | 21.7794 | 20.8576 | 25.5134 | 25.391 | 25.2584 | 25.0792 | 24.8915 | 24.7002 | 24.5272 | 24.3651 | 24.2061 | 24.0564 | 23.9151 | 23.7742 | 23.6279 | 23.4853
|  | CRAIGIEBUCKLER | LW |  |  |  | 1.9305 | 25.9327 | 25.859 | 25.8263 | 25.7765 | 25.5487 | 25.3291 | 25.1236 | 24.9217 | 24.7266 | 24.5376 | 24.3628 | 23.4922 | 22.5044 | 21.1204 | 24.8595 | 24.6251 | 24.4151 | 24.1332 | 23.8586 | 23.5955 | 23.3511 | 23.1078 | 22.8734 | 22.6469 | 22.4381 | 21.4138 | 20.2848 | 18.7823 | 25.4477 | 25.218 | 25.0131 | 24.7382 | 24.4701 | 24.213 | 23.974 | 23.7365 | 23.5076 | 23.2863 | 23.0822 | 22.8905 | 22.6875 | 22.4846
|  | CRAIGIEBUCKLER | ST |  |  |  | 1.9305 | 25.9335 | 25.9243 | 25.9199 | 25.908 | 25.8936 | 25.8767 | 25.8579 | 25.8508 | 25.8437 | 25.8369 | 25.8207 | 25.4979 | 25.1082 | 24.808 | 24.9297 | 24.9205 | 24.9161 | 24.8544 | 24.7515 | 24.6474 | 24.5479 | 24.4524 | 24.3563 | 24.2639 | 24.1759 | 23.7751 | 23.3206 | 22.9606 | 25.6074 | 25.5724 | 25.5371 | 25.442 | 25.3417 | 25.2401 | 25.143 | 25.0501 | 24.9566 | 24.8667 | 24.7811 | 24.3911 | 23.9457 | 23.594
|  | CRAIGIEBUCKLER | FS |  |  |  | 1.9305 | 25.9335 | 25.9248 | 25.9244 | 25.924 | 25.9233 | 25.9223 | 25.9214 | 25.9177 | 25.9135 | 25.9089 | 25.9039 | 25.8086 | 25.5309 | 25.1883 | 24.9297 | 24.921 | 24.9206 | 24.9202 | 24.9059 | 24.8423 | 24.7799 | 24.7073 | 24.6315 | 24.5565 | 24.4821 | 24.1447 | 23.8113 | 23.4174 | 25.6185 | 25.5883 | 25.565 | 25.5355 | 25.4924 | 25.4307 | 25.3701 | 25.2995 | 25.2258 | 25.1528 | 25.0804 | 24.7525 | 24.4269 | 24.0401
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 0.61368 | 26.3512 | 26.3169 | 26.3009 | 26.2786 | 26.2533 | 26.2249 | 26.1946 | 26.1705 | 26.1454 | 26.1188 | 26.0923 | 25.6863 | 24.8618 | 23.7483 | 25.8615 | 25.8212 | 25.8004 | 25.7712 | 25.7392 | 25.7043 | 25.6681 | 25.5458 | 25.3801 | 25.2166 | 25.0598 | 24.2567 | 23.3364 | 22.1254 | 26.0985 | 26.0642 | 26.0482 | 26.026 | 26.0007 | 25.9723 | 25.942 | 25.9179 | 25.8318 | 25.6723 | 25.5193 | 25.3716 | 25.212 | 25.0523
|  | CRAIGINCHES | CT |  |  |  | 0.61368 | 26.3512 | 26.3385 | 26.3276 | 26.3131 | 26.2956 | 26.2746 | 26.2518 | 26.2364 | 26.22 | 26.2032 | 26.186 | 26.0687 | 25.7924 | 25.0865 | 25.8616 | 25.8461 | 25.832 | 25.813 | 25.7907 | 25.7651 | 25.738 | 25.7182 | 25.6973 | 25.6763 | 25.606 | 25.0373 | 24.3912 | 23.6169 | 26.0985 | 26.0858 | 26.0749 | 26.0605 | 26.043 | 26.022 | 25.9992 | 25.9838 | 25.9673 | 25.9506 | 25.9334 | 25.9153 | 25.8307 | 25.7189
|  | CRAIGINCHES | LW |  |  |  | 0.61368 | 26.3528 | 26.3169 | 26.3009 | 26.2786 | 26.2533 | 26.2249 | 26.1946 | 26.1705 | 26.1454 | 26.1188 | 26.0923 | 25.6863 | 24.8618 | 23.7483 | 25.8615 | 25.8212 | 25.8004 | 25.7712 | 25.7392 | 25.7043 | 25.6681 | 25.5458 | 25.3801 | 25.2166 | 25.0598 | 24.2567 | 23.3364 | 22.1254 | 26.1002 | 26.0642 | 26.0482 | 26.026 | 26.0007 | 25.9723 | 25.942 | 25.9179 | 25.8318 | 25.6723 | 25.5193 | 25.3716 | 25.212 | 25.0523
|  | CRAIGINCHES | ST |  |  |  | 0.61368 | 26.3537 | 26.3483 | 26.3458 | 26.3388 | 26.3304 | 26.3206 | 26.3096 | 26.3055 | 26.3014 | 26.2974 | 26.2936 | 26.2755 | 26.1754 | 26.1221 | 25.8668 | 25.8607 | 25.8574 | 25.8478 | 25.8366 | 25.824 | 25.8103 | 25.8033 | 25.7962 | 25.7893 | 25.7827 | 25.7509 | 25.4509 | 25.1081 | 26.1011 | 26.0957 | 26.0931 | 26.0862 | 26.0778 | 26.068 | 26.057 | 26.0529 | 26.0487 | 26.0448 | 26.041 | 26.0229 | 25.9014 | 25.5671
|  | CRAIGINCHES | FS |  |  |  | 0.61368 | 26.3537 | 26.3476 | 26.3474 | 26.347 | 26.3466 | 26.3459 | 26.3452 | 26.3426 | 26.3397 | 26.3365 | 26.333 | 26.3237 | 26.2735 | 26.1611 | 25.8671 | 25.8604 | 25.8595 | 25.8584 | 25.8566 | 25.8539 | 25.8512 | 25.8463 | 25.841 | 25.8355 | 25.8297 | 25.8094 | 25.7491 | 25.4964 | 26.1011 | 26.095 | 26.0947 | 26.0944 | 26.0939 | 26.0932 | 26.0926 | 26.09 | 26.0871 | 26.0838 | 26.0803 | 26.071 | 26.0209 | 25.9084
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | YES | YES | 0.62 | 16.159 | 16.1044 | 16.017 | 15.5177 | 15.0433 | 14.5996 | 14.2106 | 13.811 | 13.4373 | 13.0864 | 12.7821 | 11.4393 | 10.167 | 8.644 | 14.4389 | 13.9258 | 13.4216 | 12.8375 | 12.2885 | 11.7762 | 11.3289 | 10.8672 | 10.436 | 10.0316 | 9.6818 | 8.1509 | 6.7277 | 5.0711 | 14.992 | 14.491 | 13.9866 | 13.4023 | 12.8531 | 12.3407 | 11.8932 | 11.4314 | 11.0001 | 10.5956 | 10.2457 | 9.9364 | 9.6234 | 9.3162
|  | CRAIGTON | CT |  |  |  | 0.62 | 16.159 | 16.1332 | 16.1105 | 16.0816 | 15.9042 | 15.5606 | 15.2758 | 15.0007 | 14.7344 | 14.4963 | 14.2801 | 13.2655 | 12.3523 | 11.352 | 14.4901 | 14.3653 | 14.047 | 13.6795 | 13.2914 | 12.8926 | 12.5655 | 12.2475 | 11.9401 | 11.6657 | 11.4171 | 10.2595 | 9.2383 | 8.14 | 15.1047 | 14.9213 | 14.6122 | 14.2446 | 13.8563 | 13.4574 | 13.1302 | 12.8122 | 12.5046 | 12.2302 | 11.9815 | 11.7332 | 11.4903 | 11.2614
|  | CRAIGTON | LW |  |  |  | 0.62 | 16.1683 | 16.1044 | 16.017 | 15.5177 | 15.0433 | 14.5996 | 14.2106 | 13.811 | 13.4373 | 13.0864 | 12.7821 | 11.4393 | 10.167 | 8.644 | 14.4389 | 13.9258 | 13.4216 | 12.8375 | 12.2885 | 11.7762 | 11.3289 | 10.8672 | 10.436 | 10.0316 | 9.6818 | 8.1509 | 6.7277 | 5.0711 | 14.992 | 14.491 | 13.9866 | 13.4023 | 12.8531 | 12.3407 | 11.8932 | 11.4314 | 11.0001 | 10.5956 | 10.2457 | 9.9364 | 9.6234 | 9.3162
|  | CRAIGTON | ST |  |  |  | 0.62 | 16.17 | 16.1605 | 16.1552 | 16.1435 | 16.1296 | 16.1137 | 16.0961 | 16.0885 | 16.0612 | 15.9068 | 15.7588 | 15.0913 | 14.4996 | 14.0097 | 14.5083 | 14.4948 | 14.4846 | 14.4325 | 14.2418 | 14.0417 | 13.8599 | 13.6698 | 13.4737 | 13.2891 | 13.1151 | 12.3373 | 11.6653 | 11.1026 | 15.1157 | 15.1062 | 15.1008 | 14.9843 | 14.8047 | 14.6068 | 14.425 | 14.2349 | 14.0387 | 13.8541 | 13.68 | 12.9019 | 12.2298 | 11.6669
|  | CRAIGTON | FS |  |  |  | 0.62 | 16.1717 | 16.1644 | 16.1624 | 16.1603 | 16.158 | 16.1555 | 16.1531 | 16.1483 | 16.143 | 16.1375 | 16.1324 | 15.6343 | 15.1797 | 14.6824 | 14.5118 | 14.5011 | 14.4954 | 14.4891 | 14.4817 | 14.3521 | 14.2243 | 14.0793 | 13.924 | 13.7722 | 13.6246 | 12.9607 | 12.4385 | 11.8779 | 15.1174 | 15.1101 | 15.108 | 15.106 | 15.0329 | 14.9107 | 14.7883 | 14.6445 | 14.4892 | 14.3373 | 14.1896 | 13.5255 | 13.0032 | 12.4425
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 0.035789 | 16.1514 | 16.103 | 16.0585 | 16.0062 | 15.9482 | 15.8799 | 15.8067 | 15.7457 | 15.6831 | 15.6196 | 15.5561 | 15.1644 | 14.0364 | 12.291 | 15.4994 | 15.4509 | 15.4064 | 15.3541 | 15.2961 | 15.2279 | 15.1546 | 15.0937 | 15.031 | 14.9675 | 14.904 | 13.8902 | 12.5074 | 10.6501 | 15.5488 | 15.5003 | 15.4558 | 15.4035 | 15.3455 | 15.2773 | 15.204 | 15.1057 | 14.9206 | 14.7361 | 14.525 | 14.3115 | 14.0825 | 13.8518
|  | CRIEFF | CT |  |  |  | 0.035789 | 16.1514 | 16.103 | 16.0585 | 16.0062 | 15.9482 | 15.8838 | 15.8163 | 15.7628 | 15.7082 | 15.6533 | 15.5972 | 15.2557 | 14.7584 | 13.8366 | 15.4994 | 15.4509 | 15.4064 | 15.3541 | 15.2961 | 15.2317 | 15.1642 | 15.1108 | 15.0561 | 15.0012 | 14.9451 | 14.6036 | 13.6099 | 12.3603 | 15.5488 | 15.5003 | 15.4558 | 15.4035 | 15.3455 | 15.2811 | 15.2136 | 15.1602 | 15.1055 | 15.0506 | 14.9368 | 14.7969 | 14.6465 | 14.4911
|  | CRIEFF | LW |  |  |  | 0.035789 | 16.1919 | 16.1095 | 16.0684 | 16.0123 | 15.9491 | 15.8799 | 15.8067 | 15.7457 | 15.6831 | 15.6196 | 15.5561 | 15.1644 | 14.0364 | 12.291 | 15.5398 | 15.4574 | 15.4163 | 15.3602 | 15.297 | 15.2279 | 15.1546 | 15.0937 | 15.031 | 14.9675 | 14.904 | 13.8902 | 12.5074 | 10.6501 | 15.5892 | 15.5069 | 15.4657 | 15.4096 | 15.3464 | 15.2773 | 15.204 | 15.1057 | 14.9206 | 14.7361 | 14.525 | 14.3115 | 14.0825 | 13.8518
|  | CRIEFF | ST |  |  |  | 0.035789 | 16.1994 | 16.1836 | 16.1729 | 16.1551 | 16.1327 | 16.1077 | 16.0806 | 16.067 | 16.0535 | 16.0402 | 16.0273 | 15.9639 | 15.7683 | 15.6469 | 15.5474 | 15.5315 | 15.5209 | 15.503 | 15.4806 | 15.4556 | 15.4285 | 15.415 | 15.4014 | 15.3881 | 15.3752 | 15.3118 | 15.1162 | 14.9948 | 15.5968 | 15.5809 | 15.5703 | 15.5524 | 15.5301 | 15.505 | 15.4779 | 15.4644 | 15.4508 | 15.4375 | 15.4246 | 15.3612 | 14.9515 | 14.529
|  | CRIEFF | FS |  |  |  | 0.035789 | 16.2037 | 16.1915 | 16.1868 | 16.1821 | 16.1771 | 16.1719 | 16.1666 | 16.1583 | 16.1494 | 16.14 | 16.1311 | 16.0935 | 15.995 | 15.8043 | 15.5516 | 15.5394 | 15.5348 | 15.53 | 15.5251 | 15.5198 | 15.5145 | 15.5062 | 15.4973 | 15.488 | 15.479 | 15.4415 | 15.343 | 15.1522 | 15.601 | 15.5888 | 15.5842 | 15.5794 | 15.5745 | 15.5692 | 15.5639 | 15.5556 | 15.5467 | 15.5374 | 15.5284 | 15.4909 | 15.3924 | 15.0577
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0 | 1.1218 | 1.1129 | 1.107 | 1.0979 | 1.0883 | 1.0783 | 1.0683 | 1.0591 | 1.044 | 1.0239 | 1.0041 | 0.90363 | 0.7815 | 0.62249 | 1.0938 | 1.077 | 1.0623 | 1.0377 | 1.0128 | 0.98824 | 0.9639 | 0.93934 | 0.91495 | 0.89073 | 0.86685 | 0.74675 | 0.60444 | 0.42557 | 1.1398 | 1.1244 | 1.1113 | 1.0876 | 1.0633 | 1.0392 | 1.0153 | 0.99125 | 0.96736 | 0.94363 | 0.92023 | 0.89711 | 0.87303 | 0.84966
|  | CRINAN | CT |  |  |  | 0 | 1.1218 | 1.117 | 1.1123 | 1.1054 | 1.0979 | 1.0901 | 1.082 | 1.0753 | 1.0685 | 1.0618 | 1.0551 | 0.98685 | 0.90392 | 0.80699 | 1.0942 | 1.0845 | 1.0737 | 1.056 | 1.0379 | 1.0197 | 1.0017 | 0.98467 | 0.96775 | 0.95098 | 0.93435 | 0.84829 | 0.75194 | 0.64193 | 1.1401 | 1.1312 | 1.1216 | 1.1056 | 1.0878 | 1.07 | 1.0523 | 1.0356 | 1.019 | 1.0026 | 0.9863 | 0.97005 | 0.95313 | 0.93613
|  | CRINAN | LW |  |  |  | 0 | 1.1223 | 1.1129 | 1.107 | 1.0979 | 1.0883 | 1.0783 | 1.0683 | 1.0591 | 1.044 | 1.0239 | 1.0041 | 0.90363 | 0.7815 | 0.62249 | 1.0938 | 1.077 | 1.0623 | 1.0377 | 1.0128 | 0.98824 | 0.9639 | 0.93934 | 0.91495 | 0.89073 | 0.86685 | 0.74675 | 0.60444 | 0.42557 | 1.1398 | 1.1244 | 1.1113 | 1.0876 | 1.0633 | 1.0392 | 1.0153 | 0.99125 | 0.96736 | 0.94363 | 0.92023 | 0.89711 | 0.87303 | 0.84966
|  | CRINAN | ST |  |  |  | 0 | 1.1249 | 1.1237 | 1.123 | 1.1196 | 1.1161 | 1.1123 | 1.1084 | 1.1056 | 1.1027 | 1.1 | 1.0973 | 1.0845 | 1.0495 | 1.011 | 1.1047 | 1.1027 | 1.1011 | 1.0904 | 1.0796 | 1.0688 | 1.058 | 1.048 | 1.0381 | 1.0284 | 1.0189 | 0.97321 | 0.91831 | 0.87134 | 1.1492 | 1.1473 | 1.1459 | 1.1366 | 1.1271 | 1.1176 | 1.1077 | 1.0979 | 1.0882 | 1.0787 | 1.0694 | 1.0248 | 0.97098 | 0.92501
|  | CRINAN | FS |  |  |  | 0 | 1.1254 | 1.1244 | 1.1241 | 1.1237 | 1.1229 | 1.1214 | 1.1199 | 1.1179 | 1.1158 | 1.1137 | 1.1115 | 1.102 | 1.0878 | 1.0616 | 1.1071 | 1.1052 | 1.104 | 1.1026 | 1.0993 | 1.0933 | 1.0873 | 1.0796 | 1.072 | 1.0643 | 1.0566 | 1.0195 | 0.97918 | 0.93288 | 1.1512 | 1.1495 | 1.1485 | 1.1473 | 1.1444 | 1.1392 | 1.1341 | 1.1275 | 1.1208 | 1.1139 | 1.1063 | 1.0702 | 1.0307 | 0.98525
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.7223 | 2.7193 | 2.7165 | 2.7132 | 2.7096 | 2.6913 | 2.6686 | 2.6454 | 2.6231 | 2.6024 | 2.5834 | 2.4938 | 2.4036 | 2.2942 | 2.6549 | 2.6519 | 2.6491 | 2.6434 | 2.6126 | 2.5838 | 2.5578 | 2.5312 | 2.5056 | 2.4818 | 2.4601 | 2.3589 | 2.2587 | 2.1405 | 2.6634 | 2.6603 | 2.6575 | 2.6304 | 2.6006 | 2.5727 | 2.5474 | 2.5217 | 2.4969 | 2.4739 | 2.4528 | 2.4336 | 2.4146 | 2.3946
|  | CROMALT | CT |  |  |  | 0 | 2.7223 | 2.7193 | 2.7165 | 2.7132 | 2.7096 | 2.7057 | 2.7017 | 2.6984 | 2.6839 | 2.6687 | 2.6542 | 2.5843 | 2.5141 | 2.4387 | 2.6549 | 2.6519 | 2.6491 | 2.6459 | 2.6423 | 2.6356 | 2.6157 | 2.5965 | 2.5773 | 2.5599 | 2.5435 | 2.4649 | 2.3878 | 2.3061 | 2.6634 | 2.6603 | 2.6575 | 2.6543 | 2.6453 | 2.6225 | 2.6032 | 2.5846 | 2.5659 | 2.5491 | 2.5332 | 2.5173 | 2.5018 | 2.4871
|  | CROMALT | LW |  |  |  | 0 | 2.7257 | 2.7209 | 2.7183 | 2.7151 | 2.7115 | 2.6913 | 2.6686 | 2.6454 | 2.6231 | 2.6024 | 2.5834 | 2.4938 | 2.4036 | 2.2942 | 2.6583 | 2.6535 | 2.651 | 2.6434 | 2.6126 | 2.5838 | 2.5578 | 2.5312 | 2.5056 | 2.4818 | 2.4601 | 2.3589 | 2.2587 | 2.1405 | 2.6667 | 2.662 | 2.6594 | 2.6304 | 2.6006 | 2.5727 | 2.5474 | 2.5217 | 2.4969 | 2.4739 | 2.4528 | 2.4336 | 2.4146 | 2.3946
|  | CROMALT | ST |  |  |  | 0 | 2.7265 | 2.7252 | 2.7249 | 2.7243 | 2.7226 | 2.7208 | 2.7189 | 2.7177 | 2.7164 | 2.7152 | 2.714 | 2.7028 | 2.6586 | 2.6212 | 2.6592 | 2.6578 | 2.6576 | 2.6569 | 2.6552 | 2.6534 | 2.6515 | 2.6503 | 2.6491 | 2.6478 | 2.6466 | 2.5972 | 2.5475 | 2.505 | 2.6676 | 2.6662 | 2.666 | 2.6653 | 2.6637 | 2.6619 | 2.66 | 2.6587 | 2.6575 | 2.6465 | 2.6358 | 2.5856 | 2.5372 | 2.496
|  | CROMALT | FS |  |  |  | 0 | 2.7265 | 2.726 | 2.726 | 2.726 | 2.7259 | 2.7259 | 2.7258 | 2.7256 | 2.7254 | 2.7251 | 2.7248 | 2.7241 | 2.7201 | 2.6892 | 2.6592 | 2.6587 | 2.6586 | 2.6586 | 2.6586 | 2.6585 | 2.6585 | 2.6583 | 2.658 | 2.6577 | 2.6575 | 2.6492 | 2.6169 | 2.5806 | 2.6676 | 2.6671 | 2.6671 | 2.667 | 2.667 | 2.6669 | 2.6669 | 2.6667 | 2.6664 | 2.6662 | 2.6659 | 2.6363 | 2.605 | 2.5697
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 0 | 16.8366 | 16.7919 | 16.7627 | 16.7233 | 16.6781 | 16.6292 | 16.577 | 16.5349 | 16.4923 | 16.4481 | 16.4047 | 16.1369 | 15.3089 | 14.1018 | 15.4383 | 15.3906 | 15.3585 | 15.3139 | 15.2638 | 15.21 | 15.1532 | 15.1062 | 15.0587 | 14.943 | 14.8041 | 14.067 | 13.175 | 11.9408 | 16.068 | 16.0232 | 15.994 | 15.9546 | 15.9095 | 15.8606 | 15.8083 | 15.7663 | 15.7236 | 15.6396 | 15.4905 | 15.3434 | 15.1856 | 15.0266
|  | CROSSHILLS | CT |  |  |  | 0 | 16.8366 | 16.8074 | 16.7811 | 16.7489 | 16.7115 | 16.6693 | 16.6246 | 16.5922 | 16.559 | 16.5248 | 16.4903 | 16.2762 | 15.9544 | 15.2918 | 15.4383 | 15.4073 | 15.3791 | 15.3432 | 15.3023 | 15.2568 | 15.2089 | 15.1731 | 15.1364 | 15.0989 | 15.0611 | 14.6274 | 13.9699 | 13.1714 | 16.068 | 16.0387 | 16.0125 | 15.9802 | 15.9428 | 15.9006 | 15.856 | 15.8236 | 15.7904 | 15.7561 | 15.7217 | 15.6862 | 15.6443 | 15.5455
|  | CROSSHILLS | LW |  |  |  | 0 | 16.8526 | 16.7919 | 16.7627 | 16.7233 | 16.6781 | 16.6292 | 16.577 | 16.5349 | 16.4923 | 16.4481 | 16.4047 | 16.1369 | 15.3089 | 14.1018 | 15.4537 | 15.3906 | 15.3585 | 15.3139 | 15.2638 | 15.21 | 15.1532 | 15.1062 | 15.0587 | 14.943 | 14.8041 | 14.067 | 13.175 | 11.9408 | 16.084 | 16.0232 | 15.994 | 15.9546 | 15.9095 | 15.8606 | 15.8083 | 15.7663 | 15.7236 | 15.6396 | 15.4905 | 15.3434 | 15.1856 | 15.0266
|  | CROSSHILLS | ST |  |  |  | 0 | 16.856 | 16.8459 | 16.8397 | 16.8274 | 16.8129 | 16.7964 | 16.7782 | 16.7699 | 16.7615 | 16.7533 | 16.7454 | 16.7083 | 16.5733 | 16.4943 | 15.4605 | 15.4501 | 15.4438 | 15.4291 | 15.4123 | 15.3936 | 15.3733 | 15.3626 | 15.3519 | 15.3415 | 15.3314 | 15.2838 | 15.139 | 14.8723 | 16.0874 | 16.0772 | 16.0711 | 16.0587 | 16.0443 | 16.0277 | 16.0096 | 16.0012 | 15.9928 | 15.9847 | 15.9767 | 15.9396 | 15.8047 | 15.5563
|  | CROSSHILLS | FS |  |  |  | 0 | 16.8585 | 16.8505 | 16.8485 | 16.8465 | 16.8442 | 16.8418 | 16.8393 | 16.8345 | 16.8294 | 16.8239 | 16.8181 | 16.7987 | 16.7331 | 16.5997 | 15.4631 | 15.455 | 15.4528 | 15.4505 | 15.4475 | 15.4435 | 15.4395 | 15.4329 | 15.426 | 15.4187 | 15.4111 | 15.383 | 15.3092 | 15.1678 | 16.0899 | 16.0819 | 16.0799 | 16.0778 | 16.0756 | 16.0731 | 16.0707 | 16.0659 | 16.0608 | 16.0553 | 16.0495 | 16.0301 | 15.9645 | 15.831
| KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0.024211 | 3.0419 | 3.0167 | 2.9933 | 2.9662 | 2.9359 | 2.9034 | 2.8695 | 2.8421 | 2.8107 | 2.779 | 2.7478 | 2.557 | 2.0334 | 1.2156 | 2.9975 | 2.9697 | 2.9435 | 2.9113 | 2.8755 | 2.8343 | 2.792 | 2.7549 | 2.7168 | 2.6656 | 2.5559 | 1.9862 | 1.3221 | 0.45077 | 2.9905 | 2.9653 | 2.942 | 2.9149 | 2.8845 | 2.8473 | 2.7424 | 2.6389 | 2.5354 | 2.4325 | 2.3319 | 2.2334 | 2.1288 | 2.0225
|  | CULLEN | CT |  |  |  | 0.024211 | 3.0419 | 3.0167 | 2.9933 | 2.9662 | 2.9359 | 2.9034 | 2.8695 | 2.8425 | 2.815 | 2.7874 | 2.7598 | 2.5917 | 2.3527 | 1.9535 | 2.9975 | 2.9697 | 2.9435 | 2.9113 | 2.876 | 2.8388 | 2.8004 | 2.7686 | 2.7364 | 2.7042 | 2.6721 | 2.366 | 1.8617 | 1.2713 | 2.9905 | 2.9653 | 2.942 | 2.9149 | 2.8845 | 2.8521 | 2.8182 | 2.7824 | 2.7042 | 2.6275 | 2.5514 | 2.4754 | 2.3949 | 2.313
|  | CULLEN | LW |  |  |  | 0.024211 | 3.0638 | 3.0231 | 3.0023 | 2.9741 | 2.9428 | 2.9083 | 2.8724 | 2.8421 | 2.8107 | 2.779 | 2.7478 | 2.557 | 2.0334 | 1.2156 | 3.0184 | 2.9742 | 2.9491 | 2.9138 | 2.8755 | 2.8343 | 2.792 | 2.7549 | 2.7168 | 2.6656 | 2.5559 | 1.9862 | 1.3221 | 0.45077 | 3.0124 | 2.9717 | 2.9509 | 2.9227 | 2.8914 | 2.8473 | 2.7424 | 2.6389 | 2.5354 | 2.4325 | 2.3319 | 2.2334 | 2.1288 | 2.0225
|  | CULLEN | ST |  |  |  | 0.024211 | 3.068 | 3.0608 | 3.0561 | 3.0475 | 3.0369 | 3.0249 | 3.012 | 3.0051 | 2.9981 | 2.9913 | 2.9846 | 2.9529 | 2.8641 | 2.8066 | 3.0272 | 3.0197 | 3.0146 | 3.0028 | 2.9888 | 2.9738 | 2.9578 | 2.9476 | 2.9374 | 2.9274 | 2.9176 | 2.8715 | 2.7692 | 2.6032 | 3.0166 | 3.0094 | 3.0047 | 2.9962 | 2.9855 | 2.9736 | 2.9607 | 2.9537 | 2.9467 | 2.9399 | 2.9333 | 2.8123 | 2.5781 | 2.3806
|  | CULLEN | FS |  |  |  | 0.024211 | 3.0705 | 3.0647 | 3.0619 | 3.0592 | 3.0563 | 3.0533 | 3.0504 | 3.046 | 3.0415 | 3.0367 | 3.0318 | 3.0127 | 2.9668 | 2.8818 | 3.03 | 3.0239 | 3.0209 | 3.0177 | 3.0138 | 3.0088 | 3.0037 | 2.9969 | 2.9899 | 2.9827 | 2.9753 | 2.9444 | 2.8872 | 2.7916 | 3.0192 | 3.0133 | 3.0106 | 3.0078 | 3.005 | 3.002 | 2.999 | 2.9947 | 2.9901 | 2.9854 | 2.9804 | 2.9613 | 2.8461 | 2.6459
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 0.39895 | 18.1669 | 18.0722 | 26.3 | 26.2278 | 26.1464 | 26.057 | 25.9631 | 25.8875 | 25.8108 | 25.7331 | 25.6558 | 25.1807 | 23.9796 | 21.9218 | 18.0641 | 17.9694 | 24.9972 | 24.925 | 24.8435 | 24.7542 | 24.6603 | 24.5846 | 24.5007 | 24.255 | 24.0131 | 22.736 | 21.165 | 18.97 | 17.9308 | 17.83 | 25.452 | 25.369 | 25.2772 | 25.178 | 25.0748 | 24.9892 | 24.9028 | 24.8154 | 24.7288 | 24.6429 | 24.5403 | 24.4334
|  | CULLODEN | CT |  |  |  | 0.39895 | 18.1669 | 18.1195 | 26.3577 | 26.3047 | 26.242 | 26.1705 | 26.0945 | 26.0413 | 25.9858 | 25.93 | 25.8738 | 25.5185 | 24.9746 | 24.0619 | 18.0641 | 18.0166 | 25.0549 | 25.0019 | 24.9392 | 24.8677 | 24.7917 | 24.7385 | 24.683 | 24.6272 | 24.571 | 23.8061 | 22.6936 | 21.3234 | 17.9308 | 17.8797 | 25.5138 | 25.4534 | 25.3834 | 25.305 | 25.2224 | 25.1624 | 25.1 | 25.0376 | 24.9748 | 24.9104 | 24.8332 | 24.7542
|  | CULLODEN | LW |  |  |  | 0.39895 | 18.1855 | 18.0722 | 26.3 | 26.2278 | 26.1464 | 26.057 | 25.9631 | 25.8875 | 25.8108 | 25.7331 | 25.6558 | 25.1807 | 23.9796 | 21.9218 | 18.0826 | 17.9694 | 24.9972 | 24.925 | 24.8435 | 24.7542 | 24.6603 | 24.5846 | 24.5007 | 24.255 | 24.0131 | 22.736 | 21.165 | 18.97 | 17.9481 | 17.83 | 25.452 | 25.369 | 25.2772 | 25.178 | 25.0748 | 24.9892 | 24.9028 | 24.8154 | 24.7288 | 24.6429 | 24.5403 | 24.4334
|  | CULLODEN | ST |  |  |  | 0.39895 | 18.1897 | 18.173 | 26.4437 | 26.423 | 26.3975 | 26.369 | 26.3375 | 26.3242 | 26.3107 | 26.2978 | 26.2853 | 26.2264 | 25.9846 | 25.8514 | 18.0868 | 18.0702 | 25.1409 | 25.1202 | 25.0947 | 25.0662 | 25.0347 | 25.0214 | 25.0079 | 24.995 | 24.9824 | 24.9236 | 24.6818 | 24.2267 | 17.9592 | 17.9423 | 25.6127 | 25.5871 | 25.5569 | 25.5239 | 25.4881 | 25.47 | 25.4519 | 25.4344 | 25.4175 | 25.3382 | 25.077 | 24.9254
|  | CULLODEN | FS |  |  |  | 0.39895 | 18.1905 | 18.1754 | 26.4531 | 26.4507 | 26.448 | 26.4448 | 26.4417 | 26.4343 | 26.4261 | 26.4173 | 26.4079 | 26.3763 | 26.2612 | 26.0201 | 18.0877 | 18.0726 | 25.1503 | 25.1479 | 25.1452 | 25.142 | 25.1389 | 25.1314 | 25.1233 | 25.1145 | 25.1051 | 25.0735 | 24.9584 | 24.7172 | 17.9603 | 17.945 | 25.6225 | 25.6196 | 25.6153 | 25.6089 | 25.6025 | 25.5914 | 25.5795 | 25.5669 | 25.5538 | 25.5041 | 25.3722 | 25.1153
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 0.063158 | 17.4033 | 17.3498 | 17.3179 | 17.2736 | 17.223 | 17.168 | 17.0827 | 16.8626 | 16.6497 | 16.4439 | 16.2548 | 15.3311 | 14.3037 | 12.915 | 17.226 | 17.1725 | 17.1406 | 17.0963 | 16.834 | 16.5464 | 16.2825 | 16.0162 | 15.7593 | 15.5118 | 15.2853 | 14.1948 | 13.0159 | 11.4858 | 17.3526 | 17.2991 | 17.2673 | 17.1219 | 16.8269 | 16.546 | 16.2882 | 16.0283 | 15.7775 | 15.5358 | 15.3145 | 15.1069 | 14.8917 | 14.6769
|  | CULTER | CT |  |  |  | 0.063158 | 17.4033 | 17.3727 | 17.3455 | 17.3116 | 17.272 | 17.2271 | 17.1795 | 17.1455 | 17.1105 | 17.0753 | 16.9776 | 16.2911 | 15.5467 | 14.6589 | 17.226 | 17.1954 | 17.1682 | 17.1343 | 17.0947 | 17.0498 | 16.8726 | 16.6861 | 16.5036 | 16.3323 | 16.1685 | 15.3602 | 14.5095 | 13.521 | 17.3526 | 17.322 | 17.2948 | 17.261 | 17.2214 | 17.0538 | 16.863 | 16.681 | 16.5028 | 16.3355 | 16.1754 | 16.0164 | 15.8532 | 15.6954
|  | CULTER | LW |  |  |  | 0.063158 | 17.4184 | 17.3498 | 17.3179 | 17.2736 | 17.223 | 17.168 | 17.0827 | 16.8626 | 16.6497 | 16.4439 | 16.2548 | 15.3311 | 14.3037 | 12.915 | 17.2412 | 17.1725 | 17.1406 | 17.0963 | 16.834 | 16.5464 | 16.2825 | 16.0162 | 15.7593 | 15.5118 | 15.2853 | 14.1948 | 13.0159 | 11.4858 | 17.3678 | 17.2991 | 17.2673 | 17.1219 | 16.8269 | 16.546 | 16.2882 | 16.0283 | 15.7775 | 15.5358 | 15.3145 | 15.1069 | 14.8917 | 14.6769
|  | CULTER | ST |  |  |  | 0.063158 | 17.421 | 17.41 | 17.4043 | 17.3917 | 17.3759 | 17.3579 | 17.3381 | 17.3291 | 17.32 | 17.3113 | 17.3028 | 17.2629 | 17.0416 | 16.7104 | 17.2437 | 17.2327 | 17.227 | 17.2144 | 17.1987 | 17.1806 | 17.1608 | 17.1518 | 17.1427 | 17.134 | 17.1255 | 16.7162 | 16.2295 | 15.8322 | 17.3703 | 17.3593 | 17.3536 | 17.3411 | 17.3253 | 17.3073 | 17.2874 | 17.2784 | 17.2694 | 17.2583 | 17.1613 | 16.7137 | 16.2368 | 15.8487
|  | CULTER | FS |  |  |  | 0.063158 | 17.4227 | 17.4128 | 17.4108 | 17.4087 | 17.4063 | 17.4037 | 17.4012 | 17.396 | 17.3904 | 17.3844 | 17.378 | 17.3571 | 17.2837 | 17.1227 | 17.2454 | 17.2355 | 17.2335 | 17.2314 | 17.2291 | 17.2265 | 17.2239 | 17.2187 | 17.2131 | 17.2071 | 17.2007 | 17.1181 | 16.7517 | 16.3269 | 17.372 | 17.3622 | 17.3601 | 17.358 | 17.3557 | 17.3531 | 17.3505 | 17.3454 | 17.3397 | 17.3337 | 17.3273 | 17.1065 | 16.7487 | 16.332
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.19789 | 25.9592 | 25.9079 | 25.8844 | 25.8516 | 25.8135 | 25.7717 | 25.7275 | 25.6924 | 25.6566 | 25.6201 | 25.5841 | 25.3575 | 24.996 | 24.297 | 24.4151 | 24.3588 | 24.3304 | 24.2889 | 24.2422 | 24.192 | 24.1397 | 24.0958 | 24.0513 | 24.0062 | 23.9616 | 23.5196 | 22.3992 | 20.9336 | 25.1432 | 25.0919 | 25.0684 | 25.0356 | 24.9976 | 24.9557 | 24.9115 | 24.8765 | 24.8406 | 24.8041 | 24.7681 | 24.7323 | 24.6873 | 24.6404
|  | CUMMING STREET | CT |  |  |  | 0.19789 | 25.9592 | 25.9402 | 25.924 | 25.9023 | 25.876 | 25.8451 | 25.8117 | 25.7896 | 25.7665 | 25.7431 | 25.7194 | 25.5613 | 25.3023 | 24.9019 | 24.4151 | 24.3931 | 24.3735 | 24.3457 | 24.3133 | 24.2765 | 24.2374 | 24.2092 | 24.1799 | 24.1505 | 24.1208 | 23.933 | 23.5653 | 22.6332 | 25.1432 | 25.1242 | 25.108 | 25.0864 | 25.06 | 25.0291 | 24.9958 | 24.9736 | 24.9505 | 24.9271 | 24.9034 | 24.8787 | 24.8474 | 24.8152
|  | CUMMING STREET | LW |  |  |  | 0.19789 | 25.9609 | 25.9079 | 25.8844 | 25.8516 | 25.8135 | 25.7717 | 25.7275 | 25.6924 | 25.6566 | 25.6201 | 25.5841 | 25.3575 | 24.996 | 24.297 | 24.4158 | 24.3588 | 24.3304 | 24.2889 | 24.2422 | 24.192 | 24.1397 | 24.0958 | 24.0513 | 24.0062 | 23.9616 | 23.5196 | 22.3992 | 20.9336 | 25.1449 | 25.0919 | 25.0684 | 25.0356 | 24.9976 | 24.9557 | 24.9115 | 24.8765 | 24.8406 | 24.8041 | 24.7681 | 24.7323 | 24.6873 | 24.6404
|  | CUMMING STREET | ST |  |  |  | 0.19789 | 25.9609 | 25.9536 | 25.9501 | 25.9408 | 25.9294 | 25.9161 | 25.9013 | 25.8957 | 25.8901 | 25.8847 | 25.8796 | 25.8559 | 25.7338 | 25.6701 | 24.4212 | 24.4135 | 24.4096 | 24.3962 | 24.3808 | 24.3636 | 24.3449 | 24.3351 | 24.3254 | 24.3159 | 24.3067 | 24.2634 | 24.122 | 24.0392 | 25.1449 | 25.1376 | 25.1342 | 25.1248 | 25.1135 | 25.1001 | 25.0853 | 25.0797 | 25.0741 | 25.0688 | 25.0636 | 25.0399 | 24.9178 | 24.8542
|  | CUMMING STREET | FS |  |  |  | 0.19789 | 25.9617 | 25.9544 | 25.9541 | 25.9537 | 25.9531 | 25.9523 | 25.9515 | 25.9483 | 25.9448 | 25.9409 | 25.9367 | 25.9254 | 25.8662 | 25.7358 | 24.4222 | 24.4146 | 24.4139 | 24.4129 | 24.4109 | 24.4074 | 24.4037 | 24.3974 | 24.3906 | 24.3836 | 24.3761 | 24.3491 | 24.2746 | 24.1294 | 25.1457 | 25.1384 | 25.1381 | 25.1377 | 25.1371 | 25.1363 | 25.1355 | 25.1324 | 25.1288 | 25.1249 | 25.1207 | 25.1095 | 25.0503 | 24.9199
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | NO | 0 | 6.6524 | 6.6363 | 6.6212 | 6.6001 | 6.5772 | 6.5522 | 6.5265 | 6.5044 | 6.4823 | 6.4226 | 6.3607 | 6.0355 | 5.6504 | 5.1359 | 6.3758 | 6.3555 | 6.3365 | 6.3083 | 6.2785 | 6.2468 | 6.2145 | 6.1857 | 6.1504 | 6.0798 | 6.0102 | 5.6472 | 5.224 | 4.672 | 6.4177 | 6.4021 | 6.3878 | 6.3678 | 6.346 | 6.322 | 6.2972 | 6.2763 | 6.2551 | 6.233 | 6.2112 | 6.1896 | 6.1646 | 6.101
|  | DALCHONZIE | CT |  |  |  | 0 | 6.6524 | 6.6364 | 6.6222 | 6.6043 | 6.5845 | 6.563 | 6.5407 | 6.5221 | 6.5032 | 6.4843 | 6.4654 | 6.2569 | 5.9662 | 5.6216 | 6.3758 | 6.3573 | 6.3404 | 6.3175 | 6.2928 | 6.2666 | 6.2397 | 6.2163 | 6.1927 | 6.1691 | 6.1455 | 5.902 | 5.5846 | 5.2138 | 6.4177 | 6.4021 | 6.3883 | 6.3712 | 6.3522 | 6.3314 | 6.3097 | 6.2919 | 6.2737 | 6.2556 | 6.2374 | 6.2188 | 6.1979 | 6.1758
|  | DALCHONZIE | LW |  |  |  | 0 | 6.6628 | 6.6363 | 6.6212 | 6.6001 | 6.5772 | 6.5522 | 6.5265 | 6.5044 | 6.4823 | 6.4226 | 6.3607 | 6.0355 | 5.6504 | 5.1359 | 6.3853 | 6.3555 | 6.3365 | 6.3083 | 6.2785 | 6.2468 | 6.2145 | 6.1857 | 6.1504 | 6.0798 | 6.0102 | 5.6472 | 5.224 | 4.672 | 6.4283 | 6.4022 | 6.3878 | 6.3678 | 6.346 | 6.322 | 6.2972 | 6.2763 | 6.2551 | 6.233 | 6.2112 | 6.1896 | 6.1646 | 6.101
|  | DALCHONZIE | ST |  |  |  | 0 | 6.6681 | 6.6633 | 6.6601 | 6.6526 | 6.6443 | 6.6354 | 6.626 | 6.6201 | 6.6142 | 6.6084 | 6.6027 | 6.5759 | 6.5022 | 6.377 | 6.3952 | 6.39 | 6.3864 | 6.3756 | 6.364 | 6.3521 | 6.3397 | 6.3305 | 6.3214 | 6.3125 | 6.3037 | 6.2622 | 6.1644 | 6.0232 | 6.4329 | 6.4282 | 6.4249 | 6.418 | 6.4102 | 6.4018 | 6.3928 | 6.3874 | 6.382 | 6.3767 | 6.3715 | 6.347 | 6.2863 | 6.2447
|  | DALCHONZIE | FS |  |  |  | 0 | 6.6691 | 6.6655 | 6.6644 | 6.6631 | 6.6615 | 6.659 | 6.6566 | 6.6531 | 6.6495 | 6.6457 | 6.6418 | 6.6228 | 6.5905 | 6.5336 | 6.3963 | 6.3925 | 6.3912 | 6.3895 | 6.3868 | 6.3823 | 6.3778 | 6.3718 | 6.3658 | 6.3596 | 6.3533 | 6.3225 | 6.279 | 6.2114 | 6.4338 | 6.4302 | 6.4292 | 6.428 | 6.4265 | 6.4244 | 6.4222 | 6.4191 | 6.4159 | 6.4125 | 6.409 | 6.3918 | 6.3612 | 6.306
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 0.012632 | 15.9629 | 15.9497 | 15.9372 | 15.9234 | 15.9083 | 15.8921 | 15.8753 | 15.8614 | 15.8466 | 15.8317 | 15.8167 | 15.6984 | 15.5025 | 15.2212 | 14.8231 | 14.8093 | 14.7962 | 14.7811 | 14.7647 | 14.7474 | 14.7295 | 14.7145 | 14.6984 | 14.6824 | 14.6664 | 14.5745 | 14.4506 | 14.1626 | 15.1239 | 15.1006 | 15.0761 | 15.0365 | 14.9931 | 14.9493 | 14.906 | 14.8632 | 14.8207 | 14.7786 | 14.737 | 14.6952 | 14.6513 | 14.6063
|  | DALCROSS | CT |  |  |  | 0.012632 | 15.9629 | 15.9497 | 15.9372 | 15.9234 | 15.9083 | 15.8921 | 15.8753 | 15.8614 | 15.8466 | 15.8317 | 15.8167 | 15.7303 | 15.5716 | 15.3661 | 14.8231 | 14.8093 | 14.7962 | 14.7811 | 14.7647 | 14.7474 | 14.7295 | 14.7145 | 14.6984 | 14.6824 | 14.6664 | 14.5745 | 14.4506 | 14.2867 | 15.1239 | 15.1006 | 15.0761 | 15.0407 | 15.0045 | 14.9682 | 14.932 | 14.8979 | 14.8631 | 14.8286 | 14.7944 | 14.7603 | 14.7247 | 14.6882
|  | DALCROSS | LW |  |  |  | 0.012632 | 15.978 | 15.9614 | 15.9518 | 15.9397 | 15.9264 | 15.9114 | 15.8959 | 15.882 | 15.8679 | 15.8538 | 15.8398 | 15.6984 | 15.5025 | 15.2212 | 14.8381 | 14.8207 | 14.8101 | 14.7962 | 14.7812 | 14.7645 | 14.7474 | 14.7318 | 14.7161 | 14.7003 | 14.6848 | 14.5893 | 14.4549 | 14.1626 | 15.1365 | 15.1063 | 15.0793 | 15.0365 | 14.9931 | 14.9493 | 14.906 | 14.8632 | 14.8207 | 14.7786 | 14.737 | 14.6952 | 14.6513 | 14.6063
|  | DALCROSS | ST |  |  |  | 0.012632 | 15.9814 | 15.9771 | 15.9746 | 15.9706 | 15.9653 | 15.9596 | 15.9535 | 15.9496 | 15.9457 | 15.9419 | 15.9381 | 15.9199 | 15.8797 | 15.853 | 14.8425 | 14.8381 | 14.8355 | 14.8307 | 14.8246 | 14.8181 | 14.8112 | 14.8065 | 14.8019 | 14.7973 | 14.7927 | 14.7709 | 14.7273 | 14.6972 | 15.1578 | 15.1521 | 15.1482 | 15.1299 | 15.1104 | 15.0911 | 15.0718 | 15.0539 | 15.0363 | 15.0191 | 15.0022 | 14.9215 | 14.8219 | 14.738
|  | DALCROSS | FS |  |  |  | 0.012632 | 15.9831 | 15.9806 | 15.9789 | 15.9771 | 15.9753 | 15.9734 | 15.9716 | 15.9692 | 15.9667 | 15.9642 | 15.9616 | 15.9507 | 15.9296 | 15.8937 | 14.8443 | 14.8418 | 14.84 | 14.8381 | 14.836 | 14.8336 | 14.8313 | 14.8283 | 14.8252 | 14.822 | 14.8188 | 14.8048 | 14.7809 | 14.7421 | 15.1622 | 15.1585 | 15.1554 | 15.1518 | 15.1453 | 15.1344 | 15.1235 | 15.1103 | 15.0969 | 15.0836 | 15.0701 | 15.0062 | 14.9352 | 14.8518
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0 | 1.0462 | 1.0444 | 1.0436 | 1.0425 | 1.0412 | 1.0398 | 1.0383 | 1.0372 | 1.0361 | 1.0349 | 1.0338 | 1.0194 | 0.99508 | 0.96168 | 1.0458 | 1.044 | 1.0432 | 1.0421 | 1.0408 | 1.0394 | 1.0379 | 1.0368 | 1.0351 | 1.0306 | 1.0262 | 1.0032 | 0.97644 | 0.94071 | 1.0467 | 1.0449 | 1.0441 | 1.043 | 1.0417 | 1.0403 | 1.0388 | 1.0363 | 1.0318 | 1.0273 | 1.0229 | 1.0186 | 1.014 | 1.0094
|  | DALMALLY | CT |  |  |  | 0 | 1.0462 | 1.0456 | 1.0451 | 1.0444 | 1.0436 | 1.0426 | 1.0415 | 1.0408 | 1.0401 | 1.0394 | 1.0387 | 1.0342 | 1.0189 | 0.9978 | 1.0458 | 1.0452 | 1.0447 | 1.044 | 1.0432 | 1.0422 | 1.0411 | 1.0404 | 1.0397 | 1.039 | 1.0383 | 1.0222 | 1.0025 | 0.97962 | 1.0467 | 1.0461 | 1.0456 | 1.0449 | 1.0441 | 1.0431 | 1.042 | 1.0413 | 1.0406 | 1.0392 | 1.0359 | 1.0327 | 1.0293 | 1.0259
|  | DALMALLY | LW |  |  |  | 0 | 1.0462 | 1.0444 | 1.0436 | 1.0425 | 1.0412 | 1.0398 | 1.0383 | 1.0372 | 1.0361 | 1.0349 | 1.0338 | 1.0194 | 0.99508 | 0.96168 | 1.0458 | 1.044 | 1.0432 | 1.0421 | 1.0408 | 1.0394 | 1.0379 | 1.0368 | 1.0351 | 1.0306 | 1.0262 | 1.0032 | 0.97644 | 0.94071 | 1.0467 | 1.0449 | 1.0441 | 1.043 | 1.0417 | 1.0403 | 1.0388 | 1.0363 | 1.0318 | 1.0273 | 1.0229 | 1.0186 | 1.014 | 1.0094
|  | DALMALLY | ST |  |  |  | 0 | 1.0462 | 1.046 | 1.0459 | 1.0456 | 1.0453 | 1.0449 | 1.0444 | 1.0442 | 1.0441 | 1.0439 | 1.0438 | 1.0431 | 1.0397 | 1.038 | 1.0458 | 1.0456 | 1.0455 | 1.0452 | 1.0449 | 1.0445 | 1.044 | 1.0438 | 1.0437 | 1.0435 | 1.0434 | 1.0427 | 1.0393 | 1.0376 | 1.0467 | 1.0465 | 1.0464 | 1.0461 | 1.0458 | 1.0454 | 1.0449 | 1.0447 | 1.0446 | 1.0444 | 1.0443 | 1.0436 | 1.0402 | 1.0366
|  | DALMALLY | FS |  |  |  | 0 | 1.0462 | 1.046 | 1.046 | 1.046 | 1.046 | 1.046 | 1.0459 | 1.0459 | 1.0458 | 1.0457 | 1.0455 | 1.0453 | 1.0437 | 1.0405 | 1.0458 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 1.0455 | 1.0454 | 1.0454 | 1.0453 | 1.0451 | 1.0448 | 1.0433 | 1.0401 | 1.0467 | 1.0465 | 1.0465 | 1.0465 | 1.0465 | 1.0465 | 1.0464 | 1.0464 | 1.0463 | 1.0462 | 1.046 | 1.0458 | 1.0442 | 1.041
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49666 | 0.49948 | 0.50179 | 0.5044 | 0.51527 | 0.5325 | 0.53699 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36576 | 0.36928 | 0.37218 | 0.37544 | 0.38902 | 0.41056 | 0.41617 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.53313 | 0.53665 | 0.53954 | 0.5428 | 0.55639 | 0.57793 | 0.58353
|  | DALMALLY SCHOOL | CT |  |  |  | 0 | 0.49395 | 0.49395 | 0.49567 | 0.49873 | 0.51343 | 0.5291 | 0.53307 | 0.54001 | 0.54698 | 0.553 | 0.55962 | 0.58846 | 0.62086 | 0.65706 | 0.36237 | 0.36237 | 0.36452 | 0.36834 | 0.38672 | 0.40631 | 0.41128 | 0.41995 | 0.42866 | 0.43619 | 0.44446 | 0.48051 | 0.52101 | 0.56626 | 0.52974 | 0.52974 | 0.53189 | 0.53571 | 0.55408 | 0.57368 | 0.57865 | 0.58732 | 0.59603 | 0.60356 | 0.61183 | 0.64788 | 0.68838 | 0.73363
|  | DALMALLY SCHOOL | LW |  |  |  | 0 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49395 | 0.49666 | 0.49948 | 0.50179 | 0.5044 | 0.51527 | 0.55929 | 0.65134 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36237 | 0.36576 | 0.36928 | 0.37218 | 0.37544 | 0.38902 | 0.44404 | 0.55911 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.52974 | 0.53313 | 0.53665 | 0.53954 | 0.5428 | 0.55639 | 0.61141 | 0.72647
|  | DALMALLY SCHOOL | ST |  |  |  | 0 | 0.49395 | 0.49395 | 0.50717 | 0.51611 | 0.52201 | 0.54231 | 0.54796 | 0.56322 | 0.56864 | 0.57322 | 0.58055 | 0.60911 | 0.65136 | 0.70541 | 0.36237 | 0.36237 | 0.37559 | 0.38453 | 0.39043 | 0.41073 | 0.41638 | 0.43164 | 0.43706 | 0.44164 | 0.44897 | 0.47753 | 0.51978 | 0.58545 | 0.52974 | 0.52974 | 0.54626 | 0.55744 | 0.56482 | 0.59019 | 0.59725 | 0.61633 | 0.6231 | 0.62883 | 0.63798 | 0.67369 | 0.7265 | 0.79406
|  | DALMALLY SCHOOL | FS |  |  |  | 0 | 0.49395 | 0.49395 | 0.49665 | 0.49935 | 0.50251 | 0.50566 | 0.50836 | 0.51389 | 0.51763 | 0.52138 | 0.52513 | 0.52951 | 0.5325 | 0.53699 | 0.36237 | 0.36237 | 0.36575 | 0.36913 | 0.37307 | 0.37701 | 0.38038 | 0.38729 | 0.39198 | 0.39666 | 0.40135 | 0.40682 | 0.41056 | 0.41617 | 0.52974 | 0.52974 | 0.53312 | 0.5365 | 0.54043 | 0.54437 | 0.54775 | 0.55466 | 0.55934 | 0.56403 | 0.56871 | 0.57419 | 0.57793 | 0.58353
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 0.49158 | 14.0498 | 13.9477 | 13.9016 | 13.8365 | 13.7627 | 13.6816 | 13.5957 | 13.5279 | 13.4585 | 13.3878 | 13.3181 | 12.4298 | 10.87 | 8.6389 | 13.5737 | 13.4664 | 13.4152 | 13.3409 | 13.2581 | 13.1683 | 13.0741 | 12.9974 | 12.8276 | 12.5606 | 12.297 | 10.8911 | 9.1775 | 6.7903 | 13.6235 | 13.5214 | 13.4753 | 13.4102 | 13.3364 | 13.2552 | 13.1694 | 13.1016 | 13.0322 | 12.9533 | 12.7175 | 12.484 | 12.2289 | 11.9713
|  | DALNEIGH | CT |  |  |  | 0.49158 | 14.0498 | 14.0128 | 13.9814 | 13.9391 | 13.8874 | 13.8267 | 13.7612 | 13.718 | 13.6728 | 13.6272 | 13.581 | 13.2732 | 12.4352 | 11.0517 | 13.5737 | 13.5336 | 13.4986 | 13.4498 | 13.3918 | 13.325 | 13.2537 | 13.2042 | 13.1529 | 13.1011 | 13.0489 | 12.1278 | 10.9174 | 9.4262 | 13.6235 | 13.5865 | 13.5551 | 13.5128 | 13.4611 | 13.4004 | 13.3349 | 13.2917 | 13.2465 | 13.2009 | 13.1547 | 13.1064 | 13.0452 | 12.9325
|  | DALNEIGH | LW |  |  |  | 0.49158 | 14.0515 | 13.9477 | 13.9016 | 13.8365 | 13.7627 | 13.6816 | 13.5957 | 13.5279 | 13.4585 | 13.3878 | 13.3181 | 12.4298 | 10.87 | 8.6389 | 13.5743 | 13.4664 | 13.4152 | 13.3409 | 13.2581 | 13.1683 | 13.0741 | 12.9974 | 12.8276 | 12.5606 | 12.297 | 10.8911 | 9.1775 | 6.7903 | 13.6252 | 13.5214 | 13.4753 | 13.4102 | 13.3364 | 13.2552 | 13.1694 | 13.1016 | 13.0322 | 12.9533 | 12.7175 | 12.484 | 12.2289 | 11.9713
|  | DALNEIGH | ST |  |  |  | 0.49158 | 14.0515 | 14.0371 | 14.0302 | 14.0116 | 13.9891 | 13.9626 | 13.9331 | 13.9221 | 13.911 | 13.9003 | 13.8901 | 13.8432 | 13.6022 | 13.4768 | 13.5803 | 13.5655 | 13.5583 | 13.5356 | 13.5088 | 13.4784 | 13.445 | 13.4297 | 13.4144 | 13.3997 | 13.3855 | 13.3193 | 12.8923 | 12.3452 | 13.6252 | 13.6108 | 13.6039 | 13.5853 | 13.5628 | 13.5363 | 13.5068 | 13.4958 | 13.4847 | 13.474 | 13.4638 | 13.4169 | 13.1759 | 12.7815
|  | DALNEIGH | FS |  |  |  | 0.49158 | 14.0523 | 14.0378 | 14.0372 | 14.0364 | 14.0353 | 14.0337 | 14.0321 | 14.0259 | 14.0189 | 14.0112 | 14.0029 | 13.9807 | 13.8639 | 13.6067 | 13.5812 | 13.5665 | 13.5656 | 13.5643 | 13.5618 | 13.5572 | 13.5527 | 13.5432 | 13.5328 | 13.5218 | 13.5101 | 13.4715 | 13.339 | 12.9613 | 13.626 | 13.6115 | 13.6109 | 13.6101 | 13.609 | 13.6074 | 13.6058 | 13.5996 | 13.5926 | 13.5849 | 13.5766 | 13.5544 | 13.4376 | 13.1804
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | YES | 0.04 | 2.8459 | 2.8351 | 2.8284 | 2.8193 | 2.8091 | 2.798 | 2.7609 | 2.7175 | 2.6744 | 2.6307 | 2.5882 | 2.3692 | 2.1196 | 1.7981 | 2.8357 | 2.8238 | 2.816 | 2.805 | 2.793 | 2.7802 | 2.7669 | 2.7558 | 2.7341 | 2.6834 | 2.6343 | 2.3822 | 2.0994 | 1.7453 | 2.8753 | 2.8645 | 2.8577 | 2.8136 | 2.763 | 2.7129 | 2.6632 | 2.6138 | 2.5648 | 2.5153 | 2.4673 | 2.4197 | 2.3704 | 2.3207
|  | DALRULZION | CT |  |  |  | 0.04 | 2.8459 | 2.8389 | 2.8326 | 2.8249 | 2.8161 | 2.8071 | 2.7976 | 2.7899 | 2.7671 | 2.7364 | 2.706 | 2.548 | 2.3671 | 2.159 | 2.8357 | 2.8281 | 2.821 | 2.812 | 2.8019 | 2.7917 | 2.781 | 2.7721 | 2.7631 | 2.754 | 2.745 | 2.5916 | 2.3876 | 2.1569 | 2.8753 | 2.8683 | 2.862 | 2.8496 | 2.8126 | 2.7763 | 2.741 | 2.706 | 2.6712 | 2.6366 | 2.6023 | 2.568 | 2.5325 | 2.4968
|  | DALRULZION | LW |  |  |  | 0.04 | 2.8493 | 2.8351 | 2.8284 | 2.8193 | 2.8091 | 2.798 | 2.7609 | 2.7175 | 2.6744 | 2.6307 | 2.5882 | 2.3692 | 2.1196 | 1.7981 | 2.8388 | 2.8238 | 2.816 | 2.805 | 2.793 | 2.7802 | 2.7669 | 2.7558 | 2.7341 | 2.6834 | 2.6343 | 2.3822 | 2.0994 | 1.7453 | 2.8787 | 2.8645 | 2.8577 | 2.8136 | 2.763 | 2.7129 | 2.6632 | 2.6138 | 2.5648 | 2.5153 | 2.4673 | 2.4197 | 2.3704 | 2.3207
|  | DALRULZION | ST |  |  |  | 0.04 | 2.851 | 2.8485 | 2.8469 | 2.8439 | 2.8405 | 2.8366 | 2.8324 | 2.8303 | 2.8282 | 2.8261 | 2.8241 | 2.7789 | 2.6778 | 2.5912 | 2.8416 | 2.8391 | 2.8374 | 2.8335 | 2.8292 | 2.8245 | 2.8195 | 2.8165 | 2.8136 | 2.8107 | 2.8079 | 2.7945 | 2.7348 | 2.6337 | 2.8804 | 2.8779 | 2.8762 | 2.8733 | 2.8699 | 2.866 | 2.857 | 2.8361 | 2.8155 | 2.7953 | 2.7754 | 2.6794 | 2.566 | 2.4673
|  | DALRULZION | FS |  |  |  | 0.04 | 2.851 | 2.8495 | 2.8494 | 2.8494 | 2.8492 | 2.8491 | 2.8489 | 2.8483 | 2.8476 | 2.8468 | 2.8459 | 2.8403 | 2.8041 | 2.7289 | 2.8417 | 2.8402 | 2.84 | 2.8398 | 2.8394 | 2.8387 | 2.838 | 2.8367 | 2.8354 | 2.834 | 2.8325 | 2.8238 | 2.8074 | 2.7794 | 2.8804 | 2.8789 | 2.8788 | 2.8787 | 2.8786 | 2.8785 | 2.8783 | 2.8777 | 2.877 | 2.8731 | 2.8584 | 2.7846 | 2.7069 | 2.623
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.010526 | 1.2532 | 1.2435 | 1.234 | 1.2241 | 1.2139 | 1.2034 | 1.1936 | 1.1837 | 1.1737 | 1.1623 | 1.1457 | 1.0578 | 0.95477 | 0.83369 | 1.2346 | 1.2249 | 1.2154 | 1.2055 | 1.1883 | 1.1694 | 1.1515 | 1.1333 | 1.1151 | 1.097 | 1.0781 | 0.97854 | 0.86393 | 0.72845 | 1.2454 | 1.2357 | 1.2262 | 1.2163 | 1.2061 | 1.1956 | 1.1857 | 1.1758 | 1.1659 | 1.1503 | 1.1322 | 1.1135 | 1.0943 | 1.0743
|  | DALWHINNIE | CT |  |  |  | 0.010526 | 1.2532 | 1.2435 | 1.234 | 1.2241 | 1.2139 | 1.2034 | 1.1936 | 1.1837 | 1.1737 | 1.1623 | 1.1457 | 1.0578 | 0.95477 | 0.83369 | 1.2346 | 1.2249 | 1.2154 | 1.2055 | 1.1883 | 1.1694 | 1.1515 | 1.1333 | 1.1151 | 1.097 | 1.0781 | 0.97854 | 0.86393 | 0.73237 | 1.2454 | 1.2357 | 1.2262 | 1.2163 | 1.2061 | 1.1956 | 1.1857 | 1.1758 | 1.1659 | 1.1503 | 1.1322 | 1.1135 | 1.0943 | 1.0743
|  | DALWHINNIE | LW |  |  |  | 0.010526 | 1.2675 | 1.2613 | 1.2571 | 1.2514 | 1.2454 | 1.2383 | 1.231 | 1.2218 | 1.2061 | 1.1904 | 1.1749 | 1.0898 | 0.98253 | 0.84229 | 1.2489 | 1.2426 | 1.2384 | 1.2274 | 1.2102 | 1.1923 | 1.1745 | 1.1561 | 1.137 | 1.1179 | 1.0991 | 0.99767 | 0.87769 | 0.72845 | 1.2597 | 1.2534 | 1.2492 | 1.2435 | 1.2375 | 1.2304 | 1.2232 | 1.2096 | 1.1912 | 1.1723 | 1.1536 | 1.135 | 1.1151 | 1.0951
|  | DALWHINNIE | ST |  |  |  | 0.010526 | 1.2709 | 1.2688 | 1.2668 | 1.2645 | 1.2613 | 1.2579 | 1.2544 | 1.2515 | 1.2486 | 1.2457 | 1.2428 | 1.2287 | 1.1957 | 1.1628 | 1.2523 | 1.2501 | 1.2482 | 1.2459 | 1.2427 | 1.2393 | 1.2358 | 1.231 | 1.2231 | 1.215 | 1.2071 | 1.1684 | 1.1254 | 1.0857 | 1.2631 | 1.2609 | 1.259 | 1.2567 | 1.2534 | 1.25 | 1.2465 | 1.2436 | 1.2408 | 1.2379 | 1.235 | 1.2208 | 1.1796 | 1.1403
|  | DALWHINNIE | FS |  |  |  | 0.010526 | 1.2726 | 1.2713 | 1.2696 | 1.2679 | 1.2662 | 1.2645 | 1.2627 | 1.2609 | 1.259 | 1.257 | 1.2551 | 1.246 | 1.2342 | 1.2134 | 1.254 | 1.2527 | 1.251 | 1.2493 | 1.2476 | 1.2458 | 1.2441 | 1.2422 | 1.2404 | 1.2384 | 1.2365 | 1.2096 | 1.1799 | 1.1468 | 1.2648 | 1.2635 | 1.2618 | 1.2601 | 1.2584 | 1.2566 | 1.2549 | 1.253 | 1.2511 | 1.2492 | 1.2473 | 1.2382 | 1.2263 | 1.2007
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 0 | 24.4434 | 24.4021 | 24.3837 | 24.3582 | 24.3292 | 24.2961 | 24.2606 | 24.2323 | 24.2025 | 24.1716 | 24.1408 | 23.9339 | 23.5784 | 22.8612 | 22.6514 | 22.5184 | 22.3977 | 22.2275 | 22.0588 | 21.8924 | 21.7326 | 21.5698 | 21.4093 | 21.2508 | 21.0987 | 20.3065 | 19.3619 | 18.0409 | 21.2954 | 21.2456 | 21.2177 | 21.1787 | 21.1368 | 21.0913 | 21.0443 | 21.0035 | 20.8679 | 20.6442 | 20.4302 | 20.223 | 19.9892 | 19.7526
|  | DENBURN | CT |  |  |  | 0 | 24.4434 | 24.4305 | 24.4196 | 24.4048 | 24.3867 | 24.3644 | 24.3399 | 24.3235 | 24.3056 | 24.2872 | 24.2683 | 24.1331 | 23.8872 | 23.4877 | 22.6896 | 22.6181 | 22.5403 | 22.4302 | 22.3145 | 22.194 | 22.0811 | 21.9711 | 21.8607 | 21.754 | 21.6498 | 21.0953 | 20.4345 | 19.6101 | 21.2989 | 21.2806 | 21.2635 | 21.2398 | 21.2127 | 21.1813 | 21.1486 | 21.1235 | 21.097 | 21.0704 | 21.0436 | 21.0155 | 20.891 | 20.7356
|  | DENBURN | LW |  |  |  | 0 | 24.4434 | 24.4021 | 24.3837 | 24.3582 | 24.3292 | 24.2961 | 24.2606 | 24.2323 | 24.2025 | 24.1716 | 24.1408 | 23.9339 | 23.5784 | 22.8612 | 22.6514 | 22.5184 | 22.3977 | 22.2275 | 22.0588 | 21.8924 | 21.7326 | 21.5698 | 21.4093 | 21.2508 | 21.0987 | 20.3065 | 19.3619 | 18.0409 | 21.2954 | 21.2456 | 21.2177 | 21.1787 | 21.1368 | 21.0913 | 21.0443 | 21.0035 | 20.8679 | 20.6442 | 20.4302 | 20.223 | 19.9892 | 19.7526
|  | DENBURN | ST |  |  |  | 0 | 24.4434 | 24.437 | 24.4339 | 24.4257 | 24.4157 | 24.404 | 24.3909 | 24.386 | 24.3811 | 24.3763 | 24.3718 | 24.3498 | 24.2223 | 24.1537 | 22.7457 | 22.723 | 22.7008 | 22.6368 | 22.5693 | 22.4996 | 22.4309 | 22.3644 | 22.2969 | 22.2307 | 22.1659 | 21.8515 | 21.4537 | 21.1103 | 21.3041 | 21.2962 | 21.2914 | 21.278 | 21.2626 | 21.2455 | 21.2273 | 21.2167 | 21.2059 | 21.1955 | 21.1854 | 21.1362 | 20.9247 | 20.4413
|  | DENBURN | FS |  |  |  | 0 | 24.4434 | 24.4353 | 24.4349 | 24.4345 | 24.4339 | 24.433 | 24.4321 | 24.4287 | 24.4248 | 24.4205 | 24.4158 | 24.4034 | 24.3363 | 24.1853 | 22.7468 | 22.7251 | 22.7097 | 22.6909 | 22.662 | 22.6168 | 22.5722 | 22.5192 | 22.4647 | 22.4105 | 22.3565 | 22.1066 | 21.8198 | 21.449 | 21.3042 | 21.2949 | 21.2931 | 21.291 | 21.2877 | 21.2827 | 21.2778 | 21.2697 | 21.2612 | 21.2522 | 21.243 | 21.2086 | 21.1211 | 20.9365
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0.029474 | 4.5485 | 4.5182 | 4.5047 | 4.486 | 4.4647 | 4.4416 | 4.4172 | 4.3982 | 4.3789 | 4.3593 | 4.3401 | 4.026 | 3.5381 | 2.8896 | 4.6933 | 4.6288 | 4.5739 | 4.4813 | 4.3873 | 4.2941 | 4.2002 | 4.1013 | 4.003 | 3.9062 | 3.8117 | 3.3252 | 2.7692 | 2.0536 | 3.6894 | 3.6346 | 3.5898 | 3.509 | 3.4044 | 3.301 | 3.1986 | 3.0971 | 2.9963 | 2.8971 | 2.8002 | 2.7045 | 2.6044 | 2.5037
|  | DERVAIG | CT |  |  |  | 0.029474 | 4.5485 | 4.5382 | 4.5296 | 4.5179 | 4.5035 | 4.4868 | 4.4689 | 4.4573 | 4.4452 | 4.4331 | 4.4209 | 4.342 | 4.086 | 3.6874 | 4.7031 | 4.6682 | 4.6306 | 4.5679 | 4.5027 | 4.437 | 4.3722 | 4.3105 | 4.2498 | 4.1851 | 4.1202 | 3.7837 | 3.3996 | 2.9546 | 3.6956 | 3.6693 | 3.6388 | 3.5885 | 3.531 | 3.4581 | 3.3865 | 3.3175 | 3.2497 | 3.1825 | 3.1159 | 3.0495 | 2.9801 | 2.9103
|  | DERVAIG | LW |  |  |  | 0.029474 | 4.5485 | 4.5182 | 4.5047 | 4.486 | 4.4647 | 4.4416 | 4.4172 | 4.3982 | 4.3789 | 4.3593 | 4.3401 | 4.026 | 3.5381 | 2.8896 | 4.6933 | 4.6288 | 4.5739 | 4.4813 | 4.3873 | 4.2941 | 4.2002 | 4.1013 | 4.003 | 3.9062 | 3.8117 | 3.3252 | 2.7692 | 2.0536 | 3.6894 | 3.6346 | 3.5898 | 3.509 | 3.4044 | 3.301 | 3.1986 | 3.0971 | 2.9963 | 2.8971 | 2.8002 | 2.7045 | 2.6044 | 2.5037
|  | DERVAIG | ST |  |  |  | 0.029474 | 4.5485 | 4.5447 | 4.5429 | 4.538 | 4.5321 | 4.5251 | 4.5174 | 4.5145 | 4.5116 | 4.5088 | 4.5061 | 4.494 | 4.4348 | 4.4043 | 4.7386 | 4.7314 | 4.7263 | 4.6888 | 4.6506 | 4.6126 | 4.5745 | 4.5381 | 4.5023 | 4.4671 | 4.4326 | 4.2648 | 4.0417 | 3.8522 | 3.7179 | 3.712 | 3.7081 | 3.6827 | 3.6546 | 3.6241 | 3.5933 | 3.5651 | 3.5294 | 3.4895 | 3.4503 | 3.2628 | 3.0344 | 2.84
|  | DERVAIG | FS |  |  |  | 0.029474 | 4.5485 | 4.545 | 4.5449 | 4.5447 | 4.5444 | 4.544 | 4.5437 | 4.5422 | 4.5405 | 4.5387 | 4.5368 | 4.5315 | 4.5043 | 4.4452 | 4.7405 | 4.7348 | 4.7314 | 4.727 | 4.7156 | 4.6935 | 4.6715 | 4.6449 | 4.6182 | 4.5913 | 4.5644 | 4.4361 | 4.2906 | 4.1064 | 3.7191 | 3.7142 | 3.712 | 3.7092 | 3.7019 | 3.6879 | 3.6732 | 3.6527 | 3.632 | 3.6113 | 3.5904 | 3.4506 | 3.2891 | 3.1009
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 0.45263 | 14.9263 | 14.8773 | 14.8408 | 14.7911 | 14.7354 | 14.6742 | 14.6092 | 14.5564 | 14.502 | 14.4469 | 14.3917 | 13.8568 | 12.7435 | 11.1985 | 14.0818 | 14.0329 | 13.9964 | 13.9467 | 13.891 | 13.8298 | 13.7647 | 13.7119 | 13.6576 | 13.6024 | 13.5472 | 13.0549 | 11.8326 | 10.1788 | 14.5142 | 14.4653 | 14.4288 | 14.3791 | 14.3234 | 14.2622 | 14.1971 | 14.1444 | 14.09 | 14.0349 | 13.9796 | 13.8539 | 13.6572 | 13.4588
|  | DINGWALL | CT |  |  |  | 0.45263 | 14.9263 | 14.8877 | 14.8528 | 14.8107 | 14.7622 | 14.7088 | 14.6523 | 14.6099 | 14.5655 | 14.5209 | 14.4761 | 14.1965 | 13.6851 | 12.6757 | 14.0818 | 14.0432 | 14.0084 | 13.9662 | 13.9178 | 13.8643 | 13.8079 | 13.7655 | 13.7211 | 13.6765 | 13.6316 | 13.3521 | 12.9016 | 11.8174 | 14.5142 | 14.4757 | 14.4408 | 14.3987 | 14.3502 | 14.2968 | 14.2403 | 14.1979 | 14.1535 | 14.1089 | 14.0641 | 14.0179 | 13.963 | 13.9058
|  | DINGWALL | LW |  |  |  | 0.45263 | 14.9524 | 14.8773 | 14.8408 | 14.7911 | 14.7354 | 14.6742 | 14.6092 | 14.5564 | 14.502 | 14.4469 | 14.3917 | 13.8568 | 12.7435 | 11.1985 | 14.1079 | 14.0329 | 13.9964 | 13.9467 | 13.891 | 13.8298 | 13.7647 | 13.7119 | 13.6576 | 13.6024 | 13.5472 | 13.0549 | 11.8326 | 10.1788 | 14.5403 | 14.4653 | 14.4288 | 14.3791 | 14.3234 | 14.2622 | 14.1971 | 14.1444 | 14.09 | 14.0349 | 13.9796 | 13.8539 | 13.6572 | 13.4588
|  | DINGWALL | ST |  |  |  | 0.45263 | 14.9574 | 14.9447 | 14.9369 | 14.9215 | 14.9027 | 14.8813 | 14.858 | 14.8466 | 14.8352 | 14.8241 | 14.8141 | 14.7646 | 14.5929 | 14.4901 | 14.113 | 14.1003 | 14.0924 | 14.077 | 14.0582 | 14.0369 | 14.0135 | 14.0022 | 13.9908 | 13.9796 | 13.9697 | 13.9202 | 13.7485 | 13.6457 | 14.5454 | 14.5327 | 14.5249 | 14.5095 | 14.4906 | 14.4693 | 14.446 | 14.4346 | 14.4232 | 14.4121 | 14.4021 | 14.3526 | 14.1809 | 14.0781
|  | DINGWALL | FS |  |  |  | 0.45263 | 14.9599 | 14.9493 | 14.9464 | 14.9434 | 14.9401 | 14.9366 | 14.9331 | 14.9268 | 14.9199 | 14.9126 | 14.9049 | 14.876 | 14.7917 | 14.6221 | 14.1155 | 14.1049 | 14.1019 | 14.0989 | 14.0957 | 14.0922 | 14.0887 | 14.0823 | 14.0755 | 14.0682 | 14.0605 | 14.0316 | 13.9473 | 13.7777 | 14.5479 | 14.5373 | 14.5344 | 14.5314 | 14.5281 | 14.5246 | 14.5211 | 14.5148 | 14.5079 | 14.5006 | 14.4929 | 14.464 | 14.3797 | 14.2101
| CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0 | 1.1603 | 1.1544 | 1.1518 | 1.1481 | 1.144 | 1.1394 | 1.1347 | 1.1235 | 1.1108 | 1.0983 | 1.0859 | 1.0211 | 0.94316 | 0.8333 | 1.145 | 1.1391 | 1.1365 | 1.1328 | 1.1287 | 1.1241 | 1.1194 | 1.1157 | 1.1119 | 1.1081 | 1.1042 | 1.0346 | 0.94564 | 0.82554 | 1.1391 | 1.1331 | 1.1305 | 1.1269 | 1.1227 | 1.1182 | 1.1134 | 1.1097 | 1.1059 | 1.1021 | 1.0983 | 1.0946 | 1.0901 | 1.0832
|  | DIPPEN | CT |  |  |  | 0 | 1.1603 | 1.1583 | 1.1566 | 1.1543 | 1.1515 | 1.1482 | 1.1447 | 1.1424 | 1.1401 | 1.1322 | 1.1239 | 1.0795 | 1.0262 | 0.96085 | 1.145 | 1.143 | 1.1413 | 1.139 | 1.1362 | 1.1329 | 1.1294 | 1.1271 | 1.1248 | 1.1224 | 1.12 | 1.1018 | 1.0413 | 0.9687 | 1.1391 | 1.1371 | 1.1354 | 1.1331 | 1.1303 | 1.127 | 1.1235 | 1.1212 | 1.1188 | 1.1164 | 1.114 | 1.1116 | 1.1085 | 1.1053
|  | DIPPEN | LW |  |  |  | 0 | 1.1603 | 1.1544 | 1.1518 | 1.1481 | 1.144 | 1.1394 | 1.1347 | 1.1235 | 1.1108 | 1.0983 | 1.0859 | 1.0211 | 0.94316 | 0.8333 | 1.145 | 1.1391 | 1.1365 | 1.1328 | 1.1287 | 1.1241 | 1.1194 | 1.1157 | 1.1119 | 1.1081 | 1.1042 | 1.0346 | 0.94564 | 0.82554 | 1.1391 | 1.1331 | 1.1305 | 1.1269 | 1.1227 | 1.1182 | 1.1134 | 1.1097 | 1.1059 | 1.1021 | 1.0983 | 1.0946 | 1.0901 | 1.0832
|  | DIPPEN | ST |  |  |  | 0 | 1.1603 | 1.1596 | 1.1592 | 1.1583 | 1.1571 | 1.1558 | 1.1543 | 1.1537 | 1.1531 | 1.1526 | 1.152 | 1.1497 | 1.1236 | 1.1021 | 1.145 | 1.1443 | 1.1439 | 1.143 | 1.1418 | 1.1405 | 1.139 | 1.1384 | 1.1378 | 1.1373 | 1.1367 | 1.1344 | 1.1228 | 1.1169 | 1.1391 | 1.1383 | 1.138 | 1.137 | 1.1359 | 1.1345 | 1.133 | 1.1324 | 1.1318 | 1.1313 | 1.1308 | 1.1284 | 1.1168 | 1.1109
|  | DIPPEN | FS |  |  |  | 0 | 1.1603 | 1.1597 | 1.1596 | 1.1596 | 1.1596 | 1.1595 | 1.1594 | 1.1591 | 1.1588 | 1.1584 | 1.1581 | 1.157 | 1.1517 | 1.1275 | 1.145 | 1.1444 | 1.1443 | 1.1443 | 1.1443 | 1.1442 | 1.1441 | 1.1438 | 1.1435 | 1.1431 | 1.1428 | 1.1417 | 1.1364 | 1.1249 | 1.1391 | 1.1384 | 1.1384 | 1.1383 | 1.1383 | 1.1382 | 1.1381 | 1.1379 | 1.1375 | 1.1372 | 1.1368 | 1.1358 | 1.1305 | 1.1189
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 0.18421 | 5.3927 | 5.3694 | 5.354 | 5.3324 | 5.3082 | 5.282 | 5.2547 | 5.2318 | 5.2088 | 5.1854 | 5.1625 | 4.9374 | 4.4758 | 3.8434 | 5.2746 | 5.2513 | 5.2359 | 5.2143 | 5.1901 | 5.164 | 5.1366 | 5.1138 | 5.0907 | 5.0479 | 4.9672 | 4.5433 | 4.0436 | 3.3738 | 5.2428 | 5.2196 | 5.2042 | 5.1825 | 5.1584 | 5.1322 | 5.1049 | 5.082 | 5.0589 | 5.0356 | 5.0126 | 4.9767 | 4.8955 | 4.8136
|  | DORNOCH | CT |  |  |  | 0.18421 | 5.3927 | 5.3763 | 5.3616 | 5.3437 | 5.3232 | 5.301 | 5.2776 | 5.2598 | 5.2415 | 5.2233 | 5.2049 | 5.0919 | 4.8845 | 4.4741 | 5.2746 | 5.2583 | 5.2435 | 5.2257 | 5.2051 | 5.1829 | 5.1596 | 5.1417 | 5.1235 | 5.1052 | 5.0868 | 4.8647 | 4.497 | 4.0606 | 5.2428 | 5.2265 | 5.2118 | 5.1939 | 5.1733 | 5.1512 | 5.1278 | 5.11 | 5.0917 | 5.0734 | 5.055 | 5.0362 | 5.0142 | 4.9907
|  | DORNOCH | LW |  |  |  | 0.18421 | 5.4019 | 5.3694 | 5.354 | 5.3324 | 5.3082 | 5.282 | 5.2547 | 5.2318 | 5.2088 | 5.1854 | 5.1625 | 4.9374 | 4.4758 | 3.8434 | 5.2839 | 5.2513 | 5.2359 | 5.2143 | 5.1901 | 5.164 | 5.1366 | 5.1138 | 5.0907 | 5.0479 | 4.9672 | 4.5433 | 4.0436 | 3.3738 | 5.2521 | 5.2196 | 5.2042 | 5.1825 | 5.1584 | 5.1322 | 5.1049 | 5.082 | 5.0589 | 5.0356 | 5.0126 | 4.9767 | 4.8955 | 4.8136
|  | DORNOCH | ST |  |  |  | 0.18421 | 5.4044 | 5.3989 | 5.3953 | 5.3887 | 5.3809 | 5.3721 | 5.3625 | 5.3578 | 5.3531 | 5.3486 | 5.3441 | 5.3233 | 5.2539 | 5.2142 | 5.2864 | 5.2808 | 5.2773 | 5.2706 | 5.2628 | 5.254 | 5.2444 | 5.2397 | 5.2351 | 5.2305 | 5.2261 | 5.2053 | 5.1359 | 5.0012 | 5.2546 | 5.249 | 5.2455 | 5.2388 | 5.2311 | 5.2223 | 5.2126 | 5.208 | 5.2033 | 5.1987 | 5.1943 | 5.1735 | 5.1041 | 5.0644
|  | DORNOCH | FS |  |  |  | 0.18421 | 5.4053 | 5.4009 | 5.3999 | 5.3989 | 5.3978 | 5.3965 | 5.3953 | 5.393 | 5.3904 | 5.3877 | 5.3848 | 5.3752 | 5.343 | 5.2779 | 5.2872 | 5.2829 | 5.2819 | 5.2808 | 5.2797 | 5.2785 | 5.2772 | 5.2749 | 5.2724 | 5.2696 | 5.2668 | 5.2571 | 5.2249 | 5.1598 | 5.2555 | 5.2511 | 5.2501 | 5.2491 | 5.2479 | 5.2467 | 5.2455 | 5.2431 | 5.2406 | 5.2379 | 5.235 | 5.2254 | 5.1932 | 5.128
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0 | 1.3364 | 1.3236 | 1.3123 | 1.2935 | 1.2744 | 1.2553 | 1.2363 | 1.2174 | 1.1985 | 1.1798 | 1.1613 | 1.066 | 0.95659 | 0.8144 | 1.3126 | 1.3063 | 1.3035 | 1.2997 | 1.2952 | 1.2898 | 1.2832 | 1.2776 | 1.272 | 1.2663 | 1.2476 | 1.1406 | 1.0115 | 0.84791 | 1.2257 | 1.2189 | 1.2155 | 1.2104 | 1.2048 | 1.1989 | 1.1928 | 1.1876 | 1.1825 | 1.1773 | 1.1722 | 1.1671 | 1.1507 | 1.1288
|  | DOUGLAS PIER | CT |  |  |  | 0 | 1.3385 | 1.3314 | 1.3236 | 1.311 | 1.2979 | 1.2847 | 1.2715 | 1.2587 | 1.2459 | 1.2332 | 1.2206 | 1.1545 | 1.0793 | 0.99154 | 1.3126 | 1.3105 | 1.3087 | 1.3063 | 1.3033 | 1.2998 | 1.2962 | 1.2931 | 1.2895 | 1.2859 | 1.2822 | 1.2396 | 1.1564 | 1.0575 | 1.2259 | 1.2234 | 1.2211 | 1.2179 | 1.2141 | 1.2099 | 1.2054 | 1.2022 | 1.1989 | 1.1956 | 1.1923 | 1.1889 | 1.1849 | 1.1808
|  | DOUGLAS PIER | LW |  |  |  | 0 | 1.3364 | 1.3236 | 1.3123 | 1.2935 | 1.2744 | 1.2553 | 1.2363 | 1.2174 | 1.1985 | 1.1798 | 1.1613 | 1.066 | 0.95659 | 0.8144 | 1.3126 | 1.3063 | 1.3035 | 1.2997 | 1.2952 | 1.2898 | 1.2832 | 1.2776 | 1.272 | 1.2663 | 1.2476 | 1.1406 | 1.0115 | 0.84791 | 1.2257 | 1.2189 | 1.2155 | 1.2104 | 1.2048 | 1.1989 | 1.1928 | 1.1876 | 1.1825 | 1.1773 | 1.1722 | 1.1671 | 1.1507 | 1.1288
|  | DOUGLAS PIER | ST |  |  |  | 0 | 1.345 | 1.3434 | 1.3422 | 1.3341 | 1.3258 | 1.3175 | 1.3091 | 1.3015 | 1.294 | 1.2866 | 1.2793 | 1.2443 | 1.2006 | 1.1636 | 1.3126 | 1.3118 | 1.3114 | 1.3104 | 1.3092 | 1.3078 | 1.3062 | 1.3056 | 1.305 | 1.3044 | 1.3039 | 1.2983 | 1.2827 | 1.248 | 1.2264 | 1.2255 | 1.2251 | 1.2235 | 1.2218 | 1.2198 | 1.2177 | 1.2165 | 1.2154 | 1.2143 | 1.2132 | 1.2081 | 1.1936 | 1.1849
|  | DOUGLAS PIER | FS |  |  |  | 0 | 1.3454 | 1.3439 | 1.3431 | 1.3421 | 1.3398 | 1.3351 | 1.3304 | 1.3252 | 1.3199 | 1.3146 | 1.3093 | 1.284 | 1.2552 | 1.2208 | 1.3126 | 1.3119 | 1.3119 | 1.3118 | 1.3118 | 1.3117 | 1.3116 | 1.3113 | 1.311 | 1.3106 | 1.3102 | 1.3092 | 1.3015 | 1.2871 | 1.2264 | 1.2256 | 1.2256 | 1.2254 | 1.2252 | 1.2248 | 1.2243 | 1.2236 | 1.2229 | 1.2222 | 1.2214 | 1.2184 | 1.2111 | 1.1974
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0 | 2.6902 | 2.6832 | 2.6802 | 2.6759 | 2.671 | 2.6657 | 2.6601 | 2.6557 | 2.6512 | 2.6467 | 2.6422 | 2.6145 | 2.5318 | 2.3946 | 2.7163 | 2.7094 | 2.7063 | 2.702 | 2.6901 | 2.6717 | 2.6535 | 2.6359 | 2.6185 | 2.6011 | 2.5841 | 2.4945 | 2.3877 | 2.2416 | 2.6207 | 2.6137 | 2.6107 | 2.6064 | 2.6013 | 2.5952 | 2.5888 | 2.5836 | 2.5783 | 2.573 | 2.5678 | 2.5626 | 2.5564 | 2.5499
|  | DRIMORE | CT |  |  |  | 0 | 2.6902 | 2.6877 | 2.6857 | 2.6829 | 2.6795 | 2.6755 | 2.6712 | 2.6684 | 2.6655 | 2.6626 | 2.6597 | 2.6405 | 2.6097 | 2.552 | 2.7163 | 2.7139 | 2.7118 | 2.709 | 2.7056 | 2.6995 | 2.6865 | 2.6745 | 2.6626 | 2.6508 | 2.6392 | 2.5771 | 2.5028 | 2.4128 | 2.6207 | 2.6182 | 2.6162 | 2.6134 | 2.61 | 2.606 | 2.6013 | 2.5979 | 2.5945 | 2.591 | 2.5876 | 2.584 | 2.5796 | 2.5751
|  | DRIMORE | LW |  |  |  | 0 | 2.6902 | 2.6832 | 2.6802 | 2.6759 | 2.671 | 2.6657 | 2.6601 | 2.6557 | 2.6512 | 2.6467 | 2.6422 | 2.6145 | 2.5318 | 2.3946 | 2.7163 | 2.7094 | 2.7063 | 2.702 | 2.6901 | 2.6717 | 2.6535 | 2.6359 | 2.6185 | 2.6011 | 2.5841 | 2.4945 | 2.3877 | 2.2416 | 2.6207 | 2.6137 | 2.6107 | 2.6064 | 2.6013 | 2.5952 | 2.5888 | 2.5836 | 2.5783 | 2.573 | 2.5678 | 2.5626 | 2.5564 | 2.5499
|  | DRIMORE | ST |  |  |  | 0 | 2.6902 | 2.6892 | 2.6888 | 2.6876 | 2.6862 | 2.6845 | 2.6826 | 2.6819 | 2.6812 | 2.6805 | 2.6799 | 2.6769 | 2.6622 | 2.6547 | 2.7163 | 2.7154 | 2.7149 | 2.7137 | 2.7123 | 2.7106 | 2.7087 | 2.708 | 2.7073 | 2.7066 | 2.7001 | 2.6675 | 2.628 | 2.5966 | 2.6207 | 2.6197 | 2.6193 | 2.6181 | 2.6167 | 2.615 | 2.6131 | 2.6124 | 2.6117 | 2.611 | 2.6102 | 2.6055 | 2.5893 | 2.5803
|  | DRIMORE | FS |  |  |  | 0 | 2.6902 | 2.6893 | 2.6893 | 2.6892 | 2.6892 | 2.6891 | 2.689 | 2.6886 | 2.6882 | 2.6877 | 2.6873 | 2.686 | 2.6791 | 2.6643 | 2.7163 | 2.7154 | 2.7154 | 2.7154 | 2.7153 | 2.7152 | 2.7151 | 2.7147 | 2.7143 | 2.7139 | 2.7134 | 2.7037 | 2.6754 | 2.6399 | 2.6207 | 2.6198 | 2.6198 | 2.6197 | 2.6197 | 2.6196 | 2.6195 | 2.6191 | 2.6187 | 2.6182 | 2.6178 | 2.6162 | 2.6081 | 2.5919
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | YES | 0.031579 | 6.7096 | 6.6929 | 6.6774 | 6.6596 | 6.6399 | 6.6185 | 6.5962 | 6.5784 | 6.5604 | 6.5415 | 6.4941 | 6.2282 | 5.9023 | 5.4437 | 6.1761 | 6.1594 | 6.1438 | 6.126 | 6.1063 | 6.0849 | 6.0371 | 5.9764 | 5.9162 | 5.8556 | 5.796 | 5.4823 | 5.1082 | 4.6075 | 6.3006 | 6.2839 | 6.2684 | 6.2506 | 6.2309 | 6.2094 | 6.1871 | 6.1694 | 6.1514 | 6.1198 | 6.0578 | 5.9967 | 5.9316 | 5.8661
|  | DRUMNADROCHIT | CT |  |  |  | 0.031579 | 6.7096 | 6.6929 | 6.6774 | 6.6596 | 6.6399 | 6.6185 | 6.5962 | 6.5784 | 6.5604 | 6.5415 | 6.5225 | 6.3604 | 6.1003 | 5.7868 | 6.1761 | 6.1594 | 6.1438 | 6.126 | 6.1063 | 6.0849 | 6.0626 | 6.0449 | 5.9982 | 5.9508 | 5.9038 | 5.6573 | 5.3634 | 5.017 | 6.3006 | 6.2839 | 6.2684 | 6.2506 | 6.2309 | 6.2094 | 6.1871 | 6.1694 | 6.1514 | 6.1325 | 6.1135 | 6.0942 | 6.0727 | 6.0215
|  | DRUMNADROCHIT | LW |  |  |  | 0.031579 | 6.7256 | 6.7011 | 6.688 | 6.671 | 6.6513 | 6.6303 | 6.6076 | 6.5887 | 6.5696 | 6.544 | 6.4941 | 6.2282 | 5.9023 | 5.4437 | 6.1921 | 6.1676 | 6.1544 | 6.1374 | 6.1178 | 6.0968 | 6.0371 | 5.9764 | 5.9162 | 5.8556 | 5.796 | 5.4823 | 5.1082 | 4.6075 | 6.3166 | 6.2921 | 6.279 | 6.262 | 6.2423 | 6.2213 | 6.1986 | 6.1796 | 6.1606 | 6.1198 | 6.0578 | 5.9967 | 5.9316 | 5.8661
|  | DRUMNADROCHIT | ST |  |  |  | 0.031579 | 6.729 | 6.7237 | 6.7199 | 6.7138 | 6.707 | 6.6994 | 6.6913 | 6.6867 | 6.682 | 6.6775 | 6.673 | 6.6516 | 6.596 | 6.5184 | 6.1954 | 6.1902 | 6.1863 | 6.1803 | 6.1734 | 6.1659 | 6.1577 | 6.1531 | 6.1484 | 6.1439 | 6.1394 | 6.0713 | 5.9346 | 5.819 | 6.32 | 6.3147 | 6.3109 | 6.3048 | 6.298 | 6.2904 | 6.2823 | 6.2776 | 6.273 | 6.2684 | 6.264 | 6.2426 | 6.187 | 6.0805
|  | DRUMNADROCHIT | FS |  |  |  | 0.031579 | 6.7315 | 6.7282 | 6.7264 | 6.7246 | 6.7227 | 6.7207 | 6.7188 | 6.716 | 6.7131 | 6.7101 | 6.707 | 6.6948 | 6.6666 | 6.6152 | 6.198 | 6.1946 | 6.1928 | 6.191 | 6.1891 | 6.1872 | 6.1852 | 6.1825 | 6.1796 | 6.1766 | 6.1735 | 6.1612 | 6.0937 | 5.9769 | 6.3225 | 6.3192 | 6.3174 | 6.3156 | 6.3137 | 6.3117 | 6.3098 | 6.307 | 6.3041 | 6.3011 | 6.298 | 6.2857 | 6.2575 | 6.2061
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | YES | 0 | 0.26175 | 0.25996 | 0.25917 | 0.25807 | 0.25682 | 0.25515 | 0.25009 | 0.24444 | 0.23882 | 0.23324 | 0.22773 | 0.20237 | 0.17003 | 0.12842 | 0.24104 | 0.23916 | 0.23826 | 0.23695 | 0.2355 | 0.23394 | 0.23232 | 0.2262 | 0.21979 | 0.21342 | 0.20714 | 0.17852 | 0.14236 | 0.096991 | 0.24592 | 0.24414 | 0.24335 | 0.24225 | 0.24099 | 0.23667 | 0.23128 | 0.22523 | 0.21922 | 0.21324 | 0.20735 | 0.20151 | 0.19628 | 0.19101
|  | DRUMRUNIE | CT |  |  |  | 0 | 0.26175 | 0.26115 | 0.26064 | 0.25995 | 0.25911 | 0.25812 | 0.25681 | 0.25303 | 0.24927 | 0.24553 | 0.24183 | 0.22251 | 0.20057 | 0.1751 | 0.24106 | 0.24038 | 0.23978 | 0.23892 | 0.23791 | 0.23677 | 0.23556 | 0.23471 | 0.23139 | 0.22712 | 0.22289 | 0.20097 | 0.17643 | 0.14842 | 0.24592 | 0.24532 | 0.24482 | 0.24413 | 0.24328 | 0.2423 | 0.23833 | 0.23428 | 0.23024 | 0.22624 | 0.22227 | 0.21831 | 0.21418 | 0.21003
|  | DRUMRUNIE | LW |  |  |  | 0 | 0.26175 | 0.25996 | 0.25917 | 0.25807 | 0.25682 | 0.25515 | 0.25009 | 0.24444 | 0.23882 | 0.23324 | 0.22773 | 0.20237 | 0.17003 | 0.12842 | 0.24104 | 0.23916 | 0.23826 | 0.23695 | 0.2355 | 0.23394 | 0.23232 | 0.2262 | 0.21979 | 0.21342 | 0.20714 | 0.17852 | 0.14236 | 0.096991 | 0.24592 | 0.24414 | 0.24335 | 0.24225 | 0.24099 | 0.23667 | 0.23128 | 0.22523 | 0.21922 | 0.21324 | 0.20735 | 0.20151 | 0.19628 | 0.19101
|  | DRUMRUNIE | ST |  |  |  | 0 | 0.26175 | 0.26153 | 0.26142 | 0.26114 | 0.26079 | 0.26038 | 0.25993 | 0.25976 | 0.25959 | 0.25943 | 0.25927 | 0.25424 | 0.24284 | 0.23338 | 0.24121 | 0.24098 | 0.24088 | 0.24049 | 0.24005 | 0.23955 | 0.23901 | 0.23875 | 0.23848 | 0.23823 | 0.23798 | 0.23673 | 0.22392 | 0.21311 | 0.24592 | 0.2457 | 0.2456 | 0.24531 | 0.24497 | 0.24456 | 0.24411 | 0.24394 | 0.24377 | 0.24361 | 0.24345 | 0.23539 | 0.22329 | 0.21315
|  | DRUMRUNIE | FS |  |  |  | 0 | 0.26175 | 0.26155 | 0.26154 | 0.26153 | 0.26152 | 0.2615 | 0.26148 | 0.26139 | 0.2613 | 0.2612 | 0.26108 | 0.26079 | 0.25338 | 0.24299 | 0.24122 | 0.24102 | 0.24101 | 0.24099 | 0.24096 | 0.24086 | 0.24077 | 0.2406 | 0.24043 | 0.24025 | 0.24005 | 0.23936 | 0.2356 | 0.22396 | 0.24592 | 0.24573 | 0.24572 | 0.24571 | 0.2457 | 0.24567 | 0.24565 | 0.24557 | 0.24548 | 0.24537 | 0.24526 | 0.24387 | 0.2344 | 0.22339
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.062105 | 0.94807 | 0.93169 | 0.92292 | 0.9107 | 0.89683 | 0.88171 | 0.86496 | 0.85163 | 0.83816 | 0.82449 | 0.81107 | 0.72758 | 0.52366 | 0.12981 | 1.4134 | 1.397 | 1.3882 | 1.376 | 1.3621 | 1.347 | 1.3302 | 1.3169 | 1.3034 | 1.2898 | 1.2764 | 1.1929 | 0.94647 | 0.52773 | 0.97165 | 0.93337 | 0.9031 | 0.85099 | 0.79813 | 0.74592 | 0.69348 | 0.64197 | 0.59088 | 0.5402 | 0.49036 | 0.44126 | 0.39009 | 0.33847
|  | DRYMEN | CT |  |  |  | 0.062105 | 0.94807 | 0.93966 | 0.93229 | 0.92288 | 0.91174 | 0.89903 | 0.88552 | 0.87613 | 0.86648 | 0.85678 | 0.84704 | 0.78618 | 0.69391 | 0.55229 | 1.4134 | 1.405 | 1.3976 | 1.3882 | 1.377 | 1.3643 | 1.3508 | 1.3414 | 1.3318 | 1.3221 | 1.3123 | 1.2515 | 1.1592 | 0.98685 | 0.97371 | 0.95118 | 0.92831 | 0.89098 | 0.85255 | 0.81388 | 0.77539 | 0.739 | 0.70275 | 0.66688 | 0.63138 | 0.59598 | 0.55847 | 0.52074
|  | DRYMEN | LW |  |  |  | 0.062105 | 0.95144 | 0.93169 | 0.92292 | 0.9107 | 0.89683 | 0.88171 | 0.86496 | 0.85163 | 0.83816 | 0.82449 | 0.81107 | 0.72758 | 0.52366 | 0.12981 | 1.4167 | 1.397 | 1.3882 | 1.376 | 1.3621 | 1.347 | 1.3302 | 1.3169 | 1.3034 | 1.2898 | 1.2764 | 1.1929 | 0.94647 | 0.52773 | 0.97165 | 0.93337 | 0.9031 | 0.85099 | 0.79813 | 0.74592 | 0.69348 | 0.64197 | 0.59088 | 0.5402 | 0.49036 | 0.44126 | 0.39009 | 0.33847
|  | DRYMEN | ST |  |  |  | 0.062105 | 0.95228 | 0.94977 | 0.94857 | 0.94534 | 0.94141 | 0.9368 | 0.93166 | 0.92974 | 0.9278 | 0.92595 | 0.92417 | 0.91614 | 0.87658 | 0.85626 | 1.4176 | 1.4151 | 1.4139 | 1.4106 | 1.4067 | 1.4021 | 1.3969 | 1.395 | 1.3931 | 1.3912 | 1.3895 | 1.3814 | 1.3419 | 1.3215 | 1 | 0.99589 | 0.99312 | 0.97139 | 0.9492 | 0.92718 | 0.90518 | 0.88527 | 0.86572 | 0.84665 | 0.82806 | 0.74028 | 0.62484 | 0.53164
|  | DRYMEN | FS |  |  |  | 0.062105 | 0.95228 | 0.94996 | 0.94986 | 0.94974 | 0.94956 | 0.9493 | 0.94905 | 0.94805 | 0.94693 | 0.9457 | 0.94436 | 0.94081 | 0.92239 | 0.88232 | 1.4176 | 1.4153 | 1.4151 | 1.415 | 1.4148 | 1.4146 | 1.4143 | 1.4133 | 1.4122 | 1.411 | 1.4097 | 1.4061 | 1.3877 | 1.3476 | 1.0012 | 0.99833 | 0.99667 | 0.99429 | 0.989 | 0.97694 | 0.96495 | 0.94986 | 0.93468 | 0.91943 | 0.90411 | 0.83211 | 0.74954 | 0.64873
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 1.2642 | 4.0115 | 3.9919 | 3.9732 | 3.9527 | 3.9305 | 3.9079 | 3.8845 | 3.864 | 3.8433 | 3.8218 | 3.7811 | 3.4982 | 3.1543 | 2.703 | 3.9575 | 3.9379 | 3.9192 | 3.8987 | 3.8766 | 3.8281 | 3.7681 | 3.7083 | 3.6488 | 3.589 | 3.5301 | 3.2213 | 2.8573 | 2.3865 | 3.8496 | 3.83 | 3.8113 | 3.7695 | 3.7085 | 3.6469 | 3.586 | 3.5252 | 3.4649 | 3.4042 | 3.3443 | 3.2852 | 3.2229 | 3.1594
|  | DRYNOCH | CT |  |  |  | 1.2642 | 4.0115 | 3.9919 | 3.9732 | 3.9527 | 3.9305 | 3.9079 | 3.8845 | 3.864 | 3.8433 | 3.8218 | 3.8003 | 3.6 | 3.3141 | 2.9793 | 3.9575 | 3.9379 | 3.9192 | 3.8987 | 3.8766 | 3.8463 | 3.796 | 3.7467 | 3.6976 | 3.648 | 3.5989 | 3.3418 | 3.0408 | 2.6923 | 3.8496 | 3.83 | 3.8113 | 3.7695 | 3.7176 | 3.6664 | 3.6154 | 3.5654 | 3.5157 | 3.4655 | 3.4157 | 3.3661 | 3.314 | 3.2617
|  | DRYNOCH | LW |  |  |  | 1.2642 | 4.0359 | 4.0132 | 3.9999 | 3.9834 | 3.9645 | 3.9436 | 3.922 | 3.9028 | 3.8721 | 3.8263 | 3.7811 | 3.4982 | 3.1543 | 2.703 | 3.982 | 3.9592 | 3.9459 | 3.9294 | 3.8888 | 3.8281 | 3.7681 | 3.7083 | 3.6488 | 3.589 | 3.5301 | 3.2213 | 2.8573 | 2.3865 | 3.8741 | 3.8513 | 3.8298 | 3.7699 | 3.7085 | 3.6469 | 3.586 | 3.5252 | 3.4649 | 3.4042 | 3.3443 | 3.2852 | 3.2229 | 3.1594
|  | DRYNOCH | ST |  |  |  | 1.2642 | 4.0401 | 4.0345 | 4.0301 | 4.0238 | 4.0161 | 4.0078 | 3.9999 | 3.9948 | 3.9897 | 3.9847 | 3.9797 | 3.9541 | 3.8816 | 3.7932 | 3.9862 | 3.9806 | 3.9761 | 3.9699 | 3.9622 | 3.9539 | 3.9459 | 3.9408 | 3.9357 | 3.9261 | 3.9025 | 3.7898 | 3.6548 | 3.5392 | 3.8783 | 3.8727 | 3.8682 | 3.862 | 3.8543 | 3.846 | 3.821 | 3.7957 | 3.7707 | 3.7462 | 3.7222 | 3.6075 | 3.4706 | 3.3533
|  | DRYNOCH | FS |  |  |  | 1.2642 | 4.0427 | 4.039 | 4.0364 | 4.0338 | 4.0311 | 4.0283 | 4.0256 | 4.0222 | 4.0188 | 4.0152 | 4.0115 | 3.9959 | 3.9677 | 3.9214 | 3.9887 | 3.9851 | 3.9824 | 3.9798 | 3.9771 | 3.9744 | 3.9716 | 3.9683 | 3.9648 | 3.9612 | 3.9576 | 3.9141 | 3.8209 | 3.713 | 3.8808 | 3.8772 | 3.8745 | 3.8719 | 3.8692 | 3.8665 | 3.8637 | 3.8604 | 3.8563 | 3.8382 | 3.8201 | 3.7336 | 3.639 | 3.5297
| KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0.061053 | 6.7685 | 6.7341 | 6.7012 | 6.6663 | 6.6291 | 6.5897 | 6.5501 | 6.5144 | 6.4774 | 6.4404 | 6.4033 | 6.1858 | 5.7928 | 5.0902 | 6.5334 | 6.4991 | 6.4661 | 6.4312 | 6.394 | 6.3546 | 6.315 | 6.2551 | 6.1763 | 6.0971 | 6.018 | 5.5771 | 5.0067 | 4.2632 | 6.314 | 6.2797 | 6.2467 | 6.2118 | 6.1746 | 6.1352 | 6.0851 | 6.0088 | 5.9273 | 5.8455 | 5.7637 | 5.6828 | 5.595 | 5.5029
|  | DUFFTOWN | CT |  |  |  | 0.061053 | 6.7685 | 6.7341 | 6.7012 | 6.6663 | 6.6291 | 6.5897 | 6.5501 | 6.5144 | 6.4774 | 6.4404 | 6.4033 | 6.1858 | 5.8963 | 5.4094 | 6.5334 | 6.4991 | 6.4661 | 6.4312 | 6.394 | 6.3546 | 6.315 | 6.2553 | 6.1854 | 6.1159 | 6.0468 | 5.6718 | 5.2151 | 4.6444 | 6.314 | 6.2797 | 6.2467 | 6.2118 | 6.1746 | 6.1352 | 6.0851 | 6.0142 | 5.9424 | 5.8711 | 5.8002 | 5.7284 | 5.6528 | 5.576
|  | DUFFTOWN | LW |  |  |  | 0.061053 | 6.8114 | 6.7774 | 6.7573 | 6.7308 | 6.7013 | 6.6693 | 6.6353 | 6.6051 | 6.5738 | 6.5413 | 6.5084 | 6.3116 | 5.7928 | 5.0902 | 6.5764 | 6.5424 | 6.5222 | 6.4958 | 6.4663 | 6.4121 | 6.3334 | 6.2551 | 6.1763 | 6.0971 | 6.018 | 5.5771 | 5.0067 | 4.2632 | 6.357 | 6.323 | 6.3028 | 6.2764 | 6.2469 | 6.1711 | 6.0898 | 6.0088 | 5.9273 | 5.8455 | 5.7637 | 5.6828 | 5.595 | 5.5029
|  | DUFFTOWN | ST |  |  |  | 0.061053 | 6.8207 | 6.8114 | 6.8038 | 6.7935 | 6.7806 | 6.7675 | 6.7538 | 6.7444 | 6.735 | 6.7257 | 6.7166 | 6.671 | 6.5802 | 6.5108 | 6.5856 | 6.5763 | 6.5688 | 6.5584 | 6.5455 | 6.5325 | 6.5187 | 6.5093 | 6.4999 | 6.4907 | 6.4815 | 6.353 | 6.1643 | 6.0001 | 6.3662 | 6.3569 | 6.3494 | 6.339 | 6.3261 | 6.3131 | 6.2993 | 6.2899 | 6.2805 | 6.2713 | 6.2621 | 6.1085 | 5.9143 | 5.7446
|  | DUFFTOWN | FS |  |  |  | 0.061053 | 6.8249 | 6.8184 | 6.8132 | 6.8088 | 6.8043 | 6.7998 | 6.7952 | 6.7896 | 6.7839 | 6.778 | 6.7719 | 6.7426 | 6.6928 | 6.6163 | 6.5898 | 6.5833 | 6.5781 | 6.5737 | 6.5693 | 6.5647 | 6.5601 | 6.5546 | 6.5488 | 6.5429 | 6.5369 | 6.5076 | 6.3847 | 6.2337 | 6.3704 | 6.3639 | 6.3587 | 6.3543 | 6.3498 | 6.3453 | 6.3407 | 6.3352 | 6.3294 | 6.3235 | 6.3175 | 6.2744 | 6.1408 | 5.9856
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 0.31474 | 15.5891 | 15.5311 | 15.4859 | 15.4246 | 15.3545 | 15.2788 | 15.1986 | 15.1336 | 15.0669 | 14.9985 | 14.9303 | 14.5136 | 13.4382 | 11.6877 | 14.381 | 14.3229 | 14.2777 | 14.2165 | 14.1464 | 14.0706 | 13.9905 | 13.9254 | 13.8588 | 13.7903 | 13.7221 | 12.8262 | 11.4838 | 9.6365 | 14.5378 | 14.4798 | 14.4345 | 14.3733 | 14.3032 | 14.2275 | 14.1473 | 14.0823 | 14.0156 | 13.9472 | 13.879 | 13.8113 | 13.7296 | 13.6443
|  | DUNBLANE | CT |  |  |  | 0.31474 | 15.5891 | 15.5407 | 15.4967 | 15.444 | 15.3837 | 15.3166 | 15.2468 | 15.1931 | 15.1382 | 15.0831 | 15.0277 | 14.6842 | 14.1802 | 13.2855 | 14.381 | 14.3325 | 14.2886 | 14.2358 | 14.1756 | 14.1085 | 14.0386 | 13.985 | 13.9301 | 13.875 | 13.8196 | 13.4761 | 12.6106 | 11.4019 | 14.5378 | 14.4894 | 14.4454 | 14.3927 | 14.3324 | 14.2653 | 14.1955 | 14.1418 | 14.0869 | 14.0318 | 13.9764 | 13.9196 | 13.8519 | 13.7818
|  | DUNBLANE | LW |  |  |  | 0.31474 | 15.6236 | 15.5311 | 15.4859 | 15.4246 | 15.3545 | 15.2788 | 15.1986 | 15.1336 | 15.0669 | 14.9985 | 14.9303 | 14.5136 | 13.4382 | 11.6877 | 14.4155 | 14.3229 | 14.2777 | 14.2165 | 14.1464 | 14.0706 | 13.9905 | 13.9254 | 13.8588 | 13.7903 | 13.7221 | 12.8262 | 11.4838 | 9.6365 | 14.5723 | 14.4798 | 14.4345 | 14.3733 | 14.3032 | 14.2275 | 14.1473 | 14.0823 | 14.0156 | 13.9472 | 13.879 | 13.8113 | 13.7296 | 13.6443
|  | DUNBLANE | ST |  |  |  | 0.31474 | 15.6312 | 15.616 | 15.6065 | 15.5882 | 15.5651 | 15.539 | 15.5106 | 15.4963 | 15.4819 | 15.4679 | 15.4542 | 15.3911 | 15.1872 | 15.0636 | 14.4231 | 14.4079 | 14.3984 | 14.38 | 14.3569 | 14.3309 | 14.3024 | 14.2881 | 14.2737 | 14.2597 | 14.2461 | 14.1829 | 13.9791 | 13.8554 | 14.5799 | 14.5647 | 14.5552 | 14.5369 | 14.5138 | 14.4877 | 14.4593 | 14.4449 | 14.4306 | 14.4165 | 14.4029 | 14.3398 | 14.1359 | 14.0122
|  | DUNBLANE | FS |  |  |  | 0.31474 | 15.6346 | 15.6216 | 15.6178 | 15.6138 | 15.6097 | 15.6051 | 15.6006 | 15.5928 | 15.5844 | 15.5754 | 15.566 | 15.5306 | 15.4305 | 15.2323 | 14.4264 | 14.4135 | 14.4096 | 14.4057 | 14.4015 | 14.397 | 14.3925 | 14.3846 | 14.3762 | 14.3673 | 14.3579 | 14.3225 | 14.2224 | 14.0242 | 14.5833 | 14.5703 | 14.5665 | 14.5625 | 14.5583 | 14.5538 | 14.5493 | 14.5415 | 14.533 | 14.5241 | 14.5147 | 14.4793 | 14.3792 | 14.181
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0 | 24.7632 | 24.7011 | 24.6736 | 24.6352 | 24.5917 | 24.5436 | 24.4926 | 24.4525 | 24.4113 | 24.3693 | 24.3279 | 24.0027 | 22.9489 | 21.4905 | 24.4474 | 24.3854 | 24.3578 | 24.3194 | 24.2759 | 24.2278 | 24.1769 | 24.1367 | 24.0955 | 24.0535 | 23.9171 | 22.9359 | 21.7815 | 20.2219 | 24.4789 | 24.4169 | 24.3894 | 24.351 | 24.3075 | 24.2594 | 24.2084 | 24.1683 | 24.1271 | 24.0206 | 23.8399 | 23.6631 | 23.4734 | 23.283
|  | DUNOON | CT |  |  |  | 0 | 24.7632 | 24.7416 | 24.7234 | 24.6986 | 24.6683 | 24.6325 | 24.5938 | 24.5685 | 24.5418 | 24.5149 | 24.4876 | 24.3053 | 24.0037 | 23.1676 | 24.4474 | 24.4258 | 24.4076 | 24.3828 | 24.3525 | 24.3167 | 24.278 | 24.2527 | 24.226 | 24.1991 | 24.1718 | 23.8512 | 23.0389 | 22.0527 | 24.4789 | 24.4574 | 24.4392 | 24.4144 | 24.3841 | 24.3483 | 24.3096 | 24.2842 | 24.2576 | 24.2307 | 24.2034 | 24.1749 | 24.1384 | 24.0455
|  | DUNOON | LW |  |  |  | 0 | 24.7632 | 24.7011 | 24.6736 | 24.6352 | 24.5917 | 24.5436 | 24.4926 | 24.4525 | 24.4113 | 24.3693 | 24.3279 | 24.0027 | 22.9489 | 21.4905 | 24.4474 | 24.3854 | 24.3578 | 24.3194 | 24.2759 | 24.2278 | 24.1769 | 24.1367 | 24.0955 | 24.0535 | 23.9171 | 22.9359 | 21.7815 | 20.2219 | 24.4789 | 24.4169 | 24.3894 | 24.351 | 24.3075 | 24.2594 | 24.2084 | 24.1683 | 24.1271 | 24.0206 | 23.8399 | 23.6631 | 23.4734 | 23.283
|  | DUNOON | ST |  |  |  | 0 | 24.7632 | 24.7545 | 24.7503 | 24.7391 | 24.7255 | 24.7096 | 24.6918 | 24.6851 | 24.6784 | 24.672 | 24.6658 | 24.6374 | 24.4905 | 24.4138 | 24.4474 | 24.4387 | 24.4345 | 24.4233 | 24.4097 | 24.3938 | 24.376 | 24.3693 | 24.3626 | 24.3562 | 24.35 | 24.3216 | 24.1747 | 23.9818 | 24.4789 | 24.4703 | 24.4661 | 24.4549 | 24.4413 | 24.4253 | 24.4075 | 24.4009 | 24.3942 | 24.3877 | 24.3816 | 24.3532 | 24.2062 | 23.9058
|  | DUNOON | FS |  |  |  | 0 | 24.7632 | 24.7543 | 24.7539 | 24.7535 | 24.7528 | 24.7518 | 24.7508 | 24.7471 | 24.7428 | 24.7381 | 24.733 | 24.7195 | 24.6481 | 24.4905 | 24.4474 | 24.4386 | 24.4382 | 24.4377 | 24.437 | 24.436 | 24.4351 | 24.4313 | 24.427 | 24.4223 | 24.4172 | 24.4037 | 24.3323 | 24.1747 | 24.4789 | 24.4701 | 24.4697 | 24.4693 | 24.4686 | 24.4676 | 24.4666 | 24.4629 | 24.4586 | 24.4539 | 24.4488 | 24.4353 | 24.3639 | 24.2063
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 0 | 3.1892 | 3.1669 | 3.1455 | 3.1206 | 3.0946 | 3.067 | 3.0387 | 3.0139 | 2.9261 | 2.8636 | 2.802 | 2.4779 | 2.0848 | 1.5462 | 3.0975 | 3.0765 | 3.0567 | 3.0346 | 3.0114 | 2.9865 | 2.9514 | 2.8895 | 2.7328 | 2.6543 | 2.577 | 2.1772 | 1.7141 | 1.1203 | 3.0172 | 2.9962 | 2.9764 | 2.9543 | 2.9311 | 2.8916 | 2.8344 | 2.7782 | 2.6352 | 2.5584 | 2.4826 | 2.4078 | 2.3301 | 2.251
|  | DUNVEGAN | CT |  |  |  | 0 | 3.1892 | 3.1669 | 3.1455 | 3.1206 | 3.0946 | 3.067 | 3.0387 | 3.0139 | 2.9852 | 2.9343 | 2.8837 | 2.6176 | 2.3021 | 1.9291 | 3.0975 | 3.0765 | 3.0567 | 3.0346 | 3.0114 | 2.9865 | 2.9514 | 2.8895 | 2.8277 | 2.7656 | 2.704 | 2.385 | 2.0159 | 1.5906 | 3.0172 | 2.9962 | 2.9764 | 2.9543 | 2.9311 | 2.8916 | 2.8344 | 2.7782 | 2.7222 | 2.6655 | 2.6051 | 2.5448 | 2.4825 | 2.42
|  | DUNVEGAN | LW |  |  |  | 0 | 3.9703 | 3.9416 | 3.9251 | 3.902 | 3.8763 | 3.8484 | 3.8085 | 3.7461 | 2.9261 | 2.8636 | 2.802 | 2.4779 | 2.0848 | 1.5462 | 3.879 | 3.8522 | 3.8379 | 3.8189 | 3.7971 | 3.7258 | 3.6475 | 3.5688 | 2.7328 | 2.6543 | 2.577 | 2.1772 | 1.7141 | 1.1203 | 3.7987 | 3.7718 | 3.7576 | 3.7386 | 3.6852 | 3.6142 | 3.5438 | 3.4696 | 2.6352 | 2.5584 | 2.4826 | 2.4078 | 2.3301 | 2.251
|  | DUNVEGAN | ST |  |  |  | 0 | 3.977 | 3.9707 | 3.9659 | 3.9571 | 3.9467 | 3.9365 | 3.9258 | 3.9184 | 3.9111 | 3.9038 | 3.1388 | 3.0794 | 2.9356 | 2.8147 | 3.8832 | 3.8771 | 3.8724 | 3.8655 | 3.857 | 3.8486 | 3.8396 | 3.8342 | 3.8287 | 3.8233 | 3.0601 | 2.9129 | 2.7365 | 2.5842 | 3.8029 | 3.7968 | 3.7921 | 3.7852 | 3.7767 | 3.7683 | 3.7593 | 3.7538 | 3.7483 | 3.7286 | 2.9433 | 2.812 | 2.6395 | 2.4904
|  | DUNVEGAN | FS |  |  |  | 0 | 3.9797 | 3.9755 | 3.9727 | 3.9698 | 3.9665 | 3.9625 | 3.9585 | 3.9536 | 3.9485 | 3.9433 | 3.938 | 3.9149 | 3.8676 | 3.7513 | 3.8857 | 3.8816 | 3.879 | 3.8763 | 3.8736 | 3.8708 | 3.868 | 3.8645 | 3.8608 | 3.8569 | 3.853 | 3.8308 | 3.7076 | 3.5663 | 3.8054 | 3.8013 | 3.7987 | 3.796 | 3.7933 | 3.7905 | 3.7877 | 3.7841 | 3.7804 | 3.7766 | 3.7727 | 3.7132 | 3.6034 | 3.4679
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.43263 | 27.9516 | 27.9084 | 27.8823 | 27.6678 | 27.1884 | 26.7401 | 26.3462 | 25.9371 | 25.5536 | 25.1916 | 24.8765 | 23.4716 | 22.1384 | 20.5773 | 26.2637 | 25.7849 | 25.2942 | 24.7209 | 24.1806 | 23.6763 | 23.2342 | 22.7738 | 22.3425 | 21.9359 | 21.5825 | 20.0163 | 18.5417 | 16.829 | 27.2502 | 26.985 | 26.5232 | 25.9329 | 25.3769 | 24.8579 | 24.4034 | 23.9296 | 23.4859 | 23.0677 | 22.7044 | 22.3801 | 22.0511 | 21.7282
|  | DYCE NORTH | CT |  |  |  | 0.43263 | 27.9516 | 27.9266 | 27.9045 | 27.8768 | 27.8445 | 27.6919 | 27.4024 | 27.1196 | 26.8454 | 26.5982 | 26.3719 | 25.3097 | 24.3449 | 23.2942 | 26.2695 | 26.2021 | 25.8908 | 25.528 | 25.1462 | 24.7537 | 24.4295 | 24.1114 | 23.8032 | 23.5258 | 23.2722 | 22.0885 | 21.0288 | 19.8905 | 27.2502 | 27.2252 | 27.0677 | 26.7646 | 26.3717 | 25.968 | 25.6348 | 25.3075 | 24.9905 | 24.7052 | 24.4445 | 24.1848 | 23.9303 | 23.6898
|  | DYCE NORTH | LW |  |  |  | 0.43263 | 27.9634 | 27.9084 | 27.8823 | 27.6678 | 27.1884 | 26.7401 | 26.3462 | 25.9371 | 25.5536 | 25.1916 | 24.8765 | 23.4716 | 22.1384 | 20.5773 | 26.2637 | 25.7849 | 25.2942 | 24.7209 | 24.1806 | 23.6763 | 23.2342 | 22.7738 | 22.3425 | 21.9359 | 21.5825 | 20.0163 | 18.5417 | 16.829 | 27.262 | 26.985 | 26.5232 | 25.9329 | 25.3769 | 24.8579 | 24.4034 | 23.9296 | 23.4859 | 23.0677 | 22.7044 | 22.3801 | 22.0511 | 21.7282
|  | DYCE NORTH | ST |  |  |  | 0.43263 | 27.9651 | 27.9564 | 27.9514 | 27.9407 | 27.928 | 27.9135 | 27.8975 | 27.8905 | 27.8834 | 27.8766 | 27.8699 | 27.1697 | 26.5463 | 26.0101 | 26.2964 | 26.2804 | 26.2666 | 26.2423 | 26.0822 | 25.8832 | 25.7018 | 25.5111 | 25.3142 | 25.1283 | 24.9516 | 24.1549 | 23.462 | 22.8613 | 27.2637 | 27.255 | 27.25 | 27.2393 | 27.2235 | 27.0636 | 26.9172 | 26.7467 | 26.5439 | 26.3523 | 26.1702 | 25.3493 | 24.6383 | 24.0209
|  | DYCE NORTH | FS |  |  |  | 0.43263 | 27.9667 | 27.9592 | 27.9572 | 27.9551 | 27.9529 | 27.9505 | 27.9481 | 27.9435 | 27.9385 | 27.9333 | 27.9285 | 27.7369 | 27.2545 | 26.7306 | 26.3012 | 26.2874 | 26.2789 | 26.2692 | 26.2577 | 26.1895 | 26.0609 | 25.9154 | 25.7599 | 25.6087 | 25.4607 | 24.7906 | 24.2502 | 23.6712 | 27.2653 | 27.2578 | 27.2558 | 27.2537 | 27.2515 | 27.2491 | 27.211 | 27.0953 | 26.9717 | 26.846 | 26.6935 | 26.0029 | 25.4473 | 24.854
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0 | 1.0627 | 1.0579 | 1.0532 | 1.0483 | 1.0433 | 1.0381 | 1.0329 | 1.0267 | 1.0187 | 1.0108 | 1.0029 | 0.96057 | 0.91031 | 0.85197 | 1.045 | 1.0385 | 1.032 | 1.0245 | 1.017 | 1.0093 | 1.0017 | 0.9944 | 0.98623 | 0.97808 | 0.96996 | 0.92672 | 0.87551 | 0.81622 | 1.0432 | 1.0384 | 1.0337 | 1.0288 | 1.0237 | 1.018 | 1.0103 | 1.0029 | 0.99469 | 0.98648 | 0.97829 | 0.97011 | 0.96173 | 0.95332
|  | EDAY | CT |  |  |  | 0 | 1.0627 | 1.0579 | 1.0532 | 1.0483 | 1.0433 | 1.0381 | 1.0329 | 1.0267 | 1.0187 | 1.0108 | 1.0029 | 0.96057 | 0.91031 | 0.85197 | 1.045 | 1.0385 | 1.032 | 1.0245 | 1.017 | 1.0093 | 1.0017 | 0.9944 | 0.98623 | 0.97808 | 0.96996 | 0.92672 | 0.87551 | 0.81622 | 1.0432 | 1.0384 | 1.0337 | 1.0288 | 1.0237 | 1.018 | 1.0103 | 1.0029 | 0.99469 | 0.98648 | 0.97829 | 0.97011 | 0.96173 | 0.95332
|  | EDAY | LW |  |  |  | 0 | 1.0703 | 1.0669 | 1.0645 | 1.0618 | 1.0589 | 1.0531 | 1.0457 | 1.0384 | 1.0312 | 1.024 | 1.0169 | 0.97674 | 0.92661 | 0.86186 | 1.0523 | 1.0469 | 1.0423 | 1.0354 | 1.0284 | 1.0207 | 1.013 | 1.0054 | 0.99786 | 0.99035 | 0.9829 | 0.94123 | 0.88953 | 0.82322 | 1.0507 | 1.0474 | 1.0449 | 1.0422 | 1.0371 | 1.0292 | 1.0214 | 1.0137 | 1.0061 | 0.99844 | 0.99089 | 0.9834 | 0.97479 | 0.96614
|  | EDAY | ST |  |  |  | 0 | 1.072 | 1.0709 | 1.07 | 1.0688 | 1.0668 | 1.0647 | 1.0634 | 1.0624 | 1.0614 | 1.0604 | 1.0594 | 1.0466 | 1.0276 | 1.0096 | 1.0572 | 1.0561 | 1.0551 | 1.052 | 1.048 | 1.0441 | 1.0409 | 1.038 | 1.0351 | 1.0322 | 1.0294 | 1.0139 | 0.99412 | 0.97545 | 1.0524 | 1.0514 | 1.0504 | 1.0493 | 1.0473 | 1.0452 | 1.0439 | 1.0428 | 1.0418 | 1.0408 | 1.038 | 1.0222 | 1.0023 | 0.98339
|  | EDAY | FS |  |  |  | 0 | 1.072 | 1.0709 | 1.0701 | 1.0692 | 1.0684 | 1.0675 | 1.0666 | 1.0657 | 1.0648 | 1.0638 | 1.0628 | 1.0572 | 1.0439 | 1.0289 | 1.0573 | 1.0562 | 1.0553 | 1.0544 | 1.0531 | 1.0507 | 1.0483 | 1.0456 | 1.043 | 1.0404 | 1.0377 | 1.0249 | 1.011 | 0.99535 | 1.0524 | 1.0514 | 1.0505 | 1.0497 | 1.0488 | 1.0479 | 1.0471 | 1.0461 | 1.0452 | 1.0443 | 1.0433 | 1.0334 | 1.0193 | 1.0035
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0 | 0.49473 | 0.4947 | 0.49468 | 0.49465 | 0.49462 | 0.49459 | 0.49456 | 0.49454 | 0.49451 | 0.49449 | 0.49446 | 0.49431 | 0.49407 | 0.49365 | -0.24632 | -0.24635 | -0.24636 | -0.24639 | -0.24641 | -0.24644 | -0.24646 | -0.24648 | -0.24651 | -0.24653 | -0.24655 | -0.24669 | -0.2469 | -0.24731 | 0.32627 | 0.32622 | 0.32618 | 0.32612 | 0.32605 | 0.32599 | 0.32593 | 0.32587 | 0.32581 | 0.32575 | 0.32569 | 0.32563 | 0.32557 | 0.32551
|  | EDAY TIDAL | CT |  |  |  | 0 | 0.49473 | 0.49472 | 0.49471 | 0.49469 | 0.49467 | 0.49465 | 0.49462 | 0.49461 | 0.49459 | 0.49457 | 0.49456 | 0.49445 | 0.49429 | 0.49404 | -0.24632 | -0.24633 | -0.24634 | -0.24635 | -0.24637 | -0.24639 | -0.24641 | -0.24642 | -0.24644 | -0.24645 | -0.24646 | -0.24656 | -0.24671 | -0.24694 | 0.32628 | 0.32625 | 0.32622 | 0.32618 | 0.32614 | 0.32609 | 0.32604 | 0.326 | 0.32596 | 0.32592 | 0.32588 | 0.32584 | 0.3258 | 0.32576
|  | EDAY TIDAL | LW |  |  |  | 0 | 0.49473 | 0.4947 | 0.49468 | 0.49465 | 0.49462 | 0.49459 | 0.49456 | 0.49454 | 0.49451 | 0.49449 | 0.49446 | 0.49431 | 0.49407 | 0.49365 | -0.24632 | -0.24635 | -0.24636 | -0.24639 | -0.24641 | -0.24644 | -0.24646 | -0.24648 | -0.24651 | -0.24653 | -0.24655 | -0.24669 | -0.2469 | -0.24731 | 0.32627 | 0.32622 | 0.32618 | 0.32612 | 0.32605 | 0.32599 | 0.32593 | 0.32587 | 0.32581 | 0.32575 | 0.32569 | 0.32563 | 0.32557 | 0.32551
|  | EDAY TIDAL | ST |  |  |  | 0 | 0.49473 | 0.49473 | 0.49473 | 0.49472 | 0.49471 | 0.4947 | 0.49469 | 0.49468 | 0.49468 | 0.49467 | 0.49467 | 0.49465 | 0.49457 | 0.49452 | -0.24632 | -0.24632 | -0.24632 | -0.24633 | -0.24634 | -0.24634 | -0.24635 | -0.24636 | -0.24636 | -0.24636 | -0.24637 | -0.24638 | -0.24645 | -0.24649 | 0.3263 | 0.32629 | 0.32629 | 0.32627 | 0.32624 | 0.32621 | 0.32619 | 0.32617 | 0.32615 | 0.32612 | 0.3261 | 0.32601 | 0.32587 | 0.32576
|  | EDAY TIDAL | FS |  |  |  | 0 | 0.49474 | 0.49473 | 0.49473 | 0.49473 | 0.49473 | 0.49473 | 0.49473 | 0.49472 | 0.49472 | 0.49471 | 0.49471 | 0.4947 | 0.49466 | 0.49458 | -0.24632 | -0.24632 | -0.24632 | -0.24632 | -0.24632 | -0.24632 | -0.24632 | -0.24632 | -0.24633 | -0.24633 | -0.24633 | -0.24634 | -0.24637 | -0.24644 | 0.3263 | 0.32629 | 0.32629 | 0.32629 | 0.32629 | 0.32627 | 0.32626 | 0.32624 | 0.32623 | 0.32621 | 0.32619 | 0.32612 | 0.32602 | 0.32589
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 0.036842 | 3.6779 | 3.6575 | 3.6383 | 3.5887 | 3.4698 | 3.3536 | 3.2456 | 3.1368 | 3.0331 | 2.9312 | 2.8387 | 2.3915 | 1.9128 | 1.3135 | 3.924 | 3.806 | 3.6936 | 3.5499 | 3.4116 | 3.2797 | 3.1576 | 3.034 | 2.9163 | 2.8009 | 2.6965 | 2.1959 | 1.67 | 1.0263 | 3.7085 | 3.5976 | 3.4927 | 3.3586 | 3.2294 | 3.1059 | 2.9913 | 2.8755 | 2.7653 | 2.6571 | 2.559 | 2.4668 | 2.372 | 2.2766
|  | EDZELL | CT |  |  |  | 0.036842 | 3.6779 | 3.6575 | 3.6383 | 3.6176 | 3.5949 | 3.5169 | 3.4343 | 3.3515 | 3.2704 | 3.1944 | 3.1217 | 2.763 | 2.384 | 1.9485 | 3.9463 | 3.8708 | 3.7894 | 3.6887 | 3.5839 | 3.4771 | 3.3823 | 3.2892 | 3.1981 | 3.1128 | 3.0316 | 2.6342 | 2.2214 | 1.7537 | 3.7222 | 3.6562 | 3.5796 | 3.4851 | 3.3867 | 3.2862 | 3.1968 | 3.1092 | 3.0234 | 2.943 | 2.8664 | 2.7899 | 2.7134 | 2.6383
|  | EDZELL | LW |  |  |  | 0.036842 | 3.699 | 3.672 | 3.6577 | 3.5887 | 3.4698 | 3.3536 | 3.2456 | 3.1368 | 3.0331 | 2.9312 | 2.8387 | 2.3915 | 1.9128 | 1.3135 | 3.924 | 3.806 | 3.6936 | 3.5499 | 3.4116 | 3.2797 | 3.1576 | 3.034 | 2.9163 | 2.8009 | 2.6965 | 2.1959 | 1.67 | 1.0263 | 3.7085 | 3.5976 | 3.4927 | 3.3586 | 3.2294 | 3.1059 | 2.9913 | 2.8755 | 2.7653 | 2.6571 | 2.559 | 2.4668 | 2.372 | 2.2766
|  | EDZELL | ST |  |  |  | 0.036842 | 3.7032 | 3.6978 | 3.6939 | 3.6876 | 3.6797 | 3.671 | 3.6625 | 3.6578 | 3.653 | 3.6416 | 3.6037 | 3.4179 | 3.2209 | 3.0512 | 4.014 | 3.9923 | 3.9694 | 3.9203 | 3.867 | 3.8131 | 3.7627 | 3.7129 | 3.6627 | 3.6139 | 3.5674 | 3.3506 | 3.131 | 2.94 | 3.779 | 3.7615 | 3.7435 | 3.7042 | 3.6545 | 3.604 | 3.5569 | 3.5106 | 3.4638 | 3.4184 | 3.3752 | 3.1732 | 2.9656 | 2.786
|  | EDZELL | FS |  |  |  | 0.036842 | 3.704 | 3.6997 | 3.6979 | 3.696 | 3.6941 | 3.6922 | 3.6902 | 3.6873 | 3.6844 | 3.6812 | 3.678 | 3.578 | 3.4358 | 3.2751 | 4.0153 | 4.003 | 3.9868 | 3.9679 | 3.941 | 3.9073 | 3.8737 | 3.8357 | 3.7948 | 3.7548 | 3.7155 | 3.5306 | 3.3694 | 3.1907 | 3.7849 | 3.7699 | 3.7574 | 3.7429 | 3.7224 | 3.6926 | 3.6614 | 3.6261 | 3.5882 | 3.551 | 3.5145 | 3.3426 | 3.1915 | 3.0224
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 0 | 10.9166 | 10.8736 | 10.8544 | 10.8278 | 10.7976 | 10.7638 | 10.7247 | 10.6929 | 10.6607 | 10.6282 | 10.5655 | 10.1432 | 9.6213 | 8.862 | 10.5281 | 10.485 | 10.4659 | 10.4393 | 10.4091 | 10.3761 | 10.3413 | 10.314 | 10.2864 | 10.2583 | 10.1846 | 9.7107 | 9.1366 | 8.3261 | 10.5171 | 10.4721 | 10.4507 | 10.4199 | 10.3856 | 10.3487 | 10.3104 | 10.2793 | 10.2479 | 10.2161 | 10.1849 | 10.1541 | 10.1168 | 10.0593
|  | EDZELL STREET | CT |  |  |  | 0 | 10.9166 | 10.9021 | 10.8899 | 10.8733 | 10.8529 | 10.8292 | 10.8037 | 10.7867 | 10.7663 | 10.7459 | 10.7254 | 10.5517 | 10.1955 | 9.7462 | 10.5281 | 10.5136 | 10.5014 | 10.4848 | 10.4644 | 10.4407 | 10.4152 | 10.3985 | 10.3813 | 10.364 | 10.3465 | 10.1676 | 9.7757 | 9.2916 | 10.5176 | 10.5017 | 10.4879 | 10.4684 | 10.4453 | 10.4189 | 10.3908 | 10.3715 | 10.3517 | 10.3318 | 10.3118 | 10.2912 | 10.2659 | 10.24
|  | EDZELL STREET | LW |  |  |  | 0 | 10.9166 | 10.8736 | 10.8544 | 10.8278 | 10.7976 | 10.7638 | 10.7247 | 10.6929 | 10.6607 | 10.6282 | 10.5655 | 10.1432 | 9.6213 | 8.862 | 10.5281 | 10.485 | 10.4659 | 10.4393 | 10.4091 | 10.3761 | 10.3413 | 10.314 | 10.2864 | 10.2583 | 10.1846 | 9.7107 | 9.1366 | 8.3261 | 10.5171 | 10.4721 | 10.4507 | 10.4199 | 10.3856 | 10.3487 | 10.3104 | 10.2793 | 10.2479 | 10.2161 | 10.1849 | 10.1541 | 10.1168 | 10.0593
|  | EDZELL STREET | ST |  |  |  | 0 | 10.9166 | 10.9111 | 10.9085 | 10.9015 | 10.893 | 10.8829 | 10.8718 | 10.8676 | 10.8634 | 10.8593 | 10.8555 | 10.8336 | 10.7377 | 10.6697 | 10.5281 | 10.5226 | 10.52 | 10.513 | 10.5044 | 10.4944 | 10.4832 | 10.4791 | 10.4749 | 10.4708 | 10.467 | 10.4495 | 10.3623 | 10.2925 | 10.5198 | 10.5143 | 10.5116 | 10.5027 | 10.4924 | 10.4806 | 10.4678 | 10.4618 | 10.4558 | 10.45 | 10.4444 | 10.4191 | 10.3247 | 10.2729
|  | EDZELL STREET | FS |  |  |  | 0 | 10.9166 | 10.9115 | 10.9113 | 10.911 | 10.9106 | 10.91 | 10.9095 | 10.9073 | 10.9048 | 10.9021 | 10.8992 | 10.8913 | 10.8476 | 10.7521 | 10.5281 | 10.523 | 10.5227 | 10.5225 | 10.5221 | 10.5215 | 10.5209 | 10.5188 | 10.5163 | 10.5136 | 10.5107 | 10.5028 | 10.4622 | 10.3736 | 10.5199 | 10.5148 | 10.5145 | 10.514 | 10.5131 | 10.5113 | 10.5096 | 10.5061 | 10.5022 | 10.4982 | 10.4939 | 10.4795 | 10.4328 | 10.3386
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 0.1 | 11.3708 | 11.3236 | 11.2933 | 11.2524 | 11.2055 | 11.1547 | 11.1005 | 11.0568 | 11.0126 | 10.9668 | 10.9218 | 10.4252 | 9.5529 | 8.3245 | 11.0638 | 11.0166 | 10.9863 | 10.9454 | 10.8985 | 10.8477 | 10.7935 | 10.7498 | 10.7056 | 10.6598 | 10.6148 | 9.8916 | 8.9456 | 7.6441 | 11.0961 | 11.0489 | 11.0186 | 10.9777 | 10.9308 | 10.88 | 10.7367 | 10.5919 | 10.448 | 10.3043 | 10.1628 | 10.0234 | 9.8728 | 9.7209
|  | ELGIN | CT |  |  |  | 0.1 | 11.3708 | 11.3406 | 11.3137 | 11.2804 | 11.2417 | 11.1981 | 11.1527 | 11.1193 | 11.0849 | 11.0505 | 11.0149 | 10.7943 | 10.3173 | 9.536 | 11.0638 | 11.0336 | 11.0067 | 10.9734 | 10.9347 | 10.8911 | 10.8457 | 10.8123 | 10.7779 | 10.7435 | 10.7079 | 10.4775 | 9.8048 | 8.9657 | 11.0961 | 11.0659 | 11.039 | 11.0057 | 10.967 | 10.9234 | 10.878 | 10.8446 | 10.7441 | 10.6412 | 10.5385 | 10.4358 | 10.3258 | 10.2142
|  | ELGIN | LW |  |  |  | 0.1 | 11.3868 | 11.3236 | 11.2933 | 11.2524 | 11.2055 | 11.1547 | 11.1005 | 11.0568 | 11.0126 | 10.9668 | 10.9218 | 10.4252 | 9.5529 | 8.3245 | 11.0798 | 11.0166 | 10.9863 | 10.9454 | 10.8985 | 10.8477 | 10.7935 | 10.7498 | 10.7056 | 10.6598 | 10.6148 | 9.8916 | 8.9456 | 7.6441 | 11.1121 | 11.0489 | 11.0186 | 10.9777 | 10.9308 | 10.88 | 10.7367 | 10.5919 | 10.448 | 10.3043 | 10.1628 | 10.0234 | 9.8728 | 9.7209
|  | ELGIN | ST |  |  |  | 0.1 | 11.3902 | 11.3797 | 11.3733 | 11.3605 | 11.3455 | 11.3284 | 11.3095 | 11.3009 | 11.2922 | 11.2838 | 11.2756 | 11.2374 | 11.0967 | 11.0147 | 11.0832 | 11.0727 | 11.0663 | 11.0535 | 11.0385 | 11.0214 | 11.0025 | 10.9939 | 10.9852 | 10.9768 | 10.9686 | 10.9304 | 10.7897 | 10.7077 | 11.1155 | 11.105 | 11.0987 | 11.0859 | 11.0709 | 11.0537 | 11.0349 | 11.0262 | 11.0175 | 11.0091 | 11.001 | 10.8619 | 10.5178 | 10.2392
|  | ELGIN | FS |  |  |  | 0.1 | 11.3927 | 11.3843 | 11.3823 | 11.3802 | 11.3779 | 11.3754 | 11.3729 | 11.368 | 11.3627 | 11.357 | 11.351 | 11.331 | 11.2624 | 11.1223 | 11.0857 | 11.0773 | 11.0753 | 11.0732 | 11.0709 | 11.0684 | 11.0659 | 11.061 | 11.0557 | 11.05 | 11.044 | 11.024 | 10.9554 | 10.8153 | 11.118 | 11.1096 | 11.1076 | 11.1055 | 11.1033 | 11.1007 | 11.0982 | 11.0933 | 11.088 | 11.0823 | 11.0763 | 11.0563 | 10.8921 | 10.5934
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 0.16632 | 2.8593 | 2.841 | 2.831 | 2.8173 | 2.8018 | 2.785 | 2.7673 | 2.7532 | 2.7389 | 2.7244 | 2.7101 | 2.6204 | 2.4795 | 2.2161 | 2.7617 | 2.7377 | 2.7234 | 2.7044 | 2.6839 | 2.6624 | 2.6406 | 2.6222 | 2.6037 | 2.5393 | 2.459 | 2.0666 | 1.6563 | 1.14 | 2.777 | 2.7588 | 2.7487 | 2.735 | 2.7196 | 2.7028 | 2.6851 | 2.671 | 2.6567 | 2.6422 | 2.5658 | 2.4845 | 2.4005 | 2.317
|  | ELLIOT DEPOT | CT |  |  |  | 0.16632 | 2.8593 | 2.8506 | 2.8429 | 2.8332 | 2.8216 | 2.8083 | 2.7942 | 2.7844 | 2.7742 | 2.764 | 2.7537 | 2.6879 | 2.5842 | 2.4305 | 2.7617 | 2.7506 | 2.7403 | 2.7271 | 2.712 | 2.6952 | 2.6781 | 2.6653 | 2.6522 | 2.6393 | 2.6266 | 2.5164 | 2.2285 | 1.8952 | 2.777 | 2.7683 | 2.7607 | 2.7509 | 2.7393 | 2.7261 | 2.7119 | 2.7021 | 2.692 | 2.6818 | 2.6715 | 2.6608 | 2.6479 | 2.6345
|  | ELLIOT DEPOT | LW |  |  |  | 0.16632 | 2.8626 | 2.841 | 2.831 | 2.8173 | 2.8018 | 2.785 | 2.7673 | 2.7532 | 2.7389 | 2.7244 | 2.7101 | 2.6204 | 2.4795 | 2.2161 | 2.7633 | 2.7377 | 2.7234 | 2.7044 | 2.6839 | 2.6624 | 2.6406 | 2.6222 | 2.6037 | 2.5393 | 2.459 | 2.0666 | 1.6563 | 1.14 | 2.7804 | 2.7588 | 2.7487 | 2.735 | 2.7196 | 2.7028 | 2.6851 | 2.671 | 2.6567 | 2.6422 | 2.5658 | 2.4845 | 2.4005 | 2.317
|  | ELLIOT DEPOT | ST |  |  |  | 0.16632 | 2.8635 | 2.8599 | 2.8586 | 2.8552 | 2.8501 | 2.8443 | 2.8379 | 2.835 | 2.8321 | 2.8292 | 2.8265 | 2.8135 | 2.7663 | 2.7394 | 2.7678 | 2.7635 | 2.7613 | 2.7561 | 2.7491 | 2.7414 | 2.7332 | 2.7283 | 2.7234 | 2.7187 | 2.7141 | 2.6928 | 2.6387 | 2.6055 | 2.7812 | 2.7777 | 2.7764 | 2.7729 | 2.7678 | 2.762 | 2.7557 | 2.7527 | 2.7498 | 2.747 | 2.7442 | 2.7313 | 2.684 | 2.6571
|  | ELLIOT DEPOT | FS |  |  |  | 0.16632 | 2.8635 | 2.8609 | 2.8608 | 2.8607 | 2.8605 | 2.8602 | 2.8599 | 2.8588 | 2.8576 | 2.8562 | 2.8547 | 2.8508 | 2.8302 | 2.7851 | 2.7682 | 2.765 | 2.7642 | 2.7633 | 2.762 | 2.7603 | 2.7587 | 2.7561 | 2.7533 | 2.7504 | 2.7475 | 2.7366 | 2.7105 | 2.6603 | 2.7812 | 2.7787 | 2.7785 | 2.7784 | 2.7782 | 2.7779 | 2.7776 | 2.7765 | 2.7753 | 2.7739 | 2.7724 | 2.7685 | 2.7479 | 2.7028
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 0.13053 | 16.1171 | 16.0213 | 15.7599 | 14.9346 | 14.147 | 13.4027 | 12.7367 | 12.0584 | 11.4164 | 10.8054 | 10.2623 | 7.7581 | 5.2278 | 2.081 | 14.4608 | 14.1127 | 13.3089 | 12.337 | 11.4129 | 10.5425 | 9.7675 | 8.9731 | 8.2227 | 7.5098 | 6.8782 | 3.9968 | 1.1482 | -2.2877 | 15.1223 | 14.9688 | 14.7557 | 13.7868 | 12.8591 | 11.9856 | 11.2077 | 10.4104 | 9.6572 | 8.9417 | 8.3078 | 7.7329 | 7.1443 | 6.5628
|  | ELLON | CT |  |  |  | 0.13053 | 16.1171 | 16.045 | 15.9807 | 15.9027 | 15.4201 | 14.8386 | 14.3414 | 13.8615 | 13.3951 | 12.9671 | 12.5706 | 10.6611 | 8.795 | 6.6916 | 14.4608 | 14.3888 | 14.2226 | 13.5911 | 12.9288 | 12.2507 | 11.6748 | 11.1144 | 10.5706 | 10.0731 | 9.6137 | 7.4221 | 5.3293 | 3.0166 | 15.1223 | 15.0271 | 14.9366 | 14.8273 | 14.3813 | 13.7007 | 13.1228 | 12.5604 | 12.0146 | 11.5153 | 11.0542 | 10.595 | 10.1386 | 9.7027
|  | ELLON | LW |  |  |  | 0.13053 | 16.1634 | 16.0213 | 15.7599 | 14.9346 | 14.147 | 13.4027 | 12.7367 | 12.0584 | 11.4164 | 10.8054 | 10.2623 | 7.7581 | 5.2278 | 2.081 | 14.5072 | 14.1127 | 13.3089 | 12.337 | 11.4129 | 10.5425 | 9.7675 | 8.9731 | 8.2227 | 7.5098 | 6.8782 | 3.9968 | 1.1482 | -2.2877 | 15.1499 | 14.9688 | 14.7557 | 13.7868 | 12.8591 | 11.9856 | 11.2077 | 10.4104 | 9.6572 | 8.9417 | 8.3078 | 7.7329 | 7.1443 | 6.5628
|  | ELLON | ST |  |  |  | 0.13053 | 16.1727 | 16.1492 | 16.1345 | 16.107 | 16.0732 | 16.0349 | 15.993 | 15.9726 | 15.7275 | 15.4603 | 15.2058 | 14.0587 | 12.9543 | 12.0378 | 14.5164 | 14.4929 | 14.4782 | 14.4507 | 14.4169 | 14.2494 | 13.931 | 13.6037 | 13.2699 | 12.953 | 12.6512 | 11.2922 | 10.0267 | 8.9624 | 15.1942 | 15.163 | 15.1391 | 15.0957 | 15.045 | 14.9893 | 14.9317 | 14.8939 | 14.7223 | 14.4051 | 14.1021 | 12.7377 | 11.468 | 10.3999
|  | ELLON | FS |  |  |  | 0.13053 | 16.1769 | 16.1582 | 16.1524 | 16.1466 | 16.1403 | 16.1335 | 16.1277 | 16.1169 | 16.1052 | 16.0929 | 16.0207 | 15.07 | 14.2488 | 13.3272 | 14.5206 | 14.5019 | 14.4962 | 14.4903 | 14.484 | 14.4773 | 14.4714 | 14.3609 | 14.1005 | 13.846 | 13.5964 | 12.4652 | 11.5089 | 10.4607 | 15.2018 | 15.1767 | 15.164 | 15.1501 | 15.1337 | 15.1148 | 15.0971 | 15.073 | 15.0472 | 15.0211 | 14.9946 | 13.9148 | 12.955 | 11.9036
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.21504 | 0.21223 | 0.20946 | 0.20661 | 0.20368 | 0.20069 | 0.19767 | 0.19482 | 0.19197 | 0.18911 | 0.18625 | 0.17063 | 0.15045 | 0.12488 | 0.21485 | 0.21204 | 0.20927 | 0.20642 | 0.20349 | 0.2005 | 0.19748 | 0.19463 | 0.19178 | 0.18892 | 0.18606 | 0.17044 | 0.14664 | 0.1178 | 0.21527 | 0.21246 | 0.2097 | 0.20684 | 0.20392 | 0.20093 | 0.19791 | 0.19506 | 0.1922 | 0.18934 | 0.18648 | 0.18361 | 0.18066 | 0.17728
|  | EREDINE | CT |  |  |  | 0 | 0.21504 | 0.21223 | 0.20946 | 0.20661 | 0.20368 | 0.20069 | 0.19767 | 0.19482 | 0.19197 | 0.18911 | 0.18625 | 0.17063 | 0.15045 | 0.12488 | 0.21485 | 0.21204 | 0.20927 | 0.20642 | 0.20349 | 0.2005 | 0.19748 | 0.19463 | 0.19178 | 0.18892 | 0.18606 | 0.17044 | 0.14664 | 0.1178 | 0.21527 | 0.21246 | 0.2097 | 0.20684 | 0.20392 | 0.20093 | 0.19791 | 0.19506 | 0.1922 | 0.18934 | 0.18648 | 0.18361 | 0.18066 | 0.17728
|  | EREDINE | LW |  |  |  | 0 | 0.21925 | 0.21755 | 0.21633 | 0.21495 | 0.21351 | 0.21201 | 0.21049 | 0.20827 | 0.20604 | 0.20381 | 0.20159 | 0.18989 | 0.16927 | 0.14106 | 0.21906 | 0.21736 | 0.21614 | 0.21476 | 0.21332 | 0.21182 | 0.2103 | 0.20808 | 0.20585 | 0.20362 | 0.2014 | 0.18478 | 0.16172 | 0.13273 | 0.21948 | 0.21778 | 0.21656 | 0.21519 | 0.21375 | 0.21225 | 0.21072 | 0.2085 | 0.20628 | 0.20361 | 0.20028 | 0.19698 | 0.19358 | 0.19016
|  | EREDINE | ST |  |  |  | 0 | 0.22009 | 0.21914 | 0.21825 | 0.21728 | 0.21627 | 0.21524 | 0.21419 | 0.21327 | 0.21235 | 0.21143 | 0.21051 | 0.20598 | 0.20018 | 0.19517 | 0.2199 | 0.21895 | 0.21806 | 0.21709 | 0.21608 | 0.21505 | 0.214 | 0.21308 | 0.21216 | 0.21124 | 0.21033 | 0.20579 | 0.2 | 0.19498 | 0.22032 | 0.21938 | 0.21849 | 0.21751 | 0.21651 | 0.21548 | 0.21443 | 0.21351 | 0.21258 | 0.21167 | 0.21075 | 0.20621 | 0.20042 | 0.19455
|  | EREDINE | FS |  |  |  | 0 | 0.22093 | 0.22084 | 0.21999 | 0.21915 | 0.2183 | 0.21745 | 0.21659 | 0.21655 | 0.21651 | 0.21646 | 0.21641 | 0.2129 | 0.20798 | 0.20223 | 0.22074 | 0.22065 | 0.2198 | 0.21896 | 0.21811 | 0.21726 | 0.2164 | 0.21637 | 0.21632 | 0.21627 | 0.21622 | 0.21271 | 0.20779 | 0.20204 | 0.22117 | 0.22108 | 0.22023 | 0.21938 | 0.21853 | 0.21768 | 0.21683 | 0.21679 | 0.21675 | 0.2167 | 0.21665 | 0.21314 | 0.20822 | 0.20246
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0.0052632 | 1.0455 | 1.0367 | 1.0278 | 1.0189 | 1.0098 | 1.0015 | 0.99306 | 0.98411 | 0.97514 | 0.96617 | 0.9572 | 0.90649 | 0.84171 | 0.76189 | 1.0146 | 1.0057 | 0.99689 | 0.98794 | 0.97886 | 0.97051 | 0.96212 | 0.95317 | 0.9442 | 0.93422 | 0.92395 | 0.86699 | 0.79716 | 0.71634 | 1.0223 | 1.0134 | 1.0046 | 0.99562 | 0.98655 | 0.9782 | 0.96981 | 0.96086 | 0.95189 | 0.94269 | 0.93251 | 0.92234 | 0.91121 | 0.90005
|  | ERROGIE | CT |  |  |  | 0.0052632 | 1.0455 | 1.0367 | 1.0278 | 1.0189 | 1.0098 | 1.0015 | 0.99306 | 0.98411 | 0.97514 | 0.96617 | 0.9572 | 0.90649 | 0.84171 | 0.76189 | 1.0146 | 1.0057 | 0.99689 | 0.98794 | 0.97886 | 0.97051 | 0.96212 | 0.95317 | 0.9442 | 0.93422 | 0.92395 | 0.86699 | 0.79716 | 0.71634 | 1.0223 | 1.0134 | 1.0046 | 0.99562 | 0.98655 | 0.9782 | 0.96981 | 0.96086 | 0.95189 | 0.94269 | 0.93251 | 0.92234 | 0.91121 | 0.90005
|  | ERROGIE | LW |  |  |  | 0.0052632 | 1.0599 | 1.0559 | 1.0528 | 1.0485 | 1.0442 | 1.0389 | 1.0335 | 1.0285 | 1.0225 | 1.0166 | 1.009 | 0.96215 | 0.90308 | 0.82767 | 1.0289 | 1.025 | 1.0218 | 1.0176 | 1.0132 | 1.0069 | 0.99871 | 0.99071 | 0.9819 | 0.97312 | 0.96442 | 0.91523 | 0.85386 | 0.77622 | 1.0366 | 1.0327 | 1.0295 | 1.0253 | 1.0209 | 1.0153 | 1.0074 | 0.9996 | 0.991 | 0.98243 | 0.97382 | 0.96524 | 0.95564 | 0.94601
|  | ERROGIE | ST |  |  |  | 0.0052632 | 1.0632 | 1.0614 | 1.0596 | 1.0577 | 1.0549 | 1.0521 | 1.0492 | 1.0465 | 1.0439 | 1.0412 | 1.0386 | 1.0254 | 1.011 | 0.99703 | 1.0323 | 1.0304 | 1.0287 | 1.0268 | 1.024 | 1.0211 | 1.0183 | 1.0156 | 1.0129 | 1.0103 | 1.0076 | 0.99447 | 0.97658 | 0.95924 | 1.04 | 1.0381 | 1.0364 | 1.0344 | 1.0317 | 1.0288 | 1.0259 | 1.0233 | 1.0206 | 1.018 | 1.0153 | 1.0022 | 0.98523 | 0.96814
|  | ERROGIE | FS |  |  |  | 0.0052632 | 1.0649 | 1.0639 | 1.0622 | 1.0605 | 1.0588 | 1.0571 | 1.0554 | 1.0537 | 1.0519 | 1.0502 | 1.0484 | 1.0397 | 1.0301 | 1.0191 | 1.034 | 1.033 | 1.0313 | 1.0296 | 1.0279 | 1.0262 | 1.0245 | 1.0227 | 1.021 | 1.0192 | 1.0175 | 1.0088 | 0.99918 | 0.98578 | 1.0417 | 1.0407 | 1.039 | 1.0373 | 1.0356 | 1.0339 | 1.0322 | 1.0304 | 1.0287 | 1.0269 | 1.0251 | 1.0165 | 1.0069 | 0.99435
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.32842 | 5.9175 | 5.8861 | 5.857 | 5.8235 | 5.7871 | 5.7473 | 5.7057 | 5.6722 | 5.6373 | 5.5359 | 5.4349 | 4.892 | 4.2325 | 3.3212 | 5.7956 | 5.7642 | 5.7351 | 5.7016 | 5.6652 | 5.6253 | 5.5782 | 5.4642 | 5.3502 | 5.2371 | 5.1258 | 4.533 | 3.8177 | 2.8517 | 5.8424 | 5.8094 | 5.7784 | 5.7416 | 5.702 | 5.6591 | 5.6018 | 5.4868 | 5.372 | 5.258 | 5.1458 | 5.0344 | 4.9157 | 4.7951
|  | ERROL | CT |  |  |  | 0.32842 | 5.9175 | 5.8861 | 5.857 | 5.8235 | 5.7871 | 5.7473 | 5.7057 | 5.6722 | 5.6373 | 5.6023 | 5.5672 | 5.1902 | 4.6725 | 4.0464 | 5.7956 | 5.7642 | 5.7351 | 5.7016 | 5.6652 | 5.6253 | 5.5838 | 5.5503 | 5.5143 | 5.4266 | 5.3397 | 4.8761 | 4.3231 | 3.6601 | 5.8424 | 5.8094 | 5.7784 | 5.7416 | 5.702 | 5.6591 | 5.6147 | 5.5781 | 5.5381 | 5.4498 | 5.3623 | 5.275 | 5.1822 | 5.0882
|  | ERROL | LW |  |  |  | 0.32842 | 5.9469 | 5.8991 | 5.8741 | 5.8409 | 5.8032 | 5.762 | 5.719 | 5.6827 | 5.6386 | 5.5359 | 5.4349 | 4.892 | 4.2325 | 3.3212 | 5.825 | 5.7771 | 5.7522 | 5.719 | 5.6813 | 5.6401 | 5.5782 | 5.4642 | 5.3502 | 5.2371 | 5.1258 | 4.533 | 3.8177 | 2.8517 | 5.8713 | 5.8213 | 5.7937 | 5.7558 | 5.7135 | 5.6679 | 5.6018 | 5.4868 | 5.372 | 5.258 | 5.1458 | 5.0344 | 4.9157 | 4.7951
|  | ERROL | ST |  |  |  | 0.32842 | 5.952 | 5.9424 | 5.9355 | 5.9243 | 5.9108 | 5.8958 | 5.8796 | 5.8712 | 5.8628 | 5.8546 | 5.8465 | 5.8064 | 5.6826 | 5.4823 | 5.8301 | 5.8204 | 5.8136 | 5.8024 | 5.7889 | 5.7738 | 5.7577 | 5.7493 | 5.7409 | 5.7327 | 5.7246 | 5.6577 | 5.393 | 5.1723 | 5.8794 | 5.8696 | 5.8626 | 5.8493 | 5.8335 | 5.8165 | 5.7983 | 5.7879 | 5.7774 | 5.7671 | 5.7571 | 5.6811 | 5.4147 | 5.1922
|  | ERROL | FS |  |  |  | 0.32842 | 5.9554 | 5.9478 | 5.9442 | 5.9406 | 5.9368 | 5.9329 | 5.9298 | 5.9251 | 5.9201 | 5.9149 | 5.9095 | 5.8857 | 5.8287 | 5.7245 | 5.8335 | 5.8259 | 5.8223 | 5.8186 | 5.8149 | 5.811 | 5.8079 | 5.8032 | 5.7982 | 5.793 | 5.7876 | 5.7638 | 5.6864 | 5.46 | 5.8829 | 5.8752 | 5.8715 | 5.8676 | 5.8632 | 5.8578 | 5.8534 | 5.847 | 5.8404 | 5.8336 | 5.8265 | 5.7948 | 5.71 | 5.4821
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | NO | 0 | 1.0985 | 1.0954 | 1.0925 | 1.0892 | 1.0855 | 1.0815 | 1.0773 | 1.074 | 1.0705 | 1.0669 | 1.0634 | 1.0101 | 0.9457 | 0.85638 | 1.0926 | 1.0895 | 1.0866 | 1.0833 | 1.0796 | 1.0756 | 1.0714 | 1.0681 | 1.0646 | 1.0555 | 1.0444 | 0.98447 | 0.91372 | 0.8187 | 1.0662 | 1.0631 | 1.0602 | 1.0569 | 1.0532 | 1.0492 | 1.045 | 1.0417 | 1.0382 | 1.0346 | 1.0311 | 1.0276 | 1.0235 | 1.0128
|  | FASNAKYLE | CT |  |  |  | 0 | 1.0985 | 1.0954 | 1.0925 | 1.0892 | 1.0855 | 1.0815 | 1.0773 | 1.074 | 1.0706 | 1.0673 | 1.0639 | 1.0429 | 0.99427 | 0.93483 | 1.0926 | 1.0895 | 1.0866 | 1.0833 | 1.0796 | 1.0756 | 1.0714 | 1.0681 | 1.0647 | 1.0614 | 1.058 | 1.0247 | 0.97105 | 0.90765 | 1.0662 | 1.0631 | 1.0602 | 1.0569 | 1.0532 | 1.0492 | 1.045 | 1.0417 | 1.0383 | 1.0349 | 1.0316 | 1.0281 | 1.0243 | 1.0203
|  | FASNAKYLE | LW |  |  |  | 0 | 1.101 | 1.0959 | 1.0932 | 1.0897 | 1.0859 | 1.0818 | 1.0775 | 1.074 | 1.0705 | 1.0669 | 1.0634 | 1.0101 | 0.9457 | 0.85638 | 1.0951 | 1.0901 | 1.0873 | 1.0838 | 1.08 | 1.0759 | 1.0717 | 1.0682 | 1.0646 | 1.0555 | 1.0444 | 0.98447 | 0.91372 | 0.8187 | 1.0687 | 1.0636 | 1.0609 | 1.0574 | 1.0536 | 1.0495 | 1.0452 | 1.0417 | 1.0382 | 1.0346 | 1.0311 | 1.0276 | 1.0235 | 1.0128
|  | FASNAKYLE | ST |  |  |  | 0 | 1.1027 | 1.1013 | 1.1003 | 1.0987 | 1.0971 | 1.0953 | 1.0934 | 1.0921 | 1.0909 | 1.0896 | 1.0884 | 1.0826 | 1.0702 | 1.0619 | 1.0968 | 1.0955 | 1.0944 | 1.0929 | 1.0912 | 1.0894 | 1.0875 | 1.0862 | 1.085 | 1.0838 | 1.0826 | 1.0767 | 1.0643 | 1.0431 | 1.0704 | 1.069 | 1.0679 | 1.0664 | 1.0648 | 1.063 | 1.061 | 1.0598 | 1.0586 | 1.0573 | 1.0561 | 1.0502 | 1.0379 | 1.0295
|  | FASNAKYLE | FS |  |  |  | 0 | 1.1027 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 1.1021 | 1.1021 | 1.1019 | 1.1016 | 1.1014 | 1.1011 | 1.1004 | 1.0967 | 1.0886 | 1.0968 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 1.0962 | 1.0962 | 1.096 | 1.0958 | 1.0955 | 1.0952 | 1.0945 | 1.0908 | 1.0828 | 1.0704 | 1.0699 | 1.0699 | 1.0699 | 1.0698 | 1.0698 | 1.0697 | 1.0695 | 1.0693 | 1.0691 | 1.0688 | 1.0681 | 1.0644 | 1.0563
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.11824 | 0.11781 | 0.11761 | 0.11735 | 0.11704 | 0.11671 | 0.11636 | 0.11609 | 0.11581 | 0.11553 | 0.11525 | 0.11355 | 0.1109 | 0.10584 | 0.11864 | 0.1182 | 0.11801 | 0.11774 | 0.11744 | 0.11711 | 0.11676 | 0.11648 | 0.11621 | 0.11593 | 0.11565 | 0.11395 | 0.11105 | 0.10313 | 0.11932 | 0.11889 | 0.11869 | 0.11843 | 0.11812 | 0.11779 | 0.11744 | 0.11717 | 0.11689 | 0.11661 | 0.11633 | 0.11606 | 0.11572 | 0.11537
|  | FINCASTLE | CT |  |  |  | 0 | 0.11824 | 0.11809 | 0.11797 | 0.1178 | 0.11759 | 0.11734 | 0.11708 | 0.11691 | 0.11674 | 0.11656 | 0.11638 | 0.11523 | 0.1134 | 0.11059 | 0.11864 | 0.11849 | 0.11836 | 0.11819 | 0.11798 | 0.11774 | 0.11748 | 0.11731 | 0.11713 | 0.11696 | 0.11678 | 0.11563 | 0.1138 | 0.11099 | 0.11932 | 0.11917 | 0.11904 | 0.11887 | 0.11867 | 0.11842 | 0.11816 | 0.11799 | 0.11782 | 0.11764 | 0.11746 | 0.11728 | 0.11705 | 0.11681
|  | FINCASTLE | LW |  |  |  | 0 | 0.11824 | 0.11781 | 0.11761 | 0.11735 | 0.11704 | 0.11671 | 0.11636 | 0.11609 | 0.11581 | 0.11553 | 0.11525 | 0.11355 | 0.1109 | 0.10584 | 0.11864 | 0.1182 | 0.11801 | 0.11774 | 0.11744 | 0.11711 | 0.11676 | 0.11648 | 0.11621 | 0.11593 | 0.11565 | 0.11395 | 0.11105 | 0.10313 | 0.11932 | 0.11889 | 0.11869 | 0.11843 | 0.11812 | 0.11779 | 0.11744 | 0.11717 | 0.11689 | 0.11661 | 0.11633 | 0.11606 | 0.11572 | 0.11537
|  | FINCASTLE | ST |  |  |  | 0 | 0.11824 | 0.11818 | 0.11816 | 0.11809 | 0.118 | 0.1179 | 0.11779 | 0.11774 | 0.1177 | 0.11766 | 0.11762 | 0.11744 | 0.11657 | 0.11613 | 0.11864 | 0.11858 | 0.11855 | 0.11848 | 0.1184 | 0.1183 | 0.11818 | 0.11814 | 0.1181 | 0.11806 | 0.11802 | 0.11784 | 0.11697 | 0.11652 | 0.11932 | 0.11926 | 0.11924 | 0.11917 | 0.11908 | 0.11898 | 0.11886 | 0.11882 | 0.11878 | 0.11874 | 0.1187 | 0.11852 | 0.11765 | 0.1172
|  | FINCASTLE | FS |  |  |  | 0 | 0.11824 | 0.11819 | 0.11819 | 0.11819 | 0.11818 | 0.11818 | 0.11817 | 0.11815 | 0.11813 | 0.1181 | 0.11807 | 0.118 | 0.1176 | 0.11674 | 0.11864 | 0.11859 | 0.11858 | 0.11858 | 0.11858 | 0.11857 | 0.11857 | 0.11855 | 0.11852 | 0.1185 | 0.11847 | 0.11839 | 0.118 | 0.11714 | 0.11932 | 0.11927 | 0.11927 | 0.11926 | 0.11926 | 0.11925 | 0.11925 | 0.11923 | 0.1192 | 0.11918 | 0.11915 | 0.11907 | 0.11868 | 0.11782
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0 | 1.3139 | 1.3081 | 1.3056 | 1.302 | 1.298 | 1.2935 | 1.2889 | 1.2852 | 1.2815 | 1.2777 | 1.274 | 1.2401 | 1.1671 | 1.0613 | 1.4775 | 1.4709 | 1.4674 | 1.4621 | 1.4564 | 1.4505 | 1.4443 | 1.4391 | 1.4339 | 1.4258 | 1.4128 | 1.3444 | 1.2618 | 1.1464 | 1.4792 | 1.4734 | 1.4708 | 1.4673 | 1.4632 | 1.4588 | 1.4542 | 1.4505 | 1.4468 | 1.443 | 1.4339 | 1.4211 | 1.4074 | 1.3936
|  | FIRTH | CT |  |  |  | 0 | 1.3139 | 1.3119 | 1.3102 | 1.3079 | 1.305 | 1.3017 | 1.2982 | 1.2958 | 1.2934 | 1.291 | 1.2886 | 1.2726 | 1.2403 | 1.1748 | 1.4777 | 1.4752 | 1.4729 | 1.4693 | 1.4653 | 1.4609 | 1.4562 | 1.4528 | 1.4492 | 1.4457 | 1.4422 | 1.405 | 1.3458 | 1.2734 | 1.4792 | 1.4772 | 1.4754 | 1.4731 | 1.4703 | 1.467 | 1.4634 | 1.4611 | 1.4587 | 1.4563 | 1.4538 | 1.4513 | 1.4481 | 1.4448
|  | FIRTH | LW |  |  |  | 0 | 1.3139 | 1.3081 | 1.3056 | 1.302 | 1.298 | 1.2935 | 1.2889 | 1.2852 | 1.2815 | 1.2777 | 1.274 | 1.2401 | 1.1671 | 1.0613 | 1.4775 | 1.4709 | 1.4674 | 1.4621 | 1.4564 | 1.4505 | 1.4443 | 1.4391 | 1.4339 | 1.4258 | 1.4128 | 1.3444 | 1.2618 | 1.1464 | 1.4792 | 1.4734 | 1.4708 | 1.4673 | 1.4632 | 1.4588 | 1.4542 | 1.4505 | 1.4468 | 1.443 | 1.4339 | 1.4211 | 1.4074 | 1.3936
|  | FIRTH | ST |  |  |  | 0 | 1.3139 | 1.3131 | 1.3128 | 1.3118 | 1.3106 | 1.3092 | 1.3076 | 1.307 | 1.3064 | 1.3059 | 1.3053 | 1.3029 | 1.2907 | 1.2844 | 1.4785 | 1.4777 | 1.4773 | 1.4755 | 1.4735 | 1.4713 | 1.469 | 1.4675 | 1.4662 | 1.4648 | 1.4635 | 1.4574 | 1.4401 | 1.4129 | 1.4792 | 1.4784 | 1.478 | 1.477 | 1.4759 | 1.4744 | 1.4729 | 1.4723 | 1.4717 | 1.4711 | 1.4706 | 1.4681 | 1.4559 | 1.434
|  | FIRTH | FS |  |  |  | 0 | 1.3139 | 1.3132 | 1.3132 | 1.3131 | 1.3131 | 1.313 | 1.3129 | 1.3126 | 1.3123 | 1.3119 | 1.3115 | 1.3104 | 1.3047 | 1.2923 | 1.4786 | 1.4779 | 1.4778 | 1.4777 | 1.4774 | 1.4769 | 1.4764 | 1.4756 | 1.4747 | 1.4738 | 1.4729 | 1.4693 | 1.4613 | 1.4467 | 1.4792 | 1.4785 | 1.4784 | 1.4784 | 1.4783 | 1.4783 | 1.4782 | 1.4779 | 1.4775 | 1.4771 | 1.4767 | 1.4756 | 1.47 | 1.4575
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | YES | 0 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175
|  | FISHNISH | CT |  |  |  | 0 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175
|  | FISHNISH | LW |  |  |  | 0 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175
|  | FISHNISH | ST |  |  |  | 0 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175
|  | FISHNISH | FS |  |  |  | 0 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20149 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20141 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175 | 0.20175
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0 | -0.612 | -0.613 | -0.61345 | -0.61407 | -0.61477 | -0.61554 | -0.61635 | -0.61698 | -0.61763 | -0.61829 | -0.61893 | -0.62294 | -0.62925 | -0.64132 | 0.10067 | 0.099673 | 0.099228 | 0.098608 | 0.097905 | 0.097136 | 0.096326 | 0.095689 | 0.095043 | 0.094386 | 0.093741 | 0.089733 | 0.083426 | 0.071349 | -0.45277 | -0.45469 | -0.45663 | -0.45966 | -0.46275 | -0.46584 | -0.46894 | -0.47192 | -0.47489 | -0.47785 | -0.48079 | -0.4837 | -0.48678 | -0.48988
|  | FLOTTA | CT |  |  |  | 0 | -0.612 | -0.61235 | -0.61265 | -0.61305 | -0.61354 | -0.61412 | -0.61474 | -0.61514 | -0.61556 | -0.61598 | -0.6164 | -0.61918 | -0.62363 | -0.6305 | 0.10067 | 0.10032 | 0.10003 | 0.099625 | 0.099132 | 0.098557 | 0.097938 | 0.097534 | 0.097116 | 0.096694 | 0.096269 | 0.093489 | 0.089043 | 0.082178 | -0.45267 | -0.45383 | -0.45497 | -0.45701 | -0.45912 | -0.46128 | -0.46345 | -0.46544 | -0.46743 | -0.46942 | -0.4714 | -0.47338 | -0.47548 | -0.4776
|  | FLOTTA | LW |  |  |  | 0 | -0.612 | -0.613 | -0.61345 | -0.61407 | -0.61477 | -0.61554 | -0.61635 | -0.61698 | -0.61763 | -0.61829 | -0.61893 | -0.62294 | -0.62925 | -0.64132 | 0.10067 | 0.099673 | 0.099228 | 0.098608 | 0.097905 | 0.097136 | 0.096326 | 0.095689 | 0.095043 | 0.094386 | 0.093741 | 0.089733 | 0.083426 | 0.071349 | -0.45277 | -0.45469 | -0.45663 | -0.45966 | -0.46275 | -0.46584 | -0.46894 | -0.47192 | -0.47489 | -0.47785 | -0.48079 | -0.4837 | -0.48678 | -0.48988
|  | FLOTTA | ST |  |  |  | 0 | -0.612 | -0.61213 | -0.6122 | -0.61237 | -0.61258 | -0.61282 | -0.61309 | -0.61319 | -0.6133 | -0.6134 | -0.61349 | -0.61392 | -0.61604 | -0.61713 | 0.10067 | 0.10054 | 0.10048 | 0.10031 | 0.1001 | 0.099854 | 0.099581 | 0.099479 | 0.099377 | 0.099279 | 0.099185 | 0.098758 | 0.096636 | 0.095543 | -0.45118 | -0.45133 | -0.45141 | -0.453 | -0.45461 | -0.45623 | -0.45787 | -0.45937 | -0.46086 | -0.46234 | -0.4638 | -0.47094 | -0.47968 | -0.48732
|  | FLOTTA | FS |  |  |  | 0 | -0.612 | -0.61213 | -0.61213 | -0.61214 | -0.61215 | -0.61216 | -0.61218 | -0.61223 | -0.61229 | -0.61236 | -0.61243 | -0.61262 | -0.61363 | -0.61581 | 0.10067 | 0.10055 | 0.10054 | 0.10054 | 0.10053 | 0.10051 | 0.1005 | 0.10044 | 0.10038 | 0.10032 | 0.10024 | 0.10005 | 0.099049 | 0.096859 | -0.45115 | -0.45129 | -0.45132 | -0.45136 | -0.452 | -0.45279 | -0.45357 | -0.45444 | -0.45531 | -0.45619 | -0.45707 | -0.46128 | -0.46618 | -0.47218
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 0.055789 | 16.7307 | 16.6526 | 16.5842 | 16.4711 | 16.356 | 16.241 | 16.1271 | 16.0155 | 15.9048 | 15.7948 | 15.6859 | 15.1143 | 14.4207 | 13.4661 | 15.5126 | 15.4372 | 15.3712 | 15.2626 | 15.1407 | 15.0132 | 14.8871 | 14.7626 | 14.6392 | 14.5167 | 14.3954 | 13.7642 | 13.0099 | 11.9955 | 15.9284 | 15.8438 | 15.769 | 15.6444 | 15.5181 | 15.3925 | 15.2683 | 15.1457 | 15.0242 | 14.9037 | 14.7843 | 14.6666 | 14.5429 | 14.4173
|  | FOCHABERS | CT |  |  |  | 0.055789 | 16.7307 | 16.6776 | 16.6233 | 16.5388 | 16.4515 | 16.3632 | 16.2759 | 16.1944 | 16.1131 | 16.0317 | 15.951 | 15.5222 | 15.0071 | 14.3843 | 15.5126 | 15.4611 | 15.4085 | 15.3272 | 15.2429 | 15.1525 | 15.0567 | 14.9662 | 14.876 | 14.7858 | 14.6966 | 14.226 | 13.6686 | 13.0047 | 15.9284 | 15.8714 | 15.8128 | 15.7202 | 15.6249 | 15.5292 | 15.4347 | 15.3455 | 15.2566 | 15.1678 | 15.0799 | 14.9922 | 14.8996 | 14.8056
|  | FOCHABERS | LW |  |  |  | 0.055789 | 16.7393 | 16.6526 | 16.5842 | 16.4711 | 16.356 | 16.241 | 16.1271 | 16.0155 | 15.9048 | 15.7948 | 15.6859 | 15.1143 | 14.4207 | 13.4661 | 15.5217 | 15.4372 | 15.3712 | 15.2626 | 15.1407 | 15.0132 | 14.8871 | 14.7626 | 14.6392 | 14.5167 | 14.3954 | 13.7642 | 13.0099 | 11.9955 | 15.9357 | 15.8438 | 15.769 | 15.6444 | 15.5181 | 15.3925 | 15.2683 | 15.1457 | 15.0242 | 14.9037 | 14.7843 | 14.6666 | 14.5429 | 14.4173
|  | FOCHABERS | ST |  |  |  | 0.055789 | 16.7948 | 16.7833 | 16.775 | 16.7282 | 16.6803 | 16.6325 | 16.5846 | 16.5412 | 16.4985 | 16.4568 | 16.4161 | 16.2229 | 15.9658 | 15.7585 | 15.5744 | 15.5631 | 15.5549 | 15.5102 | 15.4643 | 15.4185 | 15.3724 | 15.331 | 15.2903 | 15.2479 | 15.2015 | 14.9809 | 14.6986 | 14.4671 | 15.9987 | 15.9867 | 15.978 | 15.9259 | 15.8728 | 15.8201 | 15.7674 | 15.7187 | 15.6709 | 15.6243 | 15.5787 | 15.3624 | 15.0839 | 14.856
|  | FOCHABERS | FS |  |  |  | 0.055789 | 16.7984 | 16.7895 | 16.7854 | 16.7792 | 16.7654 | 16.7392 | 16.7131 | 16.6816 | 16.6498 | 16.6179 | 16.5858 | 16.4338 | 16.2573 | 16.0371 | 15.5779 | 15.569 | 15.5651 | 15.559 | 15.5459 | 15.5211 | 15.4963 | 15.4664 | 15.4361 | 15.4057 | 15.3752 | 15.2155 | 15.0179 | 14.7776 | 16.0027 | 15.9935 | 15.9891 | 15.9822 | 15.9668 | 15.9371 | 15.9076 | 15.8721 | 15.8364 | 15.8006 | 15.7645 | 15.5933 | 15.3989 | 15.1617
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 0.096842 | 17.3106 | 17.245 | 17.1857 | 17.1145 | 17.0276 | 16.9328 | 16.8319 | 16.7485 | 16.6632 | 16.5759 | 16.4898 | 15.4166 | 13.7606 | 11.4575 | 15.7952 | 15.7295 | 15.6702 | 15.5599 | 15.2656 | 14.9731 | 14.6818 | 14.3951 | 14.1093 | 13.8243 | 13.5433 | 12.0518 | 10.2537 | 7.7787 | 16.3615 | 16.2959 | 16.2366 | 16.1654 | 16.0785 | 15.9837 | 15.8828 | 15.7994 | 15.5955 | 15.3208 | 15.05 | 14.7815 | 14.493 | 14.202
|  | FORRES | CT |  |  |  | 0.096842 | 17.3106 | 17.245 | 17.1857 | 17.1155 | 17.0368 | 16.9494 | 16.8575 | 16.7862 | 16.7132 | 16.639 | 16.5645 | 16.1055 | 15.036 | 13.5019 | 15.7952 | 15.7295 | 15.6702 | 15.6 | 15.4828 | 15.2567 | 15.0312 | 14.8172 | 14.6034 | 14.3904 | 14.179 | 13.0488 | 11.695 | 10.0637 | 16.3615 | 16.2959 | 16.2366 | 16.1664 | 16.0877 | 16.0003 | 15.9084 | 15.8371 | 15.7641 | 15.6899 | 15.6154 | 15.4514 | 15.2331 | 15.0119
|  | FORRES | LW |  |  |  | 0.096842 | 17.362 | 17.2479 | 17.1908 | 17.1145 | 17.0276 | 16.9328 | 16.8319 | 16.7485 | 16.6632 | 16.5759 | 16.4898 | 15.4166 | 13.7606 | 11.4575 | 15.8465 | 15.7324 | 15.6754 | 15.5599 | 15.2656 | 14.9731 | 14.6818 | 14.3951 | 14.1093 | 13.8243 | 13.5433 | 12.0518 | 10.2537 | 7.7787 | 16.4129 | 16.2988 | 16.2417 | 16.1654 | 16.0785 | 15.9837 | 15.8828 | 15.7994 | 15.5955 | 15.3208 | 15.05 | 14.7815 | 14.493 | 14.202
|  | FORRES | ST |  |  |  | 0.096842 | 17.3721 | 17.3506 | 17.3373 | 17.3126 | 17.2825 | 17.2486 | 17.2117 | 17.1935 | 17.1752 | 17.1573 | 17.1399 | 17.0556 | 16.7903 | 16.6253 | 15.8566 | 15.8352 | 15.8218 | 15.7972 | 15.767 | 15.7331 | 15.6962 | 15.678 | 15.6022 | 15.4916 | 15.3834 | 14.8647 | 14.1839 | 13.6121 | 16.423 | 16.4015 | 16.3882 | 16.3635 | 16.3334 | 16.2994 | 16.2626 | 16.2444 | 16.2261 | 16.2082 | 16.1908 | 16.1065 | 15.6729 | 15.1222
|  | FORRES | FS |  |  |  | 0.096842 | 17.3772 | 17.3605 | 17.3549 | 17.3491 | 17.343 | 17.3365 | 17.33 | 17.3193 | 17.3078 | 17.2957 | 17.283 | 17.2339 | 17.0999 | 16.842 | 15.8617 | 15.845 | 15.8394 | 15.8336 | 15.8275 | 15.821 | 15.8145 | 15.8038 | 15.7923 | 15.7802 | 15.7675 | 15.3992 | 14.9204 | 14.337 | 16.4281 | 16.4114 | 16.4058 | 16.4 | 16.3939 | 16.3874 | 16.3809 | 16.3702 | 16.3587 | 16.3466 | 16.3339 | 16.2848 | 16.1508 | 15.8207
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0.052632 | 1.2931 | 1.2747 | 1.2566 | 1.2378 | 1.2184 | 1.1992 | 1.1798 | 1.161 | 1.1413 | 1.1216 | 1.0973 | 0.93987 | 0.75179 | 0.53199 | 1.1535 | 1.1351 | 1.117 | 1.0982 | 1.0788 | 1.0519 | 1.021 | 0.99035 | 0.95891 | 0.92764 | 0.89652 | 0.72956 | 0.53204 | 0.30305 | 1.1882 | 1.1698 | 1.1517 | 1.1329 | 1.1135 | 1.0904 | 1.0603 | 1.0305 | 0.99991 | 0.96948 | 0.93885 | 0.90808 | 0.8758 | 0.84259
|  | FORSS | CT |  |  |  | 0.052632 | 1.2931 | 1.2747 | 1.2566 | 1.2378 | 1.2184 | 1.1992 | 1.1798 | 1.161 | 1.1413 | 1.1216 | 1.0973 | 0.93987 | 0.75179 | 0.53199 | 1.1535 | 1.1351 | 1.117 | 1.0982 | 1.0788 | 1.0519 | 1.021 | 0.99035 | 0.95891 | 0.92764 | 0.89652 | 0.72956 | 0.53204 | 0.30305 | 1.1882 | 1.1698 | 1.1517 | 1.1329 | 1.1135 | 1.0904 | 1.0603 | 1.0305 | 0.99991 | 0.96948 | 0.93885 | 0.90808 | 0.8758 | 0.84259
|  | FORSS | LW |  |  |  | 0.052632 | 1.3209 | 1.3085 | 1.2994 | 1.289 | 1.2771 | 1.264 | 1.2497 | 1.2339 | 1.2062 | 1.1778 | 1.1497 | 0.99718 | 0.81064 | 0.56877 | 1.1813 | 1.169 | 1.1598 | 1.1494 | 1.1248 | 1.0949 | 1.0643 | 1.0336 | 1.0031 | 0.97189 | 0.94105 | 0.77509 | 0.5751 | 0.32032 | 1.216 | 1.2037 | 1.1945 | 1.1841 | 1.1636 | 1.1349 | 1.1055 | 1.0758 | 1.0458 | 1.015 | 0.98457 | 0.95444 | 0.9225 | 0.88955
|  | FORSS | ST |  |  |  | 0.052632 | 1.3268 | 1.3217 | 1.3171 | 1.3117 | 1.3052 | 1.2994 | 1.2934 | 1.2885 | 1.2836 | 1.2787 | 1.2738 | 1.2491 | 1.1904 | 1.1319 | 1.1872 | 1.1821 | 1.1775 | 1.1721 | 1.1657 | 1.1598 | 1.1538 | 1.1489 | 1.144 | 1.1326 | 1.1196 | 1.0575 | 0.98632 | 0.9224 | 1.2219 | 1.2168 | 1.2122 | 1.2068 | 1.2004 | 1.1945 | 1.1885 | 1.1836 | 1.1787 | 1.1709 | 1.1585 | 1.0992 | 1.0291 | 0.96604
|  | FORSS | FS |  |  |  | 0.052632 | 1.3302 | 1.3277 | 1.3243 | 1.3217 | 1.3191 | 1.3165 | 1.3139 | 1.311 | 1.3081 | 1.3052 | 1.3022 | 1.285 | 1.2619 | 1.2243 | 1.1906 | 1.1881 | 1.1847 | 1.1821 | 1.1795 | 1.1769 | 1.1743 | 1.1715 | 1.1685 | 1.1656 | 1.1626 | 1.1258 | 1.0726 | 1.0221 | 1.2253 | 1.2228 | 1.2194 | 1.2168 | 1.2142 | 1.2116 | 1.209 | 1.2061 | 1.2032 | 1.2003 | 1.1973 | 1.1651 | 1.1141 | 1.0647
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 1.9116 | 8.808 | 8.7944 | 8.7826 | 8.7689 | 8.7537 | 8.7371 | 8.7198 | 8.7053 | 8.6906 | 8.6758 | 8.661 | 8.5108 | 8.223 | 7.8309 | 8.6203 | 8.5901 | 8.5586 | 8.5075 | 8.4549 | 8.403 | 8.3516 | 8.3001 | 8.2489 | 8.1982 | 8.1482 | 7.8834 | 7.5702 | 7.1531 | 8.7368 | 8.7232 | 8.7114 | 8.6977 | 8.6825 | 8.6659 | 8.6486 | 8.6162 | 8.5676 | 8.5194 | 8.4719 | 8.4251 | 8.3747 | 8.3235
|  | FORTEVIOT | CT |  |  |  | 1.9116 | 8.808 | 8.7944 | 8.7826 | 8.7689 | 8.7537 | 8.7371 | 8.7198 | 8.7053 | 8.6906 | 8.6758 | 8.661 | 8.5727 | 8.4159 | 8.144 | 8.6203 | 8.5934 | 8.5669 | 8.5269 | 8.4859 | 8.4448 | 8.4038 | 8.3637 | 8.3238 | 8.2842 | 8.2449 | 8.0377 | 7.793 | 7.5036 | 8.7368 | 8.7232 | 8.7114 | 8.6977 | 8.6825 | 8.6659 | 8.6486 | 8.6341 | 8.6194 | 8.5989 | 8.5614 | 8.524 | 8.4847 | 8.4443
|  | FORTEVIOT | LW |  |  |  | 1.9116 | 8.8206 | 8.8005 | 8.7901 | 8.7767 | 8.7609 | 8.744 | 8.7264 | 8.7111 | 8.6956 | 8.6799 | 8.6644 | 8.5108 | 8.223 | 7.8309 | 8.6278 | 8.5901 | 8.5586 | 8.5075 | 8.4549 | 8.403 | 8.3516 | 8.3001 | 8.2489 | 8.1982 | 8.1482 | 7.8834 | 7.5702 | 7.1531 | 8.7494 | 8.7292 | 8.7189 | 8.7054 | 8.6897 | 8.6728 | 8.6552 | 8.6162 | 8.5676 | 8.5194 | 8.4719 | 8.4251 | 8.3747 | 8.3235
|  | FORTEVIOT | ST |  |  |  | 1.9116 | 8.8223 | 8.8184 | 8.8156 | 8.811 | 8.8058 | 8.8 | 8.7937 | 8.7903 | 8.7869 | 8.7835 | 8.7803 | 8.7638 | 8.7199 | 8.6899 | 8.6537 | 8.6482 | 8.6439 | 8.6218 | 8.5993 | 8.577 | 8.5548 | 8.5343 | 8.5142 | 8.4946 | 8.4754 | 8.3831 | 8.2669 | 8.1674 | 8.7511 | 8.7472 | 8.7444 | 8.7398 | 8.7346 | 8.7288 | 8.7225 | 8.7191 | 8.7157 | 8.7123 | 8.7091 | 8.6926 | 8.5861 | 8.4916
|  | FORTEVIOT | FS |  |  |  | 1.9116 | 8.824 | 8.8211 | 8.8193 | 8.8175 | 8.8156 | 8.8146 | 8.8135 | 8.8118 | 8.8099 | 8.808 | 8.8059 | 8.7951 | 8.7701 | 8.7255 | 8.6582 | 8.6538 | 8.6505 | 8.6466 | 8.639 | 8.6267 | 8.6145 | 8.5993 | 8.5841 | 8.5688 | 8.5534 | 8.4774 | 8.3912 | 8.2886 | 8.7528 | 8.7499 | 8.7481 | 8.7463 | 8.7444 | 8.7434 | 8.7423 | 8.7406 | 8.7387 | 8.7367 | 8.7347 | 8.7239 | 8.6989 | 8.6066
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0 | 1.0805 | 1.0784 | 1.0775 | 1.0752 | 1.0698 | 1.0644 | 1.0591 | 1.054 | 1.0489 | 1.0439 | 1.0389 | 1.013 | 0.98257 | 0.94113 | 1.0726 | 1.0704 | 1.0693 | 1.0677 | 1.0659 | 1.0641 | 1.0621 | 1.0605 | 1.0589 | 1.0573 | 1.0557 | 1.0259 | 0.99034 | 0.94392 | 1.0712 | 1.0689 | 1.0678 | 1.0662 | 1.0644 | 1.0625 | 1.0605 | 1.0589 | 1.0573 | 1.0556 | 1.054 | 1.0505 | 1.0444 | 1.0381
|  | FOYERS | CT |  |  |  | 0 | 1.0805 | 1.0798 | 1.0792 | 1.0784 | 1.0751 | 1.0709 | 1.0667 | 1.0628 | 1.0589 | 1.0551 | 1.0513 | 1.0314 | 1.0084 | 0.98124 | 1.0727 | 1.0719 | 1.0711 | 1.0701 | 1.0689 | 1.0675 | 1.0661 | 1.065 | 1.064 | 1.0629 | 1.0619 | 1.0471 | 1.0199 | 0.9887 | 1.0712 | 1.0704 | 1.0696 | 1.0686 | 1.0673 | 1.066 | 1.0645 | 1.0635 | 1.0624 | 1.0613 | 1.0603 | 1.0592 | 1.0579 | 1.0565
|  | FOYERS | LW |  |  |  | 0 | 1.0805 | 1.0784 | 1.0775 | 1.0752 | 1.0698 | 1.0644 | 1.0591 | 1.054 | 1.0489 | 1.0439 | 1.0389 | 1.013 | 0.98257 | 0.94113 | 1.0726 | 1.0704 | 1.0693 | 1.0677 | 1.0659 | 1.0641 | 1.0621 | 1.0605 | 1.0589 | 1.0573 | 1.0557 | 1.0259 | 0.99034 | 0.94392 | 1.0712 | 1.0689 | 1.0678 | 1.0662 | 1.0644 | 1.0625 | 1.0605 | 1.0589 | 1.0573 | 1.0556 | 1.054 | 1.0505 | 1.0444 | 1.0381
|  | FOYERS | ST |  |  |  | 0 | 1.0805 | 1.0803 | 1.0802 | 1.0798 | 1.0794 | 1.0789 | 1.0784 | 1.0782 | 1.0772 | 1.0752 | 1.0733 | 1.0642 | 1.0522 | 1.0425 | 1.0729 | 1.0726 | 1.0725 | 1.072 | 1.0715 | 1.0709 | 1.0702 | 1.0699 | 1.0696 | 1.0692 | 1.0689 | 1.0675 | 1.0629 | 1.0602 | 1.0714 | 1.0711 | 1.071 | 1.0705 | 1.07 | 1.0694 | 1.0687 | 1.0684 | 1.068 | 1.0677 | 1.0674 | 1.0659 | 1.0613 | 1.0586
|  | FOYERS | FS |  |  |  | 0 | 1.0805 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 1.0802 | 1.0802 | 1.0801 | 1.08 | 1.0799 | 1.0797 | 1.0722 | 1.063 | 1.052 | 1.0729 | 1.0726 | 1.0726 | 1.0726 | 1.0726 | 1.0724 | 1.0723 | 1.0721 | 1.0719 | 1.0716 | 1.0714 | 1.0705 | 1.0681 | 1.0636 | 1.0714 | 1.0712 | 1.0712 | 1.0711 | 1.0711 | 1.071 | 1.0708 | 1.0706 | 1.0704 | 1.0701 | 1.0699 | 1.0689 | 1.0665 | 1.0619
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 2.2158 | 45.2505 | 45.1324 | 45.0612 | 44.9647 | 44.8544 | 44.7334 | 44.6062 | 44.5034 | 44.399 | 44.292 | 43.9618 | 41.5111 | 38.8175 | 35.3027 | 42.5802 | 42.0006 | 41.4579 | 40.7332 | 40.027 | 39.349 | 38.7196 | 38.0804 | 37.4635 | 36.8654 | 36.3089 | 33.6002 | 30.6662 | 26.8568 | 44.2432 | 44.125 | 43.6553 | 42.9278 | 42.2189 | 41.5384 | 40.9067 | 40.2651 | 39.6458 | 39.0456 | 38.487 | 37.9604 | 37.4108 | 36.8624
|  | FRASERBURGH | CT |  |  |  | 2.2158 | 45.2505 | 45.1824 | 45.1218 | 45.0463 | 44.958 | 44.8584 | 44.7526 | 44.6764 | 44.5971 | 44.5173 | 44.4369 | 43.9285 | 42.0183 | 39.7259 | 42.7331 | 42.3974 | 42.0336 | 41.5487 | 41.0427 | 40.5278 | 40.0637 | 39.6149 | 39.1725 | 38.7552 | 38.3566 | 36.3597 | 34.2349 | 31.7792 | 44.2432 | 44.175 | 44.1144 | 43.7466 | 43.2387 | 42.7219 | 42.2562 | 41.8057 | 41.3617 | 40.9428 | 40.5428 | 40.1429 | 39.7329 | 39.3319
|  | FRASERBURGH | LW |  |  |  | 2.2158 | 45.2834 | 45.1324 | 45.0612 | 44.9647 | 44.8544 | 44.7334 | 44.6062 | 44.5034 | 44.399 | 44.292 | 43.9618 | 41.5111 | 38.8175 | 35.3027 | 42.5802 | 42.0006 | 41.4579 | 40.7332 | 40.027 | 39.349 | 38.7196 | 38.0804 | 37.4635 | 36.8654 | 36.3089 | 33.6002 | 30.6662 | 26.8568 | 44.276 | 44.125 | 43.6553 | 42.9278 | 42.2189 | 41.5384 | 40.9067 | 40.2651 | 39.6458 | 39.0456 | 38.487 | 37.9604 | 37.4108 | 36.8624
|  | FRASERBURGH | ST |  |  |  | 2.2158 | 45.2893 | 45.2658 | 45.2524 | 45.2235 | 45.1875 | 45.1463 | 45.1019 | 45.0821 | 45.0622 | 45.043 | 45.0244 | 44.9353 | 44.5938 | 44.4019 | 43.0126 | 42.914 | 42.8117 | 42.5536 | 42.281 | 42.0031 | 41.738 | 41.4745 | 41.2092 | 40.9541 | 40.7084 | 39.566 | 38.3309 | 37.2897 | 44.2819 | 44.2585 | 44.2451 | 44.2161 | 44.1801 | 44.139 | 43.9364 | 43.6719 | 43.4054 | 43.1493 | 42.9026 | 41.7555 | 40.5163 | 39.4712
|  | FRASERBURGH | FS |  |  |  | 2.2158 | 45.2926 | 45.2717 | 45.2675 | 45.2632 | 45.2583 | 45.2529 | 45.2476 | 45.2363 | 45.2241 | 45.2109 | 45.1969 | 45.1518 | 44.9871 | 44.6459 | 43.0519 | 42.9686 | 42.8958 | 42.8088 | 42.6866 | 42.5146 | 42.3458 | 42.1494 | 41.9452 | 41.7431 | 41.5431 | 40.6248 | 39.7283 | 38.6877 | 44.2853 | 44.2643 | 44.2602 | 44.2558 | 44.251 | 44.2456 | 44.2402 | 44.229 | 44.1441 | 43.9411 | 43.7403 | 42.818 | 41.9182 | 40.8745
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0.014737 | 5.5029 | 5.4789 | 5.4564 | 5.4309 | 5.4038 | 5.3352 | 5.2529 | 5.1728 | 5.0939 | 5.0163 | 4.9413 | 4.5504 | 4.0871 | 3.4597 | 5.1311 | 5.0652 | 5.0001 | 4.9038 | 4.8084 | 4.714 | 4.6225 | 4.5327 | 4.4445 | 4.3578 | 4.2743 | 3.843 | 3.3405 | 2.6754 | 5.2715 | 5.2459 | 5.2131 | 5.1274 | 5.0421 | 4.9574 | 4.8748 | 4.7943 | 4.7151 | 4.6372 | 4.5547 | 4.4741 | 4.3885 | 4.3031
|  | FRIOCKHEIM | CT |  |  |  | 0.014737 | 5.5029 | 5.4789 | 5.4564 | 5.4309 | 5.4038 | 5.3744 | 5.3371 | 5.2734 | 5.2098 | 5.1473 | 5.0861 | 4.7665 | 4.3916 | 3.9443 | 5.1311 | 5.0794 | 5.0254 | 4.9511 | 4.8752 | 4.7991 | 4.726 | 4.6554 | 4.5851 | 4.5163 | 4.449 | 4.1006 | 3.698 | 3.224 | 5.2715 | 5.2459 | 5.2215 | 5.1645 | 5.0958 | 5.0265 | 4.9596 | 4.8956 | 4.8318 | 4.7691 | 4.7077 | 4.6464 | 4.5821 | 4.5173
|  | FRIOCKHEIM | LW |  |  |  | 0.014737 | 5.5274 | 5.4946 | 5.4768 | 5.4532 | 5.4197 | 5.3352 | 5.2529 | 5.1728 | 5.0939 | 5.0163 | 4.9413 | 4.5504 | 4.0871 | 3.4597 | 5.14 | 5.0652 | 5.0001 | 4.9038 | 4.8084 | 4.714 | 4.6225 | 4.5327 | 4.4445 | 4.3578 | 4.2743 | 3.843 | 3.3405 | 2.6754 | 5.295 | 5.2598 | 5.2131 | 5.1274 | 5.0421 | 4.9574 | 4.8748 | 4.7943 | 4.7151 | 4.6372 | 4.5547 | 4.4741 | 4.3885 | 4.3031
|  | FRIOCKHEIM | ST |  |  |  | 0.014737 | 5.5324 | 5.5254 | 5.5203 | 5.5123 | 5.5024 | 5.4916 | 5.48 | 5.473 | 5.466 | 5.4599 | 5.454 | 5.3383 | 5.1665 | 5.022 | 5.1946 | 5.182 | 5.1704 | 5.1332 | 5.0936 | 5.0543 | 5.0151 | 4.9779 | 4.9403 | 4.9052 | 4.8709 | 4.7133 | 4.5246 | 4.364 | 5.3029 | 5.2956 | 5.2901 | 5.2804 | 5.2688 | 5.2563 | 5.2263 | 5.1935 | 5.1604 | 5.1296 | 5.0994 | 4.9603 | 4.7879 | 4.6429
|  | FRIOCKHEIM | FS |  |  |  | 0.014737 | 5.5349 | 5.5299 | 5.5273 | 5.5246 | 5.5218 | 5.5189 | 5.516 | 5.512 | 5.5079 | 5.5036 | 5.4992 | 5.4798 | 5.3674 | 5.2234 | 5.1999 | 5.1914 | 5.1832 | 5.1739 | 5.1594 | 5.1366 | 5.1139 | 5.087 | 5.06 | 5.033 | 5.0058 | 4.8776 | 4.7445 | 4.5872 | 5.3056 | 5.3004 | 5.2974 | 5.2943 | 5.2909 | 5.2868 | 5.2828 | 5.2775 | 5.2688 | 5.245 | 5.2212 | 5.1089 | 4.9895 | 4.845
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 1.5958 | 6.2377 | 6.1926 | 6.149 | 6.0992 | 6.0409 | 5.9723 | 5.9058 | 5.8406 | 5.7445 | 5.6492 | 5.5581 | 5.0894 | 4.5401 | 3.8141 | 7.8108 | 7.7515 | 7.6917 | 7.6187 | 7.5435 | 7.4667 | 7.393 | 7.3168 | 7.2399 | 7.1631 | 7.0891 | 6.6988 | 6.2236 | 5.5686 | 5.6235 | 5.5664 | 5.5091 | 5.4396 | 5.3681 | 5.2948 | 5.2242 | 5.1569 | 5.0898 | 5.0176 | 4.9476 | 4.8794 | 4.8062 | 4.731
|  | FYVIE | CT |  |  |  | 1.5958 | 6.2377 | 6.1926 | 6.149 | 6.0992 | 6.0409 | 5.9723 | 5.9058 | 5.8427 | 5.7798 | 5.7173 | 5.6482 | 5.2289 | 4.7455 | 4.177 | 7.8108 | 7.7515 | 7.6917 | 7.6187 | 7.5435 | 7.4667 | 7.393 | 7.3224 | 7.2521 | 7.1827 | 7.1149 | 6.7519 | 6.3206 | 5.8019 | 5.6235 | 5.5664 | 5.5091 | 5.4396 | 5.3681 | 5.2948 | 5.2242 | 5.1569 | 5.0898 | 5.0233 | 4.9583 | 4.8932 | 4.8238 | 4.7532
|  | FYVIE | LW |  |  |  | 1.5958 | 6.2814 | 6.2336 | 6.199 | 6.1381 | 6.0691 | 5.999 | 5.93 | 5.8406 | 5.7445 | 5.6492 | 5.5581 | 5.0894 | 4.5401 | 3.8141 | 7.8453 | 7.7753 | 7.7159 | 7.6357 | 7.5548 | 7.4736 | 7.3946 | 7.3168 | 7.2399 | 7.1631 | 7.0891 | 6.6988 | 6.2236 | 5.5686 | 5.6594 | 5.5928 | 5.5372 | 5.4625 | 5.3866 | 5.3102 | 5.2356 | 5.1625 | 5.09 | 5.0176 | 4.9476 | 4.8794 | 4.8062 | 4.731
|  | FYVIE | ST |  |  |  | 1.5958 | 6.3031 | 6.2911 | 6.2807 | 6.263 | 6.2425 | 6.222 | 6.2012 | 6.1844 | 6.1625 | 6.1377 | 6.1132 | 5.9961 | 5.8233 | 5.6473 | 7.8842 | 7.8733 | 7.86 | 7.8288 | 7.7946 | 7.7605 | 7.7269 | 7.6963 | 7.6659 | 7.6364 | 7.6073 | 7.4689 | 7.2977 | 7.1533 | 5.7007 | 5.6859 | 5.6717 | 5.6426 | 5.6105 | 5.5785 | 5.5469 | 5.5184 | 5.4901 | 5.4627 | 5.4356 | 5.3064 | 5.143 | 5.006
|  | FYVIE | FS |  |  |  | 1.5958 | 6.309 | 6.301 | 6.2944 | 6.2873 | 6.2792 | 6.2694 | 6.2598 | 6.2486 | 6.237 | 6.2253 | 6.2142 | 6.1297 | 6.0306 | 5.9032 | 7.8896 | 7.8825 | 7.8768 | 7.8662 | 7.8521 | 7.8329 | 7.8142 | 7.7926 | 7.7703 | 7.7479 | 7.7262 | 7.6202 | 7.5059 | 7.366 | 5.7084 | 5.6978 | 5.6885 | 5.678 | 5.6648 | 5.647 | 5.6298 | 5.6097 | 5.5891 | 5.5684 | 5.5483 | 5.45 | 5.3423 | 5.2086
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | YES | 0 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079
|  | GARBAT FOREST | CT |  |  |  | 0 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079
|  | GARBAT FOREST | LW |  |  |  | 0 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079
|  | GARBAT FOREST | ST |  |  |  | 0 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079
|  | GARBAT FOREST | FS |  |  |  | 0 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10106 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10071 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079 | 0.10079
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0 | 1.7718 | 1.766 | 1.7634 | 1.7598 | 1.7557 | 1.7513 | 1.7466 | 1.7429 | 1.7391 | 1.7353 | 1.7316 | 1.7083 | 1.6718 | 1.6017 | 1.6904 | 1.6846 | 1.6821 | 1.6785 | 1.6744 | 1.6699 | 1.6652 | 1.6615 | 1.6578 | 1.654 | 1.6502 | 1.627 | 1.5904 | 1.4986 | 1.4467 | 1.4409 | 1.4383 | 1.4347 | 1.4307 | 1.4262 | 1.4215 | 1.4178 | 1.4141 | 1.4103 | 1.4065 | 1.4028 | 1.3982 | 1.3934
|  | GISLA | CT |  |  |  | 0 | 1.7718 | 1.7698 | 1.7681 | 1.7657 | 1.7629 | 1.7595 | 1.7559 | 1.7536 | 1.7512 | 1.7487 | 1.7463 | 1.7301 | 1.7043 | 1.6645 | 1.6904 | 1.6884 | 1.6867 | 1.6844 | 1.6815 | 1.6782 | 1.6746 | 1.6722 | 1.6698 | 1.6674 | 1.6649 | 1.6488 | 1.623 | 1.5832 | 1.4467 | 1.4447 | 1.443 | 1.4406 | 1.4378 | 1.4344 | 1.4309 | 1.4285 | 1.4261 | 1.4236 | 1.4212 | 1.4186 | 1.4154 | 1.4121
|  | GISLA | LW |  |  |  | 0 | 1.7718 | 1.766 | 1.7634 | 1.7598 | 1.7557 | 1.7513 | 1.7466 | 1.7429 | 1.7391 | 1.7353 | 1.7316 | 1.7083 | 1.6718 | 1.6017 | 1.6904 | 1.6846 | 1.6821 | 1.6785 | 1.6744 | 1.6699 | 1.6652 | 1.6615 | 1.6578 | 1.654 | 1.6502 | 1.627 | 1.5904 | 1.4986 | 1.4467 | 1.4409 | 1.4383 | 1.4347 | 1.4307 | 1.4262 | 1.4215 | 1.4178 | 1.4141 | 1.4103 | 1.4065 | 1.4028 | 1.3982 | 1.3934
|  | GISLA | ST |  |  |  | 0 | 1.7718 | 1.771 | 1.7707 | 1.7697 | 1.7685 | 1.767 | 1.7655 | 1.7649 | 1.7643 | 1.7637 | 1.7632 | 1.7607 | 1.7484 | 1.742 | 1.6904 | 1.6897 | 1.6893 | 1.6883 | 1.6871 | 1.6857 | 1.6841 | 1.6835 | 1.6829 | 1.6823 | 1.6818 | 1.6793 | 1.667 | 1.6607 | 1.4467 | 1.4459 | 1.4456 | 1.4446 | 1.4434 | 1.442 | 1.4404 | 1.4398 | 1.4392 | 1.4386 | 1.4381 | 1.4356 | 1.4233 | 1.417
|  | GISLA | FS |  |  |  | 0 | 1.7718 | 1.7711 | 1.771 | 1.771 | 1.7709 | 1.7709 | 1.7708 | 1.7705 | 1.7701 | 1.7697 | 1.7693 | 1.7682 | 1.7624 | 1.7497 | 1.6904 | 1.6897 | 1.6897 | 1.6896 | 1.6896 | 1.6895 | 1.6894 | 1.6891 | 1.6888 | 1.6884 | 1.6879 | 1.6868 | 1.681 | 1.6683 | 1.4467 | 1.446 | 1.446 | 1.4459 | 1.4459 | 1.4458 | 1.4457 | 1.4454 | 1.445 | 1.4447 | 1.4442 | 1.4431 | 1.4373 | 1.4246
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 0 | 1.9925 | 1.9681 | 1.9493 | 1.9182 | 1.8865 | 1.8549 | 1.8236 | 1.7931 | 1.7629 | 1.7328 | 1.7014 | 1.5359 | 1.3321 | 1.0481 | 1.8282 | 1.8144 | 1.8079 | 1.7989 | 1.7886 | 1.7612 | 1.7243 | 1.6878 | 1.6516 | 1.6157 | 1.5804 | 1.3958 | 1.1727 | 0.86975 | 2.0441 | 2.0178 | 1.9967 | 1.9615 | 1.9257 | 1.8902 | 1.8552 | 1.8207 | 1.7865 | 1.7526 | 1.7193 | 1.6865 | 1.6514 | 1.616
|  | GLASTULLICH | CT |  |  |  | 0 | 1.9939 | 1.9803 | 1.9667 | 1.9444 | 1.9212 | 1.8975 | 1.8739 | 1.8526 | 1.8314 | 1.8104 | 1.7895 | 1.6749 | 1.5334 | 1.3604 | 1.8282 | 1.8224 | 1.8173 | 1.8108 | 1.8029 | 1.7939 | 1.7836 | 1.7582 | 1.7328 | 1.7077 | 1.6829 | 1.5517 | 1.3969 | 1.211 | 2.0459 | 2.0309 | 2.0157 | 1.9903 | 1.9642 | 1.9378 | 1.9115 | 1.8874 | 1.8635 | 1.8398 | 1.8163 | 1.7929 | 1.7679 | 1.7427
|  | GLASTULLICH | LW |  |  |  | 0 | 1.9925 | 1.9681 | 1.9493 | 1.9182 | 1.8865 | 1.8549 | 1.8236 | 1.7931 | 1.7629 | 1.7328 | 1.7014 | 1.5359 | 1.3321 | 1.0481 | 1.8291 | 1.8144 | 1.8079 | 1.7989 | 1.7886 | 1.7612 | 1.7243 | 1.6878 | 1.6516 | 1.6157 | 1.5804 | 1.3958 | 1.1727 | 0.86975 | 2.0441 | 2.0178 | 1.9967 | 1.9615 | 1.9257 | 1.8902 | 1.8552 | 1.8207 | 1.7865 | 1.7526 | 1.7193 | 1.6865 | 1.6514 | 1.616
|  | GLASTULLICH | ST |  |  |  | 0 | 2.0075 | 2.0052 | 2.0032 | 1.9903 | 1.977 | 1.9637 | 1.9504 | 1.9387 | 1.9273 | 1.9162 | 1.9053 | 1.8543 | 1.7819 | 1.723 | 1.8291 | 1.8272 | 1.8263 | 1.8239 | 1.821 | 1.8175 | 1.8137 | 1.8123 | 1.8108 | 1.8094 | 1.8081 | 1.7534 | 1.6687 | 1.6006 | 2.0619 | 2.0595 | 2.0573 | 2.0424 | 2.0272 | 2.012 | 1.9969 | 1.9833 | 1.97 | 1.957 | 1.9444 | 1.8848 | 1.8043 | 1.7402
|  | GLASTULLICH | FS |  |  |  | 0 | 2.0083 | 2.0062 | 2.0058 | 2.0049 | 2.0015 | 1.9945 | 1.9876 | 1.9792 | 1.9708 | 1.9623 | 1.9537 | 1.9141 | 1.8658 | 1.8032 | 1.8291 | 1.8274 | 1.8273 | 1.8272 | 1.8271 | 1.8269 | 1.8267 | 1.8259 | 1.8251 | 1.8242 | 1.8232 | 1.8205 | 1.7668 | 1.6948 | 2.0628 | 2.0607 | 2.0602 | 2.0591 | 2.0552 | 2.0469 | 2.0387 | 2.0289 | 2.019 | 2.0091 | 1.9991 | 1.9525 | 1.8976 | 1.8288
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | YES | 0 | 2.8981 | 2.8887 | 2.88 | 2.87 | 2.8589 | 2.8468 | 2.8342 | 2.8242 | 2.8132 | 2.8022 | 2.7912 | 2.7231 | 2.5285 | 2.2545 | 2.7505 | 2.7299 | 2.7075 | 2.671 | 2.6333 | 2.596 | 2.5591 | 2.5227 | 2.4865 | 2.4507 | 2.4154 | 2.2306 | 2.0113 | 1.7202 | 2.7576 | 2.7482 | 2.7395 | 2.7295 | 2.7184 | 2.7063 | 2.6729 | 2.6365 | 2.6004 | 2.5646 | 2.5295 | 2.4948 | 2.4584 | 2.4209
|  | GLEDFIELD | CT |  |  |  | 0 | 2.8981 | 2.8887 | 2.88 | 2.87 | 2.8589 | 2.8468 | 2.8342 | 2.8242 | 2.8132 | 2.8022 | 2.7912 | 2.727 | 2.6381 | 2.474 | 2.7505 | 2.7323 | 2.7129 | 2.684 | 2.6544 | 2.6248 | 2.5953 | 2.5677 | 2.5394 | 2.5114 | 2.4836 | 2.3379 | 2.1676 | 1.9658 | 2.7576 | 2.7482 | 2.7395 | 2.7295 | 2.7184 | 2.7063 | 2.6937 | 2.6814 | 2.6531 | 2.6252 | 2.5975 | 2.5699 | 2.5411 | 2.5121
|  | GLEDFIELD | LW |  |  |  | 0 | 2.9065 | 2.892 | 2.8846 | 2.8749 | 2.8634 | 2.8511 | 2.8382 | 2.8268 | 2.8152 | 2.8036 | 2.7921 | 2.7231 | 2.5285 | 2.2545 | 2.7565 | 2.7299 | 2.7075 | 2.671 | 2.6333 | 2.596 | 2.5591 | 2.5227 | 2.4865 | 2.4507 | 2.4154 | 2.2306 | 2.0113 | 1.7202 | 2.766 | 2.7515 | 2.7441 | 2.7345 | 2.7229 | 2.7097 | 2.6729 | 2.6365 | 2.6004 | 2.5646 | 2.5295 | 2.4948 | 2.4584 | 2.4209
|  | GLEDFIELD | ST |  |  |  | 0 | 2.909 | 2.9058 | 2.9033 | 2.8996 | 2.8954 | 2.8908 | 2.8859 | 2.883 | 2.8801 | 2.8772 | 2.8744 | 2.861 | 2.8279 | 2.8069 | 2.7761 | 2.7715 | 2.7677 | 2.7519 | 2.7359 | 2.72 | 2.7042 | 2.6888 | 2.6736 | 2.6587 | 2.6442 | 2.5769 | 2.4958 | 2.4289 | 2.7686 | 2.7653 | 2.7629 | 2.7591 | 2.755 | 2.7504 | 2.7454 | 2.7425 | 2.7396 | 2.7368 | 2.734 | 2.6907 | 2.6097 | 2.543
|  | GLEDFIELD | FS |  |  |  | 0 | 2.9099 | 2.9076 | 2.9067 | 2.9058 | 2.9048 | 2.9038 | 2.9029 | 2.9014 | 2.8999 | 2.8983 | 2.8966 | 2.8903 | 2.8749 | 2.8465 | 2.7781 | 2.7755 | 2.7742 | 2.7715 | 2.767 | 2.7584 | 2.7498 | 2.739 | 2.7281 | 2.7171 | 2.7062 | 2.6541 | 2.5959 | 2.5315 | 2.7694 | 2.7672 | 2.7663 | 2.7653 | 2.7644 | 2.7634 | 2.7624 | 2.7609 | 2.7594 | 2.7578 | 2.7562 | 2.7498 | 2.7097 | 2.6454
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423
|  | GLEN LAOGH | CT |  |  |  | 0 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423
|  | GLEN LAOGH | LW |  |  |  | 0 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423
|  | GLEN LAOGH | ST |  |  |  | 0 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423
|  | GLEN LAOGH | FS |  |  |  | 0 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10446 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10431 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423 | 0.10423
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0.016842 | 3.6496 | 3.6369 | 3.6312 | 3.6234 | 3.6144 | 3.6047 | 3.5945 | 3.5791 | 3.546 | 3.5132 | 3.4809 | 3.3121 | 3.114 | 2.8472 | 3.6956 | 3.6823 | 3.6758 | 3.6665 | 3.6561 | 3.645 | 3.6334 | 3.624 | 3.6144 | 3.6048 | 3.5953 | 3.4218 | 3.2027 | 2.9151 | 3.6815 | 3.6688 | 3.6631 | 3.6553 | 3.6463 | 3.6366 | 3.6158 | 3.578 | 3.5405 | 3.5033 | 3.4666 | 3.4304 | 3.3923 | 3.3539
|  | GLENCOE | CT |  |  |  | 0.016842 | 3.6496 | 3.6453 | 3.6416 | 3.6366 | 3.6306 | 3.6235 | 3.6158 | 3.6109 | 3.6057 | 3.6006 | 3.581 | 3.4647 | 3.3291 | 3.1628 | 3.6958 | 3.691 | 3.6867 | 3.6807 | 3.6736 | 3.6656 | 3.657 | 3.651 | 3.6449 | 3.6387 | 3.6325 | 3.5925 | 3.4425 | 3.2615 | 3.6815 | 3.6772 | 3.6735 | 3.6685 | 3.6625 | 3.6553 | 3.6477 | 3.6428 | 3.6304 | 3.6044 | 3.5787 | 3.553 | 3.5269 | 3.5006
|  | GLENCOE | LW |  |  |  | 0.016842 | 3.6496 | 3.6369 | 3.6312 | 3.6234 | 3.6144 | 3.6047 | 3.5945 | 3.5791 | 3.546 | 3.5132 | 3.4809 | 3.3121 | 3.114 | 2.8472 | 3.6956 | 3.6823 | 3.6758 | 3.6665 | 3.6561 | 3.645 | 3.6334 | 3.624 | 3.6144 | 3.6048 | 3.5953 | 3.4218 | 3.2027 | 2.9151 | 3.6815 | 3.6688 | 3.6631 | 3.6553 | 3.6463 | 3.6366 | 3.6158 | 3.578 | 3.5405 | 3.5033 | 3.4666 | 3.4304 | 3.3923 | 3.3539
|  | GLENCOE | ST |  |  |  | 0.016842 | 3.6496 | 3.648 | 3.6472 | 3.6451 | 3.6426 | 3.6396 | 3.6363 | 3.6351 | 3.6338 | 3.6326 | 3.6315 | 3.6263 | 3.5558 | 3.4911 | 3.6965 | 3.6949 | 3.694 | 3.6913 | 3.6881 | 3.6845 | 3.6806 | 3.6786 | 3.6767 | 3.6749 | 3.6731 | 3.6648 | 3.6363 | 3.6189 | 3.6815 | 3.6799 | 3.6791 | 3.677 | 3.6745 | 3.6715 | 3.6682 | 3.667 | 3.6657 | 3.6645 | 3.6634 | 3.6364 | 3.548 | 3.474
|  | GLENCOE | FS |  |  |  | 0.016842 | 3.6496 | 3.6481 | 3.6481 | 3.648 | 3.6479 | 3.6477 | 3.6475 | 3.6469 | 3.6462 | 3.6454 | 3.6445 | 3.6422 | 3.6304 | 3.5815 | 3.6967 | 3.6951 | 3.695 | 3.6948 | 3.6945 | 3.6939 | 3.6932 | 3.6921 | 3.6909 | 3.6896 | 3.6882 | 3.6835 | 3.6693 | 3.6413 | 3.6815 | 3.68 | 3.68 | 3.6799 | 3.6798 | 3.6796 | 3.6794 | 3.6788 | 3.6781 | 3.6773 | 3.6764 | 3.6741 | 3.65 | 3.5777
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0 | 0.36749 | 0.36516 | 0.36293 | 0.36051 | 0.35554 | 0.34881 | 0.34195 | 0.33531 | 0.32869 | 0.3221 | 0.31559 | 0.28001 | 0.23471 | 0.17851 | 0.35333 | 0.35091 | 0.34854 | 0.34588 | 0.34306 | 0.34011 | 0.33259 | 0.32411 | 0.31568 | 0.30728 | 0.29898 | 0.25651 | 0.20644 | 0.14553 | 0.35362 | 0.35129 | 0.34906 | 0.34664 | 0.34405 | 0.34119 | 0.3329 | 0.32446 | 0.31604 | 0.30766 | 0.29937 | 0.29115 | 0.28266 | 0.27414
|  | GLENDARUEL | CT |  |  |  | 0 | 0.36749 | 0.36516 | 0.36293 | 0.36051 | 0.35554 | 0.34947 | 0.34339 | 0.33763 | 0.33187 | 0.32614 | 0.32043 | 0.29099 | 0.25704 | 0.2146 | 0.35333 | 0.35091 | 0.34854 | 0.34588 | 0.34306 | 0.34011 | 0.33664 | 0.32956 | 0.32247 | 0.31543 | 0.30842 | 0.27255 | 0.23383 | 0.18798 | 0.35362 | 0.35129 | 0.34906 | 0.34664 | 0.34405 | 0.34131 | 0.33638 | 0.32963 | 0.32278 | 0.31578 | 0.30878 | 0.30179 | 0.29462 | 0.28742
|  | GLENDARUEL | LW |  |  |  | 0 | 0.37002 | 0.3681 | 0.36641 | 0.36261 | 0.3557 | 0.34881 | 0.34195 | 0.33531 | 0.32869 | 0.3221 | 0.31559 | 0.28001 | 0.23471 | 0.17851 | 0.35584 | 0.35377 | 0.35191 | 0.34956 | 0.34706 | 0.34125 | 0.33259 | 0.32411 | 0.31568 | 0.30728 | 0.29898 | 0.25651 | 0.20644 | 0.14553 | 0.35614 | 0.35423 | 0.35253 | 0.35051 | 0.34832 | 0.34119 | 0.3329 | 0.32446 | 0.31604 | 0.30766 | 0.29937 | 0.29115 | 0.28266 | 0.27414
|  | GLENDARUEL | ST |  |  |  | 0 | 0.37002 | 0.36978 | 0.36966 | 0.36936 | 0.36899 | 0.36855 | 0.36806 | 0.36714 | 0.36473 | 0.36236 | 0.36003 | 0.34876 | 0.33483 | 0.31958 | 0.35602 | 0.35578 | 0.35566 | 0.3552 | 0.35468 | 0.3541 | 0.35347 | 0.35313 | 0.3528 | 0.35248 | 0.35217 | 0.33849 | 0.32047 | 0.30122 | 0.35614 | 0.35591 | 0.35579 | 0.35549 | 0.35512 | 0.35468 | 0.35419 | 0.35401 | 0.35383 | 0.35365 | 0.35348 | 0.33883 | 0.32084 | 0.30162
|  | GLENDARUEL | FS |  |  |  | 0 | 0.37002 | 0.3698 | 0.36979 | 0.36978 | 0.36977 | 0.36974 | 0.36972 | 0.36963 | 0.36952 | 0.36941 | 0.36824 | 0.35796 | 0.34661 | 0.33352 | 0.35603 | 0.35581 | 0.3558 | 0.35578 | 0.3557 | 0.35559 | 0.35549 | 0.35526 | 0.35502 | 0.35478 | 0.35452 | 0.35042 | 0.33521 | 0.31835 | 0.35614 | 0.35593 | 0.35592 | 0.35591 | 0.35589 | 0.35587 | 0.35585 | 0.35576 | 0.35565 | 0.35554 | 0.35542 | 0.35035 | 0.33557 | 0.31873
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.16632 | 3.18 | 3.1516 | 3.1225 | 3.084 | 3.0447 | 3.0059 | 2.9672 | 2.9283 | 2.8871 | 2.844 | 2.8014 | 2.5733 | 2.298 | 1.933 | 3.3327 | 3.3021 | 3.2703 | 3.227 | 3.183 | 3.1397 | 3.0921 | 3.0428 | 2.9938 | 2.9444 | 2.8956 | 2.6374 | 2.3318 | 1.9372 | 3.0547 | 3.0355 | 3.017 | 2.9979 | 2.9775 | 2.9569 | 2.9357 | 2.9158 | 2.8957 | 2.8756 | 2.8555 | 2.8351 | 2.7877 | 2.736
|  | GLENDEVON | CT |  |  |  | 0.16632 | 3.18 | 3.1516 | 3.1225 | 3.084 | 3.0447 | 3.0059 | 2.9672 | 2.9283 | 2.8896 | 2.8511 | 2.8129 | 2.6097 | 2.3665 | 2.0805 | 3.3327 | 3.3021 | 3.2703 | 3.227 | 3.183 | 3.1397 | 3.0966 | 3.0531 | 3.0098 | 2.9668 | 2.924 | 2.6995 | 2.4344 | 2.127 | 3.0547 | 3.0355 | 3.017 | 2.9979 | 2.9775 | 2.9569 | 2.9357 | 2.9158 | 2.8957 | 2.8756 | 2.8555 | 2.8351 | 2.8125 | 2.7817
|  | GLENDEVON | LW |  |  |  | 0.16632 | 3.2 | 3.1692 | 3.1433 | 3.1022 | 3.0595 | 3.0163 | 2.9726 | 2.9297 | 2.8871 | 2.844 | 2.8014 | 2.5733 | 2.298 | 1.933 | 3.3518 | 3.318 | 3.2884 | 3.2406 | 3.1914 | 3.1419 | 3.0921 | 3.0428 | 2.9938 | 2.9444 | 2.8956 | 2.6374 | 2.3318 | 1.9372 | 3.0783 | 3.0594 | 3.0487 | 3.0346 | 3.0185 | 3.0006 | 2.9812 | 2.9645 | 2.9476 | 2.9298 | 2.886 | 2.8382 | 2.7877 | 2.736
|  | GLENDEVON | ST |  |  |  | 0.16632 | 3.2215 | 3.2152 | 3.2098 | 3.1922 | 3.1734 | 3.1546 | 3.1366 | 3.1196 | 3.1028 | 3.0862 | 3.07 | 2.9907 | 2.8902 | 2.8045 | 3.3774 | 3.3707 | 3.3651 | 3.3445 | 3.3228 | 3.3013 | 3.2806 | 3.2605 | 3.2407 | 3.2212 | 3.2021 | 3.1092 | 2.9957 | 2.8976 | 3.0833 | 3.0782 | 3.0739 | 3.0683 | 3.0612 | 3.0537 | 3.0467 | 3.0419 | 3.0372 | 3.0325 | 3.0278 | 3.0036 | 2.9555 | 2.888
|  | GLENDEVON | FS |  |  |  | 0.16632 | 3.2262 | 3.2219 | 3.2182 | 3.214 | 3.2075 | 3.1965 | 3.1856 | 3.1733 | 3.1609 | 3.1485 | 3.136 | 3.0733 | 3.0066 | 2.9271 | 3.3826 | 3.378 | 3.374 | 3.3695 | 3.362 | 3.349 | 3.336 | 3.3215 | 3.3069 | 3.2922 | 3.2775 | 3.2039 | 3.1269 | 3.0379 | 3.0859 | 3.0825 | 3.0799 | 3.0773 | 3.0747 | 3.072 | 3.0693 | 3.066 | 3.0627 | 3.0593 | 3.0559 | 3.0374 | 3.0119 | 2.9714
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0 | 2.2896 | 2.2857 | 2.282 | 2.2779 | 2.2735 | 2.2687 | 2.2637 | 2.2596 | 2.2554 | 2.243 | 2.2295 | 2.1567 | 2.0706 | 1.9552 | 2.2788 | 2.2746 | 2.2706 | 2.2659 | 2.2608 | 2.2555 | 2.2499 | 2.2452 | 2.2404 | 2.2356 | 2.2227 | 2.1307 | 2.0163 | 1.8724 | 2.2744 | 2.2705 | 2.2668 | 2.2627 | 2.2583 | 2.2535 | 2.2485 | 2.2444 | 2.2402 | 2.236 | 2.2318 | 2.2263 | 2.2068 | 2.1873
|  | GLENDOE | CT |  |  |  | 0 | 2.2896 | 2.2857 | 2.282 | 2.2779 | 2.2735 | 2.2687 | 2.2637 | 2.2596 | 2.2554 | 2.2512 | 2.2465 | 2.1863 | 2.116 | 2.0328 | 2.2788 | 2.2746 | 2.2706 | 2.2659 | 2.2608 | 2.2555 | 2.2499 | 2.2452 | 2.2404 | 2.2356 | 2.2308 | 2.1757 | 2.0917 | 1.9895 | 2.2744 | 2.2705 | 2.2668 | 2.2627 | 2.2583 | 2.2535 | 2.2485 | 2.2444 | 2.2402 | 2.236 | 2.2318 | 2.2266 | 2.221 | 2.2153
|  | GLENDOE | LW |  |  |  | 0 | 2.2946 | 2.2897 | 2.2871 | 2.2837 | 2.28 | 2.2752 | 2.2702 | 2.2659 | 2.2567 | 2.243 | 2.2295 | 2.1567 | 2.0706 | 1.9552 | 2.2838 | 2.2785 | 2.2754 | 2.2712 | 2.2667 | 2.2611 | 2.2553 | 2.2502 | 2.245 | 2.2397 | 2.2227 | 2.1307 | 2.0163 | 1.8724 | 2.2795 | 2.2745 | 2.2719 | 2.2685 | 2.2648 | 2.26 | 2.255 | 2.2507 | 2.2464 | 2.242 | 2.2376 | 2.2263 | 2.2068 | 2.1873
|  | GLENDOE | ST |  |  |  | 0 | 2.2955 | 2.2941 | 2.293 | 2.2915 | 2.2898 | 2.288 | 2.286 | 2.2848 | 2.2835 | 2.2823 | 2.281 | 2.2751 | 2.2461 | 2.2157 | 2.2851 | 2.2837 | 2.2825 | 2.2806 | 2.2785 | 2.2764 | 2.2741 | 2.2724 | 2.2707 | 2.2691 | 2.2674 | 2.2595 | 2.2424 | 2.2031 | 2.2803 | 2.2789 | 2.2778 | 2.2763 | 2.2746 | 2.2728 | 2.2708 | 2.2696 | 2.2683 | 2.2671 | 2.2658 | 2.2599 | 2.2467 | 2.2232
|  | GLENDOE | FS |  |  |  | 0 | 2.2963 | 2.2958 | 2.2949 | 2.2941 | 2.2932 | 2.2923 | 2.2914 | 2.2903 | 2.2892 | 2.2881 | 2.2869 | 2.2819 | 2.2734 | 2.2572 | 2.2861 | 2.2855 | 2.2845 | 2.2836 | 2.2826 | 2.2814 | 2.2802 | 2.2789 | 2.2775 | 2.2761 | 2.2747 | 2.2682 | 2.2584 | 2.2434 | 2.2811 | 2.2806 | 2.2797 | 2.2789 | 2.278 | 2.2771 | 2.2762 | 2.2751 | 2.274 | 2.2729 | 2.2717 | 2.2667 | 2.2582 | 2.2446
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 0.61895 | 19.7004 | 19.6582 | 19.6204 | 19.5748 | 19.5193 | 19.4586 | 19.3942 | 19.3416 | 19.2874 | 19.2318 | 19.1769 | 18.6284 | 17.5292 | 16.0328 | 18.4608 | 18.4186 | 18.3808 | 18.3352 | 18.2797 | 18.2144 | 18.0105 | 17.8089 | 17.6077 | 17.4068 | 17.2086 | 16.1686 | 14.9383 | 13.3117 | 18.97 | 18.9278 | 18.89 | 18.8444 | 18.7889 | 18.7281 | 18.6638 | 18.6112 | 18.557 | 18.5014 | 18.4017 | 18.2131 | 18.0128 | 17.81
|  | GLENEAGLES | CT |  |  |  | 0.61895 | 19.7004 | 19.6582 | 19.6204 | 19.5757 | 19.5252 | 19.4692 | 19.4112 | 19.3656 | 19.319 | 19.2722 | 19.2244 | 18.9341 | 18.4064 | 17.4081 | 18.4608 | 18.4186 | 18.3808 | 18.3361 | 18.2855 | 18.2295 | 18.1716 | 18.1161 | 17.9668 | 17.8186 | 17.6707 | 16.8889 | 15.9699 | 14.882 | 18.97 | 18.9278 | 18.89 | 18.8453 | 18.7947 | 18.7387 | 18.6808 | 18.6352 | 18.5886 | 18.5418 | 18.4939 | 18.445 | 18.3879 | 18.3287
|  | GLENEAGLES | LW |  |  |  | 0.61895 | 19.7332 | 19.6603 | 19.6238 | 19.5748 | 19.5193 | 19.4586 | 19.3942 | 19.3416 | 19.2874 | 19.2318 | 19.1769 | 18.6284 | 17.5292 | 16.0328 | 18.4936 | 18.4207 | 18.3842 | 18.3352 | 18.2797 | 18.2144 | 18.0105 | 17.8089 | 17.6077 | 17.4068 | 17.2086 | 16.1686 | 14.9383 | 13.3117 | 19.0028 | 18.9299 | 18.8934 | 18.8444 | 18.7889 | 18.7281 | 18.6638 | 18.6112 | 18.557 | 18.5014 | 18.4017 | 18.2131 | 18.0128 | 17.81
|  | GLENEAGLES | ST |  |  |  | 0.61895 | 19.74 | 19.7263 | 19.7179 | 19.7026 | 19.6832 | 19.6622 | 19.6395 | 19.6278 | 19.6161 | 19.6046 | 19.5935 | 19.5396 | 19.3724 | 19.2681 | 18.5004 | 18.4867 | 18.4783 | 18.463 | 18.4435 | 18.4226 | 18.3999 | 18.3882 | 18.3765 | 18.365 | 18.3538 | 18.1128 | 17.6395 | 17.2374 | 19.0096 | 18.9959 | 18.9875 | 18.9722 | 18.9527 | 18.9318 | 18.9091 | 18.8974 | 18.8857 | 18.8742 | 18.863 | 18.8092 | 18.642 | 18.4337
|  | GLENEAGLES | FS |  |  |  | 0.61895 | 19.7433 | 19.7326 | 19.7289 | 19.7251 | 19.7211 | 19.7168 | 19.7125 | 19.7057 | 19.6983 | 19.6906 | 19.6825 | 19.6497 | 19.5675 | 19.408 | 18.5037 | 18.493 | 18.4893 | 18.4855 | 18.4815 | 18.4772 | 18.4729 | 18.466 | 18.4587 | 18.451 | 18.4429 | 18.4101 | 18.1592 | 17.7597 | 19.0129 | 19.0022 | 18.9985 | 18.9947 | 18.9907 | 18.9864 | 18.9821 | 18.9752 | 18.9679 | 18.9602 | 18.9521 | 18.9193 | 18.8371 | 18.6776
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.35676 | 0.35672 | 0.3567 | 0.35667 | 0.35664 | 0.35661 | 0.35658 | 0.35655 | 0.35653 | 0.3565 | 0.35647 | 0.35631 | 0.35606 | 0.35559 | 0.32889 | 0.32885 | 0.32883 | 0.3288 | 0.32874 | 0.32866 | 0.32858 | 0.32851 | 0.32844 | 0.32836 | 0.32829 | 0.3279 | 0.32337 | 0.31809 | 0.33582 | 0.33577 | 0.33576 | 0.33573 | 0.3357 | 0.33567 | 0.33563 | 0.33561 | 0.33558 | 0.33556 | 0.33553 | 0.3355 | 0.3325 | 0.32814
|  | GLENETIVE | CT |  |  |  | 0 | 0.35676 | 0.35675 | 0.35673 | 0.35672 | 0.3567 | 0.35668 | 0.35665 | 0.35663 | 0.35662 | 0.3566 | 0.35659 | 0.35648 | 0.35631 | 0.35606 | 0.32889 | 0.32888 | 0.32886 | 0.32885 | 0.32883 | 0.32877 | 0.3287 | 0.32864 | 0.32858 | 0.32852 | 0.32846 | 0.32812 | 0.32487 | 0.31988 | 0.33582 | 0.3358 | 0.33579 | 0.33577 | 0.33575 | 0.33573 | 0.33571 | 0.33569 | 0.33567 | 0.33566 | 0.33564 | 0.33562 | 0.3356 | 0.33558
|  | GLENETIVE | LW |  |  |  | 0 | 0.35676 | 0.35672 | 0.3567 | 0.35667 | 0.35664 | 0.35661 | 0.35658 | 0.35655 | 0.35653 | 0.3565 | 0.35647 | 0.35631 | 0.35606 | 0.35559 | 0.32889 | 0.32885 | 0.32883 | 0.3288 | 0.32874 | 0.32866 | 0.32858 | 0.32851 | 0.32844 | 0.32836 | 0.32829 | 0.3279 | 0.32337 | 0.31809 | 0.33582 | 0.33577 | 0.33576 | 0.33573 | 0.3357 | 0.33567 | 0.33563 | 0.33561 | 0.33558 | 0.33556 | 0.33553 | 0.3355 | 0.33547 | 0.33542
|  | GLENETIVE | ST |  |  |  | 0 | 0.35676 | 0.35675 | 0.35675 | 0.35675 | 0.35674 | 0.35673 | 0.35672 | 0.35671 | 0.35671 | 0.35671 | 0.3567 | 0.35669 | 0.35661 | 0.35657 | 0.32889 | 0.32888 | 0.32888 | 0.32888 | 0.32887 | 0.32886 | 0.32882 | 0.32877 | 0.32872 | 0.32867 | 0.32862 | 0.32839 | 0.32641 | 0.32171 | 0.33582 | 0.33581 | 0.33581 | 0.3358 | 0.33579 | 0.33578 | 0.33577 | 0.33577 | 0.33577 | 0.33576 | 0.33576 | 0.33574 | 0.3325 | 0.32814
|  | GLENETIVE | FS |  |  |  | 0 | 0.35676 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35675 | 0.35674 | 0.35674 | 0.3567 | 0.35662 | 0.32889 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32888 | 0.32887 | 0.32887 | 0.32883 | 0.32875 | 0.33582 | 0.33581 | 0.33581 | 0.33581 | 0.33581 | 0.33581 | 0.33581 | 0.33581 | 0.33581 | 0.3358 | 0.3358 | 0.33579 | 0.33576 | 0.33568
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0 | 0.11253 | 0.1121 | 0.11191 | 0.11165 | 0.11135 | 0.11103 | 0.11068 | 0.11042 | 0.11015 | 0.10987 | 0.10961 | 0.10797 | 0.10544 | 0.099884 | 0.11338 | 0.11294 | 0.11273 | 0.11244 | 0.11211 | 0.11176 | 0.11139 | 0.11109 | 0.11079 | 0.11034 | 0.10953 | 0.10524 | 0.10007 | 0.092735 | 0.11193 | 0.1115 | 0.11131 | 0.11105 | 0.11075 | 0.11043 | 0.11009 | 0.10982 | 0.10955 | 0.10928 | 0.10901 | 0.10874 | 0.10842 | 0.10808
|  | GLENUIG | CT |  |  |  | 0 | 0.11253 | 0.11239 | 0.11226 | 0.1121 | 0.1119 | 0.11167 | 0.11142 | 0.11126 | 0.11109 | 0.11093 | 0.11076 | 0.10968 | 0.10799 | 0.1054 | 0.11338 | 0.11323 | 0.1131 | 0.11291 | 0.11269 | 0.11244 | 0.11217 | 0.11199 | 0.1118 | 0.11162 | 0.11143 | 0.10941 | 0.10588 | 0.10155 | 0.11193 | 0.11179 | 0.11167 | 0.1115 | 0.1113 | 0.11107 | 0.11082 | 0.11066 | 0.1105 | 0.11033 | 0.11016 | 0.10999 | 0.10977 | 0.10955
|  | GLENUIG | LW |  |  |  | 0 | 0.11253 | 0.1121 | 0.11191 | 0.11165 | 0.11135 | 0.11103 | 0.11068 | 0.11042 | 0.11015 | 0.10987 | 0.10961 | 0.10797 | 0.10544 | 0.099884 | 0.11338 | 0.11294 | 0.11273 | 0.11244 | 0.11211 | 0.11176 | 0.11139 | 0.11109 | 0.11079 | 0.11034 | 0.10953 | 0.10524 | 0.10007 | 0.092735 | 0.11193 | 0.1115 | 0.11131 | 0.11105 | 0.11075 | 0.11043 | 0.11009 | 0.10982 | 0.10955 | 0.10928 | 0.10901 | 0.10874 | 0.10842 | 0.10808
|  | GLENUIG | ST |  |  |  | 0 | 0.11253 | 0.11248 | 0.11245 | 0.11238 | 0.1123 | 0.11221 | 0.1121 | 0.11206 | 0.11202 | 0.11198 | 0.11195 | 0.11178 | 0.11098 | 0.11057 | 0.1134 | 0.11335 | 0.11332 | 0.11324 | 0.11315 | 0.11304 | 0.11292 | 0.11287 | 0.11281 | 0.11276 | 0.11271 | 0.11249 | 0.11163 | 0.11079 | 0.11193 | 0.11188 | 0.11185 | 0.11179 | 0.1117 | 0.11161 | 0.1115 | 0.11146 | 0.11142 | 0.11138 | 0.11135 | 0.11118 | 0.11038 | 0.10997
|  | GLENUIG | FS |  |  |  | 0 | 0.11253 | 0.11248 | 0.11248 | 0.11248 | 0.11247 | 0.11247 | 0.11246 | 0.11244 | 0.11242 | 0.1124 | 0.11237 | 0.1123 | 0.11195 | 0.11117 | 0.1134 | 0.11336 | 0.11336 | 0.11335 | 0.11334 | 0.11333 | 0.11332 | 0.11329 | 0.11326 | 0.11322 | 0.11319 | 0.11307 | 0.11266 | 0.11185 | 0.11193 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11187 | 0.11187 | 0.11185 | 0.11182 | 0.1118 | 0.11177 | 0.11171 | 0.11135 | 0.11057
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 0.063158 | 3.5886 | 3.5781 | 3.5704 | 3.5591 | 3.5465 | 3.5329 | 3.5187 | 3.5072 | 3.4956 | 3.4829 | 3.4705 | 3.3307 | 3.1191 | 2.8168 | 3.4529 | 3.4424 | 3.4347 | 3.4234 | 3.3991 | 3.3571 | 3.3156 | 3.2746 | 3.2339 | 3.1926 | 3.152 | 2.9399 | 2.6864 | 2.3429 | 3.4282 | 3.4177 | 3.41 | 3.3987 | 3.3861 | 3.3726 | 3.3584 | 3.3352 | 3.2987 | 3.2615 | 3.2249 | 3.1888 | 3.1503 | 3.1114
|  | GOLSPIE | CT |  |  |  | 0.063158 | 3.5886 | 3.5799 | 3.572 | 3.5626 | 3.5517 | 3.5397 | 3.5269 | 3.5175 | 3.5078 | 3.4981 | 3.4883 | 3.4263 | 3.2869 | 3.0886 | 3.4529 | 3.4442 | 3.4363 | 3.4269 | 3.416 | 3.4028 | 3.3712 | 3.341 | 3.3108 | 3.281 | 3.2514 | 3.0923 | 2.9033 | 2.6765 | 3.4282 | 3.4195 | 3.4117 | 3.4022 | 3.3914 | 3.3793 | 3.3666 | 3.3571 | 3.3474 | 3.3377 | 3.3127 | 3.286 | 3.2567 | 3.2272
|  | GOLSPIE | LW |  |  |  | 0.063158 | 3.5945 | 3.5781 | 3.5704 | 3.5591 | 3.5465 | 3.5329 | 3.5187 | 3.5072 | 3.4956 | 3.4829 | 3.4705 | 3.3307 | 3.1191 | 2.8168 | 3.4588 | 3.4424 | 3.4347 | 3.4234 | 3.3991 | 3.3571 | 3.3156 | 3.2746 | 3.2339 | 3.1926 | 3.152 | 2.9399 | 2.6864 | 2.3429 | 3.4341 | 3.4177 | 3.41 | 3.3987 | 3.3861 | 3.3726 | 3.3584 | 3.3352 | 3.2987 | 3.2615 | 3.2249 | 3.1888 | 3.1503 | 3.1114
|  | GOLSPIE | ST |  |  |  | 0.063158 | 3.5953 | 3.5925 | 3.5907 | 3.5872 | 3.5833 | 3.5788 | 3.5738 | 3.5715 | 3.5691 | 3.5667 | 3.5645 | 3.5539 | 3.5179 | 3.4973 | 3.4596 | 3.4568 | 3.455 | 3.4515 | 3.4476 | 3.4431 | 3.4381 | 3.4357 | 3.4334 | 3.431 | 3.4199 | 3.3485 | 3.2545 | 3.1782 | 3.4349 | 3.4321 | 3.4303 | 3.4269 | 3.4229 | 3.4184 | 3.4134 | 3.4111 | 3.4087 | 3.4064 | 3.4041 | 3.3935 | 3.3195 | 3.2512
|  | GOLSPIE | FS |  |  |  | 0.063158 | 3.5961 | 3.5935 | 3.5925 | 3.5916 | 3.5906 | 3.5896 | 3.5885 | 3.5869 | 3.5851 | 3.5833 | 3.5814 | 3.5744 | 3.5554 | 3.519 | 3.4604 | 3.4578 | 3.4568 | 3.4559 | 3.4549 | 3.4539 | 3.4528 | 3.4512 | 3.4494 | 3.4476 | 3.4457 | 3.424 | 3.3582 | 3.2775 | 3.4358 | 3.4331 | 3.4322 | 3.4312 | 3.4302 | 3.4292 | 3.4281 | 3.4265 | 3.4248 | 3.4229 | 3.421 | 3.414 | 3.395 | 3.3394
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 0.20947 | 15.2978 | 15.2209 | 15.1863 | 15.1382 | 15.0835 | 15.0231 | 14.959 | 14.9084 | 14.8549 | 14.7443 | 14.5737 | 13.6479 | 12.4808 | 10.7844 | 14.1002 | 14.0233 | 13.9887 | 13.9406 | 13.8859 | 13.8255 | 13.7614 | 13.6637 | 13.4597 | 13.2561 | 13.0546 | 11.9737 | 10.6426 | 8.7783 | 14.6822 | 14.6052 | 14.5707 | 14.5225 | 14.4679 | 14.4074 | 14.3434 | 14.2928 | 14.2409 | 14.1879 | 14.1355 | 14.0833 | 14.0169 | 13.9479
|  | GOODLYBURN | CT |  |  |  | 0.20947 | 15.2978 | 15.2708 | 15.2478 | 15.2168 | 15.1787 | 15.1336 | 15.0848 | 15.0528 | 15.0192 | 14.9851 | 14.9505 | 14.4615 | 13.6402 | 12.5933 | 14.1002 | 14.0731 | 14.0502 | 14.0191 | 13.981 | 13.9359 | 13.8872 | 13.8552 | 13.8215 | 13.7875 | 13.6766 | 12.9215 | 11.9862 | 10.824 | 14.6822 | 14.6551 | 14.6322 | 14.6011 | 14.563 | 14.5179 | 14.4692 | 14.4372 | 14.4035 | 14.3694 | 14.3349 | 14.2987 | 14.2522 | 14.2043
|  | GOODLYBURN | LW |  |  |  | 0.20947 | 15.2987 | 15.2209 | 15.1863 | 15.1382 | 15.0835 | 15.0231 | 14.959 | 14.9084 | 14.8549 | 14.7443 | 14.5737 | 13.6479 | 12.4808 | 10.7844 | 14.1011 | 14.0233 | 13.9887 | 13.9406 | 13.8859 | 13.8255 | 13.7614 | 13.6637 | 13.4597 | 13.2561 | 13.0546 | 11.9737 | 10.6426 | 8.7783 | 14.683 | 14.6052 | 14.5707 | 14.5225 | 14.4679 | 14.4074 | 14.3434 | 14.2928 | 14.2409 | 14.1879 | 14.1355 | 14.0833 | 14.0169 | 13.9479
|  | GOODLYBURN | ST |  |  |  | 0.20947 | 15.2987 | 15.2876 | 15.2824 | 15.2681 | 15.2508 | 15.2305 | 15.2079 | 15.1994 | 15.1909 | 15.1827 | 15.1749 | 15.1387 | 14.941 | 14.5865 | 14.1011 | 14.09 | 14.0847 | 14.0705 | 14.0532 | 14.0329 | 14.0103 | 14.0018 | 13.9933 | 13.9851 | 13.9773 | 13.9411 | 13.4733 | 13.0445 | 14.683 | 14.672 | 14.6667 | 14.6525 | 14.6352 | 14.6149 | 14.5923 | 14.5838 | 14.5752 | 14.5671 | 14.5593 | 14.523 | 14.3343 | 14.2357
|  | GOODLYBURN | FS |  |  |  | 0.20947 | 15.2987 | 15.2873 | 15.2868 | 15.2862 | 15.2853 | 15.284 | 15.2827 | 15.2779 | 15.2723 | 15.2663 | 15.2597 | 15.2422 | 15.1496 | 14.9406 | 14.1011 | 14.0896 | 14.0891 | 14.0885 | 14.0876 | 14.0864 | 14.0851 | 14.0802 | 14.0747 | 14.0686 | 14.0621 | 14.0445 | 13.9519 | 13.5113 | 14.683 | 14.6716 | 14.6711 | 14.6705 | 14.6696 | 14.6683 | 14.6671 | 14.6622 | 14.6567 | 14.6506 | 14.644 | 14.6265 | 14.5339 | 14.3293
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0.14316 | 8.0461 | 8.0245 | 8.0082 | 7.9854 | 7.9604 | 7.933 | 7.9039 | 7.8792 | 7.8544 | 7.8294 | 7.8049 | 7.6613 | 7.2461 | 6.6647 | 6.893 | 6.8344 | 6.785 | 6.7039 | 6.6219 | 6.5401 | 6.4592 | 6.3789 | 6.2993 | 6.2203 | 6.1425 | 5.746 | 5.2757 | 4.6538 | 7.1089 | 7.0549 | 7.0105 | 6.9385 | 6.8652 | 6.7917 | 6.7188 | 6.6472 | 6.576 | 6.5053 | 6.4323 | 6.3605 | 6.2857 | 6.2102
|  | GOURDIE | CT |  |  |  | 0.14316 | 8.0461 | 8.0294 | 8.014 | 7.9945 | 7.9728 | 7.949 | 7.9243 | 7.905 | 7.8854 | 7.865 | 7.8446 | 7.7248 | 7.5581 | 7.2477 | 6.8944 | 6.8563 | 6.8177 | 6.7581 | 6.6971 | 6.6358 | 6.5748 | 6.517 | 6.4593 | 6.4023 | 6.3459 | 6.0495 | 5.7074 | 5.3027 | 7.1089 | 7.0741 | 7.0391 | 6.9857 | 6.9307 | 6.8752 | 6.8198 | 6.7679 | 6.7161 | 6.6648 | 6.6138 | 6.563 | 6.5094 | 6.4555
|  | GOURDIE | LW |  |  |  | 0.14316 | 8.0554 | 8.0245 | 8.0082 | 7.9854 | 7.9604 | 7.933 | 7.9039 | 7.8792 | 7.8544 | 7.8294 | 7.8049 | 7.6613 | 7.2461 | 6.6647 | 6.893 | 6.8344 | 6.785 | 6.7039 | 6.6219 | 6.5401 | 6.4592 | 6.3789 | 6.2993 | 6.2203 | 6.1425 | 5.746 | 5.2757 | 4.6538 | 7.1092 | 7.0549 | 7.0105 | 6.9385 | 6.8652 | 6.7917 | 6.7188 | 6.6472 | 6.576 | 6.5053 | 6.4323 | 6.3605 | 6.2857 | 6.2102
|  | GOURDIE | ST |  |  |  | 0.14316 | 8.06 | 8.0547 | 8.0512 | 8.0432 | 8.0342 | 8.0245 | 8.014 | 8.0077 | 8.0015 | 7.9954 | 7.9895 | 7.9614 | 7.8913 | 7.8477 | 6.937 | 6.929 | 6.9229 | 6.889 | 6.8544 | 6.8201 | 6.7859 | 6.7536 | 6.7217 | 6.6906 | 6.6601 | 6.5152 | 6.336 | 6.1892 | 7.1471 | 7.1396 | 7.1339 | 7.1039 | 7.0733 | 7.0428 | 7.0122 | 6.9839 | 6.956 | 6.9287 | 6.902 | 6.7751 | 6.6127 | 6.4787
|  | GOURDIE | FS |  |  |  | 0.14316 | 8.0618 | 8.0585 | 8.0565 | 8.0544 | 8.0518 | 8.0485 | 8.0451 | 8.0413 | 8.0374 | 8.0334 | 8.0292 | 8.0092 | 7.9689 | 7.8999 | 6.9411 | 6.9353 | 6.9307 | 6.9251 | 6.9145 | 6.8931 | 6.8719 | 6.8475 | 6.823 | 6.7984 | 6.7737 | 6.6532 | 6.5218 | 6.3674 | 7.1508 | 7.1455 | 7.1413 | 7.1362 | 7.1268 | 7.1082 | 7.0898 | 7.0686 | 7.0472 | 7.0258 | 7.0042 | 6.8992 | 6.7819 | 6.6405
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.17368 | 16.838 | 16.7966 | 16.7779 | 16.7518 | 16.7221 | 16.6898 | 16.6557 | 16.629 | 16.5929 | 16.5018 | 16.4122 | 15.9088 | 15.3018 | 14.4626 | 15.1557 | 15.1144 | 15.0957 | 15.0695 | 15.0399 | 15.0076 | 14.9735 | 14.9468 | 14.9198 | 14.8923 | 14.8653 | 14.3088 | 13.6024 | 12.6649 | 15.6012 | 15.5599 | 15.5412 | 15.5151 | 15.4854 | 15.4531 | 15.419 | 15.3923 | 15.3653 | 15.3149 | 15.2052 | 15.0969 | 14.9829 | 14.8679
|  | GRANTOWN | CT |  |  |  | 0.17368 | 16.838 | 16.8237 | 16.8116 | 16.7953 | 16.7752 | 16.7518 | 16.7267 | 16.7104 | 16.6934 | 16.6764 | 16.6592 | 16.3759 | 15.9568 | 15.4428 | 15.1557 | 15.1415 | 15.1294 | 15.1131 | 15.093 | 15.0696 | 15.0445 | 15.0282 | 15.0112 | 14.9942 | 14.977 | 14.8623 | 14.3739 | 13.7919 | 15.6012 | 15.587 | 15.5749 | 15.5586 | 15.5385 | 15.5151 | 15.49 | 15.4737 | 15.4567 | 15.4397 | 15.4225 | 15.4046 | 15.3823 | 15.3199
|  | GRANTOWN | LW |  |  |  | 0.17368 | 16.8388 | 16.7966 | 16.7779 | 16.7518 | 16.7221 | 16.6898 | 16.6557 | 16.629 | 16.5929 | 16.5018 | 16.4122 | 15.9088 | 15.3018 | 14.4626 | 15.1566 | 15.1144 | 15.0957 | 15.0695 | 15.0399 | 15.0076 | 14.9735 | 14.9468 | 14.9198 | 14.8923 | 14.8653 | 14.3088 | 13.6024 | 12.6649 | 15.6021 | 15.5599 | 15.5412 | 15.5151 | 15.4854 | 15.4531 | 15.419 | 15.3923 | 15.3653 | 15.3149 | 15.2052 | 15.0969 | 14.9829 | 14.8679
|  | GRANTOWN | ST |  |  |  | 0.17368 | 16.8388 | 16.8335 | 16.8309 | 16.824 | 16.8156 | 16.8058 | 16.7948 | 16.7907 | 16.7866 | 16.7826 | 16.7788 | 16.7617 | 16.6454 | 16.4712 | 15.1566 | 15.1512 | 15.1487 | 15.1418 | 15.1334 | 15.1236 | 15.1126 | 15.1085 | 15.1044 | 15.1004 | 15.0966 | 15.0795 | 14.9944 | 14.9506 | 15.6021 | 15.5967 | 15.5942 | 15.5873 | 15.5789 | 15.5691 | 15.5581 | 15.554 | 15.5499 | 15.5459 | 15.5421 | 15.525 | 15.4399 | 15.2564
|  | GRANTOWN | FS |  |  |  | 0.17368 | 16.8388 | 16.8338 | 16.8336 | 16.8333 | 16.833 | 16.8324 | 16.8319 | 16.8297 | 16.8273 | 16.8247 | 16.8218 | 16.8142 | 16.7746 | 16.6883 | 15.1566 | 15.1516 | 15.1514 | 15.1511 | 15.1507 | 15.1502 | 15.1496 | 15.1475 | 15.1451 | 15.1425 | 15.1396 | 15.132 | 15.0924 | 15.0061 | 15.6021 | 15.5971 | 15.5969 | 15.5966 | 15.5962 | 15.5957 | 15.5951 | 15.593 | 15.5906 | 15.588 | 15.5851 | 15.5775 | 15.5379 | 15.4516
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 3.3684 | 38.0891 | 38.0249 | 37.9843 | 37.9286 | 37.8652 | 37.7964 | 37.7234 | 37.6646 | 37.6042 | 37.543 | 37.4818 | 36.9579 | 35.7287 | 34.0055 | 34.2472 | 34.0866 | 33.9517 | 33.726 | 33.4961 | 33.2686 | 33.0426 | 32.8203 | 32.5987 | 32.3785 | 32.1608 | 31.0184 | 29.6577 | 27.8189 | 38.2184 | 38.0682 | 37.9434 | 37.7359 | 37.524 | 37.3136 | 37.104 | 36.8993 | 36.695 | 36.4919 | 36.291 | 36.0927 | 35.8809 | 35.6671
|  | GREMISTA | CT |  |  |  | 3.3684 | 38.0891 | 38.0478 | 38.011 | 37.9655 | 37.9127 | 37.853 | 37.7907 | 37.7451 | 37.6975 | 37.6496 | 37.6014 | 37.3005 | 36.8101 | 35.7001 | 34.2472 | 34.1481 | 34.0451 | 33.8805 | 33.7111 | 33.5402 | 33.3707 | 33.2105 | 33.0497 | 32.8903 | 32.7323 | 31.8931 | 30.8931 | 29.6931 | 38.2184 | 38.1255 | 38.0296 | 37.8779 | 37.7209 | 37.5621 | 37.4041 | 37.2561 | 37.1075 | 36.9601 | 36.8139 | 36.6678 | 36.511 | 36.3532
|  | GREMISTA | LW |  |  |  | 3.3684 | 38.111 | 38.0249 | 37.9843 | 37.9286 | 37.8652 | 37.7964 | 37.7234 | 37.6646 | 37.6042 | 37.543 | 37.4818 | 36.9579 | 35.7287 | 34.0055 | 34.2504 | 34.0866 | 33.9517 | 33.726 | 33.4961 | 33.2686 | 33.0426 | 32.8203 | 32.5987 | 32.3785 | 32.1608 | 31.0184 | 29.6577 | 27.8189 | 38.2236 | 38.0682 | 37.9434 | 37.7359 | 37.524 | 37.3136 | 37.104 | 36.8993 | 36.695 | 36.4919 | 36.291 | 36.0927 | 35.8809 | 35.6671
|  | GREMISTA | ST |  |  |  | 3.3684 | 38.1152 | 38.101 | 38.0924 | 38.0751 | 38.0547 | 38.0314 | 38.0058 | 37.9942 | 37.9824 | 37.971 | 37.96 | 37.9075 | 37.7177 | 37.6084 | 34.3621 | 34.3414 | 34.3256 | 34.2298 | 34.1318 | 34.0344 | 33.9369 | 33.8467 | 33.758 | 33.6712 | 33.5863 | 33.1846 | 32.6605 | 32.2273 | 38.3238 | 38.3037 | 38.2887 | 38.2013 | 38.1117 | 38.0223 | 37.9325 | 37.8507 | 37.7703 | 37.6916 | 37.6147 | 37.2505 | 36.7624 | 36.364
|  | GREMISTA | FS |  |  |  | 3.3684 | 38.1177 | 38.1058 | 38.1029 | 38.0998 | 38.0965 | 38.0928 | 38.0892 | 38.0823 | 38.0748 | 38.0669 | 38.0593 | 38.0319 | 37.9379 | 37.7477 | 34.3707 | 34.354 | 34.3456 | 34.3333 | 34.3053 | 34.2503 | 34.1955 | 34.1287 | 34.0615 | 33.994 | 33.927 | 33.6086 | 33.2408 | 32.7916 | 38.3317 | 38.3155 | 38.3077 | 38.2964 | 38.271 | 38.2215 | 38.1723 | 38.1119 | 38.0511 | 37.99 | 37.9294 | 37.6423 | 37.304 | 36.8826
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 2.2737 | 27.182 | 27.1239 | 27.0978 | 27.0613 | 27.0199 | 26.973 | 26.9227 | 26.6755 | 26.3616 | 26.0615 | 25.7929 | 24.5013 | 23.0997 | 21.2142 | 25.7532 | 25.6951 | 25.6689 | 25.6325 | 25.4974 | 25.0893 | 24.7258 | 24.3494 | 23.9918 | 23.6504 | 23.3456 | 21.8826 | 20.319 | 18.2741 | 26.513 | 26.4421 | 26.396 | 26.3357 | 25.934 | 25.5512 | 25.2097 | 24.8569 | 24.5215 | 24.201 | 23.9146 | 23.6526 | 23.3709 | 23.0796
|  | GREYFRIARS | CT |  |  |  | 2.2737 | 27.182 | 27.1635 | 27.1478 | 27.1265 | 27.1005 | 27.0686 | 27.0336 | 27.0103 | 26.985 | 26.9582 | 26.9307 | 26.0922 | 25.1026 | 23.9082 | 25.7532 | 25.7346 | 25.719 | 25.6977 | 25.6716 | 25.6397 | 25.6048 | 25.4511 | 25.2009 | 24.9706 | 24.7562 | 23.6955 | 22.6021 | 21.295 | 26.513 | 26.4945 | 26.4704 | 26.4342 | 26.3926 | 26.3448 | 26.1294 | 25.8903 | 25.6559 | 25.4398 | 25.2386 | 25.0364 | 24.8271 | 24.6271
|  | GREYFRIARS | LW |  |  |  | 2.2737 | 27.1829 | 27.1239 | 27.0978 | 27.0613 | 27.0199 | 26.973 | 26.9227 | 26.6755 | 26.3616 | 26.0615 | 25.7929 | 24.5013 | 23.0997 | 21.2142 | 25.754 | 25.6951 | 25.6689 | 25.6325 | 25.4974 | 25.0893 | 24.7258 | 24.3494 | 23.9918 | 23.6504 | 23.3456 | 21.8826 | 20.319 | 18.2741 | 26.5138 | 26.4421 | 26.396 | 26.3357 | 25.934 | 25.5512 | 25.2097 | 24.8569 | 24.5215 | 24.201 | 23.9146 | 23.6526 | 23.3709 | 23.0796
|  | GREYFRIARS | ST |  |  |  | 2.2737 | 27.1829 | 27.1739 | 27.1697 | 27.1582 | 27.1442 | 27.1278 | 27.1096 | 27.1027 | 27.0958 | 27.0892 | 27.0829 | 27.0523 | 26.8777 | 26.4326 | 25.754 | 25.7451 | 25.7408 | 25.7293 | 25.7154 | 25.699 | 25.6807 | 25.6739 | 25.667 | 25.6604 | 25.6541 | 25.3843 | 24.6869 | 24.0832 | 26.5138 | 26.5049 | 26.5007 | 26.4892 | 26.4742 | 26.4495 | 26.4237 | 26.4084 | 26.3928 | 26.3779 | 26.3637 | 25.8311 | 25.1704 | 24.6025
|  | GREYFRIARS | FS |  |  |  | 2.2737 | 27.1829 | 27.1719 | 27.1714 | 27.1708 | 27.17 | 27.1688 | 27.1676 | 27.1629 | 27.1576 | 27.1517 | 27.1454 | 27.1286 | 27.0375 | 26.8331 | 25.754 | 25.7431 | 25.7426 | 25.742 | 25.7411 | 25.7399 | 25.7387 | 25.734 | 25.7287 | 25.7229 | 25.7166 | 25.6997 | 25.3393 | 24.6997 | 26.5138 | 26.5029 | 26.5024 | 26.5018 | 26.5009 | 26.4997 | 26.4942 | 26.4827 | 26.4702 | 26.4574 | 26.4442 | 26.288 | 25.7882 | 25.1792
| GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309 623 | NO | YES | 0.016842 | 23.2649 | 23.2494 | 23.2321 | 23.2029 | 23.1724 | 23.1421 | 23.1121 | 23.0833 | 23.0538 | 23.0246 | 22.9959 | 22.8448 | 22.6638 | 22.419 | 22.0618 | 22.0451 | 22.025 | 21.9921 | 21.958 | 21.9243 | 21.891 | 21.8588 | 21.826 | 21.7935 | 21.7615 | 21.5946 | 21.3976 | 21.1373 | 22.6619 | 22.6451 | 22.6251 | 22.5923 | 22.5583 | 22.5246 | 22.4914 | 22.4593 | 22.4265 | 22.3941 | 22.3622 | 22.3307 | 22.2977 | 22.2645
|  | GRUDIE BRIDGE | CT |  |  |  | 0.016842 | 23.2649 | 23.2494 | 23.233 | 23.2091 | 23.1846 | 23.1599 | 23.1353 | 23.1124 | 23.0896 | 23.067 | 23.0447 | 22.9236 | 22.7796 | 22.6087 | 22.0618 | 22.0451 | 22.0272 | 22.0008 | 21.9737 | 21.9466 | 21.9197 | 21.8944 | 21.8693 | 21.8443 | 21.8197 | 21.6874 | 21.5323 | 21.3506 | 22.6619 | 22.6451 | 22.6273 | 22.6009 | 22.574 | 22.5469 | 22.52 | 22.4948 | 22.4697 | 22.4448 | 22.4202 | 22.3956 | 22.3692 | 22.3426
|  | GRUDIE BRIDGE | LW |  |  |  | 0.016842 | 23.2724 | 23.2502 | 23.2321 | 23.2029 | 23.1724 | 23.1421 | 23.1121 | 23.0833 | 23.0538 | 23.0246 | 22.9959 | 22.8448 | 22.6638 | 22.419 | 22.069 | 22.0452 | 22.025 | 21.9921 | 21.958 | 21.9243 | 21.891 | 21.8588 | 21.826 | 21.7935 | 21.7615 | 21.5946 | 21.3976 | 21.1373 | 22.669 | 22.6453 | 22.6251 | 22.5923 | 22.5583 | 22.5246 | 22.4914 | 22.4593 | 22.4265 | 22.3941 | 22.3622 | 22.3307 | 22.2977 | 22.2645
|  | GRUDIE BRIDGE | ST |  |  |  | 0.016842 | 23.2872 | 23.283 | 23.2804 | 23.2686 | 23.2556 | 23.2428 | 23.2299 | 23.2183 | 23.2068 | 23.1956 | 23.1846 | 23.1326 | 23.0657 | 23.0109 | 22.0861 | 22.0817 | 22.0789 | 22.0654 | 22.0509 | 22.0365 | 22.0221 | 22.0089 | 21.9959 | 21.9831 | 21.9707 | 21.9117 | 21.8382 | 21.7772 | 22.6861 | 22.6817 | 22.6789 | 22.6655 | 22.651 | 22.6366 | 22.6223 | 22.6091 | 22.5961 | 22.5834 | 22.571 | 22.5121 | 22.4387 | 22.3778
|  | GRUDIE BRIDGE | FS |  |  |  | 0.016842 | 23.2889 | 23.2865 | 23.2853 | 23.283 | 23.2793 | 23.2725 | 23.2658 | 23.2579 | 23.25 | 23.2413 | 23.2326 | 23.1912 | 23.1472 | 23.0943 | 22.0879 | 22.0855 | 22.0843 | 22.0817 | 22.0775 | 22.0697 | 22.0619 | 22.0529 | 22.0438 | 22.0338 | 22.0238 | 21.9761 | 21.9268 | 21.8691 | 22.6879 | 22.6856 | 22.6843 | 22.6817 | 22.6776 | 22.6697 | 22.662 | 22.653 | 22.644 | 22.634 | 22.624 | 22.5764 | 22.5272 | 22.4696
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0 | 1.208 | 1.2035 | 1.2006 | 1.1963 | 1.1917 | 1.1871 | 1.1824 | 1.1781 | 1.1739 | 1.1696 | 1.1655 | 1.1423 | 1.1115 | 1.0622 | 1.0588 | 1.0555 | 1.0541 | 1.0521 | 1.0498 | 1.0473 | 1.0447 | 1.0427 | 1.0406 | 1.0385 | 1.0364 | 1.0234 | 1.0031 | 0.96407 | 1 | 0.99677 | 0.99533 | 0.99333 | 0.99106 | 0.98858 | 0.98596 | 0.9839 | 0.98182 | 0.9797 | 0.97761 | 0.97555 | 0.97298 | 0.97031
|  | GUTCHER | CT |  |  |  | 0 | 1.2082 | 1.2064 | 1.2047 | 1.2016 | 1.1983 | 1.1948 | 1.1913 | 1.1884 | 1.1854 | 1.1825 | 1.1795 | 1.1629 | 1.1408 | 1.111 | 1.0588 | 1.0576 | 1.0567 | 1.0554 | 1.0538 | 1.0519 | 1.0499 | 1.0486 | 1.0473 | 1.0459 | 1.0445 | 1.0356 | 1.0212 | 0.99904 | 1 | 0.99887 | 0.99791 | 0.99661 | 0.99502 | 0.99316 | 0.99117 | 0.98986 | 0.98851 | 0.98715 | 0.98578 | 0.98435 | 0.98256 | 0.98071
|  | GUTCHER | LW |  |  |  | 0 | 1.208 | 1.2035 | 1.2006 | 1.1963 | 1.1917 | 1.1871 | 1.1824 | 1.1781 | 1.1739 | 1.1696 | 1.1655 | 1.1423 | 1.1115 | 1.0622 | 1.0588 | 1.0555 | 1.0541 | 1.0521 | 1.0498 | 1.0473 | 1.0447 | 1.0427 | 1.0406 | 1.0385 | 1.0364 | 1.0234 | 1.0031 | 0.96407 | 1 | 0.99677 | 0.99533 | 0.99333 | 0.99106 | 0.98858 | 0.98596 | 0.9839 | 0.98182 | 0.9797 | 0.97761 | 0.97555 | 0.97298 | 0.97031
|  | GUTCHER | ST |  |  |  | 0 | 1.2093 | 1.2088 | 1.2085 | 1.2067 | 1.2048 | 1.2029 | 1.2009 | 1.1993 | 1.1978 | 1.1963 | 1.1948 | 1.188 | 1.1759 | 1.1672 | 1.0588 | 1.0583 | 1.0581 | 1.0576 | 1.0569 | 1.0561 | 1.0552 | 1.0549 | 1.0546 | 1.0543 | 1.054 | 1.0526 | 1.0457 | 1.0422 | 1 | 0.99957 | 0.99937 | 0.99881 | 0.99814 | 0.99735 | 0.99647 | 0.99614 | 0.99581 | 0.99549 | 0.99519 | 0.99381 | 0.98696 | 0.98343
|  | GUTCHER | FS |  |  |  | 0 | 1.2093 | 1.2089 | 1.2088 | 1.2087 | 1.2084 | 1.2078 | 1.2071 | 1.2063 | 1.2054 | 1.2045 | 1.2036 | 1.1996 | 1.1933 | 1.1833 | 1.0588 | 1.0584 | 1.0583 | 1.0583 | 1.0583 | 1.0582 | 1.0582 | 1.058 | 1.0578 | 1.0576 | 1.0574 | 1.0568 | 1.0535 | 1.0464 | 1 | 0.99959 | 0.99958 | 0.99955 | 0.99952 | 0.99948 | 0.99943 | 0.99926 | 0.99906 | 0.99885 | 0.99861 | 0.99799 | 0.99475 | 0.98768
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0.015789 | 2.8323 | 2.7944 | 2.7575 | 2.7193 | 2.6794 | 2.6388 | 2.5975 | 2.5585 | 2.5185 | 2.4785 | 2.4376 | 2.1671 | 1.8034 | 1.3611 | 2.6941 | 2.6455 | 2.5968 | 2.537 | 2.4759 | 2.4154 | 2.3549 | 2.2959 | 2.2363 | 2.177 | 2.1172 | 1.7925 | 1.4022 | 0.92298 | 2.6552 | 2.6173 | 2.5803 | 2.5422 | 2.5023 | 2.4617 | 2.4068 | 2.3455 | 2.2836 | 2.222 | 2.16 | 2.0982 | 2.0327 | 1.9653
|  | HALKIRK | CT |  |  |  | 0.015789 | 2.8323 | 2.7944 | 2.7575 | 2.7193 | 2.6794 | 2.6388 | 2.5975 | 2.5585 | 2.5185 | 2.4785 | 2.4376 | 2.1671 | 1.8034 | 1.3653 | 2.6941 | 2.6455 | 2.5968 | 2.537 | 2.4759 | 2.4154 | 2.3549 | 2.2959 | 2.2363 | 2.177 | 2.1172 | 1.7925 | 1.4022 | 0.93962 | 2.6552 | 2.6173 | 2.5803 | 2.5422 | 2.5023 | 2.4617 | 2.4068 | 2.3455 | 2.2836 | 2.222 | 2.16 | 2.0982 | 2.0327 | 1.9653
|  | HALKIRK | LW |  |  |  | 0.015789 | 2.8862 | 2.8566 | 2.8366 | 2.8121 | 2.7843 | 2.7536 | 2.7212 | 2.6915 | 2.6609 | 2.6177 | 2.5662 | 2.2794 | 1.8954 | 1.3611 | 2.7449 | 2.7008 | 2.6638 | 2.6081 | 2.5499 | 2.4904 | 2.4306 | 2.3721 | 2.3131 | 2.2537 | 2.1943 | 1.8692 | 1.4651 | 0.92298 | 2.7091 | 2.6794 | 2.6594 | 2.635 | 2.6028 | 2.5399 | 2.4769 | 2.415 | 2.3527 | 2.2901 | 2.2275 | 2.1648 | 2.0986 | 2.0302
|  | HALKIRK | ST |  |  |  | 0.015789 | 2.8972 | 2.8871 | 2.8783 | 2.8675 | 2.8544 | 2.8414 | 2.8278 | 2.8175 | 2.8071 | 2.7969 | 2.7867 | 2.735 | 2.6515 | 2.5531 | 2.7765 | 2.7658 | 2.7556 | 2.7305 | 2.7032 | 2.6767 | 2.6503 | 2.6261 | 2.6022 | 2.5788 | 2.5558 | 2.4442 | 2.3046 | 2.1819 | 2.7201 | 2.71 | 2.7012 | 2.6904 | 2.6772 | 2.6642 | 2.6507 | 2.6404 | 2.63 | 2.6198 | 2.6091 | 2.4904 | 2.3443 | 2.2154
|  | HALKIRK | FS |  |  |  | 0.015789 | 2.9022 | 2.8958 | 2.8898 | 2.8838 | 2.8777 | 2.8716 | 2.8663 | 2.8603 | 2.8541 | 2.8479 | 2.8416 | 2.807 | 2.7598 | 2.692 | 2.7829 | 2.776 | 2.7694 | 2.7615 | 2.7511 | 2.7359 | 2.7215 | 2.7051 | 2.6887 | 2.6722 | 2.6557 | 2.5712 | 2.4781 | 2.3675 | 2.7251 | 2.7187 | 2.7127 | 2.7067 | 2.7006 | 2.6945 | 2.6892 | 2.6832 | 2.677 | 2.6708 | 2.6644 | 2.6239 | 2.5254 | 2.4098
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 0.14737 | 23.2713 | 23.2152 | 23.1876 | 23.1495 | 23.1063 | 23.058 | 23.007 | 22.9665 | 22.9252 | 22.8826 | 22.832 | 22.5035 | 21.5599 | 20.2178 | 22.625 | 22.569 | 22.5413 | 22.5032 | 22.46 | 22.4092 | 22.3524 | 22.3055 | 22.2579 | 22.2096 | 22.162 | 21.8703 | 21.3679 | 19.9016 | 22.6779 | 22.6218 | 22.5942 | 22.5561 | 22.5129 | 22.4646 | 22.4136 | 22.3731 | 22.3318 | 22.2897 | 22.2482 | 22.2069 | 22.068 | 21.8907
|  | HARBOUR | CT |  |  |  | 0.14737 | 23.2713 | 23.2485 | 23.2289 | 23.2031 | 23.1722 | 23.1361 | 23.0974 | 23.0712 | 23.0438 | 23.0162 | 22.9875 | 22.7868 | 22.457 | 21.6827 | 22.625 | 22.6023 | 22.5826 | 22.5569 | 22.5259 | 22.4898 | 22.4511 | 22.4221 | 22.3904 | 22.3585 | 22.3254 | 22.1185 | 21.799 | 21.3213 | 22.6779 | 22.6551 | 22.6355 | 22.6097 | 22.5788 | 22.5427 | 22.504 | 22.4778 | 22.4504 | 22.4228 | 22.3941 | 22.3642 | 22.3271 | 22.2889
|  | HARBOUR | LW |  |  |  | 0.14737 | 23.2763 | 23.2152 | 23.1876 | 23.1495 | 23.1063 | 23.058 | 23.007 | 22.9665 | 22.9252 | 22.8826 | 22.832 | 22.5035 | 21.5599 | 20.2178 | 22.6301 | 22.569 | 22.5413 | 22.5032 | 22.46 | 22.4092 | 22.3524 | 22.3055 | 22.2579 | 22.2096 | 22.162 | 21.8703 | 21.3679 | 19.9016 | 22.6829 | 22.6218 | 22.5942 | 22.5561 | 22.5129 | 22.4646 | 22.4136 | 22.3731 | 22.3318 | 22.2897 | 22.2482 | 22.2069 | 22.068 | 21.8907
|  | HARBOUR | ST |  |  |  | 0.14737 | 23.2772 | 23.2683 | 23.2636 | 23.2524 | 23.2389 | 23.2233 | 23.206 | 23.199 | 23.1919 | 23.1851 | 23.1786 | 23.1481 | 23.0087 | 22.9186 | 22.6309 | 22.622 | 22.6173 | 22.6061 | 22.5927 | 22.577 | 22.5597 | 22.5527 | 22.5456 | 22.5389 | 22.5323 | 22.4913 | 22.3384 | 22.2503 | 22.6838 | 22.6749 | 22.6702 | 22.659 | 22.6455 | 22.6299 | 22.6126 | 22.6056 | 22.5985 | 22.5917 | 22.5852 | 22.5547 | 22.4153 | 22.3406
|  | HARBOUR | FS |  |  |  | 0.14737 | 23.278 | 23.2699 | 23.2687 | 23.2675 | 23.266 | 23.2643 | 23.2625 | 23.2582 | 23.2535 | 23.2483 | 23.2428 | 23.2262 | 23.1568 | 23.009 | 22.6318 | 22.6237 | 22.6225 | 22.6212 | 22.6197 | 22.618 | 22.6163 | 22.612 | 22.6072 | 22.6021 | 22.5966 | 22.5799 | 22.4997 | 22.3412 | 22.6846 | 22.6765 | 22.6753 | 22.6741 | 22.6726 | 22.6709 | 22.6691 | 22.6648 | 22.6601 | 22.6549 | 22.6494 | 22.6328 | 22.5634 | 22.4156
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 29.9969 | 29.9934 | 29.9901 | 29.9851 | 29.98 | 29.975 | 29.9699 | 29.9651 | 29.9604 | 29.9556 | 29.9509 | 29.9262 | 29.8964 | 29.8547 | 29.9963 | 29.9926 | 29.9889 | 29.9832 | 29.9775 | 29.9718 | 29.9662 | 29.9608 | 29.9554 | 29.95 | 29.9448 | 29.9171 | 29.8843 | 29.8397 | 29.9963 | 29.9927 | 29.9889 | 29.9833 | 29.9775 | 29.9719 | 29.9663 | 29.9609 | 29.9555 | 29.9501 | 29.9449 | 29.9397 | 29.9342 | 29.9286
|  | HARRIS GRID | CT |  |  |  | 0 | 29.9972 | 29.9955 | 29.9937 | 29.9901 | 29.9863 | 29.9824 | 29.9786 | 29.975 | 29.9715 | 29.968 | 29.9646 | 29.9462 | 29.9241 | 29.8973 | 29.9967 | 29.9948 | 29.9928 | 29.9887 | 29.9844 | 29.9801 | 29.9757 | 29.9718 | 29.9678 | 29.9638 | 29.9599 | 29.9392 | 29.9149 | 29.8859 | 29.9967 | 29.9948 | 29.9929 | 29.9887 | 29.9844 | 29.9801 | 29.9758 | 29.9718 | 29.9678 | 29.9639 | 29.96 | 29.9561 | 29.952 | 29.9478
|  | HARRIS GRID | LW |  |  |  | 0 | 29.9969 | 29.9934 | 29.9901 | 29.9851 | 29.98 | 29.975 | 29.9699 | 29.9651 | 29.9604 | 29.9556 | 29.9509 | 29.9262 | 29.8964 | 29.8547 | 29.9963 | 29.9926 | 29.9889 | 29.9832 | 29.9775 | 29.9718 | 29.9662 | 29.9608 | 29.9554 | 29.95 | 29.9448 | 29.9171 | 29.8843 | 29.8397 | 29.9963 | 29.9927 | 29.9889 | 29.9833 | 29.9775 | 29.9719 | 29.9663 | 29.9609 | 29.9555 | 29.9501 | 29.9449 | 29.9397 | 29.9342 | 29.9286
|  | HARRIS GRID | ST |  |  |  | 0 | 29.9988 | 29.9984 | 29.9982 | 29.9966 | 29.9948 | 29.9931 | 29.9913 | 29.9898 | 29.9883 | 29.9869 | 29.9855 | 29.9791 | 29.9694 | 29.9621 | 29.9986 | 29.9982 | 29.998 | 29.9961 | 29.9941 | 29.9921 | 29.9902 | 29.9884 | 29.9867 | 29.9851 | 29.9835 | 29.9761 | 29.9655 | 29.9573 | 29.9986 | 29.9982 | 29.998 | 29.9961 | 29.9941 | 29.9922 | 29.9902 | 29.9885 | 29.9868 | 29.9851 | 29.9835 | 29.9761 | 29.9655 | 29.9574
|  | HARRIS GRID | FS |  |  |  | 0 | 29.9989 | 29.9986 | 29.9985 | 29.9983 | 29.9979 | 29.997 | 29.9961 | 29.995 | 29.9938 | 29.9927 | 29.9915 | 29.9862 | 29.9796 | 29.9708 | 29.9987 | 29.9984 | 29.9983 | 29.9981 | 29.9976 | 29.9965 | 29.9955 | 29.9942 | 29.9928 | 29.9915 | 29.9902 | 29.984 | 29.9766 | 29.967 | 29.9987 | 29.9984 | 29.9983 | 29.9981 | 29.9976 | 29.9965 | 29.9955 | 29.9942 | 29.9929 | 29.9915 | 29.9902 | 29.9841 | 29.9766 | 29.9671
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0.057895 | 24.129 | 24.1283 | 24.1278 | 24.127 | 24.1262 | 24.1254 | 24.1246 | 24.1238 | 24.1231 | 24.1223 | 24.1216 | 24.1176 | 24.1123 | 24.104 | 22.7526 | 22.7521 | 22.7518 | 22.7515 | 22.7511 | 22.7506 | 22.7502 | 22.7498 | 22.7495 | 22.7491 | 22.7488 | 22.7465 | 22.7431 | 22.7365 | 23.4368 | 23.4363 | 23.436 | 23.4357 | 23.4353 | 23.4349 | 23.4344 | 23.434 | 23.4337 | 23.4333 | 23.433 | 23.4326 | 23.4322 | 23.4317
|  | HARVEST AVENUE | CT |  |  |  | 0.057895 | 24.1291 | 24.1287 | 24.1284 | 24.1279 | 24.1273 | 24.1267 | 24.1261 | 24.1256 | 24.1251 | 24.1247 | 24.1242 | 24.1214 | 24.1177 | 24.1128 | 22.7526 | 22.7524 | 22.7523 | 22.7521 | 22.7518 | 22.7515 | 22.7511 | 22.7509 | 22.7507 | 22.7504 | 22.7502 | 22.7487 | 22.7463 | 22.7426 | 23.4368 | 23.4366 | 23.4365 | 23.4363 | 23.436 | 23.4357 | 23.4353 | 23.4351 | 23.4349 | 23.4347 | 23.4344 | 23.4342 | 23.4339 | 23.4336
|  | HARVEST AVENUE | LW |  |  |  | 0.057895 | 24.129 | 24.1283 | 24.1278 | 24.127 | 24.1262 | 24.1254 | 24.1246 | 24.1238 | 24.1231 | 24.1223 | 24.1216 | 24.1176 | 24.1123 | 24.104 | 22.7526 | 22.7521 | 22.7518 | 22.7515 | 22.7511 | 22.7506 | 22.7502 | 22.7498 | 22.7495 | 22.7491 | 22.7488 | 22.7465 | 22.7431 | 22.7365 | 23.4368 | 23.4363 | 23.436 | 23.4357 | 23.4353 | 23.4349 | 23.4344 | 23.434 | 23.4337 | 23.4333 | 23.433 | 23.4326 | 23.4322 | 23.4317
|  | HARVEST AVENUE | ST |  |  |  | 0.057895 | 24.1293 | 24.1292 | 24.1292 | 24.1289 | 24.1286 | 24.1283 | 24.128 | 24.1277 | 24.1275 | 24.1272 | 24.127 | 24.126 | 24.1241 | 24.1228 | 22.7526 | 22.7526 | 22.7525 | 22.7524 | 22.7523 | 22.7522 | 22.752 | 22.752 | 22.7519 | 22.7519 | 22.7518 | 22.7516 | 22.7504 | 22.7499 | 23.4368 | 23.4368 | 23.4367 | 23.4366 | 23.4365 | 23.4364 | 23.4362 | 23.4362 | 23.4361 | 23.4361 | 23.436 | 23.4358 | 23.4347 | 23.4341
|  | HARVEST AVENUE | FS |  |  |  | 0.057895 | 24.1293 | 24.1292 | 24.1292 | 24.1292 | 24.1291 | 24.129 | 24.1289 | 24.1287 | 24.1285 | 24.1283 | 24.1282 | 24.1273 | 24.1262 | 24.1244 | 22.7526 | 22.7526 | 22.7526 | 22.7526 | 22.7526 | 22.7525 | 22.7525 | 22.7525 | 22.7525 | 22.7524 | 22.7524 | 22.7523 | 22.7518 | 22.7506 | 23.4368 | 23.4368 | 23.4368 | 23.4368 | 23.4368 | 23.4368 | 23.4367 | 23.4367 | 23.4367 | 23.4367 | 23.4366 | 23.4365 | 23.436 | 23.4348
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 0.015789 | 3.2314 | 3.1934 | 3.1571 | 3.1174 | 3.0758 | 3.0316 | 2.987 | 2.9475 | 2.9067 | 2.866 | 2.8243 | 2.5835 | 2.0474 | 1.3121 | 3.3658 | 3.3084 | 3.2497 | 3.1705 | 3.0903 | 3.0096 | 2.9208 | 2.8313 | 2.7425 | 2.6537 | 2.5654 | 2.0928 | 1.5213 | 0.75343 | 3.1271 | 3.0891 | 3.0528 | 3.0132 | 2.9715 | 2.9273 | 2.8827 | 2.8432 | 2.8025 | 2.7375 | 2.6439 | 2.5507 | 2.4525 | 2.3518
|  | HASTIGROW | CT |  |  |  | 0.015789 | 3.2314 | 3.1934 | 3.1571 | 3.1174 | 3.0758 | 3.0316 | 2.987 | 2.9475 | 2.9067 | 2.866 | 2.8243 | 2.5835 | 2.2048 | 1.6463 | 3.3658 | 3.3084 | 3.2497 | 3.1705 | 3.0903 | 3.0096 | 2.9301 | 2.8532 | 2.7758 | 2.699 | 2.622 | 2.2101 | 1.72 | 1.139 | 3.1271 | 3.0891 | 3.0528 | 3.0132 | 2.9715 | 2.9273 | 2.8827 | 2.8432 | 2.8025 | 2.7617 | 2.7114 | 2.6341 | 2.5512 | 2.4648
|  | HASTIGROW | LW |  |  |  | 0.015789 | 3.2786 | 3.2369 | 3.2129 | 3.1814 | 3.1463 | 3.1083 | 3.0674 | 3.0314 | 2.9952 | 2.9579 | 2.9202 | 2.5853 | 2.0474 | 1.3121 | 3.4057 | 3.3377 | 3.2819 | 3.1933 | 3.1026 | 3.0121 | 2.9208 | 2.8313 | 2.7425 | 2.6537 | 2.5654 | 2.0928 | 1.5213 | 0.75343 | 3.1743 | 3.1326 | 3.1086 | 3.0771 | 3.042 | 3.004 | 2.9631 | 2.9208 | 2.8311 | 2.7375 | 2.6439 | 2.5507 | 2.4525 | 2.3518
|  | HASTIGROW | ST |  |  |  | 0.015789 | 3.2878 | 3.2771 | 3.2684 | 3.2565 | 3.2426 | 3.2276 | 3.2117 | 3.2011 | 3.1904 | 3.1798 | 3.1702 | 3.1204 | 3.021 | 2.9445 | 3.4392 | 3.4283 | 3.4196 | 3.3896 | 3.3498 | 3.3102 | 3.2707 | 3.2346 | 3.1992 | 3.1645 | 3.1314 | 2.9716 | 2.7693 | 2.5956 | 3.1835 | 3.1728 | 3.1641 | 3.1522 | 3.1383 | 3.1233 | 3.1075 | 3.0968 | 3.0861 | 3.0755 | 3.0659 | 3.0161 | 2.8579 | 2.6747
|  | HASTIGROW | FS |  |  |  | 0.015789 | 3.2929 | 3.2859 | 3.2807 | 3.2755 | 3.2701 | 3.2647 | 3.2593 | 3.2535 | 3.2476 | 3.2415 | 3.2352 | 3.2028 | 3.1493 | 3.0629 | 3.4444 | 3.4374 | 3.4321 | 3.4267 | 3.421 | 3.3997 | 3.3776 | 3.3531 | 3.3285 | 3.3037 | 3.2788 | 3.1531 | 3.0161 | 2.8519 | 3.1886 | 3.1817 | 3.1764 | 3.1712 | 3.1659 | 3.1604 | 3.155 | 3.1492 | 3.1433 | 3.1372 | 3.1309 | 3.0985 | 3.045 | 2.9412
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.61579 | 7.5021 | 7.3364 | 7.182 | 6.9885 | 6.8 | 6.619 | 6.4513 | 6.2821 | 6.1171 | 5.9506 | 5.7973 | 5.0581 | 4.2603 | 3.2503 | 6.8345 | 6.6401 | 6.4549 | 6.2229 | 5.9982 | 5.7838 | 5.5866 | 5.3861 | 5.1954 | 5.0118 | 4.8432 | 4.0374 | 3.1815 | 2.118 | 6.9128 | 6.7177 | 6.5318 | 6.2988 | 6.0734 | 5.8582 | 5.6603 | 5.4591 | 5.2677 | 5.0835 | 4.9143 | 4.7574 | 4.5949 | 4.4316
|  | HATTON | CT |  |  |  | 0.61579 | 7.5072 | 7.3943 | 7.2742 | 7.1304 | 6.9807 | 6.828 | 6.6916 | 6.5593 | 6.4284 | 6.3053 | 6.1875 | 5.5824 | 4.9238 | 4.1688 | 6.853 | 6.7229 | 6.5833 | 6.4149 | 6.24 | 6.0619 | 5.9046 | 5.7507 | 5.599 | 5.4568 | 5.3217 | 4.6485 | 3.9488 | 3.1555 | 6.9316 | 6.8011 | 6.661 | 6.4921 | 6.3166 | 6.1379 | 5.9801 | 5.8257 | 5.6735 | 5.5309 | 5.3954 | 5.2601 | 5.1227 | 4.9885
|  | HATTON | LW |  |  |  | 0.61579 | 7.5021 | 7.3364 | 7.182 | 6.9885 | 6.8 | 6.619 | 6.4513 | 6.2821 | 6.1171 | 5.9506 | 5.7973 | 5.0581 | 4.2603 | 3.2503 | 6.8345 | 6.6401 | 6.4549 | 6.2229 | 5.9982 | 5.7838 | 5.5866 | 5.3861 | 5.1954 | 5.0118 | 4.8432 | 4.0374 | 3.1815 | 2.118 | 6.9128 | 6.7177 | 6.5318 | 6.2988 | 6.0734 | 5.8582 | 5.6603 | 5.4591 | 5.2677 | 5.0835 | 4.9143 | 4.7574 | 4.5949 | 4.4316
|  | HATTON | ST |  |  |  | 0.61579 | 7.6214 | 7.588 | 7.5529 | 7.4862 | 7.4146 | 7.3409 | 7.2715 | 7.2031 | 7.1332 | 7.0669 | 7.0028 | 6.709 | 6.4054 | 6.149 | 6.9806 | 6.9418 | 6.9004 | 6.8206 | 6.7355 | 6.6481 | 6.5661 | 6.4838 | 6.3996 | 6.3199 | 6.2429 | 5.8909 | 5.5419 | 5.2437 | 7.0594 | 7.0205 | 6.979 | 6.8989 | 6.8135 | 6.7258 | 6.6435 | 6.5608 | 6.4763 | 6.3963 | 6.319 | 5.9656 | 5.6157 | 5.3165
|  | HATTON | FS |  |  |  | 0.61579 | 7.6372 | 7.6107 | 7.586 | 7.5572 | 7.5204 | 7.4749 | 7.431 | 7.3805 | 7.3277 | 7.2762 | 7.2245 | 6.9861 | 6.7688 | 6.5212 | 6.9989 | 6.9679 | 6.9384 | 6.904 | 6.8594 | 6.8043 | 6.751 | 6.6899 | 6.626 | 6.5637 | 6.5012 | 6.2131 | 5.958 | 5.6751 | 7.0779 | 7.0468 | 7.0171 | 6.9826 | 6.9378 | 6.8824 | 6.829 | 6.7676 | 6.7034 | 6.6409 | 6.5782 | 6.2889 | 6.033 | 5.7492
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | YES | 0.14632 | 21.6739 | 21.6059 | 21.575 | 21.5319 | 21.4829 | 21.4282 | 21.1841 | 20.9283 | 20.681 | 20.4398 | 20.2157 | 19.0903 | 17.7869 | 15.9717 | 20.2532 | 20.1738 | 20.1322 | 20.0753 | 20.0132 | 19.7047 | 19.4169 | 19.1239 | 18.8411 | 18.5658 | 18.3106 | 17.0419 | 15.6007 | 13.6477 | 20.9034 | 20.8354 | 20.8045 | 20.7518 | 20.6874 | 20.4956 | 20.2253 | 19.9511 | 19.6861 | 19.4116 | 19.1571 | 18.9177 | 18.6591 | 18.4025
|  | HAUDAGAIN | CT |  |  |  | 0.14632 | 21.6739 | 21.6498 | 21.6293 | 21.6018 | 21.5684 | 21.5284 | 21.485 | 21.456 | 21.4252 | 21.2716 | 21.116 | 20.3114 | 19.3935 | 18.2577 | 20.256 | 20.226 | 20.1987 | 20.1623 | 20.1196 | 20.0704 | 20.0192 | 19.8996 | 19.7023 | 19.5158 | 19.3382 | 18.4292 | 17.4142 | 16.1813 | 20.9034 | 20.8793 | 20.8588 | 20.8314 | 20.7976 | 20.7467 | 20.694 | 20.6554 | 20.4932 | 20.3185 | 20.152 | 19.9851 | 19.8079 | 19.6339
|  | HAUDAGAIN | LW |  |  |  | 0.14632 | 21.6755 | 21.6059 | 21.575 | 21.5319 | 21.4829 | 21.4282 | 21.1841 | 20.9283 | 20.681 | 20.4398 | 20.2157 | 19.0903 | 17.7869 | 15.9717 | 20.2532 | 20.1738 | 20.1322 | 20.0753 | 20.0132 | 19.7047 | 19.4169 | 19.1239 | 18.8411 | 18.5658 | 18.3106 | 17.0419 | 15.6007 | 13.6477 | 20.9051 | 20.8354 | 20.8045 | 20.7518 | 20.6874 | 20.4956 | 20.2253 | 19.9511 | 19.6861 | 19.4116 | 19.1571 | 18.9177 | 18.6591 | 18.4025
|  | HAUDAGAIN | ST |  |  |  | 0.14632 | 21.6764 | 21.6662 | 21.6614 | 21.6483 | 21.6324 | 21.6138 | 21.593 | 21.5852 | 21.5774 | 21.5699 | 21.5627 | 21.5288 | 21.0274 | 20.5771 | 20.2636 | 20.2517 | 20.2448 | 20.2269 | 20.2059 | 20.1822 | 20.1567 | 20.1437 | 20.1305 | 20.1179 | 20.1058 | 19.8431 | 19.237 | 18.7239 | 20.9059 | 20.8957 | 20.8909 | 20.8778 | 20.8619 | 20.8433 | 20.8225 | 20.8148 | 20.8069 | 20.7954 | 20.7823 | 20.6312 | 20.0571 | 19.5693
|  | HAUDAGAIN | FS |  |  |  | 0.14632 | 21.6764 | 21.6651 | 21.6646 | 21.6641 | 21.6632 | 21.6619 | 21.6607 | 21.6559 | 21.6505 | 21.6445 | 21.638 | 21.6207 | 21.5284 | 21.042 | 20.264 | 20.2513 | 20.2492 | 20.2466 | 20.243 | 20.238 | 20.233 | 20.224 | 20.2142 | 20.2039 | 20.1932 | 20.1562 | 19.8146 | 19.258 | 20.9059 | 20.8947 | 20.8942 | 20.8936 | 20.8927 | 20.8914 | 20.8902 | 20.8854 | 20.88 | 20.874 | 20.8675 | 20.8313 | 20.6048 | 20.0749
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 0.10947 | 23.1219 | 23.0755 | 23.0545 | 23.0253 | 22.9921 | 22.8615 | 22.6674 | 22.4703 | 22.2808 | 22.0975 | 21.93 | 21.0991 | 20.1503 | 18.8391 | 22.4396 | 22.3847 | 22.3554 | 22.3159 | 22.0972 | 21.8618 | 21.6463 | 21.426 | 21.2089 | 20.9991 | 20.808 | 19.8691 | 18.8183 | 17.4054 | 22.4359 | 22.3895 | 22.3685 | 22.2018 | 21.9571 | 21.7229 | 21.5085 | 21.2897 | 21.0796 | 20.8766 | 20.6915 | 20.5188 | 20.3325 | 20.1476
|  | HAYTON | CT |  |  |  | 0.10947 | 23.1219 | 23.1056 | 23.0916 | 23.073 | 23.0504 | 23.0232 | 22.9937 | 22.9739 | 22.8785 | 22.7543 | 22.6366 | 22.036 | 21.3674 | 20.5433 | 22.4422 | 22.4213 | 22.4022 | 22.377 | 22.3475 | 22.3135 | 22.1794 | 22.0292 | 21.8814 | 21.743 | 21.6122 | 20.9373 | 20.1968 | 19.3006 | 22.4359 | 22.4195 | 22.4056 | 22.387 | 22.3643 | 22.1932 | 22.0389 | 21.8894 | 21.7424 | 21.6047 | 21.4746 | 21.3442 | 21.2066 | 21.0745
|  | HAYTON | LW |  |  |  | 0.10947 | 23.1228 | 23.0755 | 23.0545 | 23.0253 | 22.9921 | 22.8615 | 22.6674 | 22.4703 | 22.2808 | 22.0975 | 21.93 | 21.0991 | 20.1503 | 18.8391 | 22.4396 | 22.3847 | 22.3554 | 22.3159 | 22.0972 | 21.8618 | 21.6463 | 21.426 | 21.2089 | 20.9991 | 20.808 | 19.8691 | 18.8183 | 17.4054 | 22.4367 | 22.3895 | 22.3685 | 22.2018 | 21.9571 | 21.7229 | 21.5085 | 21.2897 | 21.0796 | 20.8766 | 20.6915 | 20.5188 | 20.3325 | 20.1476
|  | HAYTON | ST |  |  |  | 0.10947 | 23.1228 | 23.1158 | 23.1124 | 23.1035 | 23.0925 | 23.0797 | 23.0654 | 23.06 | 23.0547 | 23.0495 | 23.0446 | 22.9806 | 22.5786 | 22.242 | 22.4467 | 22.4382 | 22.4332 | 22.4208 | 22.4062 | 22.3897 | 22.3719 | 22.3628 | 22.3534 | 22.3445 | 22.336 | 21.9882 | 21.5486 | 21.1683 | 22.4367 | 22.4297 | 22.4264 | 22.4174 | 22.4065 | 22.3937 | 22.3794 | 22.374 | 22.3686 | 22.323 | 22.2394 | 21.849 | 21.4112 | 21.0395
|  | HAYTON | FS |  |  |  | 0.10947 | 23.1228 | 23.1149 | 23.1145 | 23.1141 | 23.1135 | 23.1126 | 23.1118 | 23.1084 | 23.1046 | 23.1004 | 23.0959 | 23.0838 | 22.9732 | 22.6002 | 22.4471 | 22.438 | 22.4363 | 22.4343 | 22.4316 | 22.428 | 22.4245 | 22.4181 | 22.4111 | 22.4038 | 22.3962 | 22.3047 | 21.9802 | 21.5757 | 22.4367 | 22.4289 | 22.4285 | 22.4281 | 22.4275 | 22.4266 | 22.4257 | 22.4224 | 22.4186 | 22.4144 | 22.4098 | 22.164 | 21.841 | 21.4381
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 0 | 1.5576 | 1.5371 | 1.5172 | 1.497 | 1.4759 | 1.454 | 1.4316 | 1.4106 | 1.3894 | 1.3674 | 1.3454 | 1.164 | 0.94031 | 0.65077 | 1.4901 | 1.4696 | 1.4497 | 1.4295 | 1.4084 | 1.3865 | 1.3634 | 1.3279 | 1.2925 | 1.2564 | 1.2204 | 1.0272 | 0.79765 | 0.49007 | 1.507 | 1.4865 | 1.4666 | 1.4464 | 1.4253 | 1.4034 | 1.3709 | 1.3366 | 1.3023 | 1.2673 | 1.2325 | 1.1977 | 1.161 | 1.1232
|  | HELMSDALE | CT |  |  |  | 0 | 1.5576 | 1.5371 | 1.5172 | 1.497 | 1.4759 | 1.454 | 1.4316 | 1.4106 | 1.3894 | 1.3674 | 1.3454 | 1.164 | 0.94031 | 0.67634 | 1.4901 | 1.4696 | 1.4497 | 1.4295 | 1.4084 | 1.3865 | 1.3634 | 1.3279 | 1.2925 | 1.2564 | 1.2204 | 1.0272 | 0.79765 | 0.52796 | 1.507 | 1.4865 | 1.4666 | 1.4464 | 1.4253 | 1.4034 | 1.3709 | 1.3366 | 1.3023 | 1.2673 | 1.2325 | 1.1977 | 1.161 | 1.1232
|  | HELMSDALE | LW |  |  |  | 0 | 1.587 | 1.5713 | 1.5607 | 1.5473 | 1.5322 | 1.5164 | 1.4994 | 1.4834 | 1.4578 | 1.4224 | 1.3875 | 1.1965 | 0.9615 | 0.65077 | 1.5196 | 1.5038 | 1.4932 | 1.4798 | 1.4647 | 1.4353 | 1.3984 | 1.3618 | 1.3254 | 1.2883 | 1.2517 | 1.0524 | 0.80903 | 0.49007 | 1.5364 | 1.5207 | 1.51 | 1.4967 | 1.4784 | 1.4438 | 1.4086 | 1.3736 | 1.3388 | 1.3033 | 1.2683 | 1.2327 | 1.1948 | 1.1565
|  | HELMSDALE | ST |  |  |  | 0 | 1.5921 | 1.5865 | 1.5817 | 1.5757 | 1.5685 | 1.561 | 1.554 | 1.5488 | 1.5435 | 1.5383 | 1.5331 | 1.506 | 1.4512 | 1.3759 | 1.5246 | 1.519 | 1.5142 | 1.5082 | 1.5011 | 1.4935 | 1.4865 | 1.4813 | 1.476 | 1.4708 | 1.4656 | 1.4052 | 1.3188 | 1.2402 | 1.5415 | 1.5359 | 1.5311 | 1.5251 | 1.5179 | 1.5104 | 1.5034 | 1.4981 | 1.4929 | 1.4877 | 1.4814 | 1.4153 | 1.3322 | 1.2567
|  | HELMSDALE | FS |  |  |  | 0 | 1.5963 | 1.5934 | 1.59 | 1.5865 | 1.5831 | 1.5804 | 1.5777 | 1.5747 | 1.5716 | 1.5684 | 1.5651 | 1.5472 | 1.5205 | 1.4822 | 1.5288 | 1.5259 | 1.5225 | 1.519 | 1.5156 | 1.5129 | 1.5103 | 1.5072 | 1.5041 | 1.5009 | 1.4977 | 1.4798 | 1.4213 | 1.3526 | 1.5457 | 1.5428 | 1.5394 | 1.5359 | 1.5324 | 1.5298 | 1.5271 | 1.5241 | 1.5209 | 1.5178 | 1.5145 | 1.4883 | 1.4313 | 1.365
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 0.38211 | 26.5256 | 26.3762 | 26.3091 | 26.2156 | 26.1095 | 25.9931 | 25.8704 | 25.7739 | 25.6758 | 25.4408 | 25.1366 | 23.5095 | 21.4797 | 18.5456 | 25.1532 | 24.9964 | 24.9221 | 24.8155 | 24.6966 | 24.4372 | 24.0717 | 23.7158 | 23.3623 | 23.0102 | 22.6639 | 20.8296 | 18.5971 | 15.4718 | 25.8621 | 25.7126 | 25.6455 | 25.552 | 25.4459 | 25.3296 | 25.0842 | 24.7351 | 24.3881 | 24.0426 | 23.7027 | 23.3676 | 23.0052 | 22.6402
|  | HILTON | CT |  |  |  | 0.38211 | 26.5256 | 26.4729 | 26.4282 | 26.3678 | 26.294 | 26.2076 | 26.1148 | 26.0539 | 25.9905 | 25.9266 | 25.8621 | 24.9919 | 23.5862 | 21.8183 | 25.1532 | 25.096 | 25.0463 | 24.9767 | 24.894 | 24.7992 | 24.6982 | 24.4915 | 24.2494 | 24.0097 | 23.7722 | 22.497 | 20.9426 | 19.0285 | 25.8621 | 25.8094 | 25.7646 | 25.7042 | 25.6304 | 25.5441 | 25.4512 | 25.3903 | 25.2604 | 25.0253 | 24.7923 | 24.5594 | 24.307 | 24.0528
|  | HILTON | LW |  |  |  | 0.38211 | 26.5273 | 26.3762 | 26.3091 | 26.2156 | 26.1095 | 25.9931 | 25.8704 | 25.7739 | 25.6758 | 25.4408 | 25.1366 | 23.5095 | 21.4797 | 18.5456 | 25.1534 | 24.9964 | 24.9221 | 24.8155 | 24.6966 | 24.4372 | 24.0717 | 23.7158 | 23.3623 | 23.0102 | 22.6639 | 20.8296 | 18.5971 | 15.4718 | 25.8638 | 25.7126 | 25.6455 | 25.552 | 25.4459 | 25.3296 | 25.0842 | 24.7351 | 24.3881 | 24.0426 | 23.7027 | 23.3676 | 23.0052 | 22.6402
|  | HILTON | ST |  |  |  | 0.38211 | 26.5282 | 26.5082 | 26.4986 | 26.4728 | 26.4415 | 26.4048 | 26.3638 | 26.3484 | 26.333 | 26.3182 | 26.304 | 26.2394 | 25.9139 | 25.3687 | 25.1627 | 25.1423 | 25.1324 | 25.1006 | 25.0634 | 25.021 | 24.9746 | 24.9534 | 24.9322 | 24.9118 | 24.8921 | 24.4094 | 23.5627 | 22.8883 | 25.8646 | 25.8446 | 25.835 | 25.8092 | 25.7779 | 25.7412 | 25.7002 | 25.6849 | 25.6694 | 25.6546 | 25.6405 | 25.4228 | 24.5895 | 23.9283
|  | HILTON | FS |  |  |  | 0.38211 | 26.5282 | 26.5087 | 26.5078 | 26.5068 | 26.5053 | 26.5031 | 26.501 | 26.4927 | 26.4833 | 26.4729 | 26.4617 | 26.4318 | 26.276 | 25.935 | 25.163 | 25.1432 | 25.142 | 25.1403 | 25.1369 | 25.1307 | 25.1245 | 25.1115 | 25.0974 | 25.0825 | 25.0666 | 25.0142 | 24.4289 | 23.6657 | 25.8646 | 25.8451 | 25.8443 | 25.8432 | 25.8417 | 25.8395 | 25.8374 | 25.8291 | 25.8197 | 25.8093 | 25.7981 | 25.7682 | 25.4427 | 24.6905
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.52105 | 26.3923 | 26.3371 | 26.3075 | 26.267 | 26.2212 | 26.1695 | 26.1147 | 26.0456 | 25.7644 | 25.4918 | 25.2382 | 23.993 | 22.6127 | 20.7917 | 24.8307 | 24.7583 | 24.716 | 24.6588 | 24.4148 | 24.0569 | 23.7272 | 23.3886 | 23.0623 | 22.7463 | 22.4532 | 21.0267 | 19.4752 | 17.4853 | 25.5965 | 25.5413 | 25.5117 | 25.4712 | 25.4254 | 25.3737 | 25.1596 | 24.8175 | 24.4878 | 24.1687 | 23.8726 | 23.5946 | 23.3017 | 23.0108
|  | HUME STREET | CT |  |  |  | 0.52105 | 26.3923 | 26.3658 | 26.3427 | 26.3131 | 26.2779 | 26.2377 | 26.1945 | 26.1637 | 26.1314 | 26.0986 | 26.0653 | 25.3043 | 24.3126 | 23.1319 | 24.8307 | 24.797 | 24.7657 | 24.7253 | 24.6791 | 24.6279 | 24.4824 | 24.2471 | 24.0154 | 23.7981 | 23.5907 | 22.5486 | 21.4363 | 20.1367 | 25.5965 | 25.57 | 25.5469 | 25.5173 | 25.4821 | 25.442 | 25.3987 | 25.368 | 25.3356 | 25.2315 | 25.0221 | 24.8126 | 24.5961 | 24.3843
|  | HUME STREET | LW |  |  |  | 0.52105 | 26.4016 | 26.3371 | 26.3075 | 26.267 | 26.2212 | 26.1695 | 26.1147 | 26.0456 | 25.7644 | 25.4918 | 25.2382 | 23.993 | 22.6127 | 20.7917 | 24.8346 | 24.7583 | 24.716 | 24.6588 | 24.4148 | 24.0569 | 23.7272 | 23.3886 | 23.0623 | 22.7463 | 22.4532 | 21.0267 | 19.4752 | 17.4853 | 25.6058 | 25.5413 | 25.5117 | 25.4712 | 25.4254 | 25.3737 | 25.1596 | 24.8175 | 24.4878 | 24.1687 | 23.8726 | 23.5946 | 23.3017 | 23.0108
|  | HUME STREET | ST |  |  |  | 0.52105 | 26.4032 | 26.3932 | 26.388 | 26.3754 | 26.3594 | 26.3409 | 26.3205 | 26.3118 | 26.303 | 26.2946 | 26.2873 | 26.2501 | 26.0795 | 25.6136 | 24.8476 | 24.8355 | 24.8277 | 24.8092 | 24.787 | 24.7623 | 24.7361 | 24.721 | 24.7058 | 24.6911 | 24.6777 | 24.1527 | 23.4769 | 22.8903 | 25.6074 | 25.5974 | 25.5922 | 25.5796 | 25.5636 | 25.5451 | 25.5247 | 25.516 | 25.5072 | 25.4988 | 25.4915 | 25.4543 | 24.9068 | 24.3143
|  | HUME STREET | FS |  |  |  | 0.52105 | 26.4032 | 26.3925 | 26.3912 | 26.3899 | 26.3883 | 26.3863 | 26.3844 | 26.3793 | 26.3737 | 26.3677 | 26.3611 | 26.3418 | 26.2567 | 26.0727 | 24.8483 | 24.8358 | 24.8326 | 24.8289 | 24.824 | 24.8176 | 24.8112 | 24.8012 | 24.7904 | 24.7793 | 24.7677 | 24.6839 | 24.187 | 23.5983 | 25.6074 | 25.5967 | 25.5955 | 25.5941 | 25.5925 | 25.5905 | 25.5886 | 25.5836 | 25.5779 | 25.5719 | 25.5653 | 25.546 | 25.4609 | 25.0297
| KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0.024211 | 16.2074 | 16.1387 | 16.0734 | 16.003 | 15.9298 | 15.8523 | 15.7735 | 15.702 | 15.6289 | 15.5556 | 15.4665 | 14.5434 | 13.4052 | 11.9098 | 14.484 | 14.2979 | 14.0961 | 13.8255 | 13.5594 | 13.3004 | 13.0557 | 12.8051 | 12.5609 | 12.3221 | 12.0962 | 10.9612 | 9.6896 | 8.0908 | 15.0098 | 14.9411 | 14.8759 | 14.8055 | 14.7322 | 14.6548 | 14.576 | 14.5045 | 14.3317 | 14.0975 | 13.8758 | 13.6629 | 13.44 | 13.2153
|  | HUNTLY | CT |  |  |  | 0.024211 | 16.2074 | 16.1387 | 16.0734 | 16.003 | 15.9298 | 15.8523 | 15.7735 | 15.702 | 15.6289 | 15.5556 | 15.4804 | 14.8738 | 13.9412 | 12.8411 | 14.484 | 14.3235 | 14.1538 | 13.9391 | 13.7194 | 13.4961 | 13.2904 | 13.0869 | 12.8844 | 12.6901 | 12.5002 | 11.5284 | 10.4554 | 9.2198 | 15.0098 | 14.9411 | 14.8759 | 14.8055 | 14.7322 | 14.6548 | 14.576 | 14.5045 | 14.4314 | 14.358 | 14.2636 | 14.0768 | 13.8852 | 13.6942
|  | HUNTLY | LW |  |  |  | 0.024211 | 16.295 | 16.2294 | 16.1894 | 16.138 | 16.0807 | 16.0175 | 15.9505 | 15.8905 | 15.8292 | 15.6464 | 15.4665 | 14.5434 | 13.4052 | 11.9098 | 14.51 | 14.2979 | 14.0961 | 13.8255 | 13.5594 | 13.3004 | 13.0557 | 12.8051 | 12.5609 | 12.3221 | 12.0962 | 10.9612 | 9.6896 | 8.0908 | 15.0974 | 15.0319 | 14.9918 | 14.9405 | 14.8832 | 14.82 | 14.753 | 14.5712 | 14.3317 | 14.0975 | 13.8758 | 13.6629 | 13.44 | 13.2153
|  | HUNTLY | ST |  |  |  | 0.024211 | 16.3135 | 16.2942 | 16.2783 | 16.2579 | 16.2331 | 16.2065 | 16.1784 | 16.1598 | 16.1412 | 16.1228 | 16.1046 | 16.0139 | 15.835 | 15.6235 | 14.6756 | 14.6315 | 14.5856 | 14.4823 | 14.3723 | 14.2609 | 14.1531 | 14.0478 | 13.9417 | 13.8385 | 13.7393 | 13.269 | 12.7662 | 12.3175 | 15.1159 | 15.0966 | 15.0808 | 15.0604 | 15.0355 | 15.0089 | 14.9809 | 14.9623 | 14.9436 | 14.9252 | 14.907 | 14.8163 | 14.5319 | 14.0912
|  | HUNTLY | FS |  |  |  | 0.024211 | 16.3219 | 16.3088 | 16.2992 | 16.2896 | 16.2798 | 16.2699 | 16.2599 | 16.2479 | 16.2364 | 16.2246 | 16.2133 | 16.1546 | 16.0544 | 15.8953 | 14.6955 | 14.6618 | 14.6295 | 14.5925 | 14.5422 | 14.4738 | 14.4065 | 14.3287 | 14.2487 | 14.1694 | 14.0917 | 13.7202 | 13.3515 | 12.9369 | 15.1244 | 15.1112 | 15.1017 | 15.0921 | 15.0823 | 15.0723 | 15.0624 | 15.0504 | 15.0388 | 15.027 | 15.0157 | 14.9571 | 14.8568 | 14.6978
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 0 | 2.7526 | 2.7306 | 2.7097 | 2.6882 | 2.6663 | 2.6439 | 2.6222 | 2.5999 | 2.5776 | 2.5544 | 2.5312 | 2.4036 | 2.2445 | 2.0553 | 2.6396 | 2.6172 | 2.5959 | 2.5739 | 2.5513 | 2.5284 | 2.5061 | 2.4832 | 2.4602 | 2.4316 | 2.3988 | 2.2243 | 2.0216 | 1.7907 | 2.6884 | 2.6664 | 2.6455 | 2.624 | 2.6021 | 2.5798 | 2.5581 | 2.5358 | 2.5134 | 2.4902 | 2.467 | 2.4437 | 2.4191 | 2.3934
|  | INCHBARE | CT |  |  |  | 0 | 2.7526 | 2.7306 | 2.7097 | 2.6882 | 2.6663 | 2.6439 | 2.6222 | 2.5999 | 2.5776 | 2.5544 | 2.5312 | 2.4036 | 2.2445 | 2.0553 | 2.6396 | 2.6172 | 2.5959 | 2.5739 | 2.5513 | 2.5284 | 2.5061 | 2.4832 | 2.4602 | 2.4316 | 2.3988 | 2.2243 | 2.0216 | 1.7907 | 2.6884 | 2.6664 | 2.6455 | 2.624 | 2.6021 | 2.5798 | 2.5581 | 2.5358 | 2.5134 | 2.4902 | 2.467 | 2.4437 | 2.4191 | 2.3934
|  | INCHBARE | LW |  |  |  | 0 | 2.7863 | 2.775 | 2.7658 | 2.7549 | 2.7426 | 2.7292 | 2.7148 | 2.7012 | 2.6868 | 2.6716 | 2.6563 | 2.5646 | 2.4353 | 2.2391 | 2.6732 | 2.6614 | 2.6516 | 2.6398 | 2.6267 | 2.6124 | 2.5971 | 2.5692 | 2.5404 | 2.5118 | 2.4834 | 2.3279 | 2.1353 | 1.8938 | 2.7221 | 2.7108 | 2.7016 | 2.6907 | 2.6785 | 2.6651 | 2.6506 | 2.6371 | 2.6227 | 2.6074 | 2.5922 | 2.577 | 2.5594 | 2.5407
|  | INCHBARE | ST |  |  |  | 0 | 2.793 | 2.7873 | 2.7828 | 2.7777 | 2.7708 | 2.7645 | 2.7581 | 2.7525 | 2.7469 | 2.7414 | 2.7359 | 2.7076 | 2.6686 | 2.6305 | 2.6805 | 2.6748 | 2.6701 | 2.6646 | 2.6573 | 2.6506 | 2.6437 | 2.6378 | 2.6318 | 2.6258 | 2.6199 | 2.5864 | 2.5212 | 2.4585 | 2.7289 | 2.7231 | 2.7186 | 2.7135 | 2.7066 | 2.7003 | 2.6939 | 2.6883 | 2.6828 | 2.6772 | 2.6717 | 2.6435 | 2.6045 | 2.5663
|  | INCHBARE | FS |  |  |  | 0 | 2.7964 | 2.7933 | 2.7899 | 2.7865 | 2.7831 | 2.7796 | 2.7762 | 2.7726 | 2.7689 | 2.7652 | 2.7615 | 2.7404 | 2.7189 | 2.6918 | 2.6839 | 2.6808 | 2.6774 | 2.6739 | 2.6703 | 2.6666 | 2.6628 | 2.6589 | 2.6549 | 2.6509 | 2.6469 | 2.6244 | 2.6016 | 2.5619 | 2.7322 | 2.7291 | 2.7257 | 2.7223 | 2.7189 | 2.7155 | 2.712 | 2.7084 | 2.7048 | 2.7011 | 2.6974 | 2.6762 | 2.6547 | 2.6276
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0 | 2.8627 | 2.8527 | 2.8434 | 2.8326 | 2.8206 | 2.8073 | 2.7834 | 2.7489 | 2.7138 | 2.6788 | 2.6451 | 2.464 | 2.2405 | 1.9269 | 2.7653 | 2.7547 | 2.7324 | 2.693 | 2.6522 | 2.6118 | 2.5717 | 2.5329 | 2.4935 | 2.4543 | 2.4165 | 2.2156 | 1.9717 | 1.6379 | 2.7649 | 2.7542 | 2.7441 | 2.7321 | 2.7187 | 2.6983 | 2.658 | 2.6188 | 2.5791 | 2.5396 | 2.5015 | 2.464 | 2.4239 | 2.3826
|  | INNELLAN | CT |  |  |  | 0 | 2.8627 | 2.8527 | 2.8434 | 2.8326 | 2.8206 | 2.8073 | 2.7934 | 2.7826 | 2.7681 | 2.7416 | 2.7152 | 2.5734 | 2.4007 | 2.187 | 2.7653 | 2.7547 | 2.7408 | 2.7101 | 2.6785 | 2.6466 | 2.6157 | 2.587 | 2.5583 | 2.529 | 2.5 | 2.3446 | 2.1581 | 1.9309 | 2.7649 | 2.7542 | 2.7441 | 2.7321 | 2.7187 | 2.7043 | 2.6893 | 2.6736 | 2.6447 | 2.6152 | 2.5859 | 2.5567 | 2.5256 | 2.4944
|  | INNELLAN | LW |  |  |  | 0 | 2.872 | 2.8559 | 2.8478 | 2.8372 | 2.8246 | 2.811 | 2.7834 | 2.7489 | 2.7138 | 2.6788 | 2.6451 | 2.464 | 2.2405 | 1.9269 | 2.7743 | 2.7569 | 2.7324 | 2.693 | 2.6522 | 2.6118 | 2.5717 | 2.5329 | 2.4935 | 2.4543 | 2.4165 | 2.2156 | 1.9717 | 1.6379 | 2.7738 | 2.7569 | 2.7477 | 2.7353 | 2.7208 | 2.6983 | 2.658 | 2.6188 | 2.5791 | 2.5396 | 2.5015 | 2.464 | 2.4239 | 2.3826
|  | INNELLAN | ST |  |  |  | 0 | 2.8737 | 2.8701 | 2.8675 | 2.8642 | 2.8595 | 2.8543 | 2.8487 | 2.8455 | 2.8424 | 2.8393 | 2.8362 | 2.8165 | 2.7338 | 2.6674 | 2.7769 | 2.7733 | 2.7707 | 2.7668 | 2.7615 | 2.7511 | 2.7343 | 2.719 | 2.7039 | 2.6892 | 2.6749 | 2.6064 | 2.5155 | 2.441 | 2.7768 | 2.7731 | 2.7705 | 2.7664 | 2.7609 | 2.755 | 2.7486 | 2.7447 | 2.7408 | 2.7369 | 2.7332 | 2.6928 | 2.6012 | 2.5262
|  | INNELLAN | FS |  |  |  | 0 | 2.8745 | 2.8718 | 2.8709 | 2.87 | 2.869 | 2.8679 | 2.8669 | 2.8652 | 2.8635 | 2.8617 | 2.8598 | 2.8528 | 2.8229 | 2.7497 | 2.7778 | 2.7751 | 2.7741 | 2.7732 | 2.772 | 2.7705 | 2.7691 | 2.767 | 2.7559 | 2.7441 | 2.7323 | 2.6766 | 2.6118 | 2.5315 | 2.7776 | 2.7749 | 2.774 | 2.773 | 2.7717 | 2.7701 | 2.7686 | 2.7663 | 2.7639 | 2.7615 | 2.7589 | 2.7487 | 2.698 | 2.6173
| KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0.061053 | 8.9442 | 8.8852 | 16.1042 | 16.0429 | 15.9764 | 15.9061 | 15.8343 | 15.7724 | 15.7089 | 15.6444 | 15.5799 | 15.106 | 14.0133 | 12.5817 | 7.4935 | 7.3227 | 14.0526 | 13.8199 | 13.5894 | 13.3642 | 13.1501 | 12.9359 | 12.7268 | 12.522 | 12.3277 | 11.3523 | 10.2436 | 8.7969 | 8.3429 | 8.1751 | 15.0949 | 14.8655 | 14.638 | 14.4158 | 14.2043 | 13.9929 | 13.7865 | 13.5843 | 13.3924 | 13.2088 | 12.9992 | 12.7871
|  | INSCH | CT |  |  |  | 0.061053 | 8.9442 | 8.8852 | 16.1042 | 16.0429 | 15.9764 | 15.9061 | 15.8343 | 15.7724 | 15.7089 | 15.6444 | 15.5799 | 15.1998 | 14.6857 | 13.7152 | 7.4935 | 7.3596 | 14.1197 | 13.9393 | 13.7523 | 13.5636 | 13.388 | 13.2186 | 13.0511 | 12.8887 | 12.7322 | 11.9199 | 11.0154 | 9.9591 | 8.3429 | 8.2105 | 15.1595 | 14.9813 | 14.7965 | 14.6099 | 14.4362 | 14.2687 | 14.1032 | 13.9425 | 13.7876 | 13.6322 | 13.4708 | 13.3101
|  | INSCH | LW |  |  |  | 0.061053 | 9.0108 | 8.9383 | 16.1729 | 16.1203 | 16.0608 | 15.996 | 15.9271 | 15.8679 | 15.8075 | 15.7449 | 15.6822 | 15.106 | 14.0133 | 12.5817 | 7.5119 | 7.3227 | 14.0526 | 13.8199 | 13.5894 | 13.3642 | 13.1501 | 12.9359 | 12.7268 | 12.522 | 12.3277 | 11.3523 | 10.2436 | 8.7969 | 8.3623 | 8.1751 | 15.0949 | 14.8655 | 14.638 | 14.4158 | 14.2043 | 13.9929 | 13.7865 | 13.5843 | 13.3924 | 13.2088 | 12.9992 | 12.7871
|  | INSCH | ST |  |  |  | 0.061053 | 9.0251 | 9.0083 | 16.2705 | 16.2516 | 16.2289 | 16.2043 | 16.178 | 16.1613 | 16.1455 | 16.1298 | 16.1144 | 16.0376 | 15.8682 | 15.7472 | 7.6476 | 7.6122 | 14.4768 | 14.3889 | 14.2963 | 14.2025 | 14.1118 | 14.0237 | 13.9367 | 13.8526 | 13.7715 | 13.3931 | 12.969 | 12.6089 | 8.4957 | 8.4607 | 15.5132 | 15.4266 | 15.3352 | 15.2426 | 15.1531 | 15.0663 | 14.9806 | 14.8978 | 14.8178 | 14.4449 | 14.0254 | 13.6696
|  | INSCH | FS |  |  |  | 0.061053 | 9.0318 | 9.02 | 16.288 | 16.2809 | 16.2736 | 16.2661 | 16.2586 | 16.249 | 16.239 | 16.2287 | 16.2189 | 16.1706 | 16.08 | 15.9304 | 7.6659 | 7.6384 | 14.5144 | 14.4862 | 14.447 | 14.3913 | 14.3365 | 14.2733 | 14.2083 | 14.143 | 14.0791 | 13.774 | 13.4705 | 13.1236 | 8.5139 | 8.4866 | 15.5505 | 15.5226 | 15.484 | 15.4291 | 15.3753 | 15.313 | 15.249 | 15.1847 | 15.1218 | 14.8213 | 14.5216 | 14.1783
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 0.15789 | 25.6063 | 25.6061 | 25.606 | 25.6059 | 25.6058 | 25.6056 | 25.6055 | 25.6053 | 25.6052 | 25.6051 | 25.6049 | 25.6042 | 25.603 | 25.6007 | 25.2587 | 25.2528 | 25.2454 | 25.2323 | 25.2191 | 25.206 | 25.1929 | 25.179 | 25.1652 | 25.1513 | 25.1374 | 25.0688 | 24.9989 | 24.928 | 25.3127 | 25.3076 | 25.3013 | 25.2902 | 25.279 | 25.2679 | 25.2567 | 25.2449 | 25.2331 | 25.2213 | 25.2095 | 25.1977 | 25.1859 | 25.1741
|  | INVERALMOND | CT |  |  |  | 0.15789 | 25.6063 | 25.6062 | 25.6062 | 25.6061 | 25.606 | 25.6059 | 25.6058 | 25.6057 | 25.6056 | 25.6056 | 25.6055 | 25.605 | 25.6041 | 25.6029 | 25.2603 | 25.2561 | 25.2512 | 25.2422 | 25.2332 | 25.2242 | 25.2151 | 25.2053 | 25.1956 | 25.1858 | 25.176 | 25.1278 | 25.0785 | 25.0288 | 25.314 | 25.3105 | 25.3063 | 25.2987 | 25.291 | 25.2833 | 25.2756 | 25.2673 | 25.259 | 25.2507 | 25.2423 | 25.234 | 25.2257 | 25.2173
|  | INVERALMOND | LW |  |  |  | 0.15789 | 25.6063 | 25.6061 | 25.606 | 25.6059 | 25.6058 | 25.6056 | 25.6055 | 25.6053 | 25.6052 | 25.6051 | 25.6049 | 25.6042 | 25.603 | 25.6007 | 25.2587 | 25.2528 | 25.2454 | 25.2323 | 25.2191 | 25.206 | 25.1929 | 25.179 | 25.1652 | 25.1513 | 25.1374 | 25.0688 | 24.9989 | 24.928 | 25.3127 | 25.3076 | 25.3013 | 25.2902 | 25.279 | 25.2679 | 25.2567 | 25.2449 | 25.2331 | 25.2213 | 25.2095 | 25.1977 | 25.1859 | 25.1741
|  | INVERALMOND | ST |  |  |  | 0.15789 | 25.6063 | 25.6063 | 25.6063 | 25.6062 | 25.6062 | 25.6062 | 25.6061 | 25.6061 | 25.6061 | 25.6061 | 25.606 | 25.606 | 25.6056 | 25.6054 | 25.2652 | 25.2644 | 25.2636 | 25.257 | 25.2505 | 25.244 | 25.2375 | 25.231 | 25.2245 | 25.218 | 25.2115 | 25.1792 | 25.1465 | 25.1141 | 25.3182 | 25.3175 | 25.3168 | 25.3113 | 25.3057 | 25.3002 | 25.2947 | 25.2891 | 25.2836 | 25.2781 | 25.2726 | 25.2451 | 25.2173 | 25.1898
|  | INVERALMOND | FS |  |  |  | 0.15789 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6063 | 25.6062 | 25.6062 | 25.606 | 25.6056 | 25.2652 | 25.2644 | 25.2636 | 25.2628 | 25.2604 | 25.2563 | 25.2523 | 25.2474 | 25.2425 | 25.2376 | 25.2328 | 25.2085 | 25.1841 | 25.1595 | 25.3182 | 25.3175 | 25.3169 | 25.3162 | 25.3141 | 25.3107 | 25.3072 | 25.3031 | 25.2989 | 25.2948 | 25.2907 | 25.27 | 25.2493 | 25.2283
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0.2 | 2.8791 | 2.8721 | 2.865 | 2.8549 | 2.8454 | 2.8358 | 2.8248 | 2.8131 | 2.8014 | 2.7897 | 2.7781 | 2.7177 | 2.6456 | 2.5532 | 2.86 | 2.8558 | 2.8518 | 2.8475 | 2.8438 | 2.8399 | 2.836 | 2.8316 | 2.8273 | 2.8229 | 2.8185 | 2.7939 | 2.7614 | 2.6543 | 2.86 | 2.8558 | 2.8518 | 2.8475 | 2.8438 | 2.8399 | 2.836 | 2.8316 | 2.8273 | 2.8229 | 2.8185 | 2.814 | 2.8093 | 2.8045
|  | INVERARAY | CT |  |  |  | 0.2 | 2.8791 | 2.8721 | 2.865 | 2.8549 | 2.8454 | 2.8358 | 2.8262 | 2.8161 | 2.806 | 2.7959 | 2.7858 | 2.7328 | 2.6713 | 2.5997 | 2.86 | 2.8558 | 2.8518 | 2.8475 | 2.8438 | 2.8399 | 2.836 | 2.8316 | 2.8273 | 2.8229 | 2.8185 | 2.7939 | 2.7614 | 2.719 | 2.86 | 2.8558 | 2.8518 | 2.8475 | 2.8438 | 2.8399 | 2.836 | 2.8316 | 2.8273 | 2.8229 | 2.8185 | 2.814 | 2.8093 | 2.8045
|  | INVERARAY | LW |  |  |  | 0.2 | 2.8826 | 2.8755 | 2.8689 | 2.8586 | 2.8474 | 2.8361 | 2.8248 | 2.8131 | 2.8014 | 2.7897 | 2.7781 | 2.7177 | 2.6456 | 2.5532 | 2.8651 | 2.8619 | 2.86 | 2.8577 | 2.8544 | 2.8509 | 2.8473 | 2.8441 | 2.8409 | 2.8376 | 2.8343 | 2.8134 | 2.7629 | 2.6543 | 2.8651 | 2.8619 | 2.86 | 2.8577 | 2.8544 | 2.8509 | 2.8473 | 2.8441 | 2.8409 | 2.8376 | 2.8343 | 2.8311 | 2.8274 | 2.8228
|  | INVERARAY | ST |  |  |  | 0.2 | 2.8891 | 2.8872 | 2.8855 | 2.8804 | 2.8752 | 2.87 | 2.8647 | 2.8598 | 2.8548 | 2.8499 | 2.8451 | 2.8211 | 2.7927 | 2.7669 | 2.8659 | 2.8647 | 2.8637 | 2.8625 | 2.8611 | 2.8597 | 2.8581 | 2.857 | 2.856 | 2.8549 | 2.8538 | 2.8485 | 2.8387 | 2.8315 | 2.8659 | 2.8647 | 2.8637 | 2.8625 | 2.8611 | 2.8597 | 2.8581 | 2.857 | 2.856 | 2.8549 | 2.8538 | 2.8485 | 2.8387 | 2.8315
|  | INVERARAY | FS |  |  |  | 0.2 | 2.8908 | 2.8904 | 2.8888 | 2.8872 | 2.8853 | 2.8816 | 2.8778 | 2.8739 | 2.8699 | 2.8659 | 2.8619 | 2.8425 | 2.821 | 2.7963 | 2.8676 | 2.8672 | 2.8664 | 2.8655 | 2.8647 | 2.8638 | 2.8629 | 2.8619 | 2.8609 | 2.8599 | 2.8588 | 2.8541 | 2.8472 | 2.8369 | 2.8676 | 2.8672 | 2.8664 | 2.8655 | 2.8647 | 2.8638 | 2.8629 | 2.8619 | 2.8609 | 2.8599 | 2.8588 | 2.8541 | 2.8472 | 2.8369
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0.015789 | 1.1149 | 1.0975 | 1.0795 | 1.0609 | 1.0418 | 1.0225 | 1.0035 | 0.98441 | 0.96533 | 0.94628 | 0.92642 | 0.81857 | 0.6876 | 0.53276 | 1.1083 | 1.088 | 1.0658 | 1.0406 | 1.0152 | 0.98971 | 0.96521 | 0.94057 | 0.91597 | 0.89146 | 0.8662 | 0.73185 | 0.57609 | 0.39824 | 1.0284 | 1.0082 | 0.98616 | 0.96128 | 0.93614 | 0.91095 | 0.88669 | 0.8623 | 0.83794 | 0.81368 | 0.78866 | 0.76367 | 0.73735 | 0.71097
|  | INVERARITY | CT |  |  |  | 0.015789 | 1.1149 | 1.0975 | 1.0795 | 1.0609 | 1.0418 | 1.0225 | 1.0035 | 0.98441 | 0.96533 | 0.94628 | 0.92642 | 0.81857 | 0.6876 | 0.53276 | 1.1083 | 1.088 | 1.0658 | 1.0406 | 1.0152 | 0.98971 | 0.96521 | 0.94057 | 0.91597 | 0.89146 | 0.8662 | 0.73185 | 0.57609 | 0.39824 | 1.0284 | 1.0082 | 0.98616 | 0.96128 | 0.93614 | 0.91095 | 0.88669 | 0.8623 | 0.83794 | 0.81368 | 0.78866 | 0.76367 | 0.73735 | 0.71097
|  | INVERARITY | LW |  |  |  | 0.015789 | 1.1387 | 1.1274 | 1.1173 | 1.1037 | 1.0901 | 1.0756 | 1.0601 | 1.0454 | 1.0298 | 1.0142 | 0.99901 | 0.91078 | 0.79536 | 0.64017 | 1.1309 | 1.115 | 1.0991 | 1.0764 | 1.0544 | 1.0317 | 1.0083 | 0.9854 | 0.96173 | 0.93816 | 0.91572 | 0.79178 | 0.64036 | 0.4497 | 1.0511 | 1.0353 | 1.0197 | 0.99735 | 0.97572 | 0.95342 | 0.93042 | 0.90784 | 0.88453 | 0.86132 | 0.8392 | 0.81642 | 0.79294 | 0.76852
|  | INVERARITY | ST |  |  |  | 0.015789 | 1.1467 | 1.1423 | 1.1383 | 1.1321 | 1.1249 | 1.1175 | 1.1101 | 1.1034 | 1.0975 | 1.0917 | 1.086 | 1.0552 | 1.0178 | 0.98132 | 1.1446 | 1.1396 | 1.1348 | 1.1245 | 1.1133 | 1.1021 | 1.0909 | 1.0802 | 1.0704 | 1.0607 | 1.0512 | 1.0022 | 0.94966 | 0.89906 | 1.0645 | 1.0595 | 1.0548 | 1.0446 | 1.0336 | 1.0225 | 1.0115 | 1.001 | 0.99139 | 0.9819 | 0.97253 | 0.92438 | 0.87247 | 0.8225
|  | INVERARITY | FS |  |  |  | 0.015789 | 1.1493 | 1.1471 | 1.1445 | 1.1415 | 1.138 | 1.134 | 1.1301 | 1.1259 | 1.1216 | 1.1173 | 1.113 | 1.0916 | 1.0694 | 1.0425 | 1.1475 | 1.1452 | 1.1425 | 1.1387 | 1.1333 | 1.1268 | 1.1202 | 1.1132 | 1.1061 | 1.099 | 1.0919 | 1.0566 | 1.0242 | 0.98758 | 1.0674 | 1.0651 | 1.0624 | 1.0586 | 1.0533 | 1.0469 | 1.0404 | 1.0335 | 1.0266 | 1.0196 | 1.0126 | 0.97793 | 0.946 | 0.9098
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 0.0010526 | 2.5848 | 2.5669 | 2.5494 | 2.5319 | 2.5137 | 2.4949 | 2.4758 | 2.4575 | 2.4387 | 2.4195 | 2.3996 | 2.2885 | 2.149 | 1.9766 | 2.5474 | 2.5244 | 2.5002 | 2.4713 | 2.442 | 2.4126 | 2.3832 | 2.3543 | 2.3255 | 2.2969 | 2.2676 | 2.1112 | 1.9266 | 1.711 | 2.6369 | 2.6167 | 2.5954 | 2.5661 | 2.5364 | 2.5067 | 2.477 | 2.4478 | 2.4186 | 2.3897 | 2.36 | 2.3305 | 2.2994 | 2.2674
|  | INVERARNIE | CT |  |  |  | 0.0010526 | 2.5848 | 2.5669 | 2.5494 | 2.5319 | 2.5137 | 2.4949 | 2.4758 | 2.4575 | 2.4387 | 2.4195 | 2.3996 | 2.2885 | 2.149 | 1.9766 | 2.5474 | 2.5244 | 2.5002 | 2.4713 | 2.442 | 2.4126 | 2.3832 | 2.3543 | 2.3255 | 2.2969 | 2.2676 | 2.1112 | 1.9266 | 1.711 | 2.6369 | 2.6167 | 2.5954 | 2.5661 | 2.5364 | 2.5067 | 2.477 | 2.4478 | 2.4186 | 2.3897 | 2.36 | 2.3305 | 2.2994 | 2.2674
|  | INVERARNIE | LW |  |  |  | 0.0010526 | 2.61 | 2.5975 | 2.5888 | 2.5778 | 2.5652 | 2.5522 | 2.5373 | 2.5226 | 2.5079 | 2.4923 | 2.4768 | 2.3854 | 2.2601 | 2.074 | 2.5712 | 2.5512 | 2.5338 | 2.5067 | 2.4784 | 2.4504 | 2.4219 | 2.3934 | 2.365 | 2.3361 | 2.3075 | 2.1526 | 1.9637 | 1.7177 | 2.6615 | 2.6456 | 2.6287 | 2.6011 | 2.5723 | 2.5439 | 2.5149 | 2.4859 | 2.4571 | 2.4277 | 2.3987 | 2.37 | 2.3394 | 2.3078
|  | INVERARNIE | ST |  |  |  | 0.0010526 | 2.6159 | 2.6116 | 2.6077 | 2.6031 | 2.5973 | 2.5913 | 2.585 | 2.58 | 2.575 | 2.5701 | 2.5652 | 2.5402 | 2.5024 | 2.4682 | 2.5872 | 2.5825 | 2.5784 | 2.5663 | 2.5531 | 2.5401 | 2.5271 | 2.5149 | 2.5029 | 2.4911 | 2.4794 | 2.4237 | 2.3586 | 2.2983 | 2.672 | 2.6675 | 2.6635 | 2.6555 | 2.6463 | 2.6352 | 2.6219 | 2.6095 | 2.5973 | 2.5853 | 2.5734 | 2.5167 | 2.4507 | 2.3895
|  | INVERARNIE | FS |  |  |  | 0.0010526 | 2.6185 | 2.6159 | 2.6133 | 2.6108 | 2.6082 | 2.6055 | 2.6029 | 2.6 | 2.5971 | 2.5941 | 2.591 | 2.5737 | 2.553 | 2.5238 | 2.5904 | 2.5876 | 2.5848 | 2.5817 | 2.5765 | 2.5695 | 2.5624 | 2.5545 | 2.5465 | 2.5386 | 2.5306 | 2.4863 | 2.4437 | 2.3953 | 2.6748 | 2.6722 | 2.6695 | 2.6667 | 2.6629 | 2.6582 | 2.6536 | 2.6484 | 2.6416 | 2.6335 | 2.6254 | 2.5803 | 2.5369 | 2.4879
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 0.21895 | 6.5664 | 6.4619 | 6.3757 | 6.2503 | 6.1251 | 6.0012 | 5.8796 | 5.7581 | 5.6394 | 5.5227 | 5.412 | 4.8524 | 4.2123 | 3.3559 | 5.3011 | 5.1828 | 5.0762 | 4.9248 | 4.7748 | 4.6295 | 4.4918 | 4.353 | 4.2176 | 4.0848 | 3.959 | 3.33 | 2.624 | 1.7039 | 5.8369 | 5.7361 | 5.6671 | 5.5565 | 5.4454 | 5.3368 | 5.2324 | 5.1294 | 5.0284 | 4.9289 | 4.8343 | 4.7428 | 4.646 | 4.5421
|  | INVERBERVIE | CT |  |  |  | 0.21895 | 6.5686 | 6.4619 | 6.3943 | 6.3028 | 6.2074 | 6.1104 | 6.0191 | 5.9323 | 5.8437 | 5.7568 | 5.6726 | 5.2358 | 4.742 | 4.1545 | 5.3098 | 5.1926 | 5.1133 | 5.0045 | 4.8919 | 4.7777 | 4.6712 | 4.5685 | 4.4679 | 4.3699 | 4.2752 | 3.7883 | 3.2479 | 2.6156 | 5.8369 | 5.7361 | 5.6752 | 5.5935 | 5.508 | 5.4207 | 5.338 | 5.2603 | 5.1838 | 5.1087 | 5.0357 | 4.9627 | 4.8852 | 4.8085
|  | INVERBERVIE | LW |  |  |  | 0.21895 | 6.5664 | 6.4642 | 6.3757 | 6.2503 | 6.1251 | 6.0012 | 5.8796 | 5.7581 | 5.6394 | 5.5227 | 5.412 | 4.8524 | 4.2123 | 3.3559 | 5.3011 | 5.1828 | 5.0762 | 4.9248 | 4.7748 | 4.6295 | 4.4918 | 4.353 | 4.2176 | 4.0848 | 3.959 | 3.33 | 2.624 | 1.7039 | 5.8383 | 5.7453 | 5.6671 | 5.5565 | 5.4454 | 5.3368 | 5.2324 | 5.1294 | 5.0284 | 4.9289 | 4.8343 | 4.7428 | 4.646 | 4.5421
|  | INVERBERVIE | ST |  |  |  | 0.21895 | 6.637 | 6.6191 | 6.6024 | 6.5547 | 6.5053 | 6.4552 | 6.4063 | 6.3605 | 6.3144 | 6.2699 | 6.2268 | 6.0224 | 5.7719 | 5.5623 | 5.3894 | 5.3689 | 5.3492 | 5.2914 | 5.2317 | 5.1714 | 5.1129 | 5.0567 | 5.0003 | 4.9456 | 4.8928 | 4.6465 | 4.3661 | 4.1279 | 5.899 | 5.8825 | 5.8675 | 5.8256 | 5.7821 | 5.7377 | 5.6943 | 5.6543 | 5.6142 | 5.5754 | 5.5379 | 5.3625 | 5.1438 | 4.9647
|  | INVERBERVIE | FS |  |  |  | 0.21895 | 6.6424 | 6.6289 | 6.6181 | 6.6046 | 6.5852 | 6.5559 | 6.5266 | 6.4922 | 6.4569 | 6.4221 | 6.388 | 6.2291 | 6.0576 | 5.8443 | 5.3958 | 5.3804 | 5.3673 | 5.351 | 5.3272 | 5.2907 | 5.2545 | 5.212 | 5.1685 | 5.1257 | 5.0836 | 4.8871 | 4.6854 | 4.4489 | 5.9038 | 5.8914 | 5.8818 | 5.87 | 5.8531 | 5.8278 | 5.8025 | 5.7727 | 5.742 | 5.7118 | 5.6823 | 5.5447 | 5.3937 | 5.2052
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | YES | 0 | 0.24486 | 0.24306 | 0.24226 | 0.24115 | 0.23989 | 0.23835 | 0.23407 | 0.22997 | 0.22591 | 0.22189 | 0.21795 | 0.19736 | 0.17299 | 0.13949 | 0.22984 | 0.22799 | 0.22712 | 0.22584 | 0.22441 | 0.22289 | 0.2213 | 0.21675 | 0.21218 | 0.20765 | 0.20321 | 0.1802 | 0.15341 | 0.11756 | 0.23336 | 0.23157 | 0.23077 | 0.22965 | 0.22839 | 0.22493 | 0.22039 | 0.21603 | 0.21172 | 0.20744 | 0.20325 | 0.19912 | 0.19476 | 0.19036
|  | INVERBROOM | CT |  |  |  | 0 | 0.24486 | 0.24426 | 0.24375 | 0.24306 | 0.24222 | 0.24124 | 0.24019 | 0.23951 | 0.23881 | 0.23736 | 0.23523 | 0.22379 | 0.20983 | 0.19247 | 0.22986 | 0.22921 | 0.22866 | 0.22788 | 0.22695 | 0.22589 | 0.22477 | 0.22401 | 0.22323 | 0.22245 | 0.22166 | 0.21003 | 0.19487 | 0.17636 | 0.23336 | 0.23276 | 0.23226 | 0.23157 | 0.23072 | 0.22975 | 0.2287 | 0.22801 | 0.22618 | 0.22389 | 0.22162 | 0.21937 | 0.21696 | 0.21453
|  | INVERBROOM | LW |  |  |  | 0 | 0.24486 | 0.24306 | 0.24226 | 0.24115 | 0.23989 | 0.23835 | 0.23407 | 0.22997 | 0.22591 | 0.22189 | 0.21795 | 0.19736 | 0.17299 | 0.13949 | 0.22984 | 0.22799 | 0.22712 | 0.22584 | 0.22441 | 0.22289 | 0.2213 | 0.21675 | 0.21218 | 0.20765 | 0.20321 | 0.1802 | 0.15341 | 0.11756 | 0.23336 | 0.23157 | 0.23077 | 0.22965 | 0.22839 | 0.22493 | 0.22039 | 0.21603 | 0.21172 | 0.20744 | 0.20325 | 0.19912 | 0.19476 | 0.19036
|  | INVERBROOM | ST |  |  |  | 0 | 0.24486 | 0.24464 | 0.24454 | 0.24425 | 0.24391 | 0.24351 | 0.24306 | 0.24289 | 0.24272 | 0.24256 | 0.24241 | 0.24171 | 0.23484 | 0.22939 | 0.22992 | 0.2297 | 0.22959 | 0.22926 | 0.22886 | 0.2284 | 0.2279 | 0.22768 | 0.22746 | 0.22725 | 0.22704 | 0.22612 | 0.22206 | 0.21595 | 0.23336 | 0.23315 | 0.23304 | 0.23276 | 0.23242 | 0.23201 | 0.23157 | 0.2314 | 0.23123 | 0.23107 | 0.23091 | 0.22887 | 0.22112 | 0.21534
|  | INVERBROOM | FS |  |  |  | 0 | 0.24486 | 0.24466 | 0.24466 | 0.24464 | 0.24463 | 0.24461 | 0.24459 | 0.2445 | 0.24441 | 0.2443 | 0.24419 | 0.24389 | 0.24235 | 0.2367 | 0.22993 | 0.22973 | 0.22972 | 0.22971 | 0.22967 | 0.22962 | 0.22956 | 0.22943 | 0.2293 | 0.22915 | 0.229 | 0.2285 | 0.22677 | 0.22327 | 0.23336 | 0.23317 | 0.23316 | 0.23315 | 0.23313 | 0.23311 | 0.23309 | 0.23301 | 0.23291 | 0.23281 | 0.2327 | 0.2324 | 0.22987 | 0.22309
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 1.1504 | 1.1461 | 1.142 | 1.1375 | 1.1329 | 1.128 | 1.123 | 1.1186 | 1.1141 | 1.1097 | 1.1052 | 1.0787 | 1.0257 | 0.95251 | 1.072 | 1.0677 | 1.0636 | 1.0591 | 1.0545 | 1.0496 | 1.0446 | 1.0402 | 1.0325 | 1.0235 | 1.0146 | 0.96637 | 0.90602 | 0.82751 | 1.0915 | 1.0872 | 1.083 | 1.0786 | 1.074 | 1.0691 | 1.0641 | 1.0597 | 1.054 | 1.0454 | 1.0368 | 1.0282 | 1.0194 | 1.0097
|  | INVERGARRY | CT |  |  |  | 0 | 1.1504 | 1.1461 | 1.142 | 1.1375 | 1.1329 | 1.128 | 1.123 | 1.1186 | 1.1141 | 1.1097 | 1.1052 | 1.0787 | 1.0257 | 0.96366 | 1.072 | 1.0677 | 1.0636 | 1.0591 | 1.0545 | 1.0496 | 1.0446 | 1.0402 | 1.0325 | 1.0235 | 1.0146 | 0.96637 | 0.90966 | 0.84403 | 1.0915 | 1.0872 | 1.083 | 1.0786 | 1.074 | 1.0691 | 1.0641 | 1.0597 | 1.054 | 1.0454 | 1.0368 | 1.0282 | 1.0194 | 1.0097
|  | INVERGARRY | LW |  |  |  | 0 | 1.1563 | 1.1527 | 1.1507 | 1.1474 | 1.1438 | 1.14 | 1.1362 | 1.1328 | 1.1294 | 1.126 | 1.1226 | 1.0825 | 1.0264 | 0.95251 | 1.0779 | 1.0744 | 1.0723 | 1.069 | 1.0654 | 1.0616 | 1.0534 | 1.0443 | 1.0351 | 1.0261 | 1.0171 | 0.96675 | 0.90602 | 0.82751 | 1.0974 | 1.0938 | 1.0918 | 1.0885 | 1.0849 | 1.0811 | 1.075 | 1.0663 | 1.0576 | 1.0489 | 1.0404 | 1.0311 | 1.0212 | 1.0112
|  | INVERGARRY | ST |  |  |  | 0 | 1.1571 | 1.1559 | 1.1549 | 1.1537 | 1.1523 | 1.1508 | 1.1493 | 1.1482 | 1.1471 | 1.146 | 1.1449 | 1.1396 | 1.13 | 1.123 | 1.0787 | 1.0775 | 1.0765 | 1.0753 | 1.0739 | 1.0724 | 1.0709 | 1.0698 | 1.0687 | 1.0676 | 1.0665 | 1.0565 | 1.0348 | 1.0162 | 1.0982 | 1.097 | 1.096 | 1.0947 | 1.0934 | 1.0919 | 1.0904 | 1.0893 | 1.0881 | 1.0871 | 1.086 | 1.0781 | 1.0573 | 1.0396
|  | INVERGARRY | FS |  |  |  | 0 | 1.158 | 1.1568 | 1.156 | 1.1551 | 1.1542 | 1.1534 | 1.1525 | 1.1515 | 1.1505 | 1.1495 | 1.1485 | 1.1438 | 1.1371 | 1.1275 | 1.0796 | 1.0784 | 1.0776 | 1.0767 | 1.0758 | 1.075 | 1.0741 | 1.0731 | 1.0721 | 1.0711 | 1.0701 | 1.0654 | 1.0516 | 1.0315 | 1.0991 | 1.0979 | 1.097 | 1.0962 | 1.0953 | 1.0944 | 1.0936 | 1.0926 | 1.0916 | 1.0906 | 1.0896 | 1.0849 | 1.0734 | 1.0541
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 0.052632 | 15.0332 | 15.0053 | 14.9511 | 14.8541 | 14.7544 | 14.6551 | 14.5557 | 14.4591 | 14.363 | 14.2672 | 14.1727 | 13.6658 | 13.0484 | 12.1897 | 15.577 | 15.5491 | 15.5294 | 15.5029 | 15.4722 | 15.439 | 15.4032 | 15.3742 | 15.3447 | 15.2841 | 15.1784 | 14.6155 | 13.9404 | 13.0241 | 14.7992 | 14.725 | 14.6595 | 14.5502 | 14.4384 | 14.3277 | 14.2171 | 14.1088 | 14.001 | 13.8938 | 13.788 | 13.6825 | 13.5699 | 13.4563
|  | INVERGORDON | CT |  |  |  | 0.052632 | 15.0332 | 15.0122 | 14.9872 | 14.9155 | 14.8413 | 14.7669 | 14.6924 | 14.6216 | 14.5507 | 14.4803 | 14.4103 | 14.0336 | 13.5738 | 13.0117 | 15.577 | 15.5561 | 15.5372 | 15.5143 | 15.4879 | 15.4591 | 15.4286 | 15.4055 | 15.3818 | 15.3579 | 15.3339 | 15.0329 | 14.5327 | 13.9304 | 14.7992 | 14.7511 | 14.7006 | 14.6203 | 14.5378 | 14.4554 | 14.3733 | 14.2941 | 14.215 | 14.1365 | 14.0585 | 13.9805 | 13.8965 | 13.813
|  | INVERGORDON | LW |  |  |  | 0.052632 | 15.0467 | 15.0053 | 14.9511 | 14.8541 | 14.7544 | 14.6551 | 14.5557 | 14.4591 | 14.363 | 14.2672 | 14.1727 | 13.6658 | 13.0484 | 12.1897 | 15.5905 | 15.5491 | 15.5294 | 15.5029 | 15.4722 | 15.439 | 15.4032 | 15.3742 | 15.3447 | 15.2841 | 15.1784 | 14.6155 | 13.9404 | 13.0241 | 14.8042 | 14.725 | 14.6595 | 14.5502 | 14.4384 | 14.3277 | 14.2171 | 14.1088 | 14.001 | 13.8938 | 13.788 | 13.6825 | 13.5699 | 13.4563
|  | INVERGORDON | ST |  |  |  | 0.052632 | 15.0483 | 15.0415 | 15.0373 | 15.0289 | 15.0183 | 14.9882 | 14.9463 | 14.9081 | 14.8704 | 14.8336 | 14.7975 | 14.6245 | 14.3888 | 14.1961 | 15.5922 | 15.5853 | 15.5811 | 15.5728 | 15.5621 | 15.5509 | 15.5386 | 15.533 | 15.5273 | 15.5218 | 15.5164 | 15.4904 | 15.3939 | 15.1968 | 14.8358 | 14.8278 | 14.8225 | 14.7941 | 14.7465 | 14.6994 | 14.6522 | 14.6083 | 14.5651 | 14.5228 | 14.4814 | 14.2828 | 14.0228 | 13.8063
|  | INVERGORDON | FS |  |  |  | 0.052632 | 15.05 | 15.0442 | 15.0422 | 15.0403 | 15.0382 | 15.036 | 15.0337 | 15.026 | 14.9975 | 14.9689 | 14.9401 | 14.8022 | 14.6362 | 14.4264 | 15.5938 | 15.588 | 15.5861 | 15.5841 | 15.582 | 15.5798 | 15.5776 | 15.5746 | 15.5713 | 15.5678 | 15.564 | 15.5488 | 15.5 | 15.4031 | 14.838 | 14.8314 | 14.8287 | 14.8251 | 14.8187 | 14.7999 | 14.7722 | 14.7396 | 14.7067 | 14.6737 | 14.6406 | 14.4813 | 14.2948 | 14.0653
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 0.02 | 16.1219 | 16.0807 | 16.0531 | 16.0151 | 15.9725 | 15.9255 | 15.8761 | 15.8363 | 15.795 | 15.7531 | 15.7119 | 15.4547 | 14.9175 | 13.7141 | 15.2675 | 15.2232 | 15.1925 | 15.1489 | 15.1008 | 15.0485 | 14.9941 | 14.9488 | 14.9022 | 14.8551 | 14.8086 | 14.5258 | 13.8343 | 12.5183 | 15.7605 | 15.7194 | 15.6918 | 15.6538 | 15.6112 | 15.5641 | 15.5148 | 15.4749 | 15.4337 | 15.3918 | 15.3505 | 15.3088 | 15.2461 | 15.0797
|  | INVERLOCHY | CT |  |  |  | 0.02 | 16.1219 | 16.093 | 16.0669 | 16.0352 | 15.9994 | 15.9591 | 15.9165 | 15.8846 | 15.8519 | 15.819 | 15.7859 | 15.5778 | 15.267 | 14.8126 | 15.2675 | 15.2366 | 15.2084 | 15.1728 | 15.1332 | 15.0892 | 15.0431 | 15.0074 | 14.971 | 14.9344 | 14.8976 | 14.6715 | 14.3425 | 13.87 | 15.7605 | 15.7316 | 15.7056 | 15.6738 | 15.6381 | 15.5978 | 15.5552 | 15.5233 | 15.4906 | 15.4577 | 15.4246 | 15.3905 | 15.3495 | 15.3066
|  | INVERLOCHY | LW |  |  |  | 0.02 | 16.1387 | 16.0807 | 16.0531 | 16.0151 | 15.9725 | 15.9255 | 15.8761 | 15.8363 | 15.795 | 15.7531 | 15.7119 | 15.4547 | 14.9175 | 13.7141 | 15.2837 | 15.2232 | 15.1925 | 15.1489 | 15.1008 | 15.0485 | 14.9941 | 14.9488 | 14.9022 | 14.8551 | 14.8086 | 14.5258 | 13.8343 | 12.5183 | 15.7774 | 15.7194 | 15.6918 | 15.6538 | 15.6112 | 15.5641 | 15.5148 | 15.4749 | 15.4337 | 15.3918 | 15.3505 | 15.3088 | 15.2461 | 15.0797
|  | INVERLOCHY | ST |  |  |  | 0.02 | 16.1421 | 16.1324 | 16.1264 | 16.1146 | 16.1008 | 16.085 | 16.0677 | 16.0596 | 16.0515 | 16.0437 | 16.0361 | 16.0002 | 15.8712 | 15.7951 | 15.2906 | 15.2807 | 15.2745 | 15.2601 | 15.2437 | 15.2255 | 15.2059 | 15.1952 | 15.1846 | 15.1742 | 15.1641 | 15.1165 | 14.9763 | 14.8892 | 15.7808 | 15.771 | 15.765 | 15.7532 | 15.7394 | 15.7236 | 15.7063 | 15.6983 | 15.6902 | 15.6823 | 15.6747 | 15.6388 | 15.5098 | 15.4337
|  | INVERLOCHY | FS |  |  |  | 0.02 | 16.1438 | 16.136 | 16.1341 | 16.132 | 16.1298 | 16.1273 | 16.1249 | 16.1202 | 16.1152 | 16.1099 | 16.1042 | 16.0852 | 16.0216 | 15.8924 | 15.2924 | 15.2845 | 15.2823 | 15.2799 | 15.2769 | 15.2727 | 15.2685 | 15.2619 | 15.2549 | 15.2476 | 15.2399 | 15.2112 | 15.1384 | 15.0004 | 15.7824 | 15.7747 | 15.7727 | 15.7707 | 15.7684 | 15.766 | 15.7635 | 15.7589 | 15.7539 | 15.7485 | 15.7429 | 15.7238 | 15.6602 | 15.5311
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0 | 6.2204 | 6.215 | 6.21 | 6.2044 | 6.1982 | 6.1916 | 6.1847 | 6.171 | 6.1521 | 6.1332 | 6.1145 | 6.0127 | 5.8926 | 5.735 | 6.0212 | 6.0159 | 6.0108 | 6.0052 | 5.999 | 5.9924 | 5.9856 | 5.9799 | 5.9741 | 5.9684 | 5.9626 | 5.8523 | 5.7205 | 5.5512 | 6.04 | 6.0347 | 6.0297 | 6.024 | 6.0179 | 6.0113 | 6.0044 | 5.9987 | 5.9794 | 5.9582 | 5.9372 | 5.9156 | 5.8929 | 5.87
|  | INVERNEIL | CT |  |  |  | 0 | 6.2204 | 6.215 | 6.21 | 6.2044 | 6.1982 | 6.1916 | 6.1847 | 6.1791 | 6.1733 | 6.1599 | 6.1453 | 6.0662 | 5.9732 | 5.8629 | 6.0212 | 6.0159 | 6.0108 | 6.0052 | 5.999 | 5.9924 | 5.9856 | 5.9799 | 5.9741 | 5.9684 | 5.9626 | 5.9166 | 5.8158 | 5.6979 | 6.04 | 6.0347 | 6.0297 | 6.024 | 6.0179 | 6.0113 | 6.0044 | 5.9987 | 5.993 | 5.9872 | 5.975 | 5.9589 | 5.942 | 5.9242
|  | INVERNEIL | LW |  |  |  | 0 | 6.2263 | 6.2197 | 6.2163 | 6.2111 | 6.2054 | 6.1993 | 6.19 | 6.171 | 6.1521 | 6.1332 | 6.1145 | 6.0127 | 5.8926 | 5.735 | 6.0271 | 6.0205 | 6.0171 | 6.0119 | 6.0062 | 6.0001 | 5.9937 | 5.9884 | 5.983 | 5.9775 | 5.9656 | 5.8523 | 5.7205 | 5.5512 | 6.0459 | 6.0394 | 6.036 | 6.0307 | 6.025 | 6.0189 | 6.0126 | 6.0007 | 5.9794 | 5.9582 | 5.9372 | 5.9156 | 5.8929 | 5.87
|  | INVERNEIL | ST |  |  |  | 0 | 6.2271 | 6.2255 | 6.2243 | 6.2225 | 6.2204 | 6.2182 | 6.2158 | 6.2144 | 6.2129 | 6.2115 | 6.2101 | 6.1952 | 6.1483 | 6.1078 | 6.0279 | 6.0263 | 6.0251 | 6.0233 | 6.0213 | 6.019 | 6.0166 | 6.0152 | 6.0138 | 6.0123 | 6.011 | 6.0043 | 5.9876 | 5.9569 | 6.0468 | 6.0452 | 6.044 | 6.0421 | 6.0401 | 6.0378 | 6.0354 | 6.034 | 6.0326 | 6.0312 | 6.0298 | 6.0231 | 5.9742 | 5.9285
|  | INVERNEIL | FS |  |  |  | 0 | 6.2288 | 6.2281 | 6.2272 | 6.2263 | 6.2254 | 6.2245 | 6.2236 | 6.2224 | 6.2212 | 6.22 | 6.2187 | 6.2134 | 6.1953 | 6.1545 | 6.0296 | 6.0289 | 6.028 | 6.0271 | 6.0262 | 6.0253 | 6.0244 | 6.0232 | 6.022 | 6.0208 | 6.0195 | 6.0142 | 6.0041 | 5.9869 | 6.0485 | 6.0477 | 6.0468 | 6.046 | 6.0451 | 6.0441 | 6.0432 | 6.0421 | 6.0409 | 6.0396 | 6.0384 | 6.033 | 6.0229 | 5.9816
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 0.35263 | 17.5549 | 17.4832 | 17.4424 | 17.3868 | 17.3242 | 17.2552 | 17.1827 | 17.124 | 17.0644 | 17.004 | 16.9445 | 16.2205 | 15.031 | 13.3459 | 16.3735 | 16.3018 | 16.2586 | 16.0436 | 15.8253 | 15.6085 | 15.3942 | 15.1843 | 14.9758 | 14.7688 | 14.5651 | 13.4855 | 12.1831 | 10.3858 | 16.8274 | 16.7557 | 16.7149 | 16.6593 | 16.5967 | 16.5277 | 16.4552 | 16.3591 | 16.1724 | 15.9855 | 15.7842 | 15.5848 | 15.371 | 15.1544
|  | INVERNESS | CT |  |  |  | 0.35263 | 17.5549 | 17.518 | 17.4855 | 17.4444 | 17.396 | 17.3408 | 17.282 | 17.2407 | 17.1973 | 17.1537 | 17.1097 | 16.8324 | 16.1604 | 15.1035 | 16.3735 | 16.3367 | 16.3042 | 16.2138 | 16.0565 | 15.898 | 15.7402 | 15.5927 | 15.4447 | 15.2981 | 15.1528 | 14.3792 | 13.4451 | 12.3107 | 16.8274 | 16.7905 | 16.758 | 16.7169 | 16.6685 | 16.6132 | 16.5545 | 16.5132 | 16.4698 | 16.4261 | 16.3302 | 16.1997 | 16.0591 | 15.9133
|  | INVERNESS | LW |  |  |  | 0.35263 | 17.5701 | 17.4832 | 17.4424 | 17.3868 | 17.3242 | 17.2552 | 17.1827 | 17.124 | 17.0644 | 17.004 | 16.9445 | 16.2205 | 15.031 | 13.3459 | 16.3887 | 16.3018 | 16.2586 | 16.0436 | 15.8253 | 15.6085 | 15.3942 | 15.1843 | 14.9758 | 14.7688 | 14.5651 | 13.4855 | 12.1831 | 10.3858 | 16.8425 | 16.7557 | 16.7149 | 16.6593 | 16.5967 | 16.5277 | 16.4552 | 16.3591 | 16.1724 | 15.9855 | 15.7842 | 15.5848 | 15.371 | 15.1544
|  | INVERNESS | ST |  |  |  | 0.35263 | 17.5734 | 17.56 | 17.5531 | 17.5374 | 17.5179 | 17.4954 | 17.4706 | 17.4597 | 17.4488 | 17.4382 | 17.428 | 17.3803 | 17.1917 | 17.0881 | 16.3921 | 16.3786 | 16.3718 | 16.3561 | 16.3365 | 16.314 | 16.2635 | 16.1801 | 16.0981 | 16.0181 | 15.9401 | 15.5733 | 15.0801 | 14.6816 | 16.8459 | 16.8325 | 16.8256 | 16.8099 | 16.7903 | 16.7678 | 16.743 | 16.7322 | 16.7212 | 16.7107 | 16.7005 | 16.6528 | 16.2801 | 15.9012
|  | INVERNESS | FS |  |  |  | 0.35263 | 17.5751 | 17.5639 | 17.5617 | 17.5595 | 17.557 | 17.5542 | 17.5513 | 17.5452 | 17.5385 | 17.5313 | 17.5236 | 17.4992 | 17.4077 | 17.2177 | 16.3937 | 16.3825 | 16.3804 | 16.3781 | 16.3756 | 16.3728 | 16.37 | 16.3638 | 16.3571 | 16.3113 | 16.2476 | 15.9501 | 15.6021 | 15.1717 | 16.8476 | 16.8363 | 16.8342 | 16.832 | 16.8295 | 16.8266 | 16.8238 | 16.8177 | 16.811 | 16.8038 | 16.7961 | 16.7717 | 16.6802 | 16.3621
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 0.26421 | 31.5702 | 31.4595 | 31.3893 | 31.2936 | 31.1853 | 30.5139 | 29.7095 | 28.8841 | 28.1056 | 27.3677 | 26.7163 | 23.7514 | 20.8111 | 17.2075 | 30.744 | 30.6333 | 30.5631 | 29.9411 | 28.8264 | 27.7801 | 26.8548 | 25.9006 | 25.0019 | 24.1514 | 23.4025 | 20.0243 | 16.737 | 12.8174 | 30.9099 | 30.7992 | 30.729 | 30.2938 | 29.2085 | 28.1893 | 27.2874 | 26.3581 | 25.4826 | 24.6539 | 23.9239 | 23.2669 | 22.595 | 21.9307
|  | INVERURIE | CT |  |  |  | 0.26421 | 31.5702 | 31.5005 | 31.439 | 31.3631 | 31.2749 | 31.176 | 31.0714 | 30.9943 | 30.6204 | 30.1094 | 29.6382 | 27.3893 | 25.2434 | 22.8418 | 30.744 | 30.6743 | 30.6128 | 30.5369 | 30.4487 | 29.9278 | 29.246 | 28.5794 | 27.9326 | 27.3449 | 26.8043 | 24.245 | 21.8524 | 19.222 | 30.9099 | 30.8402 | 30.7787 | 30.7028 | 30.6146 | 30.2775 | 29.6125 | 28.9631 | 28.3329 | 27.76 | 27.2329 | 26.7069 | 26.1864 | 25.6909
|  | INVERURIE | LW |  |  |  | 0.26421 | 31.6072 | 31.4595 | 31.3893 | 31.2936 | 31.1853 | 30.5139 | 29.7095 | 28.8841 | 28.1056 | 27.3677 | 26.7163 | 23.7514 | 20.8111 | 17.2075 | 30.7811 | 30.6333 | 30.5631 | 29.9411 | 28.8264 | 27.7801 | 26.8548 | 25.9006 | 25.0019 | 24.1514 | 23.4025 | 20.0243 | 16.737 | 12.8174 | 30.9469 | 30.7992 | 30.729 | 30.2938 | 29.2085 | 28.1893 | 27.2874 | 26.3581 | 25.4826 | 24.6539 | 23.9239 | 23.2669 | 22.595 | 21.9307
|  | INVERURIE | ST |  |  |  | 0.26421 | 31.6148 | 31.5915 | 31.5778 | 31.5493 | 31.5149 | 31.4756 | 31.4324 | 31.4125 | 31.3926 | 31.3732 | 31.3545 | 31.2655 | 30.0281 | 28.923 | 30.7886 | 30.7654 | 30.7516 | 30.7231 | 30.6887 | 30.6494 | 30.6062 | 30.5864 | 30.5664 | 30.5471 | 30.3663 | 28.7245 | 27.2298 | 25.9614 | 30.9545 | 30.9312 | 30.9175 | 30.889 | 30.8546 | 30.8152 | 30.7721 | 30.7522 | 30.7323 | 30.7129 | 30.6941 | 29.1119 | 27.6515 | 26.4146
|  | INVERURIE | FS |  |  |  | 0.26421 | 31.619 | 31.5992 | 31.5942 | 31.5891 | 31.5835 | 31.5774 | 31.5721 | 31.5613 | 31.5496 | 31.5371 | 31.5237 | 31.4769 | 31.3177 | 30.4374 | 30.7928 | 30.773 | 30.768 | 30.7629 | 30.7573 | 30.7512 | 30.746 | 30.7352 | 30.7235 | 30.7109 | 30.6975 | 30.095 | 28.9531 | 27.7028 | 30.9587 | 30.9389 | 30.9339 | 30.9288 | 30.9232 | 30.9171 | 30.9118 | 30.901 | 30.8893 | 30.8767 | 30.8634 | 30.4485 | 29.3353 | 28.1122
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0 | 2.66 | 2.6562 | 2.6545 | 2.6521 | 2.6494 | 2.6465 | 2.6432 | 2.6337 | 2.6243 | 2.615 | 2.6057 | 2.5533 | 2.49 | 2.4069 | 2.6163 | 2.6125 | 2.6108 | 2.6084 | 2.6057 | 2.5976 | 2.5856 | 2.5731 | 2.5607 | 2.5484 | 2.5362 | 2.4746 | 2.4039 | 2.3135 | 2.6283 | 2.6245 | 2.6228 | 2.6205 | 2.6109 | 2.5988 | 2.5869 | 2.5744 | 2.562 | 2.5497 | 2.5376 | 2.5257 | 2.5132 | 2.5006
|  | KALNAKIL | CT |  |  |  | 0 | 2.66 | 2.6587 | 2.6576 | 2.6562 | 2.6544 | 2.6523 | 2.65 | 2.6485 | 2.647 | 2.6412 | 2.6353 | 2.6036 | 2.5633 | 2.5141 | 2.6163 | 2.615 | 2.6139 | 2.6125 | 2.6107 | 2.6086 | 2.606 | 2.5979 | 2.5898 | 2.5819 | 2.574 | 2.533 | 2.4865 | 2.4327 | 2.6283 | 2.6271 | 2.626 | 2.6245 | 2.6227 | 2.6158 | 2.6072 | 2.5992 | 2.5911 | 2.5832 | 2.5753 | 2.5675 | 2.5593 | 2.5511
|  | KALNAKIL | LW |  |  |  | 0 | 2.66 | 2.6562 | 2.6545 | 2.6521 | 2.6494 | 2.6465 | 2.6432 | 2.6337 | 2.6243 | 2.615 | 2.6057 | 2.5533 | 2.49 | 2.4069 | 2.6163 | 2.6125 | 2.6108 | 2.6084 | 2.6057 | 2.5976 | 2.5856 | 2.5731 | 2.5607 | 2.5484 | 2.5362 | 2.4746 | 2.4039 | 2.3135 | 2.6283 | 2.6245 | 2.6228 | 2.6205 | 2.6109 | 2.5988 | 2.5869 | 2.5744 | 2.562 | 2.5497 | 2.5376 | 2.5257 | 2.5132 | 2.5006
|  | KALNAKIL | ST |  |  |  | 0 | 2.66 | 2.6595 | 2.6593 | 2.6587 | 2.658 | 2.6571 | 2.6561 | 2.6558 | 2.6554 | 2.6551 | 2.6547 | 2.6511 | 2.6303 | 2.6134 | 2.6163 | 2.6158 | 2.6156 | 2.615 | 2.6143 | 2.6134 | 2.6124 | 2.6121 | 2.6117 | 2.6114 | 2.611 | 2.5927 | 2.566 | 2.5436 | 2.6283 | 2.6279 | 2.6276 | 2.627 | 2.6263 | 2.6254 | 2.6245 | 2.6241 | 2.6237 | 2.6202 | 2.6157 | 2.594 | 2.5674 | 2.545
|  | KALNAKIL | FS |  |  |  | 0 | 2.66 | 2.6596 | 2.6596 | 2.6595 | 2.6595 | 2.6595 | 2.6594 | 2.6592 | 2.659 | 2.6588 | 2.6586 | 2.6579 | 2.6501 | 2.6309 | 2.6163 | 2.6159 | 2.6159 | 2.6158 | 2.6158 | 2.6158 | 2.6157 | 2.6155 | 2.6153 | 2.6151 | 2.6149 | 2.6119 | 2.5907 | 2.5663 | 2.6283 | 2.6279 | 2.6279 | 2.6279 | 2.6278 | 2.6278 | 2.6278 | 2.6276 | 2.6274 | 2.6271 | 2.6269 | 2.6131 | 2.592 | 2.5677
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0.0052632 | 2.7915 | 2.782 | 2.7778 | 2.772 | 2.7461 | 2.7199 | 2.6945 | 2.6687 | 2.6437 | 2.6188 | 2.5942 | 2.4667 | 2.2973 | 2.0697 | 2.7189 | 2.7088 | 2.7038 | 2.6967 | 2.6887 | 2.6802 | 2.6561 | 2.6224 | 2.5899 | 2.5575 | 2.5255 | 2.3624 | 2.1707 | 1.923 | 2.7204 | 2.7109 | 2.7067 | 2.7009 | 2.6942 | 2.6863 | 2.6556 | 2.6238 | 2.5917 | 2.5593 | 2.5273 | 2.4957 | 2.4632 | 2.4305
|  | KAMES | CT |  |  |  | 0.0052632 | 2.7915 | 2.7881 | 2.7853 | 2.7815 | 2.7768 | 2.7625 | 2.7444 | 2.7273 | 2.7101 | 2.6931 | 2.6761 | 2.5853 | 2.4771 | 2.3394 | 2.7191 | 2.7153 | 2.712 | 2.7073 | 2.7017 | 2.6954 | 2.6886 | 2.6839 | 2.675 | 2.6529 | 2.6307 | 2.5144 | 2.3803 | 2.2231 | 2.7204 | 2.7171 | 2.7142 | 2.7104 | 2.7057 | 2.7002 | 2.6943 | 2.6904 | 2.6738 | 2.6529 | 2.6319 | 2.6104 | 2.5871 | 2.5636
|  | KAMES | LW |  |  |  | 0.0052632 | 2.7915 | 2.782 | 2.7778 | 2.772 | 2.7461 | 2.7199 | 2.6945 | 2.6687 | 2.6437 | 2.6188 | 2.5942 | 2.4667 | 2.2973 | 2.0697 | 2.7189 | 2.7088 | 2.7038 | 2.6967 | 2.6887 | 2.6802 | 2.6561 | 2.6224 | 2.5899 | 2.5575 | 2.5255 | 2.3624 | 2.1707 | 1.923 | 2.7204 | 2.7109 | 2.7067 | 2.7009 | 2.6942 | 2.6863 | 2.6556 | 2.6238 | 2.5917 | 2.5593 | 2.5273 | 2.4957 | 2.4632 | 2.4305
|  | KAMES | ST |  |  |  | 0.0052632 | 2.7915 | 2.7902 | 2.7896 | 2.7879 | 2.7859 | 2.7835 | 2.7809 | 2.7799 | 2.7768 | 2.7672 | 2.7577 | 2.7121 | 2.6509 | 2.6005 | 2.7197 | 2.7183 | 2.7176 | 2.7154 | 2.7128 | 2.7098 | 2.7066 | 2.705 | 2.7035 | 2.7019 | 2.7004 | 2.6717 | 2.5944 | 2.528 | 2.7204 | 2.7191 | 2.7185 | 2.7168 | 2.7148 | 2.7125 | 2.7098 | 2.7088 | 2.7078 | 2.7069 | 2.706 | 2.6718 | 2.5962 | 2.53
|  | KAMES | FS |  |  |  | 0.0052632 | 2.7915 | 2.7902 | 2.7902 | 2.7901 | 2.79 | 2.7899 | 2.7898 | 2.7892 | 2.7886 | 2.788 | 2.7873 | 2.7634 | 2.7226 | 2.6709 | 2.7198 | 2.7185 | 2.7184 | 2.7182 | 2.7179 | 2.7174 | 2.7169 | 2.7159 | 2.7149 | 2.7138 | 2.7126 | 2.7086 | 2.6854 | 2.6217 | 2.7204 | 2.7192 | 2.7191 | 2.719 | 2.7189 | 2.7188 | 2.7187 | 2.7181 | 2.7175 | 2.7169 | 2.7162 | 2.7143 | 2.6846 | 2.6234
| KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 0.23368 | 18.3356 | 18.2891 | 18.2464 | 18.1989 | 18.1465 | 18.0898 | 18.0307 | 17.9814 | 17.9312 | 17.8801 | 17.8288 | 17.2463 | 16.3023 | 15.0204 | 15.8952 | 15.8468 | 15.8017 | 15.75 | 15.6936 | 15.633 | 15.5403 | 15.3711 | 15.202 | 15.0339 | 14.8673 | 13.9922 | 12.9496 | 11.57 | 16.6386 | 16.5922 | 16.5494 | 16.5019 | 16.4496 | 16.3928 | 16.3337 | 16.2844 | 16.2343 | 16.1831 | 16.067 | 15.9107 | 15.7454 | 15.5771
|  | KEITH | CT |  |  |  | 0.23368 | 18.3356 | 18.2891 | 18.2464 | 18.1989 | 18.1465 | 18.0898 | 18.0307 | 17.9814 | 17.9312 | 17.8801 | 17.8288 | 17.5235 | 16.8744 | 15.967 | 15.8952 | 15.8468 | 15.8017 | 15.75 | 15.6936 | 15.633 | 15.5702 | 15.5169 | 15.4187 | 15.2866 | 15.1554 | 14.4617 | 13.6393 | 12.6648 | 16.6386 | 16.5922 | 16.5494 | 16.5019 | 16.4496 | 16.3928 | 16.3337 | 16.2844 | 16.2343 | 16.1831 | 16.1318 | 16.0796 | 16.0196 | 15.9383
|  | KEITH | LW |  |  |  | 0.23368 | 18.3827 | 18.3202 | 18.2861 | 18.2417 | 18.192 | 18.1378 | 18.0805 | 18.031 | 17.98 | 17.9285 | 17.8759 | 17.2463 | 16.3023 | 15.0204 | 15.9417 | 15.8764 | 15.8389 | 15.7886 | 15.7331 | 15.6734 | 15.5403 | 15.3711 | 15.202 | 15.0339 | 14.8673 | 13.9922 | 12.9496 | 11.57 | 16.6857 | 16.6233 | 16.5891 | 16.5447 | 16.495 | 16.4408 | 16.3835 | 16.334 | 16.2831 | 16.2249 | 16.067 | 15.9107 | 15.7454 | 15.5771
|  | KEITH | ST |  |  |  | 0.23368 | 18.392 | 18.3781 | 18.368 | 18.353 | 18.3343 | 18.3136 | 18.2915 | 18.2785 | 18.2654 | 18.2526 | 18.24 | 18.1792 | 18.028 | 17.9245 | 15.9546 | 15.9405 | 15.9301 | 15.9124 | 15.891 | 15.8678 | 15.8432 | 15.8275 | 15.8117 | 15.7963 | 15.7812 | 15.612 | 15.2144 | 14.8711 | 16.695 | 16.6812 | 16.671 | 16.656 | 16.6373 | 16.6167 | 16.5945 | 16.5815 | 16.5684 | 16.5556 | 16.543 | 16.4822 | 16.3311 | 16.0741
|  | KEITH | FS |  |  |  | 0.23368 | 18.397 | 18.387 | 18.3816 | 18.3762 | 18.3706 | 18.3649 | 18.3591 | 18.3512 | 18.3429 | 18.3343 | 18.3254 | 18.289 | 18.2102 | 18.068 | 15.96 | 15.9497 | 15.9441 | 15.9384 | 15.9319 | 15.9243 | 15.9168 | 15.9068 | 15.8965 | 15.8858 | 15.8749 | 15.8286 | 15.6639 | 15.3295 | 16.7001 | 16.69 | 16.6847 | 16.6793 | 16.6737 | 16.6679 | 16.6621 | 16.6542 | 16.6459 | 16.6373 | 16.6284 | 16.592 | 16.5133 | 16.371
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0.02 | 15.6709 | 15.6426 | 15.6231 | 15.5968 | 15.4801 | 15.3557 | 15.2376 | 15.1209 | 15.008 | 14.898 | 14.7941 | 14.2715 | 13.6753 | 12.8697 | 14.1427 | 14.0281 | 13.9258 | 13.784 | 13.6434 | 13.5082 | 13.3802 | 13.2531 | 13.1303 | 13.0107 | 12.898 | 12.3348 | 11.7004 | 10.8582 | 14.9525 | 14.8453 | 14.7512 | 14.621 | 14.4914 | 14.3665 | 14.2479 | 14.1307 | 14.0172 | 13.9068 | 13.8024 | 13.7033 | 13.5981 | 13.492
|  | KEMNAY | CT |  |  |  | 0.02 | 15.6709 | 15.6502 | 15.6324 | 15.6106 | 15.5854 | 15.5467 | 15.4577 | 15.3731 | 15.2902 | 15.2103 | 15.1332 | 14.738 | 14.2953 | 13.7682 | 14.1613 | 14.0936 | 14.0218 | 13.924 | 13.8222 | 13.7189 | 13.6229 | 13.5311 | 13.4411 | 13.3545 | 13.2711 | 12.8463 | 12.3765 | 11.8237 | 14.9679 | 14.9049 | 14.8386 | 14.7483 | 14.6542 | 14.5585 | 14.4691 | 14.3842 | 14.3009 | 14.2206 | 14.1433 | 14.066 | 13.986 | 13.9063
|  | KEMNAY | LW |  |  |  | 0.02 | 15.6835 | 15.6426 | 15.6231 | 15.5968 | 15.4801 | 15.3557 | 15.2376 | 15.1209 | 15.008 | 14.898 | 14.7941 | 14.2715 | 13.6753 | 12.8697 | 14.1427 | 14.0281 | 13.9258 | 13.784 | 13.6434 | 13.5082 | 13.3802 | 13.2531 | 13.1303 | 13.0107 | 12.898 | 12.3348 | 11.7004 | 10.8582 | 14.9525 | 14.8453 | 14.7512 | 14.621 | 14.4914 | 14.3665 | 14.2479 | 14.1307 | 14.0172 | 13.9068 | 13.8024 | 13.7033 | 13.5981 | 13.492
|  | KEMNAY | ST |  |  |  | 0.02 | 15.6852 | 15.6786 | 15.6746 | 15.6665 | 15.6572 | 15.6464 | 15.6347 | 15.6292 | 15.6237 | 15.6184 | 15.6013 | 15.4029 | 15.168 | 14.9778 | 14.2223 | 14.2039 | 14.1864 | 14.1343 | 14.0794 | 14.024 | 13.9703 | 13.9199 | 13.8693 | 13.8204 | 13.7733 | 13.5545 | 13.3021 | 13.0956 | 15.0243 | 15.007 | 14.9909 | 14.9432 | 14.8929 | 14.8419 | 14.7924 | 14.7465 | 14.7004 | 14.6559 | 14.6131 | 14.4137 | 14.1779 | 13.9869
|  | KEMNAY | FS |  |  |  | 0.02 | 15.6869 | 15.6815 | 15.6796 | 15.6777 | 15.6757 | 15.6735 | 15.6721 | 15.6694 | 15.6663 | 15.6631 | 15.6596 | 15.6065 | 15.4403 | 15.2367 | 14.2316 | 14.2166 | 14.2039 | 14.189 | 14.1668 | 14.1335 | 14.1021 | 14.0647 | 14.0262 | 13.9885 | 13.9506 | 13.7754 | 13.5949 | 13.3775 | 15.0328 | 15.0187 | 15.0071 | 14.9935 | 14.9734 | 14.9432 | 14.9148 | 14.8808 | 14.8459 | 14.8116 | 14.7772 | 14.6181 | 14.4512 | 14.2469
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 0.62565 | 0.62428 | 0.623 | 0.62155 | 0.61997 | 0.61827 | 0.61651 | 0.61507 | 0.61361 | 0.61215 | 0.61068 | 0.59949 | 0.57331 | 0.53645 | 0.5623 | 0.56093 | 0.55965 | 0.5582 | 0.55662 | 0.55493 | 0.55316 | 0.55172 | 0.55026 | 0.5488 | 0.54593 | 0.52193 | 0.49433 | 0.45569 | 0.57804 | 0.57668 | 0.57539 | 0.57395 | 0.57237 | 0.57067 | 0.56891 | 0.56747 | 0.56601 | 0.56135 | 0.5565 | 0.55172 | 0.54671 | 0.54167
|  | KENMORE | CT |  |  |  | 0 | 0.62565 | 0.62428 | 0.623 | 0.62155 | 0.61997 | 0.61827 | 0.61651 | 0.61507 | 0.61361 | 0.61215 | 0.61068 | 0.5999 | 0.58288 | 0.55502 | 0.5623 | 0.56093 | 0.55965 | 0.5582 | 0.55662 | 0.55493 | 0.55316 | 0.55172 | 0.55026 | 0.5488 | 0.54734 | 0.53092 | 0.50521 | 0.47629 | 0.57804 | 0.57668 | 0.57539 | 0.57395 | 0.57237 | 0.57067 | 0.56891 | 0.56747 | 0.56601 | 0.56455 | 0.56308 | 0.55985 | 0.55585 | 0.55098
|  | KENMORE | LW |  |  |  | 0 | 0.62817 | 0.62663 | 0.62594 | 0.62414 | 0.62221 | 0.62019 | 0.6181 | 0.61629 | 0.61446 | 0.61262 | 0.61079 | 0.59949 | 0.57331 | 0.53645 | 0.56482 | 0.56328 | 0.56259 | 0.56079 | 0.55886 | 0.55684 | 0.55475 | 0.55294 | 0.55111 | 0.54927 | 0.54593 | 0.52193 | 0.49433 | 0.45569 | 0.58057 | 0.57902 | 0.57833 | 0.57654 | 0.57461 | 0.57258 | 0.5705 | 0.56868 | 0.56627 | 0.56135 | 0.5565 | 0.55172 | 0.54671 | 0.54167
|  | KENMORE | ST |  |  |  | 0 | 0.62817 | 0.62798 | 0.62789 | 0.62764 | 0.62733 | 0.62698 | 0.62658 | 0.62643 | 0.62628 | 0.62614 | 0.626 | 0.62539 | 0.62236 | 0.62081 | 0.56482 | 0.56463 | 0.56454 | 0.56429 | 0.56399 | 0.56363 | 0.56323 | 0.56308 | 0.56293 | 0.56279 | 0.56265 | 0.56204 | 0.5578 | 0.54832 | 0.58057 | 0.58037 | 0.58028 | 0.58003 | 0.57973 | 0.57937 | 0.57898 | 0.57883 | 0.57868 | 0.57854 | 0.5784 | 0.57778 | 0.5684 | 0.55834
|  | KENMORE | FS |  |  |  | 0 | 0.62901 | 0.62884 | 0.62883 | 0.62882 | 0.62881 | 0.62879 | 0.62877 | 0.6287 | 0.62861 | 0.62852 | 0.62842 | 0.62815 | 0.62677 | 0.62376 | 0.56567 | 0.56549 | 0.56548 | 0.56548 | 0.56546 | 0.56544 | 0.56542 | 0.56535 | 0.56526 | 0.56517 | 0.56507 | 0.5648 | 0.56342 | 0.56041 | 0.58141 | 0.58124 | 0.58123 | 0.58122 | 0.5812 | 0.58119 | 0.58117 | 0.58109 | 0.58101 | 0.58092 | 0.58081 | 0.58055 | 0.57916 | 0.57615
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 0.06 | 5.9647 | 5.9247 | 5.8873 | 5.8255 | 5.7622 | 5.6991 | 5.6354 | 5.5742 | 5.5134 | 5.4528 | 5.3924 | 5.0715 | 4.6719 | 4.1035 | 6.1403 | 6.1227 | 6.1071 | 6.0865 | 6.0631 | 6.0378 | 6.0105 | 5.9882 | 5.9657 | 5.9428 | 5.9194 | 5.7007 | 5.2404 | 4.612 | 6.5487 | 6.5311 | 6.5155 | 6.4949 | 6.4715 | 6.4462 | 6.419 | 6.3966 | 6.3741 | 6.3512 | 6.3278 | 6.3046 | 6.2771 | 6.2478
|  | KEPCULLOCH | CT |  |  |  | 0.06 | 5.9647 | 5.9338 | 5.9023 | 5.8551 | 5.806 | 5.7559 | 5.7057 | 5.6602 | 5.6148 | 5.5696 | 5.5248 | 5.279 | 4.9767 | 4.602 | 6.1403 | 6.123 | 6.1071 | 6.0884 | 6.0671 | 6.0435 | 6.0187 | 6 | 5.9808 | 5.9615 | 5.9421 | 5.8213 | 5.6182 | 5.2031 | 6.5487 | 6.5314 | 6.5155 | 6.4968 | 6.4755 | 6.4519 | 6.4272 | 6.4084 | 6.3892 | 6.3699 | 6.3505 | 6.3299 | 6.3061 | 6.2818
|  | KEPCULLOCH | LW |  |  |  | 0.06 | 5.9743 | 5.9247 | 5.8873 | 5.8255 | 5.7622 | 5.6991 | 5.6354 | 5.5742 | 5.5134 | 5.4528 | 5.3924 | 5.0715 | 4.6719 | 4.1035 | 6.1537 | 6.1227 | 6.1075 | 6.0865 | 6.0631 | 6.0378 | 6.0105 | 5.9882 | 5.9657 | 5.9428 | 5.9194 | 5.7007 | 5.2404 | 4.612 | 6.5622 | 6.5311 | 6.5159 | 6.4949 | 6.4715 | 6.4462 | 6.419 | 6.3966 | 6.3741 | 6.3512 | 6.3278 | 6.3046 | 6.2771 | 6.2478
|  | KEPCULLOCH | ST |  |  |  | 0.06 | 6.0012 | 5.9944 | 5.9896 | 5.9647 | 5.9381 | 5.9113 | 5.8852 | 5.862 | 5.8392 | 5.8168 | 5.795 | 5.6921 | 5.5449 | 5.428 | 6.1554 | 6.1501 | 6.1466 | 6.1402 | 6.1319 | 6.1226 | 6.1134 | 6.1089 | 6.1043 | 6.0999 | 6.0956 | 6.0737 | 6.0031 | 5.9602 | 6.5638 | 6.5585 | 6.555 | 6.5486 | 6.5403 | 6.531 | 6.5218 | 6.5173 | 6.5128 | 6.5084 | 6.5041 | 6.4821 | 6.4115 | 6.3686
|  | KEPCULLOCH | FS |  |  |  | 0.06 | 6.0039 | 5.9984 | 5.9953 | 5.9913 | 5.9836 | 5.9693 | 5.9551 | 5.9376 | 5.92 | 5.9031 | 5.886 | 5.8036 | 5.7022 | 5.5713 | 6.1571 | 6.1528 | 6.151 | 6.1491 | 6.1472 | 6.1451 | 6.143 | 6.1399 | 6.1365 | 6.1338 | 6.131 | 6.1181 | 6.0821 | 6.0136 | 6.5655 | 6.5612 | 6.5594 | 6.5575 | 6.5556 | 6.5535 | 6.5514 | 6.5483 | 6.5449 | 6.5422 | 6.5394 | 6.5265 | 6.4905 | 6.422
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.31965 | 0.31904 | 0.31876 | 0.31838 | 0.31795 | 0.31749 | 0.31699 | 0.31661 | 0.31622 | 0.31583 | 0.31544 | 0.31308 | 0.30943 | 0.30005 | 0.31948 | 0.31886 | 0.31859 | 0.31821 | 0.31778 | 0.31731 | 0.31682 | 0.31644 | 0.31605 | 0.31566 | 0.31527 | 0.31161 | 0.30399 | 0.29327 | 0.31986 | 0.31925 | 0.31898 | 0.3186 | 0.31817 | 0.3177 | 0.31721 | 0.31682 | 0.31643 | 0.31604 | 0.31565 | 0.31527 | 0.31402 | 0.31275
|  | KERRERA | CT |  |  |  | 0 | 0.31965 | 0.31944 | 0.31927 | 0.31903 | 0.31875 | 0.31841 | 0.31805 | 0.31782 | 0.31758 | 0.31734 | 0.3171 | 0.31553 | 0.31308 | 0.30934 | 0.31948 | 0.31927 | 0.3191 | 0.31886 | 0.31858 | 0.31824 | 0.31788 | 0.31765 | 0.31741 | 0.31717 | 0.31692 | 0.31536 | 0.31254 | 0.30618 | 0.31986 | 0.31966 | 0.31948 | 0.31925 | 0.31896 | 0.31863 | 0.31827 | 0.31803 | 0.31779 | 0.31755 | 0.31731 | 0.31706 | 0.31675 | 0.31642
|  | KERRERA | LW |  |  |  | 0 | 0.31965 | 0.31904 | 0.31876 | 0.31838 | 0.31795 | 0.31749 | 0.31699 | 0.31661 | 0.31622 | 0.31583 | 0.31544 | 0.31308 | 0.30943 | 0.30005 | 0.31948 | 0.31886 | 0.31859 | 0.31821 | 0.31778 | 0.31731 | 0.31682 | 0.31644 | 0.31605 | 0.31566 | 0.31527 | 0.31161 | 0.30399 | 0.29327 | 0.31986 | 0.31925 | 0.31898 | 0.3186 | 0.31817 | 0.3177 | 0.31721 | 0.31682 | 0.31643 | 0.31604 | 0.31565 | 0.31527 | 0.31402 | 0.31275
|  | KERRERA | ST |  |  |  | 0 | 0.31965 | 0.31957 | 0.31954 | 0.31944 | 0.31932 | 0.31919 | 0.31903 | 0.31897 | 0.31892 | 0.31886 | 0.31881 | 0.31857 | 0.31741 | 0.31681 | 0.31948 | 0.3194 | 0.31937 | 0.31927 | 0.31915 | 0.31901 | 0.31886 | 0.3188 | 0.31875 | 0.31869 | 0.31864 | 0.3184 | 0.31724 | 0.31664 | 0.31986 | 0.31979 | 0.31975 | 0.31965 | 0.31954 | 0.3194 | 0.31925 | 0.31919 | 0.31913 | 0.31908 | 0.31902 | 0.31878 | 0.31762 | 0.31703
|  | KERRERA | FS |  |  |  | 0 | 0.31965 | 0.31958 | 0.31958 | 0.31958 | 0.31957 | 0.31956 | 0.31956 | 0.31953 | 0.3195 | 0.31946 | 0.31943 | 0.31933 | 0.31881 | 0.31769 | 0.31948 | 0.31941 | 0.31941 | 0.31941 | 0.3194 | 0.31939 | 0.31939 | 0.31936 | 0.31933 | 0.31929 | 0.31926 | 0.31916 | 0.31864 | 0.31752 | 0.31986 | 0.3198 | 0.31979 | 0.31979 | 0.31979 | 0.31978 | 0.31977 | 0.31974 | 0.31971 | 0.31968 | 0.31964 | 0.31954 | 0.31902 | 0.3179
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | YES | 0.042105 | 1.8947 | 1.8786 | 1.8714 | 1.8614 | 1.8501 | 1.8378 | 1.8249 | 1.8148 | 1.8045 | 1.7835 | 1.7598 | 1.5631 | 1.3145 | 0.98251 | 1.853 | 1.8369 | 1.8297 | 1.8198 | 1.7995 | 1.755 | 1.7109 | 1.6678 | 1.6249 | 1.5824 | 1.5405 | 1.3231 | 1.0708 | 0.73519 | 1.9122 | 1.8897 | 1.8747 | 1.8508 | 1.8259 | 1.7849 | 1.7376 | 1.691 | 1.6447 | 1.5988 | 1.5537 | 1.5091 | 1.4624 | 1.4153
|  | KERRY FALLS | CT |  |  |  | 0.042105 | 1.8947 | 1.8892 | 1.8847 | 1.8784 | 1.8708 | 1.862 | 1.8525 | 1.8463 | 1.84 | 1.8336 | 1.8271 | 1.7559 | 1.5954 | 1.3934 | 1.853 | 1.8476 | 1.843 | 1.8368 | 1.8292 | 1.8203 | 1.7939 | 1.7648 | 1.7357 | 1.707 | 1.6785 | 1.5292 | 1.3563 | 1.1518 | 1.9139 | 1.9038 | 1.8938 | 1.878 | 1.861 | 1.8432 | 1.825 | 1.7948 | 1.7634 | 1.7323 | 1.7016 | 1.6709 | 1.6387 | 1.6064
|  | KERRY FALLS | LW |  |  |  | 0.042105 | 1.8947 | 1.8786 | 1.8714 | 1.8614 | 1.8501 | 1.8378 | 1.8249 | 1.8148 | 1.8045 | 1.7835 | 1.7598 | 1.5631 | 1.3145 | 0.98251 | 1.853 | 1.8369 | 1.8297 | 1.8198 | 1.7995 | 1.755 | 1.7109 | 1.6678 | 1.6249 | 1.5824 | 1.5405 | 1.3231 | 1.0708 | 0.73519 | 1.9122 | 1.8897 | 1.8747 | 1.8508 | 1.8259 | 1.7849 | 1.7376 | 1.691 | 1.6447 | 1.5988 | 1.5537 | 1.5091 | 1.4624 | 1.4153
|  | KERRY FALLS | ST |  |  |  | 0.042105 | 1.8947 | 1.8927 | 1.8917 | 1.8892 | 1.886 | 1.8824 | 1.8783 | 1.8768 | 1.8752 | 1.8738 | 1.8724 | 1.866 | 1.834 | 1.7912 | 1.853 | 1.851 | 1.8501 | 1.8475 | 1.8444 | 1.8407 | 1.8366 | 1.8351 | 1.8336 | 1.8321 | 1.8202 | 1.7421 | 1.6457 | 1.5669 | 1.9203 | 1.9182 | 1.9167 | 1.9078 | 1.8984 | 1.8887 | 1.8788 | 1.8707 | 1.8628 | 1.855 | 1.8475 | 1.7677 | 1.6645 | 1.5791
|  | KERRY FALLS | FS |  |  |  | 0.042105 | 1.8947 | 1.8929 | 1.8928 | 1.8927 | 1.8926 | 1.8924 | 1.8922 | 1.8914 | 1.8906 | 1.8896 | 1.8886 | 1.8859 | 1.8718 | 1.8413 | 1.853 | 1.8512 | 1.8511 | 1.8511 | 1.8509 | 1.8507 | 1.8505 | 1.8498 | 1.8489 | 1.848 | 1.8469 | 1.8242 | 1.7568 | 1.677 | 1.9204 | 1.9185 | 1.9183 | 1.9176 | 1.9153 | 1.9109 | 1.9066 | 1.9012 | 1.8955 | 1.8897 | 1.8838 | 1.8564 | 1.7833 | 1.6984
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.0063158 | 1.0311 | 1.0209 | 1.0098 | 0.99435 | 0.9776 | 0.95939 | 0.94133 | 0.92304 | 0.90487 | 0.88682 | 0.86901 | 0.77566 | 0.66561 | 0.52299 | 1.163 | 1.157 | 1.1512 | 1.1448 | 1.1379 | 1.1307 | 1.1232 | 1.1168 | 1.1104 | 1.104 | 1.0976 | 1.0403 | 0.92314 | 0.77361 | 1.0368 | 1.0294 | 1.0179 | 1.0016 | 0.98285 | 0.9635 | 0.94433 | 0.92489 | 0.9056 | 0.88643 | 0.86753 | 0.84884 | 0.82944 | 0.80903
|  | KILCHRENAN | CT |  |  |  | 0.0063158 | 1.0311 | 1.0209 | 1.0098 | 0.99435 | 0.97854 | 0.96265 | 0.94679 | 0.93182 | 0.91689 | 0.90208 | 0.88737 | 0.809 | 0.71871 | 0.61375 | 1.163 | 1.157 | 1.1512 | 1.1448 | 1.1379 | 1.1307 | 1.1232 | 1.1168 | 1.1104 | 1.104 | 1.0976 | 1.0598 | 0.98449 | 0.8747 | 1.0368 | 1.0294 | 1.0179 | 1.0016 | 0.98492 | 0.96822 | 0.95158 | 0.9358 | 0.92008 | 0.90448 | 0.88899 | 0.87355 | 0.8576 | 0.84076
|  | KILCHRENAN | LW |  |  |  | 0.0063158 | 1.0377 | 1.0255 | 1.0141 | 0.99595 | 0.9776 | 0.95939 | 0.94133 | 0.92304 | 0.90487 | 0.88682 | 0.86901 | 0.77566 | 0.66561 | 0.52299 | 1.1706 | 1.1641 | 1.1599 | 1.1547 | 1.149 | 1.143 | 1.1368 | 1.1307 | 1.1246 | 1.1185 | 1.1124 | 1.0403 | 0.92314 | 0.77361 | 1.0444 | 1.0338 | 1.0217 | 1.0024 | 0.98285 | 0.9635 | 0.94433 | 0.92489 | 0.9056 | 0.88643 | 0.86753 | 0.84884 | 0.82944 | 0.80903
|  | KILCHRENAN | ST |  |  |  | 0.0063158 | 1.0466 | 1.0442 | 1.0421 | 1.0346 | 1.027 | 1.0195 | 1.012 | 1.0043 | 0.99665 | 0.98917 | 0.98182 | 0.94803 | 0.90937 | 0.8734 | 1.1715 | 1.1699 | 1.1688 | 1.167 | 1.1651 | 1.163 | 1.1608 | 1.1594 | 1.1581 | 1.1567 | 1.1554 | 1.149 | 1.1343 | 1.1214 | 1.0453 | 1.0437 | 1.0426 | 1.0408 | 1.0354 | 1.0274 | 1.0193 | 1.011 | 1.0028 | 0.99479 | 0.98687 | 0.95051 | 0.90961 | 0.87149
|  | KILCHRENAN | FS |  |  |  | 0.0063158 | 1.0479 | 1.0463 | 1.0453 | 1.0433 | 1.0407 | 1.0361 | 1.0316 | 1.0257 | 1.0198 | 1.0139 | 1.008 | 0.97947 | 0.94835 | 0.91651 | 1.1723 | 1.1709 | 1.17 | 1.1691 | 1.1682 | 1.1673 | 1.1664 | 1.1653 | 1.1642 | 1.163 | 1.1618 | 1.1567 | 1.1478 | 1.1333 | 1.0461 | 1.0447 | 1.0438 | 1.0429 | 1.042 | 1.0411 | 1.0402 | 1.0339 | 1.0276 | 1.0212 | 1.0149 | 0.98419 | 0.95099 | 0.91752
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.10947 | 1.6925 | 1.6746 | 1.6579 | 1.6398 | 1.62 | 1.5986 | 1.5629 | 1.511 | 1.4595 | 1.4075 | 1.3564 | 1.0855 | 0.75625 | 0.30847 | 1.4309 | 1.3992 | 1.3663 | 1.3108 | 1.2526 | 1.1942 | 1.1357 | 1.0782 | 1.0211 | 0.96374 | 0.90727 | 0.61058 | 0.25515 | -0.21818 | 1.5631 | 1.5453 | 1.5285 | 1.5105 | 1.4907 | 1.4693 | 1.4471 | 1.4283 | 1.385 | 1.3275 | 1.2708 | 1.215 | 1.1555 | 1.0955
|  | KILLEARN | CT |  |  |  | 0.10947 | 1.6925 | 1.6746 | 1.6579 | 1.6398 | 1.62 | 1.5986 | 1.5764 | 1.5543 | 1.5125 | 1.4709 | 1.4298 | 1.2078 | 0.94181 | 0.62468 | 1.4309 | 1.3992 | 1.3663 | 1.3201 | 1.2728 | 1.2253 | 1.1781 | 1.1321 | 1.0864 | 1.0411 | 0.9962 | 0.75604 | 0.47186 | 0.13713 | 1.5631 | 1.5453 | 1.5285 | 1.5105 | 1.4907 | 1.4693 | 1.4471 | 1.4283 | 1.4092 | 1.3901 | 1.3602 | 1.3154 | 1.2676 | 1.2188
|  | KILLEARN | LW |  |  |  | 0.10947 | 1.711 | 1.6871 | 1.6747 | 1.6578 | 1.6392 | 1.6162 | 1.5629 | 1.511 | 1.4595 | 1.4075 | 1.3564 | 1.0855 | 0.75625 | 0.30847 | 1.4456 | 1.4033 | 1.3684 | 1.3108 | 1.2526 | 1.1942 | 1.1357 | 1.0782 | 1.0211 | 0.96374 | 0.90727 | 0.61058 | 0.25515 | -0.21818 | 1.5817 | 1.5578 | 1.5453 | 1.5284 | 1.5098 | 1.4891 | 1.4667 | 1.4422 | 1.385 | 1.3275 | 1.2708 | 1.215 | 1.1555 | 1.0955
|  | KILLEARN | ST |  |  |  | 0.10947 | 1.7152 | 1.7101 | 1.7064 | 1.7006 | 1.6932 | 1.6852 | 1.6775 | 1.673 | 1.6685 | 1.6641 | 1.6597 | 1.5973 | 1.4749 | 1.3741 | 1.4748 | 1.4681 | 1.4627 | 1.4385 | 1.4131 | 1.3879 | 1.3635 | 1.3404 | 1.3176 | 1.2953 | 1.2736 | 1.1689 | 1.0353 | 0.92365 | 1.5859 | 1.5808 | 1.5771 | 1.5712 | 1.5639 | 1.5558 | 1.5481 | 1.5436 | 1.5391 | 1.5347 | 1.5304 | 1.508 | 1.3991 | 1.2872
|  | KILLEARN | FS |  |  |  | 0.10947 | 1.7161 | 1.7121 | 1.7103 | 1.7085 | 1.7066 | 1.7047 | 1.7027 | 1.7 | 1.6972 | 1.6943 | 1.6913 | 1.676 | 1.6198 | 1.5223 | 1.4788 | 1.4734 | 1.47 | 1.4659 | 1.4578 | 1.4437 | 1.4296 | 1.4133 | 1.3968 | 1.3803 | 1.3638 | 1.2823 | 1.1933 | 1.0875 | 1.5867 | 1.5827 | 1.5809 | 1.5791 | 1.5772 | 1.5753 | 1.5734 | 1.5707 | 1.5679 | 1.565 | 1.562 | 1.5466 | 1.519 | 1.4515
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0.0063158 | 2.792 | 2.7854 | 2.7791 | 2.7714 | 2.7631 | 2.7542 | 2.7449 | 2.7373 | 2.7295 | 2.7218 | 2.7132 | 2.6612 | 2.5484 | 2.355 | 2.6313 | 2.6248 | 2.6187 | 2.6114 | 2.6034 | 2.5947 | 2.5806 | 2.5554 | 2.5303 | 2.5054 | 2.48 | 2.3505 | 2.1941 | 1.9885 | 2.9208 | 2.9147 | 2.9089 | 2.9024 | 2.8951 | 2.882 | 2.8572 | 2.8323 | 2.8075 | 2.7828 | 2.7576 | 2.7328 | 2.7065 | 2.681
|  | KILLIN TOWN | CT |  |  |  | 0.0063158 | 2.792 | 2.7854 | 2.7791 | 2.7714 | 2.7631 | 2.7542 | 2.7449 | 2.7373 | 2.7295 | 2.7218 | 2.714 | 2.6675 | 2.6035 | 2.5087 | 2.6313 | 2.6248 | 2.6187 | 2.6114 | 2.6034 | 2.5947 | 2.5858 | 2.5784 | 2.5654 | 2.546 | 2.5268 | 2.4256 | 2.3044 | 2.16 | 2.9208 | 2.9147 | 2.9089 | 2.9024 | 2.8951 | 2.8871 | 2.8788 | 2.8613 | 2.8419 | 2.8228 | 2.8037 | 2.7847 | 2.7647 | 2.7438
|  | KILLIN TOWN | LW |  |  |  | 0.0063158 | 2.7986 | 2.789 | 2.7837 | 2.7755 | 2.7666 | 2.7573 | 2.7477 | 2.7393 | 2.7309 | 2.7224 | 2.7132 | 2.6612 | 2.5484 | 2.355 | 2.6379 | 2.6285 | 2.6235 | 2.6157 | 2.6073 | 2.5984 | 2.5806 | 2.5554 | 2.5303 | 2.5054 | 2.48 | 2.3505 | 2.1941 | 1.9885 | 2.9275 | 2.9186 | 2.9142 | 2.9075 | 2.9001 | 2.882 | 2.8572 | 2.8323 | 2.8075 | 2.7828 | 2.7576 | 2.7328 | 2.7065 | 2.681
|  | KILLIN TOWN | ST |  |  |  | 0.0063158 | 2.8005 | 2.7986 | 2.7971 | 2.7942 | 2.791 | 2.7875 | 2.7839 | 2.7815 | 2.7792 | 2.7769 | 2.7746 | 2.7639 | 2.7397 | 2.7238 | 2.6391 | 2.6372 | 2.6359 | 2.6335 | 2.6305 | 2.6272 | 2.6237 | 2.6216 | 2.6195 | 2.6174 | 2.6153 | 2.5927 | 2.5347 | 2.4859 | 2.9284 | 2.9265 | 2.9251 | 2.9229 | 2.9204 | 2.9177 | 2.9146 | 2.913 | 2.9113 | 2.9097 | 2.9081 | 2.8694 | 2.8119 | 2.7637
|  | KILLIN TOWN | FS |  |  |  | 0.0063158 | 2.8014 | 2.7995 | 2.7986 | 2.7976 | 2.7964 | 2.795 | 2.7936 | 2.7918 | 2.79 | 2.7881 | 2.7862 | 2.7779 | 2.7634 | 2.7396 | 2.64 | 2.6382 | 2.6373 | 2.6364 | 2.6355 | 2.6343 | 2.633 | 2.6314 | 2.6297 | 2.628 | 2.6262 | 2.6187 | 2.5978 | 2.5485 | 2.9292 | 2.9274 | 2.9265 | 2.9256 | 2.9247 | 2.9237 | 2.9228 | 2.9215 | 2.9202 | 2.9188 | 2.9174 | 2.9117 | 2.8743 | 2.8255
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0 | 1.8072 | 1.7959 | 1.7897 | 1.7808 | 1.7712 | 1.761 | 1.7507 | 1.7419 | 1.7331 | 1.7243 | 1.7157 | 1.6662 | 1.5791 | 1.3518 | 1.4193 | 1.3901 | 1.3622 | 1.3171 | 1.2716 | 1.2274 | 1.1854 | 1.1424 | 1.1005 | 1.0598 | 1.0204 | 0.82307 | 0.61055 | 0.34997 | 1.4172 | 1.4076 | 1.4033 | 1.3973 | 1.3906 | 1.3473 | 1.3053 | 1.2624 | 1.2206 | 1.1799 | 1.1406 | 1.1025 | 1.0631 | 1.0235
|  | KILMELFORD | CT |  |  |  | 0 | 1.8077 | 1.8034 | 1.7994 | 1.7937 | 1.7871 | 1.7798 | 1.7722 | 1.7666 | 1.7609 | 1.7552 | 1.7495 | 1.7157 | 1.6678 | 1.5987 | 1.4257 | 1.4099 | 1.3924 | 1.3644 | 1.3329 | 1.3013 | 1.2717 | 1.2425 | 1.2135 | 1.1856 | 1.1578 | 1.0184 | 0.86973 | 0.70166 | 1.4172 | 1.4139 | 1.4112 | 1.4074 | 1.4028 | 1.3975 | 1.3914 | 1.3624 | 1.3334 | 1.3055 | 1.2778 | 1.2501 | 1.2224 | 1.1946
|  | KILMELFORD | LW |  |  |  | 0 | 1.8072 | 1.7959 | 1.7897 | 1.7808 | 1.7712 | 1.761 | 1.7507 | 1.7419 | 1.7331 | 1.7243 | 1.7157 | 1.6662 | 1.5791 | 1.3518 | 1.4193 | 1.3901 | 1.3622 | 1.3171 | 1.2716 | 1.2274 | 1.1854 | 1.1424 | 1.1005 | 1.0598 | 1.0204 | 0.82307 | 0.61055 | 0.34997 | 1.4172 | 1.4076 | 1.4033 | 1.3973 | 1.3906 | 1.3473 | 1.3053 | 1.2624 | 1.2206 | 1.1799 | 1.1406 | 1.1025 | 1.0631 | 1.0235
|  | KILMELFORD | ST |  |  |  | 0 | 1.809 | 1.8076 | 1.8067 | 1.8038 | 1.8007 | 1.7972 | 1.7935 | 1.7913 | 1.7892 | 1.787 | 1.785 | 1.7754 | 1.7513 | 1.7366 | 1.4409 | 1.437 | 1.4322 | 1.4158 | 1.3991 | 1.3826 | 1.3647 | 1.347 | 1.3295 | 1.3122 | 1.2952 | 1.2154 | 1.1271 | 1.0514 | 1.4172 | 1.416 | 1.4154 | 1.4138 | 1.4119 | 1.4097 | 1.4072 | 1.4063 | 1.4054 | 1.4045 | 1.4036 | 1.3353 | 1.2471 | 1.1716
|  | KILMELFORD | FS |  |  |  | 0 | 1.8092 | 1.8078 | 1.8075 | 1.8072 | 1.8066 | 1.8057 | 1.8048 | 1.8034 | 1.8018 | 1.8002 | 1.7987 | 1.7924 | 1.7794 | 1.7564 | 1.4423 | 1.4385 | 1.4358 | 1.4328 | 1.4269 | 1.4173 | 1.4077 | 1.3963 | 1.3841 | 1.3705 | 1.3574 | 1.2941 | 1.2296 | 1.1576 | 1.4172 | 1.4161 | 1.416 | 1.416 | 1.4159 | 1.4157 | 1.4156 | 1.4152 | 1.4146 | 1.414 | 1.4134 | 1.4117 | 1.3495 | 1.2776
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.078947 | 1.1341 | 1.1222 | 1.1169 | 1.1096 | 1.1013 | 1.0922 | 1.0826 | 1.0751 | 1.0675 | 1.0598 | 1.0522 | 1.0054 | 0.84601 | 0.57672 | 1.2332 | 1.2053 | 1.1811 | 1.1407 | 1.0999 | 1.0595 | 1.0195 | 0.97873 | 0.93821 | 0.89885 | 0.86001 | 0.66196 | 0.43345 | 0.14046 | 1.0576 | 1.0303 | 1.0069 | 0.96777 | 0.92819 | 0.889 | 0.85016 | 0.81066 | 0.77139 | 0.73325 | 0.69561 | 0.6584 | 0.61938 | 0.58097
|  | KILNINVER | CT |  |  |  | 0.078947 | 1.1341 | 1.13 | 1.1265 | 1.1219 | 1.1161 | 1.1094 | 1.1023 | 1.0976 | 1.0927 | 1.0879 | 1.083 | 1.0511 | 1.0006 | 0.90555 | 1.2382 | 1.223 | 1.2066 | 1.1793 | 1.1503 | 1.1213 | 1.0933 | 1.0661 | 1.039 | 1.0122 | 0.98561 | 0.84679 | 0.68879 | 0.50559 | 1.0625 | 1.0477 | 1.0318 | 1.0053 | 0.97724 | 0.94904 | 0.92182 | 0.89554 | 0.86933 | 0.84334 | 0.81757 | 0.79186 | 0.76484 | 0.73769
|  | KILNINVER | LW |  |  |  | 0.078947 | 1.1341 | 1.1222 | 1.1169 | 1.1096 | 1.1013 | 1.0922 | 1.0826 | 1.0751 | 1.0675 | 1.0598 | 1.0522 | 1.0054 | 0.84601 | 0.57672 | 1.2332 | 1.2053 | 1.1811 | 1.1407 | 1.0999 | 1.0595 | 1.0195 | 0.97873 | 0.93821 | 0.89885 | 0.86001 | 0.66196 | 0.43345 | 0.14046 | 1.0576 | 1.0303 | 1.0069 | 0.96777 | 0.92819 | 0.889 | 0.85016 | 0.81066 | 0.77139 | 0.73325 | 0.69561 | 0.6584 | 0.61938 | 0.58097
|  | KILNINVER | ST |  |  |  | 0.078947 | 1.1341 | 1.1325 | 1.1318 | 1.1298 | 1.1275 | 1.1247 | 1.1215 | 1.1204 | 1.1192 | 1.1181 | 1.117 | 1.1121 | 1.088 | 1.0756 | 1.2542 | 1.2513 | 1.2492 | 1.2321 | 1.2147 | 1.1974 | 1.1801 | 1.1632 | 1.1465 | 1.13 | 1.1139 | 1.0401 | 0.95045 | 0.87428 | 1.0778 | 1.0749 | 1.0729 | 1.0564 | 1.0396 | 1.0228 | 1.0061 | 0.98976 | 0.97364 | 0.95781 | 0.94227 | 0.87113 | 0.78396 | 0.71023
|  | KILNINVER | FS |  |  |  | 0.078947 | 1.1341 | 1.1326 | 1.1326 | 1.1325 | 1.1324 | 1.1322 | 1.1321 | 1.1315 | 1.1308 | 1.13 | 1.1292 | 1.1271 | 1.1158 | 1.0913 | 1.2549 | 1.2522 | 1.2508 | 1.249 | 1.2435 | 1.233 | 1.2226 | 1.2108 | 1.199 | 1.1871 | 1.1752 | 1.1185 | 1.0553 | 0.98095 | 1.0785 | 1.0758 | 1.0745 | 1.0727 | 1.0674 | 1.0574 | 1.0474 | 1.036 | 1.0246 | 1.0132 | 1.0017 | 0.94703 | 0.88584 | 0.81341
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 0.056842 | 6.135 | 6.1175 | 6.0996 | 6.0711 | 6.0408 | 6.0081 | 5.9757 | 5.945 | 5.9137 | 5.8826 | 5.8521 | 5.6886 | 5.4851 | 5.1892 | 5.9379 | 5.9154 | 5.8927 | 5.8554 | 5.8167 | 5.7784 | 5.7406 | 5.7043 | 5.6675 | 5.6311 | 5.5953 | 5.4014 | 5.1655 | 4.8452 | 6.0031 | 5.9849 | 5.9663 | 5.9333 | 5.8934 | 5.854 | 5.8152 | 5.7778 | 5.7399 | 5.7024 | 5.6656 | 5.6294 | 5.5911 | 5.5516
|  | KILTARLITY | CT |  |  |  | 0.056842 | 6.135 | 6.1191 | 6.1027 | 6.0796 | 6.0554 | 6.0307 | 6.0048 | 5.9807 | 5.9567 | 5.9321 | 5.9078 | 5.777 | 5.6177 | 5.4219 | 5.9379 | 5.9191 | 5.8992 | 5.8698 | 5.8395 | 5.809 | 5.7787 | 5.7507 | 5.7228 | 5.6944 | 5.6663 | 5.5174 | 5.3366 | 5.1187 | 6.0031 | 5.9868 | 5.9699 | 5.9459 | 5.9173 | 5.8861 | 5.855 | 5.8263 | 5.7976 | 5.7685 | 5.7397 | 5.7109 | 5.6807 | 5.6503
|  | KILTARLITY | LW |  |  |  | 0.056842 | 6.1425 | 6.1175 | 6.0996 | 6.0711 | 6.0408 | 6.0081 | 5.9757 | 5.945 | 5.9137 | 5.8826 | 5.8521 | 5.6886 | 5.4851 | 5.1892 | 5.9445 | 5.9154 | 5.8927 | 5.8554 | 5.8167 | 5.7784 | 5.7406 | 5.7043 | 5.6675 | 5.6311 | 5.5953 | 5.4014 | 5.1655 | 4.8452 | 6.0104 | 5.9849 | 5.9663 | 5.9333 | 5.8934 | 5.854 | 5.8152 | 5.7778 | 5.7399 | 5.7024 | 5.6656 | 5.6294 | 5.5911 | 5.5516
|  | KILTARLITY | ST |  |  |  | 0.056842 | 6.1552 | 6.1512 | 6.1483 | 6.1371 | 6.1246 | 6.1121 | 6.0994 | 6.0886 | 6.078 | 6.0676 | 6.0575 | 6.0048 | 5.9308 | 5.8731 | 5.9629 | 5.9587 | 5.9556 | 5.9403 | 5.9239 | 5.9075 | 5.8912 | 5.8765 | 5.862 | 5.8479 | 5.8342 | 5.7697 | 5.6849 | 5.617 | 6.024 | 6.02 | 6.017 | 6.0052 | 5.9922 | 5.9791 | 5.9659 | 5.9545 | 5.9399 | 5.9253 | 5.9111 | 5.8443 | 5.7573 | 5.6874
|  | KILTARLITY | FS |  |  |  | 0.056842 | 6.1567 | 6.1539 | 6.1526 | 6.1511 | 6.1475 | 6.1416 | 6.1357 | 6.1285 | 6.1213 | 6.114 | 6.1066 | 6.0708 | 6.0243 | 5.9639 | 5.9647 | 5.9618 | 5.9604 | 5.9584 | 5.9536 | 5.9451 | 5.9367 | 5.9267 | 5.9166 | 5.9065 | 5.8963 | 5.8461 | 5.791 | 5.7226 | 6.0255 | 6.0227 | 6.0214 | 6.0198 | 6.0161 | 6.0098 | 6.0035 | 5.9959 | 5.9883 | 5.9806 | 5.9728 | 5.9228 | 5.8659 | 5.796
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 0.052632 | 14.8969 | 14.8504 | 14.8291 | 14.6116 | 14.3686 | 14.1367 | 13.9262 | 13.7113 | 13.5062 | 13.3093 | 13.1301 | 12.2716 | 11.3404 | 10.1056 | 14.3736 | 14.3272 | 14.3058 | 14.276 | 14.1293 | 13.8577 | 13.6123 | 13.36 | 13.1195 | 12.8892 | 12.6801 | 11.6892 | 10.6376 | 9.2869 | 14.8772 | 14.8175 | 14.7836 | 14.7382 | 14.6898 | 14.5595 | 14.3194 | 14.0728 | 13.8378 | 13.6125 | 13.408 | 13.2194 | 13.0216 | 12.8253
|  | KINCORTH | CT |  |  |  | 0.052632 | 14.8969 | 14.8792 | 14.8642 | 14.8441 | 14.7773 | 14.6007 | 14.447 | 14.2999 | 14.156 | 14.0221 | 13.8967 | 13.27 | 12.6041 | 11.8104 | 14.3736 | 14.356 | 14.341 | 14.3209 | 14.2964 | 14.2676 | 14.225 | 14.0519 | 13.8829 | 13.7261 | 13.5796 | 12.8551 | 12.1039 | 11.2279 | 14.881 | 14.8564 | 14.8335 | 14.8035 | 14.7688 | 14.7296 | 14.6899 | 14.6603 | 14.5838 | 14.4305 | 14.2872 | 14.1434 | 13.9955 | 13.854
|  | KINCORTH | LW |  |  |  | 0.052632 | 14.8985 | 14.8504 | 14.8291 | 14.6116 | 14.3686 | 14.1367 | 13.9262 | 13.7113 | 13.5062 | 13.3093 | 13.1301 | 12.2716 | 11.3404 | 10.1056 | 14.3753 | 14.3272 | 14.3058 | 14.276 | 14.1293 | 13.8577 | 13.6123 | 13.36 | 13.1195 | 12.8892 | 12.6801 | 11.6892 | 10.6376 | 9.2869 | 14.8772 | 14.8175 | 14.7836 | 14.7382 | 14.6898 | 14.5595 | 14.3194 | 14.0728 | 13.8378 | 13.6125 | 13.408 | 13.2194 | 13.0216 | 12.8253
|  | KINCORTH | ST |  |  |  | 0.052632 | 14.8994 | 14.8925 | 14.8891 | 14.8802 | 14.8694 | 14.8567 | 14.8425 | 14.8372 | 14.8294 | 14.7461 | 14.6657 | 14.2962 | 13.894 | 13.5615 | 14.3761 | 14.3692 | 14.3659 | 14.357 | 14.3461 | 14.3334 | 14.3192 | 14.3139 | 14.3086 | 14.3035 | 14.2986 | 14.0352 | 13.5749 | 13.1871 | 14.8889 | 14.8798 | 14.8738 | 14.8597 | 14.8434 | 14.8251 | 14.8058 | 14.7949 | 14.7837 | 14.7731 | 14.763 | 14.7159 | 14.2828 | 13.9034
|  | KINCORTH | FS |  |  |  | 0.052632 | 14.8994 | 14.8921 | 14.8918 | 14.8914 | 14.8908 | 14.89 | 14.8892 | 14.8861 | 14.8825 | 14.8786 | 14.8744 | 14.6022 | 14.3049 | 13.9429 | 14.3761 | 14.3688 | 14.3685 | 14.3681 | 14.3675 | 14.3667 | 14.3659 | 14.3628 | 14.3593 | 14.3554 | 14.3512 | 14.34 | 14.0447 | 13.6353 | 14.8896 | 14.8805 | 14.8782 | 14.8754 | 14.8717 | 14.8668 | 14.862 | 14.8544 | 14.8462 | 14.8378 | 14.8291 | 14.797 | 14.7211 | 14.3415
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0 | 0.11253 | 0.11236 | 0.11229 | 0.11219 | 0.11207 | 0.11194 | 0.11181 | 0.11171 | 0.1116 | 0.11149 | 0.11139 | 0.10834 | 0.10265 | 0.096096 | 0.1134 | 0.11323 | 0.11311 | 0.11295 | 0.11278 | 0.11259 | 0.11189 | 0.11066 | 0.10945 | 0.10823 | 0.10703 | 0.10091 | 0.094437 | 0.087097 | 0.11193 | 0.11176 | 0.11169 | 0.11159 | 0.11147 | 0.11134 | 0.11121 | 0.11111 | 0.111 | 0.11089 | 0.11079 | 0.10963 | 0.10743 | 0.10243
|  | KINGAIRLOCH | CT |  |  |  | 0 | 0.11253 | 0.11247 | 0.11242 | 0.11236 | 0.11228 | 0.11219 | 0.11209 | 0.11203 | 0.11196 | 0.1119 | 0.11183 | 0.11058 | 0.10549 | 0.10007 | 0.1134 | 0.11334 | 0.11329 | 0.11317 | 0.11304 | 0.1129 | 0.11275 | 0.11233 | 0.11122 | 0.11011 | 0.10901 | 0.10343 | 0.097596 | 0.091437 | 0.11193 | 0.11187 | 0.11183 | 0.11176 | 0.11168 | 0.11159 | 0.11149 | 0.11143 | 0.11136 | 0.1113 | 0.11123 | 0.11116 | 0.1106 | 0.10948
|  | KINGAIRLOCH | LW |  |  |  | 0 | 0.11253 | 0.11236 | 0.11229 | 0.11219 | 0.11207 | 0.11194 | 0.11181 | 0.11171 | 0.1116 | 0.11149 | 0.11139 | 0.10834 | 0.10265 | 0.096096 | 0.1134 | 0.11323 | 0.11311 | 0.11295 | 0.11278 | 0.11259 | 0.11189 | 0.11066 | 0.10945 | 0.10823 | 0.10703 | 0.10091 | 0.094437 | 0.087097 | 0.11193 | 0.11176 | 0.11169 | 0.11159 | 0.11147 | 0.11134 | 0.11121 | 0.11111 | 0.111 | 0.11089 | 0.11079 | 0.10963 | 0.10841 | 0.10717
|  | KINGAIRLOCH | ST |  |  |  | 0 | 0.11253 | 0.11251 | 0.1125 | 0.11247 | 0.11244 | 0.1124 | 0.11236 | 0.11234 | 0.11233 | 0.11231 | 0.1123 | 0.11223 | 0.11084 | 0.10655 | 0.11341 | 0.11339 | 0.11338 | 0.11335 | 0.11331 | 0.11327 | 0.11322 | 0.11315 | 0.11309 | 0.11303 | 0.11296 | 0.10881 | 0.10364 | 0.098654 | 0.11193 | 0.11191 | 0.1119 | 0.11187 | 0.11184 | 0.1118 | 0.11176 | 0.11174 | 0.11173 | 0.11171 | 0.1117 | 0.11163 | 0.10743 | 0.10243
|  | KINGAIRLOCH | FS |  |  |  | 0 | 0.11253 | 0.11251 | 0.11251 | 0.11251 | 0.11251 | 0.1125 | 0.1125 | 0.11249 | 0.11249 | 0.11248 | 0.11247 | 0.11244 | 0.11229 | 0.11198 | 0.11341 | 0.11339 | 0.11339 | 0.11339 | 0.11339 | 0.11338 | 0.11338 | 0.11336 | 0.11335 | 0.11334 | 0.11332 | 0.11328 | 0.11312 | 0.11279 | 0.11193 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.1119 | 0.1119 | 0.11189 | 0.11188 | 0.11187 | 0.11184 | 0.1117 | 0.11138
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.1116 | 6.5074 | 6.479 | 16.003 | 15.9724 | 15.7291 | 15.4527 | 15.2082 | 14.9571 | 14.7212 | 14.4973 | 14.3001 | 13.4093 | 12.5269 | 11.4491 | 5.5792 | 5.2962 | 13.8223 | 13.4989 | 13.1918 | 12.9033 | 12.6484 | 12.3862 | 12.1399 | 11.9064 | 11.7009 | 10.6905 | 9.6951 | 8.5166 | 6.1157 | 5.9569 | 14.832 | 14.4782 | 14.1428 | 13.8234 | 13.5375 | 13.242 | 12.9649 | 12.7026 | 12.4724 | 12.2667 | 12.0576 | 11.8513
|  | KINGSEAT | CT |  |  |  | 1.1116 | 6.5074 | 6.479 | 16.003 | 15.9724 | 15.938 | 15.9002 | 15.7971 | 15.6176 | 15.4427 | 15.2837 | 15.1376 | 14.4364 | 13.7695 | 13.0248 | 5.6709 | 5.5056 | 14.124 | 13.9122 | 13.6892 | 13.4598 | 13.2673 | 13.0801 | 12.8979 | 12.7323 | 12.5803 | 11.853 | 11.1659 | 10.3523 | 6.1157 | 6.0873 | 15.1657 | 14.935 | 14.6922 | 14.4428 | 14.2343 | 14.0307 | 13.8317 | 13.6466 | 13.477 | 13.3077 | 13.1406 | 12.9812
|  | KINGSEAT | LW |  |  |  | 1.1116 | 6.5309 | 6.4825 | 16.0077 | 15.9753 | 15.7291 | 15.4527 | 15.2082 | 14.9571 | 14.7212 | 14.4973 | 14.3001 | 13.4093 | 12.5269 | 11.4491 | 5.5792 | 5.2962 | 13.8223 | 13.4989 | 13.1918 | 12.9033 | 12.6484 | 12.3862 | 12.1399 | 11.9064 | 11.7009 | 10.6905 | 9.6951 | 8.5166 | 6.1392 | 5.9569 | 14.832 | 14.4782 | 14.1428 | 13.8234 | 13.5375 | 13.242 | 12.9649 | 12.7026 | 12.4724 | 12.2667 | 12.0576 | 11.8513
|  | KINGSEAT | ST |  |  |  | 1.1116 | 6.536 | 6.5271 | 16.0712 | 16.0607 | 16.0479 | 16.0336 | 16.019 | 16.0115 | 16.0039 | 15.9964 | 15.9892 | 15.7212 | 15.3307 | 15.0078 | 5.7892 | 5.7328 | 14.4706 | 14.3696 | 14.2603 | 14.1465 | 14.0423 | 13.9357 | 13.8267 | 13.7234 | 13.6252 | 13.1828 | 12.7776 | 12.4414 | 6.1443 | 6.1354 | 15.3044 | 15.294 | 15.2812 | 15.1874 | 15.0738 | 14.9569 | 14.8373 | 14.724 | 14.6162 | 14.1313 | 13.6867 | 13.3108
|  | KINGSEAT | FS |  |  |  | 1.1116 | 6.5385 | 6.5318 | 16.0791 | 16.0763 | 16.0734 | 16.0703 | 16.0672 | 16.0626 | 16.0576 | 16.0524 | 16.047 | 16.0267 | 15.7974 | 15.4757 | 5.8133 | 5.7666 | 14.5212 | 14.4696 | 14.4067 | 14.334 | 14.263 | 14.1828 | 14.0975 | 14.0145 | 13.933 | 13.5657 | 13.2618 | 12.9286 | 6.1468 | 6.1401 | 15.3124 | 15.3096 | 15.3067 | 15.3036 | 15.3005 | 15.2244 | 15.1308 | 15.0397 | 14.9501 | 14.5466 | 14.2164 | 13.8556
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 0.081053 | 7.8311 | 7.7952 | 7.7792 | 7.757 | 7.7318 | 7.7043 | 7.6753 | 7.6526 | 7.6297 | 7.6063 | 7.5835 | 7.3756 | 6.8521 | 6.1102 | 7.1604 | 7.0869 | 7.0253 | 6.9209 | 6.8152 | 6.7107 | 6.6074 | 6.5046 | 6.4025 | 6.3012 | 6.2015 | 5.6866 | 5.0859 | 4.2904 | 7.5339 | 7.498 | 7.4821 | 7.4599 | 7.4347 | 7.4072 | 7.3782 | 7.2786 | 7.1777 | 7.0775 | 6.9789 | 6.8816 | 6.7798 | 6.6772
|  | KINGUSSIE | CT |  |  |  | 0.081053 | 7.8311 | 7.8189 | 7.8086 | 7.7947 | 7.7776 | 7.7576 | 7.7362 | 7.7223 | 7.7079 | 7.6934 | 7.6788 | 7.5839 | 7.4243 | 6.9909 | 7.1707 | 7.1302 | 7.0881 | 7.0162 | 6.9425 | 6.8683 | 6.7944 | 6.725 | 6.6559 | 6.5875 | 6.5197 | 6.1637 | 5.7508 | 5.2631 | 7.5339 | 7.5218 | 7.5115 | 7.4975 | 7.4805 | 7.4605 | 7.4391 | 7.4252 | 7.4108 | 7.3608 | 7.2938 | 7.227 | 7.1564 | 7.0853
|  | KINGUSSIE | LW |  |  |  | 0.081053 | 7.8311 | 7.7952 | 7.7792 | 7.757 | 7.7318 | 7.7043 | 7.6753 | 7.6526 | 7.6297 | 7.6063 | 7.5835 | 7.3756 | 6.8521 | 6.1102 | 7.1604 | 7.0869 | 7.0253 | 6.9209 | 6.8152 | 6.7107 | 6.6074 | 6.5046 | 6.4025 | 6.3012 | 6.2015 | 5.6866 | 5.0859 | 4.2904 | 7.5339 | 7.498 | 7.4821 | 7.4599 | 7.4347 | 7.4072 | 7.3782 | 7.2786 | 7.1777 | 7.0775 | 6.9789 | 6.8816 | 6.7798 | 6.6772
|  | KINGUSSIE | ST |  |  |  | 0.081053 | 7.8311 | 7.8265 | 7.8243 | 7.8185 | 7.8114 | 7.803 | 7.7937 | 7.7902 | 7.7867 | 7.7834 | 7.7802 | 7.7656 | 7.6938 | 7.657 | 7.2123 | 7.2046 | 7.1985 | 7.1542 | 7.1091 | 7.0644 | 7.0197 | 6.9778 | 6.9366 | 6.8963 | 6.8568 | 6.6707 | 6.4372 | 6.2439 | 7.5339 | 7.5294 | 7.5272 | 7.5214 | 7.5143 | 7.5059 | 7.4966 | 7.4931 | 7.4896 | 7.4863 | 7.4831 | 7.4439 | 7.2127 | 7.0218
|  | KINGUSSIE | FS |  |  |  | 0.081053 | 7.8311 | 7.8269 | 7.8267 | 7.8265 | 7.8261 | 7.8257 | 7.8252 | 7.8234 | 7.8214 | 7.8192 | 7.8168 | 7.8103 | 7.7771 | 7.7046 | 7.2164 | 7.2094 | 7.2062 | 7.2008 | 7.1882 | 7.163 | 7.1379 | 7.1079 | 7.0777 | 7.0465 | 7.0151 | 6.8667 | 6.7018 | 6.5055 | 7.5339 | 7.5298 | 7.5296 | 7.5294 | 7.529 | 7.5286 | 7.5281 | 7.5263 | 7.5243 | 7.5221 | 7.5197 | 7.5132 | 7.4747 | 7.2803
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.012632 | 1.3674 | 1.3562 | 1.3513 | 1.3444 | 1.3366 | 1.3281 | 1.3191 | 1.3015 | 1.2646 | 1.2279 | 1.1917 | 1.0072 | 0.79597 | 0.52655 | 1.2918 | 1.2807 | 1.2757 | 1.2688 | 1.261 | 1.2525 | 1.2152 | 1.174 | 1.133 | 1.0922 | 1.052 | 0.84786 | 0.61669 | 0.32758 | 1.2818 | 1.2706 | 1.2657 | 1.2588 | 1.251 | 1.2425 | 1.2119 | 1.1696 | 1.1275 | 1.0857 | 1.0444 | 1.0035 | 0.96113 | 0.91939
|  | KINLOCH | CT |  |  |  | 0.012632 | 1.3674 | 1.3636 | 1.3604 | 1.3561 | 1.3508 | 1.3447 | 1.3381 | 1.3338 | 1.3294 | 1.325 | 1.3077 | 1.1802 | 1.033 | 0.8636 | 1.2918 | 1.288 | 1.2849 | 1.2805 | 1.2753 | 1.2691 | 1.2625 | 1.2583 | 1.2361 | 1.2079 | 1.1799 | 1.0387 | 0.87743 | 0.69423 | 1.2818 | 1.278 | 1.2748 | 1.2705 | 1.2652 | 1.2591 | 1.2525 | 1.2482 | 1.2331 | 1.2042 | 1.1754 | 1.1468 | 1.118 | 1.089
|  | KINLOCH | LW |  |  |  | 0.012632 | 1.3674 | 1.3562 | 1.3513 | 1.3444 | 1.3366 | 1.3281 | 1.3191 | 1.3015 | 1.2646 | 1.2279 | 1.1917 | 1.0072 | 0.79597 | 0.52655 | 1.2918 | 1.2807 | 1.2757 | 1.2688 | 1.261 | 1.2525 | 1.2152 | 1.174 | 1.133 | 1.0922 | 1.052 | 0.84786 | 0.61669 | 0.32758 | 1.2818 | 1.2706 | 1.2657 | 1.2588 | 1.251 | 1.2425 | 1.2119 | 1.1696 | 1.1275 | 1.0857 | 1.0444 | 1.0035 | 0.96113 | 0.91939
|  | KINLOCH | ST |  |  |  | 0.012632 | 1.3674 | 1.366 | 1.3653 | 1.3635 | 1.3614 | 1.3588 | 1.356 | 1.3549 | 1.3539 | 1.3528 | 1.3519 | 1.3474 | 1.2715 | 1.1977 | 1.2918 | 1.2904 | 1.2897 | 1.288 | 1.2858 | 1.2832 | 1.2804 | 1.2794 | 1.2783 | 1.2773 | 1.2763 | 1.2329 | 1.138 | 1.0555 | 1.2818 | 1.2804 | 1.2797 | 1.2779 | 1.2758 | 1.2732 | 1.2704 | 1.2693 | 1.2683 | 1.2672 | 1.2663 | 1.2292 | 1.132 | 1.0472
|  | KINLOCH | FS |  |  |  | 0.012632 | 1.3674 | 1.3661 | 1.3661 | 1.366 | 1.3659 | 1.3658 | 1.3656 | 1.3651 | 1.3645 | 1.3638 | 1.3631 | 1.3612 | 1.3513 | 1.3046 | 1.2918 | 1.2905 | 1.2905 | 1.2904 | 1.2903 | 1.2902 | 1.2901 | 1.2895 | 1.2889 | 1.2883 | 1.2875 | 1.2856 | 1.2504 | 1.1751 | 1.2818 | 1.2805 | 1.2805 | 1.2804 | 1.2803 | 1.2802 | 1.28 | 1.2795 | 1.2789 | 1.2782 | 1.2775 | 1.2756 | 1.2471 | 1.1701
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | 1.5267 | 1.523 | 1.5213 | 1.519 | 1.5164 | 1.4998 | 1.4809 | 1.4615 | 1.4422 | 1.4229 | 1.4038 | 1.3068 | 1.2004 | 1.0737 | 1.2954 | 1.2916 | 1.29 | 1.2877 | 1.2851 | 1.2822 | 1.2792 | 1.2769 | 1.2745 | 1.2721 | 1.2697 | 1.2267 | 1.1064 | 0.96592 | 1.4064 | 1.3956 | 1.385 | 1.366 | 1.3455 | 1.325 | 1.3043 | 1.2826 | 1.261 | 1.2394 | 1.218 | 1.1967 | 1.1749 | 1.153
|  | KINLOCH RANNOCH | CT |  |  |  | 0 | 1.5267 | 1.5254 | 1.5244 | 1.5229 | 1.5211 | 1.519 | 1.5149 | 1.5017 | 1.4885 | 1.4753 | 1.4622 | 1.3949 | 1.3216 | 1.2403 | 1.2954 | 1.2941 | 1.293 | 1.2916 | 1.2898 | 1.2877 | 1.2855 | 1.284 | 1.2825 | 1.281 | 1.2795 | 1.2695 | 1.2442 | 1.1534 | 1.4064 | 1.4023 | 1.3947 | 1.3819 | 1.3689 | 1.355 | 1.3411 | 1.3269 | 1.3125 | 1.2978 | 1.2831 | 1.2685 | 1.2534 | 1.2383
|  | KINLOCH RANNOCH | LW |  |  |  | 0 | 1.5267 | 1.523 | 1.5213 | 1.519 | 1.5164 | 1.4998 | 1.4809 | 1.4615 | 1.4422 | 1.4229 | 1.4038 | 1.3068 | 1.2004 | 1.0737 | 1.2954 | 1.2916 | 1.29 | 1.2877 | 1.2851 | 1.2822 | 1.2792 | 1.2769 | 1.2745 | 1.2721 | 1.2697 | 1.2267 | 1.1064 | 0.96592 | 1.4064 | 1.3956 | 1.385 | 1.366 | 1.3455 | 1.325 | 1.3043 | 1.2826 | 1.261 | 1.2394 | 1.218 | 1.1967 | 1.1749 | 1.153
|  | KINLOCH RANNOCH | ST |  |  |  | 0 | 1.5267 | 1.5262 | 1.526 | 1.5254 | 1.5246 | 1.5238 | 1.5228 | 1.5224 | 1.5221 | 1.5217 | 1.5179 | 1.4775 | 1.4341 | 1.3948 | 1.2954 | 1.2949 | 1.2947 | 1.294 | 1.2933 | 1.2924 | 1.2914 | 1.2911 | 1.2907 | 1.2904 | 1.29 | 1.2885 | 1.281 | 1.2771 | 1.4064 | 1.4059 | 1.4057 | 1.4051 | 1.3974 | 1.3889 | 1.3805 | 1.3717 | 1.3625 | 1.3532 | 1.344 | 1.2993 | 1.2509 | 1.2068
|  | KINLOCH RANNOCH | FS |  |  |  | 0 | 1.5267 | 1.5263 | 1.5262 | 1.5262 | 1.5262 | 1.5261 | 1.5261 | 1.5259 | 1.5257 | 1.5255 | 1.5252 | 1.5159 | 1.4856 | 1.4517 | 1.2954 | 1.2949 | 1.2949 | 1.2949 | 1.2948 | 1.2948 | 1.2947 | 1.2946 | 1.2943 | 1.2941 | 1.2939 | 1.2932 | 1.2897 | 1.2821 | 1.4064 | 1.406 | 1.4059 | 1.4059 | 1.4059 | 1.4052 | 1.3998 | 1.394 | 1.3882 | 1.3825 | 1.3759 | 1.3415 | 1.3083 | 1.2707
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | YES | 0 | 0.47609 | 0.47022 | 0.46761 | 0.46397 | 0.45985 | 0.45537 | 0.44807 | 0.43408 | 0.41801 | 0.40205 | 0.38634 | 0.30494 | 0.21125 | 0.087587 | 0.47509 | 0.46235 | 0.45111 | 0.43203 | 0.41275 | 0.3937 | 0.37485 | 0.35657 | 0.33844 | 0.32045 | 0.30274 | 0.21156 | 0.10808 | -0.024988 | 0.39526 | 0.38939 | 0.38678 | 0.38315 | 0.37902 | 0.37454 | 0.36983 | 0.36615 | 0.36243 | 0.35866 | 0.35497 | 0.35133 | 0.34687 | 0.34223
|  | KINLOCHEWE | CT |  |  |  | 0 | 0.47609 | 0.47413 | 0.47247 | 0.47023 | 0.46748 | 0.46428 | 0.46086 | 0.45863 | 0.45523 | 0.44667 | 0.43629 | 0.3798 | 0.3151 | 0.23929 | 0.47617 | 0.46929 | 0.46141 | 0.44826 | 0.43481 | 0.42132 | 0.40791 | 0.39538 | 0.38291 | 0.37056 | 0.35835 | 0.29494 | 0.22335 | 0.14085 | 0.39526 | 0.3933 | 0.39165 | 0.3894 | 0.38665 | 0.38345 | 0.38003 | 0.3778 | 0.37551 | 0.37321 | 0.3709 | 0.36851 | 0.36554 | 0.36248
|  | KINLOCHEWE | LW |  |  |  | 0 | 0.47609 | 0.47022 | 0.46761 | 0.46397 | 0.45985 | 0.45537 | 0.44807 | 0.43408 | 0.41801 | 0.40205 | 0.38634 | 0.30494 | 0.21125 | 0.087587 | 0.47509 | 0.46235 | 0.45111 | 0.43203 | 0.41275 | 0.3937 | 0.37485 | 0.35657 | 0.33844 | 0.32045 | 0.30274 | 0.21156 | 0.10808 | -0.024988 | 0.39526 | 0.38939 | 0.38678 | 0.38315 | 0.37902 | 0.37454 | 0.36983 | 0.36615 | 0.36243 | 0.35866 | 0.35497 | 0.35133 | 0.34687 | 0.34223
|  | KINLOCHEWE | ST |  |  |  | 0 | 0.47609 | 0.47537 | 0.47503 | 0.47411 | 0.47299 | 0.47168 | 0.47022 | 0.46967 | 0.46912 | 0.46859 | 0.46809 | 0.46312 | 0.42968 | 0.40038 | 0.47726 | 0.47655 | 0.47621 | 0.47369 | 0.46581 | 0.45799 | 0.45019 | 0.44298 | 0.43588 | 0.42894 | 0.42214 | 0.38984 | 0.35013 | 0.3169 | 0.39526 | 0.39455 | 0.39421 | 0.39329 | 0.39217 | 0.39086 | 0.38939 | 0.38885 | 0.3883 | 0.38777 | 0.38726 | 0.38499 | 0.37395 | 0.36831
|  | KINLOCHEWE | FS |  |  |  | 0 | 0.47609 | 0.47546 | 0.47543 | 0.4754 | 0.47535 | 0.47528 | 0.47521 | 0.47494 | 0.47463 | 0.4743 | 0.47393 | 0.47297 | 0.466 | 0.43977 | 0.47726 | 0.47663 | 0.47661 | 0.47657 | 0.47652 | 0.47631 | 0.47188 | 0.46683 | 0.46176 | 0.45577 | 0.44976 | 0.42097 | 0.39315 | 0.3615 | 0.39526 | 0.39463 | 0.3946 | 0.39457 | 0.39452 | 0.39445 | 0.39438 | 0.39411 | 0.39381 | 0.39347 | 0.39311 | 0.39214 | 0.38716 | 0.37635
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0.0052632 | 2.8277 | 2.8184 | 2.8143 | 2.8085 | 2.802 | 2.7948 | 2.7873 | 2.7814 | 2.7753 | 2.7692 | 2.7512 | 2.6379 | 2.5001 | 2.3065 | 2.867 | 2.8573 | 2.8527 | 2.846 | 2.8386 | 2.8305 | 2.8221 | 2.8153 | 2.8084 | 2.8013 | 2.7944 | 2.7445 | 2.5931 | 2.3859 | 2.3842 | 2.3749 | 2.3707 | 2.365 | 2.3585 | 2.3513 | 2.3438 | 2.3378 | 2.3318 | 2.3256 | 2.3196 | 2.3136 | 2.306 | 2.2982
|  | KINLOCHLEVEN | CT |  |  |  | 0.0052632 | 2.8277 | 2.8245 | 2.8218 | 2.8181 | 2.8136 | 2.8084 | 2.8027 | 2.799 | 2.7951 | 2.7913 | 2.7873 | 2.7369 | 2.6389 | 2.5183 | 2.8672 | 2.8637 | 2.8606 | 2.8563 | 2.8511 | 2.8452 | 2.8389 | 2.8346 | 2.8301 | 2.8256 | 2.821 | 2.792 | 2.7467 | 2.6163 | 2.3842 | 2.381 | 2.3783 | 2.3746 | 2.3701 | 2.3649 | 2.3592 | 2.3555 | 2.3516 | 2.3477 | 2.3438 | 2.3397 | 2.3345 | 2.3292
|  | KINLOCHLEVEN | LW |  |  |  | 0.0052632 | 2.8277 | 2.8184 | 2.8143 | 2.8085 | 2.802 | 2.7948 | 2.7873 | 2.7814 | 2.7753 | 2.7692 | 2.7512 | 2.6379 | 2.5001 | 2.3065 | 2.867 | 2.8573 | 2.8527 | 2.846 | 2.8386 | 2.8305 | 2.8221 | 2.8153 | 2.8084 | 2.8013 | 2.7944 | 2.7445 | 2.5931 | 2.3859 | 2.3842 | 2.3749 | 2.3707 | 2.365 | 2.3585 | 2.3513 | 2.3438 | 2.3378 | 2.3318 | 2.3256 | 2.3196 | 2.3136 | 2.306 | 2.2982
|  | KINLOCHLEVEN | ST |  |  |  | 0.0052632 | 2.8277 | 2.8264 | 2.8258 | 2.8243 | 2.8223 | 2.82 | 2.8175 | 2.8166 | 2.8156 | 2.8147 | 2.8138 | 2.8098 | 2.7896 | 2.7546 | 2.8677 | 2.8664 | 2.8658 | 2.8638 | 2.8615 | 2.8588 | 2.8559 | 2.8545 | 2.8531 | 2.8517 | 2.8504 | 2.8444 | 2.8221 | 2.8097 | 2.3842 | 2.3829 | 2.3823 | 2.3807 | 2.3788 | 2.3765 | 2.374 | 2.373 | 2.3721 | 2.3712 | 2.3703 | 2.3663 | 2.346 | 2.3355
|  | KINLOCHLEVEN | FS |  |  |  | 0.0052632 | 2.8277 | 2.8265 | 2.8264 | 2.8264 | 2.8263 | 2.8261 | 2.826 | 2.8255 | 2.8249 | 2.8243 | 2.8236 | 2.8218 | 2.8122 | 2.7911 | 2.8677 | 2.8665 | 2.8664 | 2.8663 | 2.8661 | 2.8657 | 2.8652 | 2.8644 | 2.8635 | 2.8625 | 2.8615 | 2.858 | 2.8468 | 2.8242 | 2.3842 | 2.383 | 2.3829 | 2.3828 | 2.3827 | 2.3826 | 2.3825 | 2.382 | 2.3814 | 2.3808 | 2.3801 | 2.3782 | 2.3686 | 2.3476
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 0 | 1.0347 | 1.0344 | 1.0343 | 1.034 | 1.0338 | 1.0335 | 1.0333 | 1.033 | 1.0328 | 1.0326 | 1.0323 | 1.0253 | 1.0177 | 1.0083 | 1.0177 | 1.0173 | 1.0172 | 1.017 | 1.0167 | 1.0165 | 1.0162 | 1.0159 | 1.0144 | 1.0129 | 1.0114 | 1.0037 | 0.9952 | 0.98487 | 1.0219 | 1.0216 | 1.0214 | 1.0212 | 1.021 | 1.0207 | 1.0204 | 1.0188 | 1.0172 | 1.0156 | 1.014 | 1.0124 | 1.0109 | 1.0092
|  | KINLOCHMOIDART | CT |  |  |  | 0 | 1.0347 | 1.0346 | 1.0345 | 1.0344 | 1.0343 | 1.0341 | 1.0339 | 1.0337 | 1.0336 | 1.0335 | 1.0333 | 1.0325 | 1.0312 | 1.0292 | 1.0177 | 1.0176 | 1.0175 | 1.0173 | 1.0172 | 1.017 | 1.0168 | 1.0167 | 1.0166 | 1.0164 | 1.0163 | 1.0154 | 1.0141 | 1.0121 | 1.0219 | 1.0218 | 1.0217 | 1.0216 | 1.0214 | 1.0212 | 1.021 | 1.0209 | 1.0208 | 1.0207 | 1.0205 | 1.0204 | 1.0202 | 1.02
|  | KINLOCHMOIDART | LW |  |  |  | 0 | 1.0347 | 1.0344 | 1.0343 | 1.034 | 1.0338 | 1.0335 | 1.0333 | 1.033 | 1.0328 | 1.0326 | 1.0323 | 1.0253 | 1.0177 | 1.0083 | 1.0177 | 1.0173 | 1.0172 | 1.017 | 1.0167 | 1.0165 | 1.0162 | 1.0159 | 1.0144 | 1.0129 | 1.0114 | 1.0037 | 0.9952 | 0.98487 | 1.0219 | 1.0216 | 1.0214 | 1.0212 | 1.021 | 1.0207 | 1.0204 | 1.0188 | 1.0172 | 1.0156 | 1.014 | 1.0124 | 1.0109 | 1.0092
|  | KINLOCHMOIDART | ST |  |  |  | 0 | 1.0347 | 1.0347 | 1.0347 | 1.0346 | 1.0346 | 1.0345 | 1.0344 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0342 | 1.0335 | 1.0332 | 1.0177 | 1.0176 | 1.0176 | 1.0176 | 1.0175 | 1.0174 | 1.0174 | 1.0173 | 1.0173 | 1.0173 | 1.0172 | 1.0171 | 1.0165 | 1.0162 | 1.0219 | 1.0219 | 1.0219 | 1.0218 | 1.0217 | 1.0217 | 1.0216 | 1.0216 | 1.0215 | 1.0215 | 1.0215 | 1.0213 | 1.0207 | 1.0204
|  | KINLOCHMOIDART | FS |  |  |  | 0 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0347 | 1.0346 | 1.0346 | 1.0346 | 1.0343 | 1.0337 | 1.0177 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0176 | 1.0175 | 1.0172 | 1.0166 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 1.0218 | 1.0218 | 1.0218 | 1.0217 | 1.0215 | 1.0209
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.021053 | 14.5702 | 14.5546 | 14.5431 | 14.5276 | 14.5103 | 14.4907 | 14.4702 | 14.4536 | 14.4367 | 14.4197 | 14.4029 | 14.2969 | 14.136 | 13.8451 | 13.8168 | 13.799 | 13.7814 | 13.7161 | 13.65 | 13.5837 | 13.5182 | 13.4537 | 13.3897 | 13.3261 | 13.2634 | 12.9339 | 12.5443 | 12.0275 | 14.222 | 14.1818 | 14.1469 | 14.0888 | 14.0296 | 13.97 | 13.911 | 13.8533 | 13.796 | 13.7391 | 13.683 | 13.6268 | 13.5671 | 13.5069
|  | KINLOSS | CT |  |  |  | 0.021053 | 14.5702 | 14.5575 | 14.5468 | 14.5338 | 14.5189 | 14.5022 | 14.4845 | 14.4707 | 14.4565 | 14.4423 | 14.4281 | 14.3411 | 14.2135 | 14.0291 | 13.8168 | 13.8028 | 13.7906 | 13.7575 | 13.7089 | 13.6599 | 13.6112 | 13.5641 | 13.5171 | 13.4705 | 13.4243 | 13.1803 | 12.8944 | 12.5552 | 14.222 | 14.1949 | 14.1676 | 14.1251 | 14.0813 | 14.037 | 13.9927 | 13.9503 | 13.908 | 13.8661 | 13.8245 | 13.7829 | 13.7388 | 13.6945
|  | KINLOSS | LW |  |  |  | 0.021053 | 14.5786 | 14.5546 | 14.5431 | 14.5276 | 14.5103 | 14.4907 | 14.4702 | 14.4536 | 14.4367 | 14.4197 | 14.4029 | 14.2969 | 14.136 | 13.8451 | 13.8248 | 13.799 | 13.7814 | 13.7161 | 13.65 | 13.5837 | 13.5182 | 13.4537 | 13.3897 | 13.3261 | 13.2634 | 12.9339 | 12.5443 | 12.0275 | 14.2253 | 14.1818 | 14.1469 | 14.0888 | 14.0296 | 13.97 | 13.911 | 13.8533 | 13.796 | 13.7391 | 13.683 | 13.6268 | 13.5671 | 13.5069
|  | KINLOSS | ST |  |  |  | 0.021053 | 14.5803 | 14.5766 | 14.5743 | 14.5698 | 14.5636 | 14.5567 | 14.5491 | 14.5452 | 14.5421 | 14.5392 | 14.5363 | 14.5203 | 14.4671 | 14.4352 | 13.8289 | 13.8251 | 13.8227 | 13.8164 | 13.8084 | 13.7997 | 13.7773 | 13.7502 | 13.7245 | 13.6992 | 13.6745 | 13.5571 | 13.4083 | 13.284 | 14.2536 | 14.2483 | 14.2447 | 14.2206 | 14.1951 | 14.1697 | 14.1442 | 14.1205 | 14.098 | 14.076 | 14.0544 | 13.9514 | 13.8164 | 13.7053
|  | KINLOSS | FS |  |  |  | 0.021053 | 14.5803 | 14.5767 | 14.5758 | 14.5748 | 14.5737 | 14.5726 | 14.5715 | 14.5695 | 14.5673 | 14.5651 | 14.5627 | 14.5543 | 14.5287 | 14.4777 | 13.829 | 13.8254 | 13.8243 | 13.8231 | 13.8214 | 13.8191 | 13.8167 | 13.8134 | 13.8098 | 13.7906 | 13.7713 | 13.6802 | 13.5767 | 13.4516 | 14.2546 | 14.2497 | 14.2473 | 14.2441 | 14.2365 | 14.2222 | 14.2079 | 14.1914 | 14.1747 | 14.1579 | 14.141 | 14.0618 | 13.9694 | 13.855
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0.22526 | 9.7228 | 9.6924 | 9.6762 | 9.654 | 9.628 | 9.5999 | 9.5704 | 9.547 | 9.5233 | 9.4992 | 9.4757 | 9.1972 | 8.7324 | 8.0826 | 8.3069 | 8.2421 | 8.1904 | 8.1037 | 8.0149 | 7.9273 | 7.8409 | 7.7568 | 7.6736 | 7.5911 | 7.5102 | 7.0877 | 6.5828 | 5.8939 | 8.642 | 8.6116 | 8.5954 | 8.5732 | 8.5472 | 8.5191 | 8.4896 | 8.4662 | 8.4425 | 8.4184 | 8.3949 | 8.3716 | 8.2873 | 8.2015
|  | KIPPEN | CT |  |  |  | 0.22526 | 9.7228 | 9.7078 | 9.6945 | 9.6777 | 9.6579 | 9.6355 | 9.6116 | 9.5949 | 9.5778 | 9.5606 | 9.5433 | 9.4348 | 9.1899 | 8.7874 | 8.31 | 8.2728 | 8.2349 | 8.1727 | 8.1086 | 8.0443 | 7.9803 | 7.9216 | 7.8631 | 7.8053 | 7.7483 | 7.4461 | 7.0889 | 6.6597 | 8.642 | 8.6269 | 8.6137 | 8.5969 | 8.5771 | 8.5547 | 8.5308 | 8.5141 | 8.497 | 8.4798 | 8.4625 | 8.4447 | 8.4234 | 8.4015
|  | KIPPEN | LW |  |  |  | 0.22526 | 9.7278 | 9.6924 | 9.6762 | 9.654 | 9.628 | 9.5999 | 9.5704 | 9.547 | 9.5233 | 9.4992 | 9.4757 | 9.1972 | 8.7324 | 8.0826 | 8.3069 | 8.2421 | 8.1904 | 8.1037 | 8.0149 | 7.9273 | 7.8409 | 7.7568 | 7.6736 | 7.5911 | 7.5102 | 7.0877 | 6.5828 | 5.8939 | 8.647 | 8.6116 | 8.5954 | 8.5732 | 8.5472 | 8.5191 | 8.4896 | 8.4662 | 8.4425 | 8.4184 | 8.3949 | 8.3716 | 8.2873 | 8.2015
|  | KIPPEN | ST |  |  |  | 0.22526 | 9.7287 | 9.7235 | 9.7206 | 9.7142 | 9.7066 | 9.6979 | 9.6882 | 9.6841 | 9.6799 | 9.6759 | 9.672 | 9.654 | 9.5824 | 9.5437 | 8.3491 | 8.3418 | 8.3367 | 8.3011 | 8.2647 | 8.2286 | 8.1927 | 8.1594 | 8.1267 | 8.0949 | 8.064 | 7.9216 | 7.7348 | 7.5867 | 8.6479 | 8.6427 | 8.6398 | 8.6334 | 8.6258 | 8.6171 | 8.6074 | 8.6033 | 8.5991 | 8.5951 | 8.5912 | 8.5732 | 8.5016 | 8.4629
|  | KIPPEN | FS |  |  |  | 0.22526 | 9.7304 | 9.7264 | 9.7254 | 9.7244 | 9.7232 | 9.722 | 9.7207 | 9.7182 | 9.7154 | 9.7125 | 9.7094 | 9.6992 | 9.6639 | 9.5921 | 8.3549 | 8.3491 | 8.346 | 8.3417 | 8.3314 | 8.3115 | 8.2908 | 8.2663 | 8.2417 | 8.2169 | 8.1921 | 8.0755 | 7.942 | 7.7785 | 8.6496 | 8.6456 | 8.6446 | 8.6436 | 8.6424 | 8.6411 | 8.6399 | 8.6374 | 8.6346 | 8.6317 | 8.6286 | 8.6183 | 8.5831 | 8.5113
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 7.9389 | 36.1954 | 36.0295 | 35.9052 | 35.7011 | 35.4914 | 35.2804 | 35.0387 | 34.7985 | 34.5597 | 34.3223 | 34.0884 | 32.8537 | 31.355 | 29.2615 | 35.2421 | 35.1484 | 35.102 | 35.0382 | 34.8026 | 34.5243 | 34.2488 | 33.9781 | 33.7092 | 33.4421 | 33.179 | 31.8009 | 30.1697 | 27.9701 | 34.9137 | 34.8199 | 34.7736 | 34.7098 | 34.6375 | 34.5578 | 34.474 | 34.4077 | 34.3405 | 34.2721 | 34.205 | 34.1377 | 34.0549 | 33.969
|  | KIRKWALL | CT |  |  |  | 7.9389 | 36.2035 | 36.1158 | 36.0276 | 35.8854 | 35.7361 | 35.5828 | 35.4285 | 35.2887 | 35.1263 | 34.9609 | 34.7969 | 33.9217 | 32.8688 | 31.583 | 35.2421 | 35.2021 | 35.1683 | 35.1239 | 35.0705 | 34.919 | 34.7194 | 34.5311 | 34.3433 | 34.1572 | 33.9727 | 32.9971 | 31.8424 | 30.4567 | 34.9137 | 34.8737 | 34.8398 | 34.7955 | 34.7421 | 34.6804 | 34.6145 | 34.5692 | 34.5224 | 34.4754 | 34.428 | 34.379 | 34.3188 | 34.2568
|  | KIRKWALL | LW |  |  |  | 7.9389 | 36.1954 | 36.0295 | 35.9052 | 35.7011 | 35.4914 | 35.2804 | 35.0387 | 34.7985 | 34.5597 | 34.3223 | 34.0884 | 32.8537 | 31.355 | 29.2615 | 35.2505 | 35.1484 | 35.102 | 35.0382 | 34.8026 | 34.5243 | 34.2488 | 33.9781 | 33.7092 | 33.4421 | 33.179 | 31.8009 | 30.1697 | 27.9701 | 34.9221 | 34.8199 | 34.7736 | 34.7098 | 34.6375 | 34.5578 | 34.474 | 34.4077 | 34.3405 | 34.2721 | 34.205 | 34.1377 | 34.0549 | 33.969
|  | KIRKWALL | ST |  |  |  | 7.9389 | 36.2856 | 36.2663 | 36.2535 | 36.1708 | 36.0844 | 35.9971 | 35.9088 | 35.8325 | 35.7581 | 35.6855 | 35.6146 | 35.2349 | 34.6614 | 34.2 | 35.2522 | 35.2381 | 35.231 | 35.2131 | 35.1907 | 35.1648 | 35.136 | 35.1242 | 35.1131 | 35.0263 | 34.9242 | 34.4372 | 33.8013 | 33.2794 | 34.9238 | 34.9097 | 34.9026 | 34.8847 | 34.8623 | 34.8363 | 34.8076 | 34.7958 | 34.7847 | 34.7741 | 34.7639 | 34.7148 | 34.4968 | 34.3802
|  | KIRKWALL | FS |  |  |  | 7.9389 | 36.29 | 36.2727 | 36.2663 | 36.2569 | 36.2342 | 36.1893 | 36.1445 | 36.0892 | 36.0334 | 35.977 | 35.9203 | 35.6581 | 35.2937 | 34.7956 | 35.2522 | 35.239 | 35.2376 | 35.2361 | 35.2342 | 35.232 | 35.2298 | 35.2237 | 35.2168 | 35.2094 | 35.2014 | 34.946 | 34.5007 | 33.9538 | 34.9238 | 34.9105 | 34.9091 | 34.9076 | 34.9058 | 34.9036 | 34.9014 | 34.8953 | 34.8884 | 34.881 | 34.873 | 34.8497 | 34.7465 | 34.5263
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0 | 1.3531 | 1.3506 | 1.3493 | 1.3475 | 1.3455 | 1.3434 | 1.3412 | 1.3394 | 1.3375 | 1.3357 | 1.3339 | 1.3224 | 1.288 | 1.2418 | 1.2357 | 1.2333 | 1.2323 | 1.2309 | 1.2292 | 1.2275 | 1.2256 | 1.2241 | 1.2227 | 1.2212 | 1.2197 | 1.2108 | 1.197 | 1.1629 | 1.2946 | 1.2922 | 1.2912 | 1.2898 | 1.2881 | 1.2864 | 1.2845 | 1.2831 | 1.2816 | 1.2801 | 1.2786 | 1.2772 | 1.2745 | 1.268
|  | KISHORNHILL | CT |  |  |  | 0 | 1.3531 | 1.3522 | 1.3514 | 1.3502 | 1.3488 | 1.3472 | 1.3456 | 1.3444 | 1.3432 | 1.342 | 1.3408 | 1.3335 | 1.3176 | 1.2872 | 1.2357 | 1.2349 | 1.2342 | 1.2333 | 1.2322 | 1.231 | 1.2296 | 1.2287 | 1.2278 | 1.2269 | 1.226 | 1.22 | 1.2108 | 1.1966 | 1.2946 | 1.2938 | 1.2931 | 1.2922 | 1.2911 | 1.2899 | 1.2885 | 1.2876 | 1.2867 | 1.2858 | 1.2849 | 1.2839 | 1.2828 | 1.2815
|  | KISHORNHILL | LW |  |  |  | 0 | 1.3531 | 1.3506 | 1.3493 | 1.3475 | 1.3455 | 1.3434 | 1.3412 | 1.3394 | 1.3375 | 1.3357 | 1.3339 | 1.3224 | 1.288 | 1.2418 | 1.2357 | 1.2333 | 1.2323 | 1.2309 | 1.2292 | 1.2275 | 1.2256 | 1.2241 | 1.2227 | 1.2212 | 1.2197 | 1.2108 | 1.197 | 1.1629 | 1.2946 | 1.2922 | 1.2912 | 1.2898 | 1.2881 | 1.2864 | 1.2845 | 1.2831 | 1.2816 | 1.2801 | 1.2786 | 1.2772 | 1.2745 | 1.268
|  | KISHORNHILL | ST |  |  |  | 0 | 1.3534 | 1.3531 | 1.3529 | 1.3524 | 1.3518 | 1.3511 | 1.3503 | 1.3499 | 1.3495 | 1.3492 | 1.3488 | 1.3471 | 1.342 | 1.339 | 1.2357 | 1.2354 | 1.2352 | 1.2349 | 1.2344 | 1.2339 | 1.2333 | 1.2331 | 1.2329 | 1.2327 | 1.2325 | 1.2316 | 1.2272 | 1.2249 | 1.2946 | 1.2943 | 1.2941 | 1.2938 | 1.2933 | 1.2928 | 1.2922 | 1.292 | 1.2918 | 1.2916 | 1.2914 | 1.2905 | 1.2861 | 1.2838
|  | KISHORNHILL | FS |  |  |  | 0 | 1.3534 | 1.3531 | 1.3531 | 1.3531 | 1.353 | 1.3529 | 1.3527 | 1.3524 | 1.3522 | 1.3519 | 1.3516 | 1.3505 | 1.3478 | 1.3427 | 1.2357 | 1.2354 | 1.2354 | 1.2354 | 1.2354 | 1.2353 | 1.2353 | 1.2352 | 1.2351 | 1.2349 | 1.2348 | 1.2344 | 1.2324 | 1.228 | 1.2946 | 1.2943 | 1.2943 | 1.2943 | 1.2943 | 1.2942 | 1.2942 | 1.2941 | 1.294 | 1.2938 | 1.2937 | 1.2933 | 1.2913 | 1.2869
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0 | 5.9367 | 7.2258 | 7.2199 | 7.2108 | 7.2006 | 7.1895 | 7.1778 | 7.1685 | 7.1309 | 7.0934 | 7.0563 | 6.8622 | 6.6357 | 6.3293 | 5.8515 | 7.1398 | 7.1323 | 7.1114 | 7.0778 | 7.0339 | 6.9905 | 6.9472 | 6.9043 | 6.8616 | 6.8194 | 6.6003 | 6.3483 | 6.0167 | 5.7942 | 7.0834 | 7.0774 | 7.0683 | 7.0581 | 7.047 | 7.0085 | 6.9658 | 6.9234 | 6.8813 | 6.8396 | 6.7985 | 6.7551 | 6.7115
|  | KYLE | CT |  |  |  | 0 | 5.9367 | 7.2312 | 7.2265 | 7.2204 | 7.2131 | 7.2047 | 7.1957 | 7.1896 | 7.1833 | 7.1769 | 7.1633 | 7.0249 | 6.8598 | 6.6645 | 5.8515 | 7.1458 | 7.14 | 7.1319 | 7.1133 | 7.09 | 7.0609 | 7.0305 | 7.0003 | 6.9703 | 6.9405 | 6.7847 | 6.6015 | 6.3884 | 5.7942 | 7.0888 | 7.084 | 7.0779 | 7.0706 | 7.0622 | 7.0533 | 7.0471 | 7.0183 | 6.9886 | 6.9592 | 6.9299 | 6.899 | 6.868
|  | KYLE | LW |  |  |  | 0 | 5.9392 | 7.2258 | 7.2199 | 7.2108 | 7.2006 | 7.1895 | 7.1778 | 7.1685 | 7.1309 | 7.0934 | 7.0563 | 6.8622 | 6.6357 | 6.3293 | 5.854 | 7.1398 | 7.1323 | 7.1114 | 7.0778 | 7.0339 | 6.9905 | 6.9472 | 6.9043 | 6.8616 | 6.8194 | 6.6003 | 6.3483 | 6.0167 | 5.7967 | 7.0834 | 7.0774 | 7.0683 | 7.0581 | 7.047 | 7.0085 | 6.9658 | 6.9234 | 6.8813 | 6.8396 | 6.7985 | 6.7551 | 6.7115
|  | KYLE | ST |  |  |  | 0 | 5.9392 | 7.2375 | 7.2366 | 7.2344 | 7.2316 | 7.2284 | 7.2249 | 7.2235 | 7.2222 | 7.2209 | 7.2197 | 7.2141 | 7.1448 | 7.0719 | 5.854 | 7.1523 | 7.1514 | 7.1492 | 7.1457 | 7.1413 | 7.1365 | 7.1299 | 7.1184 | 7.1072 | 7.0935 | 7.0145 | 6.9157 | 6.8321 | 5.7967 | 7.095 | 7.0941 | 7.0919 | 7.0892 | 7.086 | 7.0824 | 7.0811 | 7.0797 | 7.0784 | 7.0772 | 7.0328 | 6.9351 | 6.8527
|  | KYLE | FS |  |  |  | 0 | 5.94 | 7.2384 | 7.2383 | 7.2382 | 7.2381 | 7.2379 | 7.2378 | 7.2371 | 7.2363 | 7.2354 | 7.2345 | 7.232 | 7.2189 | 7.1707 | 5.8548 | 7.1532 | 7.1531 | 7.1531 | 7.1529 | 7.1527 | 7.1522 | 7.1506 | 7.1488 | 7.147 | 7.1432 | 7.0973 | 7.0281 | 6.9456 | 5.7976 | 7.0959 | 7.0959 | 7.0958 | 7.0956 | 7.0955 | 7.0953 | 7.0946 | 7.0938 | 7.0929 | 7.092 | 7.0895 | 7.0462 | 6.9646
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 0.22105 | 1.4799 | 1.4538 | 1.4293 | 1.4033 | 1.376 | 1.3476 | 1.3194 | 1.2926 | 1.2551 | 1.215 | 1.1751 | 0.95723 | 0.69126 | 0.29431 | 1.3704 | 1.3443 | 1.3199 | 1.2939 | 1.2565 | 1.208 | 1.1605 | 1.1137 | 1.067 | 1.0197 | 0.97273 | 0.72065 | 0.40114 | -0.030603 | 1.3675 | 1.3414 | 1.3169 | 1.2869 | 1.2403 | 1.1934 | 1.1475 | 1.1022 | 1.0571 | 1.0114 | 0.96597 | 0.92062 | 0.873 | 0.82352
|  | LAIRG | CT |  |  |  | 0.22105 | 1.4799 | 1.4538 | 1.4293 | 1.4033 | 1.376 | 1.3476 | 1.3194 | 1.2926 | 1.2551 | 1.215 | 1.1751 | 0.95723 | 0.69126 | 0.36048 | 1.3704 | 1.3443 | 1.3199 | 1.2939 | 1.2565 | 1.208 | 1.1605 | 1.1137 | 1.067 | 1.0197 | 0.97273 | 0.72065 | 0.42433 | 0.071454 | 1.3675 | 1.3414 | 1.3169 | 1.2869 | 1.2403 | 1.1934 | 1.1475 | 1.1022 | 1.0571 | 1.0114 | 0.96597 | 0.92062 | 0.873 | 0.82352
|  | LAIRG | LW |  |  |  | 0.22105 | 1.5161 | 1.4951 | 1.4809 | 1.4631 | 1.4433 | 1.4217 | 1.3867 | 1.3481 | 1.309 | 1.2691 | 1.2297 | 1.0052 | 0.70228 | 0.29431 | 1.4066 | 1.3857 | 1.3714 | 1.3457 | 1.2967 | 1.2474 | 1.1977 | 1.1486 | 1.099 | 1.0489 | 0.99953 | 0.73269 | 0.40114 | -0.030603 | 1.4037 | 1.3827 | 1.3685 | 1.3293 | 1.2827 | 1.2356 | 1.188 | 1.1412 | 1.0939 | 1.0461 | 0.99885 | 0.95134 | 0.90096 | 0.84939
|  | LAIRG | ST |  |  |  | 0.22105 | 1.522 | 1.5151 | 1.5092 | 1.5017 | 1.4929 | 1.4837 | 1.474 | 1.4667 | 1.4593 | 1.4521 | 1.4457 | 1.3949 | 1.3008 | 1.2181 | 1.4125 | 1.4056 | 1.3997 | 1.3923 | 1.3835 | 1.3742 | 1.3645 | 1.3572 | 1.338 | 1.3175 | 1.2981 | 1.2029 | 1.0873 | 0.98407 | 1.4096 | 1.4027 | 1.3968 | 1.3893 | 1.3805 | 1.3713 | 1.3616 | 1.3418 | 1.3219 | 1.3025 | 1.2842 | 1.1939 | 1.083 | 0.98422
|  | LAIRG | FS |  |  |  | 0.22105 | 1.5262 | 1.522 | 1.5178 | 1.5143 | 1.5108 | 1.5073 | 1.5037 | 1.4996 | 1.4955 | 1.4912 | 1.4869 | 1.4642 | 1.423 | 1.3517 | 1.4167 | 1.4126 | 1.4083 | 1.4048 | 1.4013 | 1.3978 | 1.3943 | 1.3902 | 1.386 | 1.3818 | 1.3775 | 1.3149 | 1.2367 | 1.1501 | 1.4138 | 1.4096 | 1.4054 | 1.4019 | 1.3984 | 1.3949 | 1.3913 | 1.3872 | 1.3831 | 1.3789 | 1.3674 | 1.3011 | 1.2264 | 1.1432
| MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0.0010526 | 3.3723 | 3.3482 | 3.3252 | 3.2999 | 3.2729 | 3.2449 | 3.2161 | 3.191 | 3.1647 | 3.1384 | 3.112 | 2.959 | 2.6462 | 2.1626 | 3.3342 | 3.31 | 3.2869 | 3.2334 | 3.1786 | 3.1211 | 3.0597 | 2.9985 | 2.937 | 2.876 | 2.8151 | 2.4915 | 2.1026 | 1.5823 | 3.3683 | 3.3441 | 3.3211 | 3.2959 | 3.2688 | 3.2409 | 3.2121 | 3.187 | 3.1607 | 3.1344 | 3.108 | 3.0813 | 3.0516 | 3.0207
|  | LATHERON | CT |  |  |  | 0.0010526 | 3.3723 | 3.3482 | 3.3252 | 3.2999 | 3.2729 | 3.2449 | 3.2161 | 3.191 | 3.1647 | 3.1384 | 3.112 | 2.959 | 2.7525 | 2.3861 | 3.3342 | 3.31 | 3.2869 | 3.2334 | 3.1786 | 3.1246 | 3.0707 | 3.0184 | 2.9654 | 2.9129 | 2.8608 | 2.5852 | 2.2536 | 1.8615 | 3.3683 | 3.3441 | 3.3211 | 3.2959 | 3.2688 | 3.2409 | 3.2121 | 3.187 | 3.1607 | 3.1344 | 3.108 | 3.0813 | 3.0516 | 3.0207
|  | LATHERON | LW |  |  |  | 0.0010526 | 3.4026 | 3.3759 | 3.3604 | 3.3403 | 3.3175 | 3.2926 | 3.2667 | 3.2439 | 3.22 | 3.1959 | 3.1713 | 2.9975 | 2.6462 | 2.1626 | 3.3645 | 3.3378 | 3.306 | 3.2455 | 3.1833 | 3.1211 | 3.0597 | 2.9985 | 2.937 | 2.876 | 2.8151 | 2.4915 | 2.1026 | 1.5823 | 3.3986 | 3.3719 | 3.3564 | 3.3363 | 3.3135 | 3.2885 | 3.2627 | 3.2398 | 3.216 | 3.1919 | 3.1673 | 3.1428 | 3.1143 | 3.0844
|  | LATHERON | ST |  |  |  | 0.0010526 | 3.4077 | 3.4008 | 3.3953 | 3.3876 | 3.3783 | 3.3683 | 3.3578 | 3.3515 | 3.3452 | 3.339 | 3.3329 | 3.3016 | 3.2351 | 3.185 | 3.3695 | 3.3626 | 3.3571 | 3.3494 | 3.3402 | 3.3233 | 3.2955 | 3.2708 | 3.2465 | 3.2228 | 3.1996 | 3.0878 | 2.9455 | 2.8232 | 3.4036 | 3.3967 | 3.3912 | 3.3836 | 3.3743 | 3.3643 | 3.3538 | 3.3475 | 3.3412 | 3.335 | 3.3289 | 3.2976 | 3.2311 | 3.1809
|  | LATHERON | FS |  |  |  | 0.0010526 | 3.411 | 3.4061 | 3.4026 | 3.3991 | 3.3956 | 3.3919 | 3.3883 | 3.3847 | 3.381 | 3.3772 | 3.3733 | 3.3536 | 3.3176 | 3.2592 | 3.3729 | 3.3679 | 3.3645 | 3.361 | 3.3574 | 3.3538 | 3.3502 | 3.3466 | 3.3361 | 3.3185 | 3.3008 | 3.2137 | 3.1151 | 2.9977 | 3.407 | 3.4021 | 3.3986 | 3.3951 | 3.3915 | 3.3879 | 3.3843 | 3.3807 | 3.377 | 3.3732 | 3.3693 | 3.3496 | 3.3136 | 3.2551
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 0.093684 | 15.5675 | 15.5186 | 15.4722 | 15.4217 | 15.2327 | 15.0002 | 14.7842 | 14.5656 | 14.3548 | 14.1509 | 13.9628 | 13.0461 | 12.0493 | 10.7812 | 14.0572 | 13.8227 | 13.5993 | 13.313 | 13.036 | 12.7709 | 12.5259 | 12.2764 | 12.0363 | 11.8047 | 11.5918 | 10.5647 | 9.4696 | 8.1099 | 14.8556 | 14.7695 | 14.5534 | 14.2765 | 14.0081 | 13.7512 | 13.5108 | 13.2617 | 13.022 | 12.7907 | 12.5782 | 12.3794 | 12.1734 | 11.9665
|  | LAURENCEKIRK | CT |  |  |  | 0.093684 | 15.5675 | 15.5186 | 15.4722 | 15.4217 | 15.3667 | 15.282 | 15.1084 | 14.9395 | 14.7731 | 14.616 | 14.4651 | 13.7043 | 12.893 | 11.9597 | 14.0795 | 13.9238 | 13.7562 | 13.55 | 13.3356 | 13.1179 | 12.9236 | 12.7333 | 12.5461 | 12.3701 | 12.2014 | 11.3597 | 10.4787 | 9.4799 | 14.8556 | 14.8067 | 14.7021 | 14.5018 | 14.2935 | 14.082 | 13.8928 | 13.7078 | 13.5258 | 13.3545 | 13.1865 | 13.0184 | 12.848 | 12.6799
|  | LAURENCEKIRK | LW |  |  |  | 0.093684 | 15.6231 | 15.5638 | 15.5306 | 15.4745 | 15.2327 | 15.0002 | 14.7842 | 14.5656 | 14.3548 | 14.1509 | 13.9628 | 13.0461 | 12.0493 | 10.7812 | 14.0572 | 13.8227 | 13.5993 | 13.313 | 13.036 | 12.7709 | 12.5259 | 12.2764 | 12.0363 | 11.8047 | 11.5918 | 10.5647 | 9.4696 | 8.1099 | 14.9112 | 14.7695 | 14.5534 | 14.2765 | 14.0081 | 13.7512 | 13.5108 | 13.2617 | 13.022 | 12.7907 | 12.5782 | 12.3794 | 12.1734 | 11.9665
|  | LAURENCEKIRK | ST |  |  |  | 0.093684 | 15.6348 | 15.621 | 15.6104 | 15.5947 | 15.5756 | 15.5548 | 15.5335 | 15.5203 | 15.507 | 15.494 | 15.4744 | 15.0892 | 14.6881 | 14.3443 | 14.235 | 14.1891 | 14.1403 | 14.0399 | 13.933 | 13.823 | 13.7194 | 13.6164 | 13.5116 | 13.4108 | 13.314 | 12.8702 | 12.4221 | 12.0345 | 14.923 | 14.9091 | 14.8986 | 14.8829 | 14.8638 | 14.7694 | 14.669 | 14.5694 | 14.4682 | 14.3707 | 14.2771 | 13.8479 | 13.4071 | 13.0201
|  | LAURENCEKIRK | FS |  |  |  | 0.093684 | 15.6399 | 15.6299 | 15.6237 | 15.6175 | 15.6112 | 15.6046 | 15.5981 | 15.5906 | 15.5827 | 15.5746 | 15.5662 | 15.4503 | 15.1583 | 14.8233 | 14.2566 | 14.2206 | 14.1853 | 14.1454 | 14.0916 | 14.022 | 13.9545 | 13.8775 | 13.7976 | 13.7184 | 13.6409 | 13.2774 | 12.9459 | 12.5735 | 14.9281 | 14.918 | 14.9119 | 14.9057 | 14.8993 | 14.8928 | 14.8863 | 14.8233 | 14.7461 | 14.6697 | 14.5948 | 14.2436 | 13.922 | 13.5583
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0 | 1.3772 | 1.3653 | 1.3543 | 1.3415 | 1.3272 | 1.3114 | 1.2957 | 1.2829 | 1.2687 | 1.254 | 1.2396 | 1.0725 | 0.81137 | 0.44647 | 1.3309 | 1.319 | 1.308 | 1.2952 | 1.2809 | 1.2485 | 1.2018 | 1.1566 | 1.1117 | 1.0672 | 1.0233 | 0.78911 | 0.50552 | 0.11838 | 1.2641 | 1.2522 | 1.2412 | 1.2284 | 1.214 | 1.1982 | 1.1825 | 1.1697 | 1.135 | 1.0904 | 1.0465 | 1.0033 | 0.95631 | 0.90896
|  | LAXAY | CT |  |  |  | 0 | 1.3772 | 1.3653 | 1.3543 | 1.3415 | 1.3272 | 1.3114 | 1.2957 | 1.2829 | 1.2698 | 1.2566 | 1.2435 | 1.162 | 0.99913 | 0.75178 | 1.3309 | 1.319 | 1.308 | 1.2952 | 1.2809 | 1.2651 | 1.2494 | 1.2195 | 1.1856 | 1.152 | 1.1187 | 0.93842 | 0.72134 | 0.45906 | 1.2641 | 1.2522 | 1.2412 | 1.2284 | 1.214 | 1.1982 | 1.1825 | 1.1697 | 1.1566 | 1.1435 | 1.1303 | 1.1086 | 1.0725 | 1.0361
|  | LAXAY | LW |  |  |  | 0 | 1.3865 | 1.3676 | 1.3583 | 1.3451 | 1.3305 | 1.3148 | 1.2975 | 1.2832 | 1.2687 | 1.254 | 1.2396 | 1.0725 | 0.81137 | 0.44647 | 1.3402 | 1.3213 | 1.312 | 1.2988 | 1.2842 | 1.2485 | 1.2018 | 1.1566 | 1.1117 | 1.0672 | 1.0233 | 0.78911 | 0.50552 | 0.11838 | 1.2733 | 1.2544 | 1.2451 | 1.232 | 1.2173 | 1.2016 | 1.1843 | 1.17 | 1.135 | 1.0904 | 1.0465 | 1.0033 | 0.95631 | 0.90896
|  | LAXAY | ST |  |  |  | 0 | 1.389 | 1.385 | 1.3823 | 1.3776 | 1.3724 | 1.3665 | 1.3601 | 1.3567 | 1.3533 | 1.3499 | 1.3466 | 1.3308 | 1.286 | 1.2588 | 1.3427 | 1.3388 | 1.336 | 1.3314 | 1.3261 | 1.3202 | 1.3139 | 1.3104 | 1.307 | 1.3036 | 1.3003 | 1.2399 | 1.1349 | 1.0499 | 1.2759 | 1.2719 | 1.2691 | 1.2645 | 1.2592 | 1.2533 | 1.247 | 1.2436 | 1.2401 | 1.2367 | 1.2334 | 1.2177 | 1.1581 | 1.0731
|  | LAXAY | FS |  |  |  | 0 | 1.3899 | 1.3869 | 1.3859 | 1.385 | 1.384 | 1.3829 | 1.3818 | 1.38 | 1.3781 | 1.3762 | 1.3741 | 1.3665 | 1.3451 | 1.3033 | 1.3436 | 1.3406 | 1.3396 | 1.3387 | 1.3377 | 1.3366 | 1.3355 | 1.3337 | 1.3318 | 1.3299 | 1.3278 | 1.3202 | 1.2489 | 1.1567 | 1.2767 | 1.2737 | 1.2728 | 1.2718 | 1.2708 | 1.2697 | 1.2686 | 1.2669 | 1.265 | 1.263 | 1.2609 | 1.2534 | 1.2319 | 1.18
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0.041053 | 0.99379 | 0.96745 | 0.94367 | 0.91652 | 0.88648 | 0.85383 | 0.81984 | 0.79186 | 0.76344 | 0.73496 | 0.70638 | 0.53404 | 0.20951 | -0.46671 | 0.94572 | 0.91938 | 0.8956 | 0.86845 | 0.83841 | 0.80575 | 0.77177 | 0.74379 | 0.71537 | 0.68689 | 0.6264 | 0.19406 | -0.32865 | -1.0594 | 0.7159 | 0.67403 | 0.63012 | 0.55949 | 0.46534 | 0.37233 | 0.28138 | 0.19164 | 0.10353 | 0.015276 | -0.070629 | -0.15439 | -0.24397 | -0.33514
|  | LEOCH | CT |  |  |  | 0.041053 | 0.99379 | 0.96745 | 0.94367 | 0.91652 | 0.88648 | 0.85383 | 0.81984 | 0.79186 | 0.76344 | 0.73496 | 0.70638 | 0.53404 | 0.293 | -0.038377 | 0.94572 | 0.91938 | 0.8956 | 0.86845 | 0.83841 | 0.80575 | 0.77177 | 0.74379 | 0.71537 | 0.68689 | 0.65831 | 0.42752 | 0.013798 | -0.48332 | 0.7159 | 0.67403 | 0.63197 | 0.57432 | 0.51448 | 0.44117 | 0.36692 | 0.29674 | 0.2268 | 0.15841 | 0.090651 | 0.022241 | -0.049708 | -0.12196
|  | LEOCH | LW |  |  |  | 0.041053 | 1.0199 | 0.98263 | 0.9629 | 0.93656 | 0.9066 | 0.87456 | 0.84034 | 0.81102 | 0.78145 | 0.75071 | 0.7204 | 0.53655 | 0.20951 | -0.46671 | 0.97182 | 0.93456 | 0.91483 | 0.88848 | 0.85853 | 0.82648 | 0.79227 | 0.76295 | 0.73338 | 0.70264 | 0.6264 | 0.19406 | -0.32865 | -1.0594 | 0.73548 | 0.6763 | 0.63012 | 0.55949 | 0.46534 | 0.37233 | 0.28138 | 0.19164 | 0.10353 | 0.015276 | -0.070629 | -0.15439 | -0.24397 | -0.33514
|  | LEOCH | ST |  |  |  | 0.041053 | 1.0249 | 1.0174 | 1.012 | 1.0033 | 0.99253 | 0.98065 | 0.96788 | 0.96047 | 0.95303 | 0.94573 | 0.93857 | 0.90414 | 0.81791 | 0.75956 | 0.97687 | 0.96933 | 0.96396 | 0.95521 | 0.94446 | 0.93258 | 0.91981 | 0.9124 | 0.90496 | 0.89766 | 0.8905 | 0.85607 | 0.76984 | 0.69866 | 0.76959 | 0.7594 | 0.75146 | 0.72385 | 0.6945 | 0.66497 | 0.63518 | 0.60946 | 0.58355 | 0.55335 | 0.52046 | 0.36479 | 0.16752 | 0.0040758
|  | LEOCH | FS |  |  |  | 0.041053 | 1.0283 | 1.0228 | 1.0201 | 1.0173 | 1.0145 | 1.0116 | 1.0086 | 1.0044 | 1 | 0.99547 | 0.99072 | 0.9688 | 0.92552 | 0.84616 | 0.98024 | 0.9747 | 0.97201 | 0.96927 | 0.96644 | 0.96349 | 0.96054 | 0.95637 | 0.95198 | 0.9474 | 0.94265 | 0.92073 | 0.87745 | 0.79809 | 0.7743 | 0.76756 | 0.7635 | 0.75743 | 0.74804 | 0.7324 | 0.71684 | 0.6984 | 0.67978 | 0.66103 | 0.64214 | 0.52988 | 0.39374 | 0.22723
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.041053 | 1.6854 | 1.6399 | 1.5968 | 1.5522 | 1.507 | 1.4608 | 1.4139 | 1.3676 | 1.3212 | 1.2739 | 1.2265 | 0.95995 | 0.56437 | 0.087102 | 1.4994 | 1.4538 | 1.4107 | 1.3661 | 1.321 | 1.2747 | 1.2208 | 1.1557 | 1.0907 | 1.0251 | 0.95984 | 0.60608 | 0.18255 | -0.31147 | 1.5219 | 1.4763 | 1.4333 | 1.3886 | 1.3435 | 1.2972 | 1.2503 | 1.2041 | 1.1438 | 1.0779 | 1.0123 | 0.94686 | 0.87743 | 0.80585
|  | LETHEN | CT |  |  |  | 0.041053 | 1.6854 | 1.6399 | 1.5968 | 1.5522 | 1.507 | 1.4608 | 1.4139 | 1.3676 | 1.3212 | 1.2739 | 1.2265 | 0.95995 | 0.56437 | 0.087102 | 1.4994 | 1.4538 | 1.4107 | 1.3661 | 1.321 | 1.2747 | 1.2208 | 1.1557 | 1.0907 | 1.0251 | 0.95984 | 0.60608 | 0.18255 | -0.31147 | 1.5219 | 1.4763 | 1.4333 | 1.3886 | 1.3435 | 1.2972 | 1.2503 | 1.2041 | 1.1438 | 1.0779 | 1.0123 | 0.94686 | 0.87743 | 0.80585
|  | LETHEN | LW |  |  |  | 0.041053 | 1.7545 | 1.7273 | 1.707 | 1.6815 | 1.6539 | 1.6236 | 1.5911 | 1.5595 | 1.5271 | 1.4936 | 1.4595 | 1.1729 | 0.78574 | 0.26563 | 1.5684 | 1.5413 | 1.521 | 1.4955 | 1.4678 | 1.412 | 1.3532 | 1.2944 | 1.235 | 1.1752 | 1.1151 | 0.78483 | 0.37824 | -0.14955 | 1.5909 | 1.5638 | 1.5435 | 1.518 | 1.4903 | 1.4601 | 1.4062 | 1.3469 | 1.2871 | 1.2265 | 1.1637 | 1.1006 | 1.0339 | 0.96425
|  | LETHEN | ST |  |  |  | 0.041053 | 2.5259 | 1.756 | 1.7458 | 1.7341 | 1.7202 | 1.7058 | 1.6911 | 1.6787 | 1.6663 | 1.6539 | 1.6425 | 1.5826 | 1.4996 | 1.4191 | 2.3398 | 1.5699 | 1.5598 | 1.5481 | 1.5342 | 1.5198 | 1.505 | 1.4926 | 1.4802 | 1.4679 | 1.4564 | 1.3461 | 1.2101 | 1.0791 | 2.3623 | 1.5924 | 1.5823 | 1.5706 | 1.5567 | 1.5423 | 1.5275 | 1.5151 | 1.5027 | 1.4904 | 1.479 | 1.3991 | 1.2622 | 1.1281
|  | LETHEN | FS |  |  |  | 0.041053 | 2.5326 | 2.5259 | 1.7603 | 1.7527 | 1.745 | 1.7372 | 1.7294 | 1.722 | 1.7153 | 1.7085 | 1.7017 | 1.6595 | 1.6085 | 1.5421 | 2.3465 | 2.3398 | 1.5743 | 1.5666 | 1.5589 | 1.5511 | 1.5434 | 1.5359 | 1.5292 | 1.5225 | 1.5156 | 1.4735 | 1.3797 | 1.2725 | 2.3691 | 2.3623 | 1.5968 | 1.5891 | 1.5814 | 1.5737 | 1.5659 | 1.5584 | 1.5518 | 1.545 | 1.5381 | 1.496 | 1.4329 | 1.3249
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | YES | 0 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203
|  | LETTEREWE | CT |  |  |  | 0 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203
|  | LETTEREWE | LW |  |  |  | 0 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203
|  | LETTEREWE | ST |  |  |  | 0 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203
|  | LETTEREWE | FS |  |  |  | 0 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10266 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10164 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203 | 0.10203
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0.011579 | 5.1092 | 5.0954 | 5.0834 | 5.0675 | 5.0494 | 5.0298 | 5.0085 | 4.991 | 4.9733 | 4.9554 | 4.9377 | 4.8279 | 4.5444 | 4.1066 | 5.0641 | 5.0503 | 5.0383 | 5.0225 | 5.0044 | 4.9606 | 4.9052 | 4.8508 | 4.7967 | 4.7431 | 4.6904 | 4.4087 | 4.0655 | 3.589 | 5.0759 | 5.0621 | 5.0501 | 5.0342 | 5.0161 | 4.9841 | 4.9338 | 4.885 | 4.8365 | 4.7883 | 4.7379 | 4.6873 | 4.6321 | 4.5765
|  | LHANBRYDE | CT |  |  |  | 0.011579 | 5.1092 | 5.0957 | 5.0834 | 5.0688 | 5.0522 | 5.0339 | 5.0146 | 4.9999 | 4.985 | 4.9699 | 4.9548 | 4.8609 | 4.7241 | 4.4752 | 5.0641 | 5.0506 | 5.0383 | 5.0237 | 5.0072 | 4.9888 | 4.9695 | 4.931 | 4.8904 | 4.8502 | 4.8104 | 4.597 | 4.337 | 4.0199 | 5.0759 | 5.0624 | 5.0501 | 5.0355 | 5.0189 | 5.0006 | 4.9813 | 4.9544 | 4.9177 | 4.8813 | 4.8453 | 4.8092 | 4.7697 | 4.73
|  | LHANBRYDE | LW |  |  |  | 0.011579 | 5.1193 | 5.0954 | 5.0838 | 5.0675 | 5.0494 | 5.0298 | 5.0085 | 4.991 | 4.9733 | 4.9554 | 4.9377 | 4.8279 | 4.5444 | 4.1066 | 5.0742 | 5.0503 | 5.0388 | 5.0225 | 5.0044 | 4.9606 | 4.9052 | 4.8508 | 4.7967 | 4.7431 | 4.6904 | 4.4087 | 4.0655 | 3.589 | 5.086 | 5.0621 | 5.0505 | 5.0342 | 5.0161 | 4.9841 | 4.9338 | 4.885 | 4.8365 | 4.7883 | 4.7379 | 4.6873 | 4.6321 | 4.5765
|  | LHANBRYDE | ST |  |  |  | 0.011579 | 5.1218 | 5.1172 | 5.1142 | 5.1088 | 5.1026 | 5.0956 | 5.088 | 5.0841 | 5.0802 | 5.0764 | 5.0727 | 5.055 | 5.0004 | 4.9682 | 5.0768 | 5.0722 | 5.0691 | 5.0637 | 5.0575 | 5.0506 | 5.043 | 5.0391 | 5.0352 | 5.0314 | 5.0277 | 4.9468 | 4.8186 | 4.7157 | 5.0885 | 5.0839 | 5.0809 | 5.0755 | 5.0693 | 5.0623 | 5.0547 | 5.0508 | 5.0469 | 5.0431 | 5.0394 | 4.9762 | 4.8592 | 4.7634
|  | LHANBRYDE | FS |  |  |  | 0.011579 | 5.1226 | 5.1191 | 5.1181 | 5.1172 | 5.1161 | 5.115 | 5.1138 | 5.1118 | 5.1097 | 5.1074 | 5.105 | 5.0967 | 5.0709 | 5.0196 | 5.0776 | 5.0741 | 5.0731 | 5.0721 | 5.0711 | 5.0699 | 5.0688 | 5.0668 | 5.0646 | 5.0624 | 5.06 | 5.0516 | 4.9735 | 4.866 | 5.0893 | 5.0858 | 5.0849 | 5.0839 | 5.0828 | 5.0817 | 5.0805 | 5.0785 | 5.0764 | 5.0741 | 5.0717 | 5.0634 | 5.0012 | 4.9023
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0 | 0.26891 | 0.26886 | 0.26883 | 0.26879 | 0.26875 | 0.26871 | 0.26866 | 0.26863 | 0.26859 | 0.26855 | 0.26852 | 0.26829 | 0.26795 | 0.26731 | 0.22044 | 0.22038 | 0.22036 | 0.22032 | 0.22028 | 0.22024 | 0.22019 | 0.22016 | 0.22012 | 0.22008 | 0.22005 | 0.21982 | 0.21948 | 0.21884 | 0.2175 | 0.21745 | 0.21742 | 0.21739 | 0.21734 | 0.2173 | 0.21725 | 0.21722 | 0.21718 | 0.21714 | 0.21711 | 0.21707 | 0.21703 | 0.21698
|  | LIDDESDALE | CT |  |  |  | 0 | 0.26891 | 0.26889 | 0.26888 | 0.26886 | 0.26883 | 0.2688 | 0.26876 | 0.26874 | 0.26872 | 0.2687 | 0.26867 | 0.26853 | 0.2683 | 0.26795 | 0.22044 | 0.22042 | 0.22041 | 0.22038 | 0.22036 | 0.22033 | 0.22029 | 0.22027 | 0.22025 | 0.22023 | 0.2202 | 0.22006 | 0.21983 | 0.21948 | 0.2175 | 0.21749 | 0.21747 | 0.21745 | 0.21742 | 0.21739 | 0.21736 | 0.21733 | 0.21731 | 0.21729 | 0.21727 | 0.21724 | 0.21721 | 0.21718
|  | LIDDESDALE | LW |  |  |  | 0 | 0.26891 | 0.26886 | 0.26883 | 0.26879 | 0.26875 | 0.26871 | 0.26866 | 0.26863 | 0.26859 | 0.26855 | 0.26852 | 0.26829 | 0.26795 | 0.26731 | 0.22044 | 0.22038 | 0.22036 | 0.22032 | 0.22028 | 0.22024 | 0.22019 | 0.22016 | 0.22012 | 0.22008 | 0.22005 | 0.21982 | 0.21948 | 0.21884 | 0.2175 | 0.21745 | 0.21742 | 0.21739 | 0.21734 | 0.2173 | 0.21725 | 0.21722 | 0.21718 | 0.21714 | 0.21711 | 0.21707 | 0.21703 | 0.21698
|  | LIDDESDALE | ST |  |  |  | 0 | 0.26891 | 0.26891 | 0.2689 | 0.26889 | 0.26888 | 0.26887 | 0.26886 | 0.26885 | 0.26884 | 0.26884 | 0.26883 | 0.26881 | 0.2687 | 0.26865 | 0.22044 | 0.22044 | 0.22043 | 0.22042 | 0.22041 | 0.2204 | 0.22038 | 0.22038 | 0.22037 | 0.22037 | 0.22036 | 0.22034 | 0.22023 | 0.22018 | 0.2175 | 0.2175 | 0.21749 | 0.21749 | 0.21747 | 0.21746 | 0.21745 | 0.21744 | 0.21744 | 0.21743 | 0.21743 | 0.2174 | 0.2173 | 0.21724
|  | LIDDESDALE | FS |  |  |  | 0 | 0.26891 | 0.26891 | 0.26891 | 0.26891 | 0.26891 | 0.26891 | 0.2689 | 0.2689 | 0.2689 | 0.2689 | 0.26889 | 0.26888 | 0.26883 | 0.26873 | 0.22044 | 0.22044 | 0.22044 | 0.22044 | 0.22044 | 0.22043 | 0.22043 | 0.22043 | 0.22043 | 0.22043 | 0.22042 | 0.22041 | 0.22036 | 0.22026 | 0.2175 | 0.2175 | 0.2175 | 0.2175 | 0.2175 | 0.2175 | 0.2175 | 0.21749 | 0.21749 | 0.21749 | 0.21748 | 0.21747 | 0.21743 | 0.21732
| KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0.036842 | 1.1135 | 1.0729 | 1.0318 | 0.98185 | 0.93095 | 0.879 | 0.82834 | 0.77935 | 0.73107 | 0.68219 | 0.63418 | 0.3758 | 0.070248 | -0.30255 | 1.0993 | 1.0562 | 1.0123 | 0.95782 | 0.9025 | 0.84616 | 0.79152 | 0.73841 | 0.68621 | 0.63347 | 0.5818 | 0.30594 | -0.016171 | -0.44151 | 1.2041 | 1.1597 | 1.1141 | 1.057 | 0.9991 | 0.9402 | 0.88324 | 0.82774 | 0.77326 | 0.71827 | 0.66447 | 0.60995 | 0.55402 | 0.49712
|  | LIMEHILLOCKS | CT |  |  |  | 0.036842 | 1.1135 | 1.0729 | 1.0318 | 0.98185 | 0.93095 | 0.879 | 0.82834 | 0.77935 | 0.73107 | 0.68219 | 0.63418 | 0.3758 | 0.070248 | -0.2895 | 1.0993 | 1.0562 | 1.0123 | 0.95782 | 0.9025 | 0.84616 | 0.79152 | 0.73841 | 0.68621 | 0.63347 | 0.5818 | 0.30594 | -0.016171 | -0.39179 | 1.2041 | 1.1597 | 1.1141 | 1.057 | 0.9991 | 0.9402 | 0.88324 | 0.82774 | 0.77326 | 0.71827 | 0.66447 | 0.60995 | 0.55402 | 0.49712
|  | LIMEHILLOCKS | LW |  |  |  | 0.036842 | 1.1496 | 1.11 | 1.0755 | 1.0272 | 0.97714 | 0.92722 | 0.87713 | 0.828 | 0.77912 | 0.72945 | 0.681 | 0.42399 | 0.11161 | -0.30255 | 1.1341 | 1.0906 | 1.0519 | 0.99714 | 0.94082 | 0.8849 | 0.82929 | 0.77445 | 0.71993 | 0.66484 | 0.61119 | 0.33012 | -0.0053864 | -0.44151 | 1.2382 | 1.1925 | 1.1514 | 1.0928 | 1.0328 | 0.97344 | 0.91461 | 0.85644 | 0.79865 | 0.74041 | 0.68374 | 0.62856 | 0.57056 | 0.51138
|  | LIMEHILLOCKS | ST |  |  |  | 0.036842 | 1.1779 | 1.1684 | 1.1593 | 1.1387 | 1.1168 | 1.0942 | 1.0722 | 1.0514 | 1.0308 | 1.0111 | 0.99169 | 0.89936 | 0.78944 | 0.68805 | 1.1667 | 1.1569 | 1.1473 | 1.1239 | 1.0993 | 1.0741 | 1.0496 | 1.026 | 1.0026 | 0.98037 | 0.95849 | 0.85461 | 0.73411 | 0.62259 | 1.269 | 1.2601 | 1.2519 | 1.2284 | 1.2023 | 1.1755 | 1.1495 | 1.1243 | 1.0993 | 1.0756 | 1.0523 | 0.94172 | 0.81508 | 0.69766
|  | LIMEHILLOCKS | FS |  |  |  | 0.036842 | 1.1847 | 1.179 | 1.173 | 1.1667 | 1.1568 | 1.1443 | 1.1325 | 1.118 | 1.1035 | 1.0889 | 1.0743 | 1.0027 | 0.92981 | 0.84502 | 1.1738 | 1.1676 | 1.1613 | 1.1546 | 1.1435 | 1.1292 | 1.1157 | 1.0992 | 1.0826 | 1.0659 | 1.0492 | 0.96785 | 0.88645 | 0.79389 | 1.2754 | 1.2703 | 1.265 | 1.2594 | 1.2489 | 1.2335 | 1.2191 | 1.2014 | 1.1836 | 1.1657 | 1.1478 | 1.0607 | 0.97438 | 0.87729
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0 | 10.1639 | 10.1613 | 10.1601 | 10.1585 | 10.1567 | 10.1547 | 10.1526 | 10.151 | 10.1493 | 10.1476 | 10.1459 | 10.1355 | 10.1112 | 10.0602 | 9.6543 | 9.6517 | 9.6506 | 9.649 | 9.6467 | 9.6399 | 9.6332 | 9.6267 | 9.6202 | 9.6138 | 9.6075 | 9.5745 | 9.535 | 9.4807 | 9.8762 | 9.8736 | 9.8724 | 9.8708 | 9.869 | 9.8667 | 9.8644 | 9.8624 | 9.8604 | 9.8584 | 9.8565 | 9.8546 | 9.8522 | 9.8498
|  | LOCH CARNAN | CT |  |  |  | 0 | 10.1639 | 10.163 | 10.1622 | 10.1612 | 10.1599 | 10.1584 | 10.1568 | 10.1557 | 10.1547 | 10.1536 | 10.1525 | 10.1452 | 10.1337 | 10.1131 | 9.6543 | 9.6534 | 9.6527 | 9.6516 | 9.6503 | 9.6488 | 9.6447 | 9.64 | 9.6353 | 9.6307 | 9.6261 | 9.6017 | 9.5727 | 9.5377 | 9.8762 | 9.8753 | 9.8745 | 9.8734 | 9.8722 | 9.8707 | 9.869 | 9.8677 | 9.8664 | 9.8651 | 9.8638 | 9.8624 | 9.8608 | 9.8591
|  | LOCH CARNAN | LW |  |  |  | 0 | 10.1639 | 10.1613 | 10.1601 | 10.1585 | 10.1567 | 10.1547 | 10.1526 | 10.151 | 10.1493 | 10.1476 | 10.1459 | 10.1355 | 10.1112 | 10.0602 | 9.6543 | 9.6517 | 9.6506 | 9.649 | 9.6467 | 9.6399 | 9.6332 | 9.6267 | 9.6202 | 9.6138 | 9.6075 | 9.5745 | 9.535 | 9.4807 | 9.8762 | 9.8736 | 9.8724 | 9.8708 | 9.869 | 9.8667 | 9.8644 | 9.8624 | 9.8604 | 9.8584 | 9.8565 | 9.8546 | 9.8522 | 9.8498
|  | LOCH CARNAN | ST |  |  |  | 0 | 10.1639 | 10.1636 | 10.1634 | 10.1629 | 10.1624 | 10.1618 | 10.1611 | 10.1608 | 10.1605 | 10.1603 | 10.16 | 10.1589 | 10.1534 | 10.1506 | 9.6543 | 9.654 | 9.6538 | 9.6534 | 9.6528 | 9.6522 | 9.6515 | 9.6512 | 9.651 | 9.6507 | 9.6499 | 9.6362 | 9.6185 | 9.6039 | 9.8762 | 9.8758 | 9.8757 | 9.8752 | 9.8747 | 9.874 | 9.8733 | 9.8731 | 9.8728 | 9.8725 | 9.8723 | 9.8705 | 9.8642 | 9.8607
|  | LOCH CARNAN | FS |  |  |  | 0 | 10.1639 | 10.1636 | 10.1636 | 10.1635 | 10.1635 | 10.1635 | 10.1635 | 10.1633 | 10.1632 | 10.163 | 10.1628 | 10.1623 | 10.1598 | 10.1542 | 9.6543 | 9.654 | 9.654 | 9.654 | 9.654 | 9.6539 | 9.6539 | 9.6537 | 9.6536 | 9.6534 | 9.6532 | 9.6528 | 9.6459 | 9.6342 | 9.8762 | 9.8758 | 9.8758 | 9.8758 | 9.8758 | 9.8758 | 9.8757 | 9.8756 | 9.8754 | 9.8753 | 9.8751 | 9.8746 | 9.8719 | 9.8659
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | YES | 0 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051
|  | LOCH GLASCARNOCH | CT |  |  |  | 0 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051
|  | LOCH GLASCARNOCH | LW |  |  |  | 0 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051
|  | LOCH GLASCARNOCH | ST |  |  |  | 0 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051
|  | LOCH GLASCARNOCH | FS |  |  |  | 0 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50066 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50041 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051 | 0.50051
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 0.0052632 | 1.0773 | 1.0704 | 1.0645 | 1.0548 | 1.045 | 1.0353 | 1.0256 | 1.0163 | 1.007 | 0.9978 | 0.98874 | 0.94096 | 0.88383 | 0.80486 | 1.1551 | 1.1476 | 1.141 | 1.13 | 1.119 | 1.108 | 1.0972 | 1.0867 | 1.0762 | 1.0659 | 1.0556 | 1.0022 | 0.93929 | 0.85461 | 1.11 | 1.1059 | 1.1038 | 1.1008 | 1.0975 | 1.094 | 1.0903 | 1.0873 | 1.0843 | 1.0812 | 1.0782 | 1.0752 | 1.0716 | 1.0679
|  | LOCHALINE | CT |  |  |  | 0.0052632 | 1.0779 | 1.0741 | 1.0703 | 1.0638 | 1.057 | 1.0501 | 1.0432 | 1.0369 | 1.0306 | 1.0244 | 1.0183 | 0.9853 | 0.94575 | 0.89739 | 1.1558 | 1.1515 | 1.1473 | 1.1398 | 1.1322 | 1.1245 | 1.1168 | 1.1097 | 1.1026 | 1.0956 | 1.0886 | 1.0517 | 1.0082 | 0.956 | 1.11 | 1.1085 | 1.1071 | 1.1052 | 1.1029 | 1.1003 | 1.0975 | 1.0956 | 1.0936 | 1.0916 | 1.0896 | 1.0875 | 1.0851 | 1.0825
|  | LOCHALINE | LW |  |  |  | 0.0052632 | 1.0773 | 1.0704 | 1.0645 | 1.0548 | 1.045 | 1.0353 | 1.0256 | 1.0163 | 1.007 | 0.9978 | 0.98874 | 0.94096 | 0.88383 | 0.80486 | 1.1551 | 1.1476 | 1.141 | 1.13 | 1.119 | 1.108 | 1.0972 | 1.0867 | 1.0762 | 1.0659 | 1.0556 | 1.0022 | 0.93929 | 0.85461 | 1.11 | 1.1059 | 1.1038 | 1.1008 | 1.0975 | 1.094 | 1.0903 | 1.0873 | 1.0843 | 1.0812 | 1.0782 | 1.0752 | 1.0716 | 1.0679
|  | LOCHALINE | ST |  |  |  | 0.0052632 | 1.0821 | 1.0815 | 1.0811 | 1.0767 | 1.0722 | 1.0677 | 1.0632 | 1.0591 | 1.0551 | 1.0512 | 1.0473 | 1.0289 | 1.0046 | 0.98459 | 1.1607 | 1.16 | 1.1597 | 1.1546 | 1.1495 | 1.1443 | 1.1392 | 1.1345 | 1.1298 | 1.1253 | 1.1208 | 1.0995 | 1.0723 | 1.0495 | 1.1104 | 1.1098 | 1.1096 | 1.1086 | 1.1075 | 1.1063 | 1.105 | 1.1043 | 1.1036 | 1.1029 | 1.1023 | 1.0993 | 1.0899 | 1.0844
|  | LOCHALINE | FS |  |  |  | 0.0052632 | 1.0823 | 1.0817 | 1.0816 | 1.0813 | 1.0799 | 1.0776 | 1.0753 | 1.0726 | 1.0699 | 1.0672 | 1.0645 | 1.0517 | 1.0365 | 1.0173 | 1.1609 | 1.1603 | 1.1601 | 1.1599 | 1.1581 | 1.1555 | 1.1528 | 1.1497 | 1.1466 | 1.1434 | 1.1403 | 1.1254 | 1.1082 | 1.0871 | 1.1104 | 1.1099 | 1.1099 | 1.1098 | 1.1097 | 1.1094 | 1.1092 | 1.1088 | 1.1084 | 1.1079 | 1.1074 | 1.1057 | 1.101 | 1.0917
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | YES | 0 | 1.3209 | 1.3102 | 1.3055 | 1.2837 | 1.2558 | 1.2282 | 1.2008 | 1.1745 | 1.1485 | 1.1226 | 1.0972 | 0.9648 | 0.80956 | 0.5994 | 1.1895 | 1.1783 | 1.173 | 1.1653 | 1.1567 | 1.1475 | 1.1379 | 1.1134 | 1.0834 | 1.0536 | 1.0243 | 0.8729 | 0.69863 | 0.46985 | 1.2387 | 1.228 | 1.2233 | 1.2167 | 1.2092 | 1.1842 | 1.1546 | 1.1261 | 1.0978 | 1.0697 | 1.0421 | 1.0149 | 0.98628 | 0.95741
|  | LOCHCARRON | CT |  |  |  | 0 | 1.3209 | 1.3173 | 1.3143 | 1.3102 | 1.2917 | 1.2725 | 1.2532 | 1.2357 | 1.2182 | 1.201 | 1.1839 | 1.0937 | 0.98819 | 0.86191 | 1.1896 | 1.1857 | 1.1823 | 1.1774 | 1.1716 | 1.1651 | 1.1581 | 1.1533 | 1.1484 | 1.1427 | 1.123 | 1.0198 | 0.90123 | 0.76233 | 1.2387 | 1.2351 | 1.2321 | 1.2279 | 1.2229 | 1.2171 | 1.2108 | 1.192 | 1.1729 | 1.1541 | 1.1355 | 1.117 | 1.0975 | 1.0778
|  | LOCHCARRON | LW |  |  |  | 0 | 1.3209 | 1.3102 | 1.3055 | 1.2837 | 1.2558 | 1.2282 | 1.2008 | 1.1745 | 1.1485 | 1.1226 | 1.0972 | 0.9648 | 0.80956 | 0.5994 | 1.1895 | 1.1783 | 1.173 | 1.1653 | 1.1567 | 1.1475 | 1.1379 | 1.1134 | 1.0834 | 1.0536 | 1.0243 | 0.8729 | 0.69863 | 0.46985 | 1.2387 | 1.228 | 1.2233 | 1.2167 | 1.2092 | 1.1842 | 1.1546 | 1.1261 | 1.0978 | 1.0697 | 1.0421 | 1.0149 | 0.98628 | 0.95741
|  | LOCHCARRON | ST |  |  |  | 0 | 1.3209 | 1.3196 | 1.3189 | 1.3172 | 1.3152 | 1.3128 | 1.3101 | 1.302 | 1.2921 | 1.2824 | 1.2729 | 1.2281 | 1.1692 | 1.1217 | 1.1902 | 1.1888 | 1.1882 | 1.186 | 1.1834 | 1.1805 | 1.1774 | 1.1759 | 1.1744 | 1.173 | 1.1716 | 1.1653 | 1.1041 | 1.049 | 1.2387 | 1.2373 | 1.2367 | 1.235 | 1.233 | 1.2306 | 1.2279 | 1.2269 | 1.2259 | 1.2249 | 1.224 | 1.182 | 1.1185 | 1.0667
|  | LOCHCARRON | FS |  |  |  | 0 | 1.3209 | 1.3197 | 1.3197 | 1.3196 | 1.3195 | 1.3194 | 1.3193 | 1.3188 | 1.3182 | 1.3176 | 1.3132 | 1.2782 | 1.2378 | 1.1882 | 1.1903 | 1.1891 | 1.189 | 1.1888 | 1.1886 | 1.1881 | 1.1877 | 1.1868 | 1.1859 | 1.1849 | 1.1839 | 1.1803 | 1.1695 | 1.1262 | 1.2387 | 1.2375 | 1.2374 | 1.2374 | 1.2373 | 1.2372 | 1.237 | 1.2365 | 1.236 | 1.2354 | 1.2347 | 1.2329 | 1.1923 | 1.1392
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.064211 | 1.4385 | 1.434 | 1.432 | 1.4293 | 1.4262 | 1.4228 | 1.4192 | 1.4164 | 1.4135 | 1.4056 | 1.3913 | 1.3176 | 1.2339 | 1.1265 | 1.293 | 1.2885 | 1.2866 | 1.2838 | 1.2807 | 1.2773 | 1.2737 | 1.2708 | 1.2591 | 1.2427 | 1.2266 | 1.1433 | 1.0501 | 0.93315 | 1.3413 | 1.3369 | 1.3349 | 1.3321 | 1.329 | 1.3256 | 1.322 | 1.3081 | 1.2916 | 1.2751 | 1.2589 | 1.2428 | 1.2261 | 1.2093
|  | LOCHDONHEAD | CT |  |  |  | 0.064211 | 1.4385 | 1.437 | 1.4357 | 1.434 | 1.4318 | 1.4294 | 1.4267 | 1.425 | 1.4232 | 1.4214 | 1.4196 | 1.3832 | 1.3237 | 1.255 | 1.293 | 1.2915 | 1.2902 | 1.2885 | 1.2863 | 1.2839 | 1.2812 | 1.2795 | 1.2777 | 1.2759 | 1.2737 | 1.2171 | 1.1506 | 1.0751 | 1.3413 | 1.3398 | 1.3385 | 1.3368 | 1.3347 | 1.3322 | 1.3295 | 1.3278 | 1.326 | 1.318 | 1.3065 | 1.2949 | 1.2829 | 1.2718
|  | LOCHDONHEAD | LW |  |  |  | 0.064211 | 1.4385 | 1.434 | 1.432 | 1.4293 | 1.4262 | 1.4228 | 1.4192 | 1.4164 | 1.4135 | 1.4056 | 1.3913 | 1.3176 | 1.2339 | 1.1265 | 1.293 | 1.2885 | 1.2866 | 1.2838 | 1.2807 | 1.2773 | 1.2737 | 1.2708 | 1.2591 | 1.2427 | 1.2266 | 1.1433 | 1.0501 | 0.93315 | 1.3413 | 1.3369 | 1.3349 | 1.3321 | 1.329 | 1.3256 | 1.322 | 1.3081 | 1.2916 | 1.2751 | 1.2589 | 1.2428 | 1.2261 | 1.2093
|  | LOCHDONHEAD | ST |  |  |  | 0.064211 | 1.4385 | 1.4379 | 1.4376 | 1.4369 | 1.436 | 1.435 | 1.4339 | 1.4334 | 1.433 | 1.4326 | 1.4322 | 1.4304 | 1.4163 | 1.3864 | 1.293 | 1.2924 | 1.2922 | 1.2914 | 1.2906 | 1.2895 | 1.2884 | 1.2879 | 1.2875 | 1.2871 | 1.2867 | 1.2849 | 1.2534 | 1.2193 | 1.3413 | 1.3408 | 1.3405 | 1.3398 | 1.3389 | 1.3379 | 1.3367 | 1.3363 | 1.3358 | 1.3354 | 1.335 | 1.3251 | 1.2858 | 1.2515
|  | LOCHDONHEAD | FS |  |  |  | 0.064211 | 1.4385 | 1.438 | 1.4379 | 1.4379 | 1.4379 | 1.4378 | 1.4378 | 1.4376 | 1.4373 | 1.437 | 1.4367 | 1.436 | 1.4319 | 1.4231 | 1.293 | 1.2925 | 1.2925 | 1.2924 | 1.2924 | 1.2923 | 1.2923 | 1.2921 | 1.2918 | 1.2915 | 1.2912 | 1.2905 | 1.2864 | 1.2676 | 1.3413 | 1.3408 | 1.3408 | 1.3408 | 1.3407 | 1.3407 | 1.3406 | 1.3404 | 1.3401 | 1.3399 | 1.3396 | 1.3388 | 1.3322 | 1.3
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.11895 | 0.23009 | 0.22066 | 0.21178 | 0.20183 | 0.19097 | 0.1793 | 0.16722 | 0.1573 | 0.14641 | 0.1355 | 0.12458 | 0.058748 | -0.029209 | -0.1806 | -0.17028 | -0.1797 | -0.18859 | -0.19853 | -0.2094 | -0.22107 | -0.23315 | -0.24307 | -0.25396 | -0.26486 | -0.27579 | -0.34162 | -0.42957 | -0.58097 | -0.24935 | -0.26606 | -0.28476 | -0.31468 | -0.34829 | -0.38153 | -0.41442 | -0.44631 | -0.47878 | -0.51101 | -0.54276 | -0.57411 | -0.60688 | -0.64073
|  | LOCHEARNHEAD | CT |  |  |  | 0.11895 | 0.23009 | 0.22066 | 0.21178 | 0.20183 | 0.19097 | 0.1793 | 0.16722 | 0.1573 | 0.14641 | 0.1355 | 0.12458 | 0.058748 | -0.029209 | -0.14645 | -0.17028 | -0.1797 | -0.18859 | -0.19853 | -0.2094 | -0.22107 | -0.23315 | -0.24307 | -0.25396 | -0.26486 | -0.27579 | -0.34162 | -0.42957 | -0.54681 | -0.24935 | -0.26606 | -0.28476 | -0.31141 | -0.33863 | -0.36594 | -0.39313 | -0.41874 | -0.44509 | -0.47122 | -0.49714 | -0.52298 | -0.55068 | -0.57848
|  | LOCHEARNHEAD | LW |  |  |  | 0.11895 | 0.24104 | 0.22884 | 0.22248 | 0.21345 | 0.20269 | 0.19129 | 0.17948 | 0.1695 | 0.15861 | 0.14763 | 0.13678 | 0.072514 | -0.020795 | -0.1806 | -0.15933 | -0.17153 | -0.17788 | -0.18692 | -0.19767 | -0.20907 | -0.22088 | -0.23086 | -0.24176 | -0.25274 | -0.26358 | -0.32785 | -0.42116 | -0.58097 | -0.24028 | -0.26343 | -0.28229 | -0.31468 | -0.34829 | -0.38153 | -0.41442 | -0.44631 | -0.47878 | -0.51101 | -0.54276 | -0.57411 | -0.60688 | -0.64073
|  | LOCHEARNHEAD | ST |  |  |  | 0.11895 | 0.24356 | 0.24058 | 0.23828 | 0.23492 | 0.2312 | 0.22714 | 0.22279 | 0.22011 | 0.21743 | 0.21478 | 0.21218 | 0.19963 | 0.17102 | 0.15226 | -0.1568 | -0.15978 | -0.16209 | -0.16545 | -0.16916 | -0.17323 | -0.17757 | -0.18025 | -0.18294 | -0.18558 | -0.18818 | -0.20074 | -0.22934 | -0.2481 | -0.22892 | -0.23212 | -0.23463 | -0.24413 | -0.25828 | -0.27268 | -0.28706 | -0.30035 | -0.31344 | -0.32627 | -0.33884 | -0.39879 | -0.4725 | -0.53454
|  | LOCHEARNHEAD | FS |  |  |  | 0.11895 | 0.24525 | 0.24324 | 0.24234 | 0.24144 | 0.2405 | 0.23953 | 0.23856 | 0.23722 | 0.23581 | 0.23435 | 0.23283 | 0.22683 | 0.21337 | 0.18909 | -0.15512 | -0.15713 | -0.15802 | -0.15893 | -0.15986 | -0.16083 | -0.1618 | -0.16315 | -0.16455 | -0.16602 | -0.16753 | -0.17354 | -0.187 | -0.21128 | -0.22682 | -0.22898 | -0.23007 | -0.23137 | -0.23452 | -0.23913 | -0.24589 | -0.2562 | -0.26655 | -0.27694 | -0.28736 | -0.33714 | -0.39193 | -0.4556
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0 | 24.0991 | 24.0546 | 24.0345 | 24.0065 | 23.9747 | 23.9392 | 23.9014 | 23.8715 | 23.8406 | 23.8089 | 23.7775 | 23.5743 | 22.8778 | 21.73 | 22.5269 | 22.4825 | 22.4624 | 22.4343 | 22.4025 | 22.367 | 22.3293 | 22.296 | 22.2603 | 22.2239 | 22.1877 | 21.6464 | 20.7659 | 19.5329 | 23.2117 | 23.1672 | 23.1471 | 23.1191 | 23.0873 | 23.0518 | 23.014 | 22.9841 | 22.9532 | 22.9215 | 22.8901 | 22.7841 | 22.6432 | 22.5012
|  | LOCHEE | CT |  |  |  | 0 | 24.0991 | 24.0843 | 24.0718 | 24.0548 | 24.034 | 24.0091 | 23.982 | 23.9641 | 23.9443 | 23.9241 | 23.9035 | 23.7643 | 23.5285 | 22.9691 | 22.5269 | 22.5122 | 22.4996 | 22.4826 | 22.4618 | 22.4369 | 22.4098 | 22.392 | 22.3721 | 22.3509 | 22.327 | 22.1709 | 21.6519 | 20.8878 | 23.2117 | 23.1969 | 23.1844 | 23.1674 | 23.1466 | 23.1217 | 23.0946 | 23.0767 | 23.0569 | 23.0367 | 23.0161 | 22.9945 | 22.9666 | 22.9377
|  | LOCHEE | LW |  |  |  | 0 | 24.0999 | 24.0546 | 24.0345 | 24.0065 | 23.9747 | 23.9392 | 23.9014 | 23.8715 | 23.8406 | 23.8089 | 23.7775 | 23.5743 | 22.8778 | 21.73 | 22.5278 | 22.4825 | 22.4624 | 22.4343 | 22.4025 | 22.367 | 22.3293 | 22.296 | 22.2603 | 22.2239 | 22.1877 | 21.6464 | 20.7659 | 19.5329 | 23.2126 | 23.1672 | 23.1471 | 23.1191 | 23.0873 | 23.0518 | 23.014 | 22.9841 | 22.9532 | 22.9215 | 22.8901 | 22.7841 | 22.6432 | 22.5012
|  | LOCHEE | ST |  |  |  | 0 | 24.0999 | 24.0935 | 24.0905 | 24.0822 | 24.0722 | 24.0604 | 24.0473 | 24.0423 | 24.0374 | 24.0327 | 24.0281 | 24.0067 | 23.8906 | 23.8291 | 22.5278 | 22.5214 | 22.5183 | 22.5101 | 22.5 | 22.4882 | 22.4751 | 22.4702 | 22.4652 | 22.4605 | 22.456 | 22.4336 | 22.3064 | 22.2337 | 23.2126 | 23.2061 | 23.2031 | 23.1948 | 23.1848 | 23.173 | 23.1599 | 23.1549 | 23.15 | 23.1453 | 23.1407 | 23.1193 | 23.0032 | 22.8478
|  | LOCHEE | FS |  |  |  | 0 | 24.0999 | 24.093 | 24.0927 | 24.0923 | 24.0918 | 24.091 | 24.0902 | 24.0873 | 24.0839 | 24.0802 | 24.0762 | 24.0655 | 24.0083 | 23.8808 | 22.5278 | 22.5208 | 22.5205 | 22.5202 | 22.5196 | 22.5188 | 22.5181 | 22.5151 | 22.5117 | 22.508 | 22.504 | 22.4934 | 22.4345 | 22.2981 | 23.2126 | 23.2056 | 23.2053 | 23.2049 | 23.2044 | 23.2036 | 23.2028 | 23.1999 | 23.1965 | 23.1928 | 23.1888 | 23.1781 | 23.1209 | 22.9934
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 0.18632 | 25.1375 | 25.1035 | 25.0794 | 25.0472 | 25.0111 | 24.9711 | 24.9291 | 24.8066 | 24.6629 | 24.5211 | 24.3845 | 23.6859 | 22.8525 | 21.7437 | 23.1833 | 23.1493 | 23.1253 | 23.0931 | 23.057 | 23.0169 | 22.8587 | 22.6827 | 22.5103 | 22.3404 | 22.177 | 21.3515 | 20.4214 | 19.223 | 23.8765 | 23.8426 | 23.8185 | 23.7863 | 23.7502 | 23.7101 | 23.6082 | 23.4527 | 23.3001 | 23.1498 | 23.0049 | 22.8637 | 22.7162 | 22.5666
|  | LOCHGILPHEAD | CT |  |  |  | 0.18632 | 25.1375 | 25.1132 | 25.0913 | 25.0646 | 25.0339 | 24.9993 | 24.9628 | 24.936 | 24.9077 | 24.8792 | 24.7887 | 24.2703 | 23.6771 | 22.9606 | 23.1833 | 23.159 | 23.1371 | 23.1105 | 23.0797 | 23.0452 | 23.0086 | 22.9818 | 22.9118 | 22.7905 | 22.6717 | 22.0628 | 21.3825 | 20.587 | 23.8765 | 23.8522 | 23.8304 | 23.8037 | 23.7729 | 23.7384 | 23.7018 | 23.6751 | 23.6467 | 23.5426 | 23.4368 | 23.3311 | 23.2213 | 23.1116
|  | LOCHGILPHEAD | LW |  |  |  | 0.18632 | 25.1526 | 25.1035 | 25.0794 | 25.0472 | 25.0111 | 24.9711 | 24.9291 | 24.8066 | 24.6629 | 24.5211 | 24.3845 | 23.6859 | 22.8525 | 21.7437 | 23.1985 | 23.1493 | 23.1253 | 23.0931 | 23.057 | 23.0169 | 22.8587 | 22.6827 | 22.5103 | 22.3404 | 22.177 | 21.3515 | 20.4214 | 19.223 | 23.8917 | 23.8426 | 23.8185 | 23.7863 | 23.7502 | 23.7101 | 23.6082 | 23.4527 | 23.3001 | 23.1498 | 23.0049 | 22.8637 | 22.7162 | 22.5666
|  | LOCHGILPHEAD | ST |  |  |  | 0.18632 | 25.156 | 25.1474 | 25.1428 | 25.1333 | 25.1212 | 25.1076 | 25.0926 | 25.0854 | 25.0782 | 25.0712 | 25.0643 | 25.0321 | 24.7667 | 24.4982 | 23.2018 | 23.1932 | 23.1886 | 23.1791 | 23.1671 | 23.1534 | 23.1384 | 23.1312 | 23.124 | 23.117 | 23.1102 | 23.0034 | 22.6251 | 22.3023 | 23.8951 | 23.8864 | 23.8819 | 23.8723 | 23.8603 | 23.8466 | 23.8316 | 23.8245 | 23.8172 | 23.8102 | 23.8034 | 23.7468 | 23.4073 | 23.1222
|  | LOCHGILPHEAD | FS |  |  |  | 0.18632 | 25.1577 | 25.1511 | 25.1491 | 25.1471 | 25.145 | 25.1427 | 25.1404 | 25.1362 | 25.1317 | 25.127 | 25.122 | 25.1047 | 25.0501 | 24.8538 | 23.2035 | 23.1969 | 23.195 | 23.193 | 23.1908 | 23.1885 | 23.1862 | 23.1821 | 23.1776 | 23.1728 | 23.1678 | 23.1505 | 23.0461 | 22.7302 | 23.8967 | 23.8901 | 23.8882 | 23.8862 | 23.8841 | 23.8817 | 23.8794 | 23.8753 | 23.8708 | 23.866 | 23.861 | 23.8437 | 23.7859 | 23.4999
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0.013684 | 1.3761 | 1.3728 | 1.3714 | 1.3694 | 1.3668 | 1.3638 | 1.3607 | 1.3581 | 1.3554 | 1.3527 | 1.3501 | 1.3134 | 1.2651 | 1.1992 | 1.718 | 1.7148 | 1.7133 | 1.7114 | 1.7091 | 1.7066 | 1.704 | 1.702 | 1.6999 | 1.6978 | 1.6958 | 1.6831 | 1.6632 | 1.6254 | 1.3856 | 1.3823 | 1.3809 | 1.3789 | 1.3766 | 1.3742 | 1.3716 | 1.3695 | 1.3675 | 1.3654 | 1.3633 | 1.3613 | 1.3588 | 1.3562
|  | LOCHGOILHEAD | CT |  |  |  | 0.013684 | 1.3761 | 1.3749 | 1.374 | 1.3727 | 1.3712 | 1.369 | 1.3667 | 1.365 | 1.3633 | 1.3616 | 1.3598 | 1.3483 | 1.3151 | 1.2749 | 1.718 | 1.7169 | 1.716 | 1.7147 | 1.7131 | 1.7113 | 1.7094 | 1.7081 | 1.7068 | 1.7055 | 1.7041 | 1.6955 | 1.6818 | 1.6607 | 1.3856 | 1.3844 | 1.3835 | 1.3822 | 1.3807 | 1.3789 | 1.3769 | 1.3757 | 1.3743 | 1.373 | 1.3717 | 1.3703 | 1.3686 | 1.3668
|  | LOCHGOILHEAD | LW |  |  |  | 0.013684 | 1.3761 | 1.3728 | 1.3714 | 1.3694 | 1.3668 | 1.3638 | 1.3607 | 1.3581 | 1.3554 | 1.3527 | 1.3501 | 1.3134 | 1.2651 | 1.1992 | 1.718 | 1.7148 | 1.7133 | 1.7114 | 1.7091 | 1.7066 | 1.704 | 1.702 | 1.6999 | 1.6978 | 1.6958 | 1.6831 | 1.6632 | 1.6254 | 1.3856 | 1.3823 | 1.3809 | 1.3789 | 1.3766 | 1.3742 | 1.3716 | 1.3695 | 1.3675 | 1.3654 | 1.3633 | 1.3613 | 1.3588 | 1.3562
|  | LOCHGOILHEAD | ST |  |  |  | 0.013684 | 1.3761 | 1.3756 | 1.3754 | 1.3749 | 1.3743 | 1.3735 | 1.3727 | 1.3723 | 1.372 | 1.3717 | 1.3712 | 1.3687 | 1.3611 | 1.3567 | 1.718 | 1.7176 | 1.7174 | 1.7169 | 1.7162 | 1.7154 | 1.7146 | 1.7143 | 1.714 | 1.7137 | 1.7134 | 1.712 | 1.7055 | 1.7022 | 1.3856 | 1.3851 | 1.3849 | 1.3844 | 1.3838 | 1.383 | 1.3822 | 1.3818 | 1.3815 | 1.3812 | 1.3809 | 1.3796 | 1.3731 | 1.3697
|  | LOCHGOILHEAD | FS |  |  |  | 0.013684 | 1.3761 | 1.3757 | 1.3757 | 1.3756 | 1.3756 | 1.3756 | 1.3755 | 1.3754 | 1.3752 | 1.375 | 1.3748 | 1.3736 | 1.3696 | 1.3621 | 1.718 | 1.7176 | 1.7176 | 1.7176 | 1.7176 | 1.7175 | 1.7175 | 1.7173 | 1.7171 | 1.7169 | 1.7167 | 1.7161 | 1.7131 | 1.7065 | 1.3856 | 1.3852 | 1.3852 | 1.3851 | 1.3851 | 1.3851 | 1.385 | 1.3849 | 1.3847 | 1.3845 | 1.3843 | 1.3837 | 1.3807 | 1.3741
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | YES | 0 | 1.2645 | 1.2501 | 1.2438 | 1.2349 | 1.2248 | 1.2139 | 1.2024 | 1.1933 | 1.1727 | 1.1388 | 1.1054 | 0.93307 | 0.72998 | 0.45119 | 1.2155 | 1.2012 | 1.1948 | 1.1859 | 1.1759 | 1.1649 | 1.1534 | 1.1351 | 1.0934 | 1.0521 | 1.0114 | 0.80394 | 0.56567 | 0.25232 | 1.2449 | 1.2305 | 1.2242 | 1.2153 | 1.2052 | 1.1826 | 1.1434 | 1.1041 | 1.0651 | 1.0264 | 0.98823 | 0.95056 | 0.91165 | 0.87241
|  | LOCHINVER | CT |  |  |  | 0 | 1.2645 | 1.2597 | 1.2556 | 1.2501 | 1.2433 | 1.2355 | 1.227 | 1.2215 | 1.2159 | 1.2102 | 1.2045 | 1.0934 | 0.95215 | 0.78186 | 1.2155 | 1.2107 | 1.2066 | 1.2011 | 1.1943 | 1.1865 | 1.1781 | 1.1726 | 1.1669 | 1.1612 | 1.1402 | 0.99534 | 0.8291 | 0.63442 | 1.2449 | 1.2401 | 1.236 | 1.2305 | 1.2237 | 1.2159 | 1.2074 | 1.1883 | 1.1619 | 1.1357 | 1.1098 | 1.0839 | 1.0566 | 1.0291
|  | LOCHINVER | LW |  |  |  | 0 | 1.2645 | 1.2501 | 1.2438 | 1.2349 | 1.2248 | 1.2139 | 1.2024 | 1.1933 | 1.1727 | 1.1388 | 1.1054 | 0.93307 | 0.72998 | 0.45119 | 1.2155 | 1.2012 | 1.1948 | 1.1859 | 1.1759 | 1.1649 | 1.1534 | 1.1351 | 1.0934 | 1.0521 | 1.0114 | 0.80394 | 0.56567 | 0.25232 | 1.2449 | 1.2305 | 1.2242 | 1.2153 | 1.2052 | 1.1826 | 1.1434 | 1.1041 | 1.0651 | 1.0264 | 0.98823 | 0.95056 | 0.91165 | 0.87241
|  | LOCHINVER | ST |  |  |  | 0 | 1.2645 | 1.2627 | 1.2618 | 1.2595 | 1.2568 | 1.2535 | 1.2499 | 1.2485 | 1.2471 | 1.2458 | 1.2446 | 1.2389 | 1.1925 | 1.1295 | 1.2155 | 1.2137 | 1.2129 | 1.2106 | 1.2078 | 1.2045 | 1.2009 | 1.1995 | 1.1982 | 1.1969 | 1.1956 | 1.1899 | 1.1112 | 1.0335 | 1.2449 | 1.2431 | 1.2422 | 1.24 | 1.2372 | 1.2339 | 1.2303 | 1.2289 | 1.2275 | 1.2262 | 1.225 | 1.1718 | 1.0836 | 1.011
|  | LOCHINVER | FS |  |  |  | 0 | 1.2645 | 1.2629 | 1.2628 | 1.2627 | 1.2626 | 1.2624 | 1.2622 | 1.2616 | 1.2608 | 1.2599 | 1.259 | 1.2566 | 1.2439 | 1.2165 | 1.2155 | 1.2139 | 1.2138 | 1.2137 | 1.2136 | 1.2134 | 1.2133 | 1.2126 | 1.2118 | 1.211 | 1.21 | 1.2076 | 1.195 | 1.144 | 1.2449 | 1.2433 | 1.2432 | 1.2431 | 1.243 | 1.2428 | 1.2426 | 1.242 | 1.2412 | 1.2404 | 1.2394 | 1.237 | 1.1872 | 1.1142
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 6.7084 | 35.9557 | 35.8886 | 35.8545 | 35.8076 | 35.7547 | 35.6964 | 35.6339 | 35.5841 | 35.5333 | 35.4814 | 35.4301 | 34.2869 | 32.8019 | 30.878 | 33.2154 | 33.1295 | 33.0813 | 32.9325 | 32.4999 | 32.0865 | 31.7078 | 31.32 | 30.948 | 30.589 | 30.2602 | 28.6683 | 26.9808 | 24.8618 | 34.4678 | 34.4007 | 34.3666 | 34.3197 | 34.2667 | 34.2084 | 34.146 | 34.0962 | 34.0453 | 33.8005 | 33.4786 | 33.1778 | 32.8644 | 32.552
|  | LOCHSIDE | CT |  |  |  | 6.7084 | 35.9557 | 35.9263 | 35.9007 | 35.8676 | 35.8279 | 35.7817 | 35.7323 | 35.6984 | 35.6631 | 35.6274 | 35.5913 | 35.354 | 34.729 | 33.4825 | 33.2154 | 33.1781 | 33.1435 | 33.0987 | 33.0471 | 32.8717 | 32.5953 | 32.3266 | 32.063 | 31.8172 | 31.5846 | 30.4314 | 29.2309 | 27.8461 | 34.4678 | 34.4384 | 34.4128 | 34.3796 | 34.3399 | 34.2938 | 34.2443 | 34.2105 | 34.1751 | 34.1395 | 34.1033 | 34.0658 | 34.0181 | 33.9691
|  | LOCHSIDE | LW |  |  |  | 6.7084 | 35.9633 | 35.8886 | 35.8545 | 35.8076 | 35.7547 | 35.6964 | 35.6339 | 35.5841 | 35.5333 | 35.4814 | 35.4301 | 34.2869 | 32.8019 | 30.878 | 33.2172 | 33.1295 | 33.0813 | 32.9325 | 32.4999 | 32.0865 | 31.7078 | 31.32 | 30.948 | 30.589 | 30.2602 | 28.6683 | 26.9808 | 24.8618 | 34.4754 | 34.4007 | 34.3666 | 34.3197 | 34.2667 | 34.2084 | 34.146 | 34.0962 | 34.0453 | 33.8005 | 33.4786 | 33.1778 | 32.8644 | 32.552
|  | LOCHSIDE | ST |  |  |  | 6.7084 | 35.965 | 35.954 | 35.9483 | 35.9344 | 35.9177 | 35.8982 | 35.8766 | 35.8679 | 35.8593 | 35.8509 | 35.8429 | 35.8047 | 35.629 | 35.532 | 33.2312 | 33.2178 | 33.2093 | 33.189 | 33.1658 | 33.1397 | 33.1119 | 33.0965 | 33.0808 | 33.0658 | 32.9611 | 32.2624 | 31.5344 | 30.908 | 34.4771 | 34.4661 | 34.4604 | 34.4465 | 34.4297 | 34.4102 | 34.3886 | 34.38 | 34.3713 | 34.363 | 34.3549 | 34.3167 | 34.1411 | 34.0441
|  | LOCHSIDE | FS |  |  |  | 6.7084 | 35.965 | 35.9539 | 35.9526 | 35.9512 | 35.9496 | 35.9476 | 35.9456 | 35.9404 | 35.9346 | 35.9283 | 35.9216 | 35.9016 | 35.8144 | 35.627 | 33.2321 | 33.219 | 33.2156 | 33.2116 | 33.2064 | 33.1996 | 33.193 | 33.1825 | 33.1712 | 33.1595 | 33.1475 | 32.858 | 32.3178 | 31.696 | 34.4771 | 34.466 | 34.4647 | 34.4633 | 34.4616 | 34.4597 | 34.4577 | 34.4525 | 34.4467 | 34.4404 | 34.4336 | 34.4137 | 34.3264 | 34.139
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 0.058947 | 5.1736 | 5.1612 | 5.1487 | 5.1318 | 5.1146 | 5.0973 | 5.0783 | 5.0596 | 5.041 | 5.0225 | 5.0034 | 4.9029 | 4.7861 | 4.6356 | 5.0734 | 5.0608 | 5.0482 | 5.0311 | 5.0136 | 4.9948 | 4.9736 | 4.953 | 4.9324 | 4.9119 | 4.8909 | 4.781 | 4.6549 | 4.4957 | 5.2476 | 5.2343 | 5.2209 | 5.2024 | 5.1837 | 5.1615 | 5.1401 | 5.1193 | 5.0985 | 5.0779 | 5.0567 | 5.0357 | 5.0138 | 4.9919
|  | LOGIE PERT | CT |  |  |  | 0.058947 | 5.1736 | 5.1612 | 5.1487 | 5.1318 | 5.1146 | 5.0973 | 5.0801 | 5.0637 | 5.0464 | 5.0292 | 5.0122 | 4.9232 | 4.8207 | 4.7012 | 5.0734 | 5.0608 | 5.0482 | 5.0311 | 5.0136 | 4.9961 | 4.9786 | 4.9615 | 4.9428 | 4.9243 | 4.9058 | 4.8104 | 4.7018 | 4.5763 | 5.2476 | 5.2343 | 5.2209 | 5.2024 | 5.1837 | 5.1648 | 5.1461 | 5.1282 | 5.1094 | 5.0907 | 5.0722 | 5.0537 | 5.0346 | 5.0146
|  | LOGIE PERT | LW |  |  |  | 0.058947 | 5.1829 | 5.1689 | 5.1562 | 5.137 | 5.1176 | 5.0975 | 5.0783 | 5.0596 | 5.041 | 5.0225 | 5.0034 | 4.9029 | 4.7861 | 4.6356 | 5.0827 | 5.0684 | 5.0555 | 5.036 | 5.0162 | 4.9948 | 4.9736 | 4.953 | 4.9324 | 4.9119 | 4.8909 | 4.781 | 4.6549 | 4.4957 | 5.2566 | 5.2413 | 5.2272 | 5.2056 | 5.1839 | 5.1615 | 5.1401 | 5.1193 | 5.0985 | 5.0779 | 5.0567 | 5.0357 | 5.0138 | 4.9919
|  | LOGIE PERT | ST |  |  |  | 0.058947 | 5.1948 | 5.1923 | 5.1894 | 5.1813 | 5.1722 | 5.1632 | 5.1542 | 5.1458 | 5.1374 | 5.1292 | 5.1211 | 5.0848 | 5.0418 | 5.0046 | 5.0949 | 5.0924 | 5.0894 | 5.0811 | 5.0719 | 5.0627 | 5.0535 | 5.0449 | 5.0364 | 5.028 | 5.0197 | 4.9802 | 4.9332 | 4.8921 | 5.2702 | 5.2677 | 5.2646 | 5.2554 | 5.2453 | 5.2352 | 5.2251 | 5.2155 | 5.206 | 5.1967 | 5.1875 | 5.1466 | 5.0993 | 5.0579
|  | LOGIE PERT | FS |  |  |  | 0.058947 | 5.196 | 5.1944 | 5.1933 | 5.1914 | 5.1887 | 5.1842 | 5.1796 | 5.1745 | 5.1694 | 5.1642 | 5.159 | 5.1319 | 5.1042 | 5.0716 | 5.096 | 5.0944 | 5.0934 | 5.0914 | 5.0887 | 5.084 | 5.0793 | 5.0741 | 5.0689 | 5.0636 | 5.0583 | 5.0306 | 5.0014 | 4.9659 | 5.2714 | 5.2698 | 5.2687 | 5.2666 | 5.2636 | 5.2584 | 5.2531 | 5.2473 | 5.2415 | 5.2356 | 5.2297 | 5.199 | 5.1681 | 5.1323
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 5.2632 | 36.6337 | 36.5752 | 36.5406 | 36.4938 | 36.4411 | 36.3825 | 36.3206 | 36.271 | 36.2194 | 36.1669 | 36.115 | 35.5284 | 34.5363 | 33.0184 | 34.6526 | 34.5879 | 34.5475 | 34.4902 | 34.4272 | 34.3589 | 34.2877 | 34.2281 | 34.057 | 33.8856 | 33.7164 | 32.8074 | 31.6785 | 30.0771 | 35.3946 | 35.3311 | 35.2919 | 35.2366 | 35.1756 | 35.1091 | 35.0398 | 34.9822 | 34.9228 | 34.8625 | 34.803 | 34.7439 | 34.6714 | 34.5965
|  | LONGHAUGH | CT |  |  |  | 5.2632 | 36.6337 | 36.6009 | 36.5718 | 36.5363 | 36.4944 | 36.4464 | 36.3951 | 36.358 | 36.3196 | 36.2808 | 36.2416 | 35.9883 | 35.394 | 34.4824 | 34.6526 | 34.6162 | 34.5831 | 34.5403 | 34.4913 | 34.4364 | 34.3786 | 34.3345 | 34.2892 | 34.2436 | 34.1867 | 33.5223 | 32.696 | 31.6663 | 35.3946 | 35.3589 | 35.3266 | 35.2852 | 35.2376 | 35.184 | 35.1275 | 35.0848 | 35.0408 | 34.9965 | 34.952 | 34.9052 | 34.8494 | 34.7924
|  | LONGHAUGH | LW |  |  |  | 5.2632 | 36.6471 | 36.5752 | 36.5406 | 36.4938 | 36.4411 | 36.3825 | 36.3206 | 36.271 | 36.2194 | 36.1669 | 36.115 | 35.5284 | 34.5363 | 33.0184 | 34.6646 | 34.5879 | 34.5475 | 34.4902 | 34.4272 | 34.3589 | 34.2877 | 34.2281 | 34.057 | 33.8856 | 33.7164 | 32.8074 | 31.6785 | 30.0771 | 35.4069 | 35.3311 | 35.2919 | 35.2366 | 35.1756 | 35.1091 | 35.0398 | 34.9822 | 34.9228 | 34.8625 | 34.803 | 34.7439 | 34.6714 | 34.5965
|  | LONGHAUGH | ST |  |  |  | 5.2632 | 36.6505 | 36.639 | 36.6327 | 36.6184 | 36.6014 | 36.5817 | 36.56 | 36.5508 | 36.5415 | 36.5326 | 36.524 | 36.4836 | 36.3102 | 36.209 | 34.6748 | 34.663 | 34.6563 | 34.6373 | 34.6156 | 34.5915 | 34.5655 | 34.5515 | 34.5376 | 34.5242 | 34.5111 | 34.4494 | 34.1191 | 33.7678 | 35.4158 | 35.404 | 35.3973 | 35.3793 | 35.3585 | 35.3353 | 35.3101 | 35.2971 | 35.2841 | 35.2715 | 35.2593 | 35.2017 | 35.0117 | 34.8942
|  | LONGHAUGH | FS |  |  |  | 5.2632 | 36.6513 | 36.6407 | 36.6394 | 36.6381 | 36.6364 | 36.6345 | 36.6326 | 36.6276 | 36.622 | 36.6159 | 36.6094 | 36.5868 | 36.4999 | 36.3204 | 34.6759 | 34.665 | 34.6634 | 34.6614 | 34.6583 | 34.6531 | 34.648 | 34.6393 | 34.63 | 34.6203 | 34.6102 | 34.5696 | 34.4657 | 34.1822 | 35.4168 | 35.4059 | 35.4044 | 35.4025 | 35.3997 | 35.3952 | 35.3907 | 35.3827 | 35.3741 | 35.3652 | 35.3557 | 35.3187 | 35.2181 | 35.0254
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | YES | 0 | 26.8145 | 26.8176 | 26.8178 | 26.8179 | 26.8182 | 26.8185 | 26.8189 | 26.8202 | 26.8218 | 26.8235 | 26.8253 | 26.8301 | 26.8558 | 26.9124 | 24.0643 | 24.0675 | 24.0677 | 24.0679 | 24.0685 | 24.0694 | 24.0703 | 24.0723 | 24.0744 | 24.0768 | 24.0792 | 24.1281 | 24.2068 | 24.2788 | 25.4251 | 25.4282 | 25.4284 | 25.4286 | 25.4288 | 25.4292 | 25.4295 | 25.4309 | 25.4324 | 25.4341 | 25.4359 | 25.4408 | 25.4664 | 25.523
|  | LONGMAN DRIVE | CT |  |  |  |  | 26.8145 | 26.8222 | 26.8287 | 26.8376 | 26.8484 | 26.8613 | 26.8751 | 26.8842 | 26.8937 | 26.9034 | 26.9132 | 26.9794 | 27.0888 | 27.2595 | 24.0648 | 24.0731 | 24.0803 | 24.0904 | 24.1025 | 24.1357 | 24.1698 | 24.2006 | 24.2315 | 24.2623 | 24.293 | 24.4622 | 24.6766 | 24.4021 | 25.4251 | 25.4328 | 25.4394 | 25.4482 | 25.4591 | 25.4719 | 25.4858 | 25.4948 | 25.5044 | 25.514 | 25.5238 | 25.534 | 25.5473 | 25.5611
|  | LONGMAN DRIVE | LW |  |  |  |  | 26.8145 | 26.8371 | 26.8472 | 26.8612 | 26.877 | 26.8946 | 26.9132 | 26.9278 | 26.9428 | 26.9581 | 26.9733 | 27.0691 | 27.2558 | 27.6852 | 24.0649 | 24.0883 | 24.0994 | 24.1152 | 24.1625 | 24.2102 | 24.2579 | 24.3038 | 24.3496 | 24.3953 | 24.4404 | 24.6834 | 24.4963 | 24.2788 | 25.4251 | 25.4478 | 25.4578 | 25.4718 | 25.4877 | 25.5053 | 25.5238 | 25.5385 | 25.5535 | 25.5688 | 25.5839 | 25.5989 | 25.618 | 25.6378
|  | LONGMAN DRIVE | ST |  |  |  |  | 26.8145 | 26.8176 | 26.8191 | 26.8231 | 26.828 | 26.8337 | 26.8401 | 26.8425 | 26.8449 | 26.8472 | 26.8494 | 26.8596 | 26.9125 | 26.9402 | 24.0643 | 24.0675 | 24.069 | 24.0739 | 24.0796 | 24.0861 | 24.0933 | 24.0965 | 24.1034 | 24.12 | 24.1362 | 24.2136 | 24.3304 | 24.4203 | 25.4251 | 25.4282 | 25.4297 | 25.4337 | 25.4386 | 25.4444 | 25.4507 | 25.4531 | 25.4555 | 25.4578 | 25.46 | 25.4702 | 25.5232 | 25.5508
|  | LONGMAN DRIVE | FS |  |  |  |  | 26.8145 | 26.8176 | 26.8178 | 26.8179 | 26.8182 | 26.8185 | 26.8189 | 26.8202 | 26.8218 | 26.8235 | 26.8253 | 26.8301 | 26.8558 | 26.9124 | 24.0643 | 24.0675 | 24.0677 | 24.0679 | 24.0685 | 24.0694 | 24.0703 | 24.0723 | 24.0744 | 24.0768 | 24.0792 | 24.1281 | 24.2068 | 24.3145 | 25.4251 | 25.4283 | 25.4284 | 25.4286 | 25.4288 | 25.4292 | 25.4295 | 25.4309 | 25.4324 | 25.4341 | 25.4359 | 25.4408 | 25.4664 | 25.523
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0.0042105 | 17.2104 | 17.1585 | 17.1338 | 17.0998 | 17.0613 | 17.0192 | 16.9747 | 16.9396 | 16.9038 | 16.8674 | 16.8316 | 16.6084 | 16.0641 | 14.9818 | 16.2168 | 16.162 | 16.1344 | 16.0951 | 16.0515 | 16.0044 | 15.9552 | 15.915 | 15.8743 | 15.8329 | 15.7923 | 15.1964 | 14.3277 | 13.1369 | 16.5965 | 16.5446 | 16.5199 | 16.4859 | 16.4474 | 16.4053 | 16.3608 | 16.3257 | 16.2899 | 16.2535 | 16.2177 | 16.1821 | 16.1378 | 16.0918
|  | LOSSIEMOUTH | CT |  |  |  | 0.0042105 | 17.2104 | 17.1899 | 17.1723 | 17.1491 | 17.1209 | 17.0882 | 17.0531 | 17.0296 | 17.0052 | 16.9806 | 16.9558 | 16.7949 | 16.5371 | 16.1242 | 16.2168 | 16.1945 | 16.1749 | 16.148 | 16.1162 | 16.0801 | 16.0417 | 16.0147 | 15.9868 | 15.9588 | 15.9306 | 15.7529 | 15.2108 | 14.4644 | 16.5965 | 16.576 | 16.5584 | 16.5351 | 16.507 | 16.4743 | 16.4392 | 16.4157 | 16.3913 | 16.3667 | 16.3419 | 16.3161 | 16.2839 | 16.2508
|  | LOSSIEMOUTH | LW |  |  |  | 0.0042105 | 17.2129 | 17.1585 | 17.1338 | 17.0998 | 17.0613 | 17.0192 | 16.9747 | 16.9396 | 16.9038 | 16.8674 | 16.8316 | 16.6084 | 16.0641 | 14.9818 | 16.2188 | 16.162 | 16.1344 | 16.0951 | 16.0515 | 16.0044 | 15.9552 | 15.915 | 15.8743 | 15.8329 | 15.7923 | 15.1964 | 14.3277 | 13.1369 | 16.599 | 16.5446 | 16.5199 | 16.4859 | 16.4474 | 16.4053 | 16.3608 | 16.3257 | 16.2899 | 16.2535 | 16.2177 | 16.1821 | 16.1378 | 16.0918
|  | LOSSIEMOUTH | ST |  |  |  | 0.0042105 | 17.2129 | 17.2057 | 17.2022 | 17.1928 | 17.1805 | 17.1663 | 17.1514 | 17.1458 | 17.1402 | 17.1348 | 17.1297 | 17.1044 | 16.9825 | 16.917 | 16.2222 | 16.2147 | 16.211 | 16.1992 | 16.1846 | 16.1681 | 16.151 | 16.143 | 16.135 | 16.1273 | 16.1199 | 16.0838 | 15.9516 | 15.876 | 16.599 | 16.5917 | 16.5882 | 16.5789 | 16.5666 | 16.5524 | 16.5375 | 16.5319 | 16.5263 | 16.5209 | 16.5157 | 16.4905 | 16.3686 | 16.303
|  | LOSSIEMOUTH | FS |  |  |  | 0.0042105 | 17.2129 | 17.2059 | 17.2056 | 17.2052 | 17.2046 | 17.2039 | 17.2031 | 17.2001 | 17.1967 | 17.1929 | 17.1888 | 17.178 | 17.1214 | 16.9973 | 16.2223 | 16.2151 | 16.2146 | 16.2139 | 16.2126 | 16.2102 | 16.2079 | 16.203 | 16.1977 | 16.1922 | 16.1862 | 16.1663 | 16.1011 | 15.9689 | 16.599 | 16.592 | 16.5916 | 16.5913 | 16.5907 | 16.5899 | 16.5892 | 16.5861 | 16.5827 | 16.579 | 16.5749 | 16.5641 | 16.5075 | 16.3834
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0 | 1.257 | 1.2478 | 1.2389 | 1.2293 | 1.2191 | 1.2082 | 1.1971 | 1.1875 | 1.1779 | 1.1682 | 1.1585 | 1.0751 | 0.94769 | 0.77328 | 1.2533 | 1.2441 | 1.2352 | 1.2256 | 1.2154 | 1.2046 | 1.1934 | 1.1839 | 1.1724 | 1.1485 | 1.1249 | 0.99905 | 0.84998 | 0.65439 | 1.2313 | 1.2217 | 1.2125 | 1.2022 | 1.1912 | 1.1798 | 1.1598 | 1.1365 | 1.1124 | 1.0885 | 1.065 | 1.0417 | 1.0165 | 0.99123
|  | LOWER OLLACH | CT |  |  |  | 0 | 1.257 | 1.2478 | 1.2389 | 1.2293 | 1.2191 | 1.2082 | 1.1971 | 1.1875 | 1.1779 | 1.1682 | 1.1585 | 1.086 | 0.97088 | 0.83386 | 1.2533 | 1.2441 | 1.2352 | 1.2256 | 1.2154 | 1.2046 | 1.1934 | 1.1839 | 1.1742 | 1.1595 | 1.1391 | 1.0278 | 0.89695 | 0.74464 | 1.2313 | 1.2217 | 1.2125 | 1.2022 | 1.1912 | 1.1798 | 1.1616 | 1.1408 | 1.1201 | 1.0995 | 1.0791 | 1.0579 | 1.036 | 1.0139
|  | LOWER OLLACH | LW |  |  |  | 0 | 1.2679 | 1.2588 | 1.253 | 1.2459 | 1.2381 | 1.2291 | 1.2197 | 1.2117 | 1.2027 | 1.1937 | 1.1795 | 1.0751 | 0.94769 | 0.77328 | 1.2643 | 1.2551 | 1.2493 | 1.2422 | 1.2344 | 1.2254 | 1.216 | 1.1965 | 1.1724 | 1.1485 | 1.1249 | 0.99905 | 0.84998 | 0.65439 | 1.242 | 1.2325 | 1.2261 | 1.218 | 1.2082 | 1.1839 | 1.1598 | 1.1365 | 1.1124 | 1.0885 | 1.065 | 1.0417 | 1.0165 | 0.99123
|  | LOWER OLLACH | ST |  |  |  | 0 | 1.2713 | 1.2687 | 1.2666 | 1.2637 | 1.2606 | 1.2572 | 1.2536 | 1.2512 | 1.2488 | 1.2465 | 1.2441 | 1.2328 | 1.2099 | 1.1783 | 1.2676 | 1.265 | 1.2629 | 1.26 | 1.2569 | 1.2535 | 1.2499 | 1.2475 | 1.2452 | 1.2428 | 1.2404 | 1.2291 | 1.1724 | 1.1206 | 1.246 | 1.2434 | 1.2413 | 1.238 | 1.2345 | 1.2307 | 1.2267 | 1.2239 | 1.221 | 1.2182 | 1.2155 | 1.1691 | 1.1124 | 1.0607
|  | LOWER OLLACH | FS |  |  |  | 0 | 1.2713 | 1.2696 | 1.2687 | 1.2678 | 1.2669 | 1.266 | 1.2651 | 1.2639 | 1.2626 | 1.2613 | 1.26 | 1.2511 | 1.2369 | 1.2181 | 1.2676 | 1.2659 | 1.2651 | 1.2642 | 1.2633 | 1.2623 | 1.2614 | 1.2602 | 1.2589 | 1.2577 | 1.2563 | 1.2475 | 1.2332 | 1.1918 | 1.2461 | 1.2444 | 1.2435 | 1.2426 | 1.2415 | 1.2403 | 1.239 | 1.2375 | 1.2359 | 1.2343 | 1.2326 | 1.2165 | 1.1757 | 1.1318
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20654 | 0.2064 | 0.20634 | 0.20626 | 0.20617 | 0.20607 | 0.20596 | 0.20587 | 0.20579 | 0.2057 | 0.20562 | 0.20511 | 0.20433 | 0.20243 | 0.20333 | 0.20319 | 0.20313 | 0.20304 | 0.20293 | 0.20282 | 0.20271 | 0.20262 | 0.20252 | 0.20242 | 0.20216 | 0.20082 | 0.19922 | 0.19696 | 0.20413 | 0.20399 | 0.20393 | 0.20385 | 0.20375 | 0.20365 | 0.20355 | 0.20346 | 0.20335 | 0.2031 | 0.20286 | 0.20262 | 0.20236 | 0.20211
|  | LUBNAIG | CT |  |  |  | 0 | 0.20654 | 0.20649 | 0.20646 | 0.20641 | 0.20634 | 0.20627 | 0.2062 | 0.20615 | 0.20609 | 0.20604 | 0.20599 | 0.20566 | 0.20515 | 0.20437 | 0.20333 | 0.20328 | 0.20325 | 0.20319 | 0.20312 | 0.20304 | 0.20296 | 0.2029 | 0.20285 | 0.20279 | 0.20273 | 0.20215 | 0.20106 | 0.19974 | 0.20413 | 0.20408 | 0.20404 | 0.20399 | 0.20393 | 0.20386 | 0.20378 | 0.20373 | 0.20368 | 0.20363 | 0.20358 | 0.20352 | 0.20338 | 0.20321
|  | LUBNAIG | LW |  |  |  | 0 | 0.20654 | 0.2064 | 0.20634 | 0.20626 | 0.20617 | 0.20607 | 0.20596 | 0.20587 | 0.20579 | 0.2057 | 0.20562 | 0.20511 | 0.20433 | 0.20243 | 0.20333 | 0.20319 | 0.20313 | 0.20304 | 0.20293 | 0.20282 | 0.20271 | 0.20262 | 0.20252 | 0.20242 | 0.20216 | 0.20082 | 0.19922 | 0.19696 | 0.20413 | 0.20399 | 0.20393 | 0.20385 | 0.20375 | 0.20365 | 0.20355 | 0.20346 | 0.20335 | 0.2031 | 0.20286 | 0.20262 | 0.20236 | 0.20211
|  | LUBNAIG | ST |  |  |  | 0 | 0.20654 | 0.20652 | 0.20651 | 0.20649 | 0.20647 | 0.20644 | 0.20641 | 0.20639 | 0.20638 | 0.20637 | 0.20636 | 0.20631 | 0.20607 | 0.20594 | 0.20333 | 0.20331 | 0.2033 | 0.20328 | 0.20326 | 0.20323 | 0.20319 | 0.20318 | 0.20316 | 0.20314 | 0.20313 | 0.20306 | 0.2028 | 0.2026 | 0.20413 | 0.20411 | 0.2041 | 0.20408 | 0.20406 | 0.20403 | 0.20399 | 0.20398 | 0.20397 | 0.20396 | 0.20395 | 0.2039 | 0.20365 | 0.20329
|  | LUBNAIG | FS |  |  |  | 0 | 0.20654 | 0.20652 | 0.20652 | 0.20652 | 0.20652 | 0.20652 | 0.20652 | 0.20651 | 0.20651 | 0.2065 | 0.20649 | 0.20647 | 0.20636 | 0.20612 | 0.20333 | 0.20331 | 0.20331 | 0.20331 | 0.20331 | 0.20331 | 0.20331 | 0.2033 | 0.2033 | 0.20328 | 0.20327 | 0.20324 | 0.20311 | 0.20287 | 0.20413 | 0.20411 | 0.20411 | 0.20411 | 0.20411 | 0.20411 | 0.20411 | 0.2041 | 0.20409 | 0.20409 | 0.20408 | 0.20406 | 0.20395 | 0.20371
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 1.0347 | 17.0406 | 16.9744 | 16.9121 | 16.8438 | 16.7712 | 16.6946 | 16.6156 | 16.5462 | 16.4751 | 16.3314 | 16.162 | 15.2611 | 14.1684 | 12.6855 | 13.9589 | 13.8415 | 13.7212 | 13.5475 | 13.351 | 13.1562 | 12.9647 | 12.7738 | 12.5838 | 12.3947 | 12.2088 | 11.2288 | 10.0566 | 8.4949 | 14.8349 | 14.7184 | 14.5993 | 14.4298 | 14.236 | 14.0437 | 13.8546 | 13.6661 | 13.4786 | 13.292 | 13.1084 | 12.9285 | 12.7356 | 12.5397
|  | LUNANHEAD | CT |  |  |  | 1.0347 | 17.0406 | 16.9744 | 16.9121 | 16.8438 | 16.7712 | 16.6946 | 16.6156 | 16.5462 | 16.4751 | 16.403 | 16.3246 | 15.546 | 14.6177 | 13.5039 | 13.9589 | 13.8415 | 13.7212 | 13.5574 | 13.39 | 13.2216 | 13.0571 | 12.8978 | 12.7386 | 12.5803 | 12.4239 | 11.5891 | 10.6053 | 9.4368 | 14.8349 | 14.7184 | 14.5993 | 14.4373 | 14.2719 | 14.1053 | 13.9425 | 13.7849 | 13.6274 | 13.4708 | 13.316 | 13.1612 | 12.9965 | 12.8303
|  | LUNANHEAD | LW |  |  |  | 1.0347 | 17.1206 | 17.0488 | 17.0069 | 16.9532 | 16.892 | 16.8252 | 16.7543 | 16.6762 | 16.5035 | 16.3314 | 16.162 | 15.2611 | 14.1684 | 12.6855 | 14.0137 | 13.8685 | 13.7408 | 13.5475 | 13.351 | 13.1562 | 12.9647 | 12.7738 | 12.5838 | 12.3947 | 12.2088 | 11.2288 | 10.0566 | 8.4949 | 14.8901 | 14.7464 | 14.6204 | 14.4298 | 14.236 | 14.0437 | 13.8546 | 13.6661 | 13.4786 | 13.292 | 13.1084 | 12.9285 | 12.7356 | 12.5397
|  | LUNANHEAD | ST |  |  |  | 1.0347 | 17.1366 | 17.118 | 17.1034 | 17.0826 | 17.0571 | 17.0304 | 17.002 | 16.9835 | 16.965 | 16.9467 | 16.9295 | 16.8416 | 16.5471 | 16.2009 | 14.1202 | 14.0932 | 14.0684 | 13.9885 | 13.9036 | 13.8199 | 13.7361 | 13.6568 | 13.5776 | 13.5006 | 13.4257 | 13.0693 | 12.6304 | 12.2511 | 14.9949 | 14.968 | 14.9435 | 14.8647 | 14.781 | 14.6984 | 14.6157 | 14.5375 | 14.4595 | 14.3837 | 14.31 | 13.9588 | 13.5249 | 13.1502
|  | LUNANHEAD | FS |  |  |  | 1.0347 | 17.145 | 17.1318 | 17.1231 | 17.1143 | 17.1053 | 17.096 | 17.0868 | 17.0761 | 17.065 | 17.0536 | 17.0418 | 16.9851 | 16.8827 | 16.6723 | 14.1351 | 14.1149 | 14.0988 | 14.0787 | 14.0479 | 13.9984 | 13.9492 | 13.8921 | 13.8348 | 13.7773 | 13.7196 | 13.4384 | 13.1322 | 12.766 | 15.0097 | 14.9896 | 14.9736 | 14.9537 | 14.9234 | 14.8747 | 14.8262 | 14.7701 | 14.7137 | 14.6571 | 14.6002 | 14.3235 | 14.0213 | 13.6589
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.11463 | 0.11434 | 0.11421 | 0.11404 | 0.11384 | 0.11362 | 0.1134 | 0.11322 | 0.11274 | 0.11223 | 0.11173 | 0.10912 | 0.10592 | 0.1013 | 0.10797 | 0.10769 | 0.10756 | 0.10738 | 0.10718 | 0.10697 | 0.10674 | 0.10656 | 0.10638 | 0.1062 | 0.10602 | 0.10404 | 0.10057 | 0.095698 | 0.1086 | 0.10831 | 0.10819 | 0.10801 | 0.10781 | 0.1076 | 0.10737 | 0.10719 | 0.10701 | 0.10652 | 0.10597 | 0.10543 | 0.10485 | 0.10427
|  | LUSSAGIVEN | CT |  |  |  | 0 | 0.11463 | 0.11453 | 0.11445 | 0.11434 | 0.11421 | 0.11406 | 0.11389 | 0.11379 | 0.11368 | 0.11357 | 0.11345 | 0.11169 | 0.10952 | 0.10683 | 0.10797 | 0.10788 | 0.1078 | 0.10769 | 0.10755 | 0.1074 | 0.10724 | 0.10713 | 0.10702 | 0.10691 | 0.1068 | 0.10609 | 0.10451 | 0.10164 | 0.1086 | 0.1085 | 0.10842 | 0.10832 | 0.10818 | 0.10803 | 0.10787 | 0.10776 | 0.10765 | 0.10754 | 0.10743 | 0.10731 | 0.10712 | 0.10673
|  | LUSSAGIVEN | LW |  |  |  | 0 | 0.11463 | 0.11434 | 0.11421 | 0.11404 | 0.11384 | 0.11362 | 0.1134 | 0.11322 | 0.11274 | 0.11223 | 0.11173 | 0.10912 | 0.10592 | 0.1013 | 0.10797 | 0.10769 | 0.10756 | 0.10738 | 0.10718 | 0.10697 | 0.10674 | 0.10656 | 0.10638 | 0.1062 | 0.10602 | 0.10404 | 0.10057 | 0.095698 | 0.1086 | 0.10831 | 0.10819 | 0.10801 | 0.10781 | 0.1076 | 0.10737 | 0.10719 | 0.10701 | 0.10652 | 0.10597 | 0.10543 | 0.10485 | 0.10427
|  | LUSSAGIVEN | ST |  |  |  | 0 | 0.11463 | 0.11459 | 0.11457 | 0.11453 | 0.11448 | 0.11441 | 0.11434 | 0.11432 | 0.11429 | 0.11427 | 0.11424 | 0.11413 | 0.11343 | 0.11259 | 0.10797 | 0.10794 | 0.10792 | 0.10787 | 0.10782 | 0.10776 | 0.10769 | 0.10766 | 0.10764 | 0.10761 | 0.10759 | 0.10748 | 0.10695 | 0.10668 | 0.1086 | 0.10856 | 0.10855 | 0.1085 | 0.10845 | 0.10839 | 0.10832 | 0.10829 | 0.10827 | 0.10824 | 0.10822 | 0.10811 | 0.10758 | 0.10686
|  | LUSSAGIVEN | FS |  |  |  | 0 | 0.11463 | 0.1146 | 0.11459 | 0.11459 | 0.11459 | 0.11459 | 0.11458 | 0.11457 | 0.11456 | 0.11454 | 0.11452 | 0.11448 | 0.11425 | 0.11374 | 0.10797 | 0.10794 | 0.10794 | 0.10794 | 0.10793 | 0.10793 | 0.10793 | 0.10792 | 0.1079 | 0.10789 | 0.10787 | 0.10782 | 0.10759 | 0.10709 | 0.1086 | 0.10857 | 0.10857 | 0.10857 | 0.10856 | 0.10856 | 0.10856 | 0.10854 | 0.10853 | 0.10852 | 0.1085 | 0.10845 | 0.10822 | 0.10771
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 0.28 | 16.2731 | 16.2487 | 16.2374 | 16.2218 | 16.2041 | 16.1844 | 16.1634 | 16.1469 | 16.1299 | 16.1125 | 16.0953 | 15.985 | 15.8047 | 15.4049 | 15.2954 | 15.2696 | 15.2571 | 15.239 | 15.2189 | 15.1969 | 15.1737 | 15.1548 | 15.1354 | 15.1157 | 15.0961 | 14.974 | 14.7812 | 14.4118 | 15.745 | 15.7189 | 15.706 | 15.6872 | 15.6664 | 15.6438 | 15.6201 | 15.6005 | 15.5804 | 15.56 | 15.5399 | 15.5197 | 15.4947 | 15.4688
|  | LYNDHURST | CT |  |  |  | 0.28 | 16.2731 | 16.2644 | 16.257 | 16.247 | 16.2347 | 16.2201 | 16.2044 | 16.194 | 16.183 | 16.1719 | 16.1606 | 16.0809 | 15.9483 | 15.7417 | 15.2954 | 15.2859 | 15.2775 | 15.2658 | 15.2519 | 15.2357 | 15.2183 | 15.2063 | 15.1936 | 15.1808 | 15.1679 | 15.08 | 14.9386 | 14.723 | 15.745 | 15.7353 | 15.7267 | 15.7145 | 15.7001 | 15.6835 | 15.6657 | 15.6531 | 15.64 | 15.6268 | 15.6134 | 15.5994 | 15.5812 | 15.5625
|  | LYNDHURST | LW |  |  |  | 0.28 | 16.2739 | 16.2487 | 16.2374 | 16.2218 | 16.2041 | 16.1844 | 16.1634 | 16.1469 | 16.1299 | 16.1125 | 16.0953 | 15.985 | 15.8047 | 15.4049 | 15.296 | 15.2696 | 15.2571 | 15.239 | 15.2189 | 15.1969 | 15.1737 | 15.1548 | 15.1354 | 15.1157 | 15.0961 | 14.974 | 14.7812 | 14.4118 | 15.7455 | 15.7189 | 15.706 | 15.6872 | 15.6664 | 15.6438 | 15.6201 | 15.6005 | 15.5804 | 15.56 | 15.5399 | 15.5197 | 15.4947 | 15.4688
|  | LYNDHURST | ST |  |  |  | 0.28 | 16.2739 | 16.2703 | 16.2686 | 16.2639 | 16.2582 | 16.2515 | 16.2441 | 16.2413 | 16.2385 | 16.2358 | 16.2333 | 16.2213 | 16.1581 | 16.1249 | 15.2975 | 15.2938 | 15.292 | 15.2862 | 15.2794 | 15.2716 | 15.2631 | 15.2592 | 15.2553 | 15.2515 | 15.2479 | 15.2306 | 15.1621 | 15.1236 | 15.7475 | 15.7437 | 15.7419 | 15.7358 | 15.7287 | 15.7206 | 15.7119 | 15.7076 | 15.7034 | 15.6993 | 15.6954 | 15.6766 | 15.6067 | 15.5667
|  | LYNDHURST | FS |  |  |  | 0.28 | 16.2739 | 16.2702 | 16.27 | 16.2698 | 16.2695 | 16.2691 | 16.2687 | 16.267 | 16.2652 | 16.2632 | 16.261 | 16.2552 | 16.2244 | 16.1559 | 15.2975 | 15.2936 | 15.2934 | 15.2931 | 15.2924 | 15.2912 | 15.29 | 15.2875 | 15.2848 | 15.2819 | 15.2788 | 15.2687 | 15.2336 | 15.1609 | 15.7475 | 15.7436 | 15.7433 | 15.7429 | 15.7422 | 15.7408 | 15.7393 | 15.7366 | 15.7336 | 15.7305 | 15.7272 | 15.7159 | 15.6797 | 15.6058
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0 | 1.0764 | 1.0723 | 1.0705 | 1.068 | 1.0651 | 1.062 | 1.0558 | 1.0455 | 1.0352 | 1.0251 | 1.015 | 0.96213 | 0.89933 | 0.81336 | 1.0554 | 1.0487 | 1.0439 | 1.0358 | 1.0274 | 1.019 | 1.0088 | 0.99647 | 0.98419 | 0.97199 | 0.95996 | 0.89727 | 0.82449 | 0.72861 | 1.0801 | 1.0714 | 1.0642 | 1.0517 | 1.039 | 1.0264 | 1.014 | 1.0019 | 0.98983 | 0.97787 | 0.96607 | 0.95442 | 0.94209 | 0.92966
|  | LYNESS | CT |  |  |  | 0 | 1.0764 | 1.075 | 1.0738 | 1.0721 | 1.0701 | 1.0678 | 1.0653 | 1.0636 | 1.0595 | 1.0524 | 1.0454 | 1.0077 | 0.96304 | 0.90895 | 1.0558 | 1.0526 | 1.0491 | 1.0434 | 1.0375 | 1.0313 | 1.0251 | 1.0197 | 1.0127 | 1.0042 | 0.99568 | 0.95098 | 0.89916 | 0.83805 | 1.0809 | 1.0764 | 1.0709 | 1.0621 | 1.053 | 1.0439 | 1.0348 | 1.0263 | 1.0179 | 1.0095 | 1.0012 | 0.99284 | 0.98404 | 0.97519
|  | LYNESS | LW |  |  |  | 0 | 1.0764 | 1.0723 | 1.0705 | 1.068 | 1.0651 | 1.062 | 1.0558 | 1.0455 | 1.0352 | 1.0251 | 1.015 | 0.96213 | 0.89933 | 0.81336 | 1.0554 | 1.0487 | 1.0439 | 1.0358 | 1.0274 | 1.019 | 1.0088 | 0.99647 | 0.98419 | 0.97199 | 0.95996 | 0.89727 | 0.82449 | 0.72861 | 1.0801 | 1.0714 | 1.0642 | 1.0517 | 1.039 | 1.0264 | 1.014 | 1.0019 | 0.98983 | 0.97787 | 0.96607 | 0.95442 | 0.94209 | 0.92966
|  | LYNESS | ST |  |  |  | 0 | 1.0764 | 1.0758 | 1.0756 | 1.0749 | 1.074 | 1.073 | 1.0719 | 1.0715 | 1.0711 | 1.0707 | 1.0703 | 1.0632 | 1.038 | 1.0175 | 1.0587 | 1.0581 | 1.0578 | 1.0544 | 1.051 | 1.0475 | 1.0439 | 1.041 | 1.038 | 1.0351 | 1.0323 | 1.0155 | 0.98601 | 0.96118 | 1.0862 | 1.0855 | 1.0851 | 1.0797 | 1.0742 | 1.0687 | 1.0632 | 1.0582 | 1.0532 | 1.0484 | 1.0436 | 1.0208 | 0.99176 | 0.96744
|  | LYNESS | FS |  |  |  | 0 | 1.0764 | 1.0759 | 1.0758 | 1.0758 | 1.0758 | 1.0757 | 1.0757 | 1.0754 | 1.0752 | 1.0749 | 1.0746 | 1.0739 | 1.0685 | 1.0484 | 1.0588 | 1.0583 | 1.0582 | 1.058 | 1.0569 | 1.0553 | 1.0537 | 1.0517 | 1.0497 | 1.0477 | 1.0457 | 1.0349 | 1.022 | 0.99894 | 1.0864 | 1.0858 | 1.0856 | 1.0853 | 1.0834 | 1.0806 | 1.0777 | 1.0743 | 1.071 | 1.0676 | 1.0642 | 1.0456 | 1.0271 | 1.0044
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0 | 0.21272 | 0.21214 | 0.21188 | 0.21152 | 0.21112 | 0.21067 | 0.21021 | 0.20984 | 0.20946 | 0.20908 | 0.20871 | 0.20639 | 0.20066 | 0.19017 | 0.20846 | 0.20788 | 0.20762 | 0.20727 | 0.20686 | 0.20641 | 0.20595 | 0.20558 | 0.2052 | 0.20482 | 0.20445 | 0.19817 | 0.19033 | 0.1792 | 0.20846 | 0.20788 | 0.20762 | 0.20727 | 0.20686 | 0.20641 | 0.20595 | 0.20558 | 0.2052 | 0.20482 | 0.20445 | 0.20408 | 0.20294 | 0.20164
|  | MAARUIG | CT |  |  |  | 0 | 0.21272 | 0.21252 | 0.21234 | 0.21211 | 0.21183 | 0.21149 | 0.21114 | 0.2109 | 0.21066 | 0.21042 | 0.21017 | 0.20857 | 0.206 | 0.20177 | 0.20846 | 0.20826 | 0.20809 | 0.20785 | 0.20757 | 0.20724 | 0.20688 | 0.20664 | 0.2064 | 0.20616 | 0.20591 | 0.20406 | 0.19858 | 0.19177 | 0.20846 | 0.20826 | 0.20809 | 0.20785 | 0.20757 | 0.20724 | 0.20688 | 0.20664 | 0.2064 | 0.20616 | 0.20591 | 0.20566 | 0.20534 | 0.20501
|  | MAARUIG | LW |  |  |  | 0 | 0.21272 | 0.21214 | 0.21188 | 0.21152 | 0.21112 | 0.21067 | 0.21021 | 0.20984 | 0.20946 | 0.20908 | 0.20871 | 0.20639 | 0.20066 | 0.19017 | 0.20846 | 0.20788 | 0.20762 | 0.20727 | 0.20686 | 0.20641 | 0.20595 | 0.20558 | 0.2052 | 0.20482 | 0.20445 | 0.19817 | 0.19033 | 0.1792 | 0.20846 | 0.20788 | 0.20762 | 0.20727 | 0.20686 | 0.20641 | 0.20595 | 0.20558 | 0.2052 | 0.20482 | 0.20445 | 0.20408 | 0.20294 | 0.20164
|  | MAARUIG | ST |  |  |  | 0 | 0.21272 | 0.21264 | 0.2126 | 0.21251 | 0.21239 | 0.21224 | 0.21209 | 0.21203 | 0.21197 | 0.21191 | 0.21186 | 0.21161 | 0.21038 | 0.20975 | 0.20846 | 0.20838 | 0.20835 | 0.20825 | 0.20813 | 0.20798 | 0.20783 | 0.20777 | 0.20771 | 0.20765 | 0.2076 | 0.20735 | 0.20613 | 0.20549 | 0.20846 | 0.20838 | 0.20835 | 0.20825 | 0.20813 | 0.20798 | 0.20783 | 0.20777 | 0.20771 | 0.20765 | 0.2076 | 0.20735 | 0.20613 | 0.20549
|  | MAARUIG | FS |  |  |  | 0 | 0.21272 | 0.21265 | 0.21264 | 0.21264 | 0.21263 | 0.21263 | 0.21262 | 0.21259 | 0.21255 | 0.21251 | 0.21247 | 0.21236 | 0.21178 | 0.21051 | 0.20846 | 0.20839 | 0.20838 | 0.20838 | 0.20837 | 0.20837 | 0.20836 | 0.20833 | 0.20829 | 0.20825 | 0.20821 | 0.2081 | 0.20752 | 0.20625 | 0.20846 | 0.20839 | 0.20838 | 0.20838 | 0.20837 | 0.20837 | 0.20836 | 0.20833 | 0.20829 | 0.20825 | 0.20821 | 0.2081 | 0.20752 | 0.20625
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0.069474 | 16.9231 | 16.8438 | 16.8079 | 16.7578 | 16.701 | 16.6386 | 16.5729 | 16.5212 | 16.4677 | 16.4133 | 16.3598 | 16.0265 | 15.5008 | 14.4411 | 16.5453 | 16.462 | 16.4222 | 16.3649 | 16.3011 | 16.2321 | 16.16 | 16.1015 | 16.0414 | 15.9804 | 15.9205 | 15.2404 | 14.0222 | 12.3225 | 16.527 | 16.4429 | 16.4021 | 16.3434 | 16.278 | 16.2076 | 16.1341 | 16.0741 | 16.0125 | 15.9502 | 15.8888 | 15.7732 | 15.5718 | 15.3685
|  | MACALPINE ROAD | CT |  |  |  | 0.069474 | 16.9231 | 16.8945 | 16.8701 | 16.8375 | 16.7976 | 16.751 | 16.7009 | 16.6679 | 16.6335 | 16.5989 | 16.564 | 16.3351 | 15.9677 | 15.3984 | 16.5453 | 16.5143 | 16.4872 | 16.4495 | 16.4048 | 16.3535 | 16.299 | 16.2612 | 16.2222 | 16.1829 | 16.1434 | 15.8923 | 15.295 | 14.2487 | 16.527 | 16.4955 | 16.4678 | 16.429 | 16.3832 | 16.3309 | 16.2754 | 16.2366 | 16.1966 | 16.1563 | 16.1159 | 16.074 | 16.0228 | 15.9702
|  | MACALPINE ROAD | LW |  |  |  | 0.069474 | 16.9247 | 16.8438 | 16.8079 | 16.7578 | 16.701 | 16.6386 | 16.5729 | 16.5212 | 16.4677 | 16.4133 | 16.3598 | 16.0265 | 15.5008 | 14.4411 | 16.5462 | 16.462 | 16.4222 | 16.3649 | 16.3011 | 16.2321 | 16.16 | 16.1015 | 16.0414 | 15.9804 | 15.9205 | 15.2404 | 14.0222 | 12.3225 | 16.5277 | 16.4429 | 16.4021 | 16.3434 | 16.278 | 16.2076 | 16.1341 | 16.0741 | 16.0125 | 15.9502 | 15.8888 | 15.7732 | 15.5718 | 15.3685
|  | MACALPINE ROAD | ST |  |  |  | 0.069474 | 16.9256 | 16.9148 | 16.9097 | 16.8959 | 16.8791 | 16.8594 | 16.8374 | 16.8292 | 16.8209 | 16.813 | 16.8054 | 16.7707 | 16.5957 | 16.505 | 16.5517 | 16.5408 | 16.5354 | 16.5183 | 16.4983 | 16.4756 | 16.4507 | 16.4392 | 16.4278 | 16.4168 | 16.4062 | 16.3572 | 16.1683 | 16.0643 | 16.5342 | 16.5233 | 16.5179 | 16.5001 | 16.4794 | 16.456 | 16.4304 | 16.4183 | 16.4061 | 16.3945 | 16.3832 | 16.3311 | 16.1393 | 16.0323
|  | MACALPINE ROAD | FS |  |  |  | 0.069474 | 16.9256 | 16.9153 | 16.9149 | 16.9143 | 16.9135 | 16.9124 | 16.9113 | 16.9069 | 16.9019 | 16.8965 | 16.8905 | 16.8748 | 16.7924 | 16.6116 | 16.5519 | 16.5415 | 16.5408 | 16.5399 | 16.5381 | 16.5348 | 16.5316 | 16.5247 | 16.5173 | 16.5094 | 16.501 | 16.4733 | 16.3796 | 16.1879 | 16.5345 | 16.524 | 16.5233 | 16.5223 | 16.5203 | 16.5166 | 16.5129 | 16.5055 | 16.4975 | 16.4891 | 16.4802 | 16.4499 | 16.3537 | 16.1596
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 0.095789 | 16.7288 | 16.5867 | 16.4799 | 16.3276 | 16.1694 | 16.0081 | 15.8476 | 15.6993 | 15.5514 | 15.4036 | 15.2609 | 14.4786 | 13.4527 | 11.8359 | 23.3573 | 23.285 | 23.2354 | 23.1678 | 23.0017 | 22.6502 | 22.3132 | 21.9768 | 21.6463 | 21.3189 | 20.9923 | 19.3411 | 17.4678 | 15.0226 | 21.5007 | 21.4123 | 21.3495 | 21.2624 | 21.1669 | 20.8995 | 20.547 | 20.194 | 19.8475 | 19.5067 | 19.1813 | 18.8665 | 18.5354 | 18.2036
|  | MACDUFF | CT |  |  |  | 0.095789 | 16.7288 | 16.6439 | 16.5598 | 16.4465 | 16.3249 | 16.1964 | 16.0691 | 15.9589 | 15.8473 | 15.7377 | 15.6297 | 15.0271 | 14.2472 | 13.2117 | 23.3573 | 23.3058 | 23.2594 | 23.2029 | 23.1385 | 23.0659 | 22.9056 | 22.6639 | 22.423 | 22.1898 | 21.9634 | 20.7776 | 19.4055 | 17.7904 | 21.5007 | 21.4415 | 21.3864 | 21.3168 | 21.2392 | 21.1537 | 21.0653 | 20.9147 | 20.6664 | 20.4224 | 20.1856 | 19.9489 | 19.7024 | 19.4572
|  | MACDUFF | LW |  |  |  | 0.095789 | 16.7406 | 16.5867 | 16.4799 | 16.3276 | 16.1694 | 16.0081 | 15.8476 | 15.6993 | 15.5514 | 15.4036 | 15.2609 | 14.4786 | 13.4527 | 11.8359 | 23.3884 | 23.285 | 23.2354 | 23.1678 | 23.0017 | 22.6502 | 22.3132 | 21.9768 | 21.6463 | 21.3189 | 20.9923 | 19.3411 | 17.4678 | 15.0226 | 21.5274 | 21.4123 | 21.3495 | 21.2624 | 21.1669 | 20.8995 | 20.547 | 20.194 | 19.8475 | 19.5067 | 19.1813 | 18.8665 | 18.5354 | 18.2036
|  | MACDUFF | ST |  |  |  | 0.095789 | 16.8024 | 16.7775 | 16.7582 | 16.7031 | 16.6431 | 16.58 | 16.516 | 16.4655 | 16.4149 | 16.3659 | 16.319 | 16.0964 | 15.721 | 15.4485 | 23.3943 | 23.3771 | 23.3667 | 23.3457 | 23.3204 | 23.2914 | 23.2598 | 23.2448 | 23.2297 | 23.215 | 23.2016 | 22.6378 | 21.9154 | 21.302 | 21.5461 | 21.5272 | 21.5147 | 21.4859 | 21.4525 | 21.4157 | 21.3766 | 21.3534 | 21.3301 | 21.3075 | 21.2864 | 20.8783 | 20.1254 | 19.4901
|  | MACDUFF | FS |  |  |  | 0.095789 | 16.8091 | 16.788 | 16.7772 | 16.7643 | 16.7454 | 16.7169 | 16.6885 | 16.6529 | 16.6161 | 16.5799 | 16.5433 | 16.3792 | 16.1487 | 15.8053 | 23.3968 | 23.382 | 23.378 | 23.374 | 23.3697 | 23.3649 | 23.3602 | 23.3516 | 23.3422 | 23.3331 | 23.3235 | 23.2424 | 22.729 | 22.1151 | 21.5496 | 21.5333 | 21.5278 | 21.5218 | 21.5141 | 21.5038 | 21.4937 | 21.4788 | 21.4631 | 21.4478 | 21.4319 | 21.3671 | 20.9729 | 20.3352
| CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0 | 2.7705 | 2.7601 | 4.2555 | 4.249 | 4.2417 | 4.2337 | 4.2187 | 4.1966 | 4.1746 | 4.1528 | 4.1314 | 4.0188 | 3.8836 | 3.6917 | 2.9358 | 2.9161 | 4.3998 | 4.3725 | 4.3449 | 4.3176 | 4.2907 | 4.2648 | 4.2391 | 4.2136 | 4.1887 | 4.0576 | 3.9032 | 3.6947 | 2.8188 | 2.8084 | 4.3038 | 4.2973 | 4.29 | 4.282 | 4.2736 | 4.2671 | 4.2604 | 4.2537 | 4.2471 | 4.2406 | 4.2226 | 4.1974
|  | MACHRIE | CT |  |  |  | 0 | 2.7705 | 2.767 | 4.2641 | 4.26 | 4.2551 | 4.2493 | 4.2432 | 4.2391 | 4.235 | 4.221 | 4.2069 | 4.1311 | 4.04 | 3.9281 | 2.9395 | 2.9286 | 4.4176 | 4.3994 | 4.3807 | 4.3619 | 4.3432 | 4.3261 | 4.309 | 4.2922 | 4.2756 | 4.1882 | 4.0847 | 3.9604 | 2.8188 | 2.8153 | 4.3123 | 4.3083 | 4.3033 | 4.2976 | 4.2914 | 4.2874 | 4.2833 | 4.2791 | 4.275 | 4.2706 | 4.2652 | 4.2597
|  | MACHRIE | LW |  |  |  | 0 | 2.7705 | 2.7601 | 4.2555 | 4.249 | 4.2417 | 4.2337 | 4.2187 | 4.1966 | 4.1746 | 4.1528 | 4.1314 | 4.0188 | 3.8836 | 3.6917 | 2.9358 | 2.9161 | 4.3998 | 4.3725 | 4.3449 | 4.3176 | 4.2907 | 4.2648 | 4.2391 | 4.2136 | 4.1887 | 4.0576 | 3.9032 | 3.6947 | 2.8188 | 2.8084 | 4.3038 | 4.2973 | 4.29 | 4.282 | 4.2736 | 4.2671 | 4.2604 | 4.2537 | 4.2471 | 4.2406 | 4.2226 | 4.1974
|  | MACHRIE | ST |  |  |  | 0 | 2.7705 | 2.7692 | 4.2686 | 4.267 | 4.2649 | 4.2626 | 4.2599 | 4.2589 | 4.2579 | 4.257 | 4.256 | 4.2495 | 4.1999 | 4.1615 | 2.9452 | 2.9439 | 4.4433 | 4.4366 | 4.4255 | 4.4145 | 4.4036 | 4.3937 | 4.384 | 4.3746 | 4.3654 | 4.3225 | 4.2657 | 4.2207 | 2.8188 | 2.8175 | 4.3169 | 4.3152 | 4.3132 | 4.3108 | 4.3082 | 4.3072 | 4.3062 | 4.3052 | 4.3043 | 4.3002 | 4.28 | 4.2697
|  | MACHRIE | FS |  |  |  | 0 | 2.7705 | 2.7694 | 4.2693 | 4.2693 | 4.2692 | 4.269 | 4.2689 | 4.2684 | 4.2679 | 4.2672 | 4.2666 | 4.2648 | 4.2516 | 4.2068 | 2.9452 | 2.944 | 4.444 | 4.4439 | 4.4438 | 4.4395 | 4.4338 | 4.4261 | 4.4183 | 4.4105 | 4.4027 | 4.366 | 4.3241 | 4.2734 | 2.8188 | 2.8177 | 4.3176 | 4.3175 | 4.3174 | 4.3173 | 4.3172 | 4.3167 | 4.3161 | 4.3155 | 4.3148 | 4.3131 | 4.3038 | 4.2838
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 0 | 2.3443 | 2.3339 | 2.3286 | 2.3208 | 2.3123 | 2.3032 | 2.286 | 2.2687 | 2.2514 | 2.2341 | 2.2171 | 2.1235 | 1.9756 | 1.7715 | 2.3049 | 2.2948 | 2.2899 | 2.2829 | 2.2751 | 2.2667 | 2.2579 | 2.2508 | 2.2428 | 2.216 | 2.1896 | 2.0517 | 1.8906 | 1.6756 | 2.2206 | 2.2086 | 2.2013 | 2.19 | 2.178 | 2.1655 | 2.1528 | 2.1406 | 2.1124 | 2.0845 | 2.0569 | 2.0296 | 2.0008 | 1.9718
|  | MALLAIG | CT |  |  |  | 0 | 2.3446 | 2.3407 | 2.3373 | 2.3323 | 2.3265 | 2.3199 | 2.313 | 2.308 | 2.2978 | 2.2859 | 2.2741 | 2.2107 | 2.1302 | 2.0076 | 2.305 | 2.3014 | 2.2982 | 2.2938 | 2.2884 | 2.2824 | 2.2759 | 2.2714 | 2.2668 | 2.2622 | 2.2575 | 2.1779 | 2.0633 | 1.9274 | 2.2215 | 2.2164 | 2.2116 | 2.2042 | 2.1959 | 2.1871 | 2.1779 | 2.1705 | 2.1629 | 2.1553 | 2.1447 | 2.1251 | 2.1045 | 2.0846
|  | MALLAIG | LW |  |  |  | 0 | 2.3443 | 2.3339 | 2.3286 | 2.3208 | 2.3123 | 2.3032 | 2.286 | 2.2687 | 2.2514 | 2.2341 | 2.2171 | 2.1235 | 1.9756 | 1.7715 | 2.3049 | 2.2948 | 2.2899 | 2.2829 | 2.2751 | 2.2667 | 2.2579 | 2.2508 | 2.2428 | 2.216 | 2.1896 | 2.0517 | 1.8906 | 1.6756 | 2.2206 | 2.2086 | 2.2013 | 2.19 | 2.178 | 2.1655 | 2.1528 | 2.1406 | 2.1124 | 2.0845 | 2.0569 | 2.0296 | 2.0008 | 1.9718
|  | MALLAIG | ST |  |  |  | 0 | 2.3455 | 2.3441 | 2.3435 | 2.3411 | 2.3383 | 2.3353 | 2.332 | 2.3302 | 2.3284 | 2.3267 | 2.325 | 2.307 | 2.2644 | 2.232 | 2.3056 | 2.3043 | 2.3036 | 2.3016 | 2.2991 | 2.2964 | 2.2934 | 2.292 | 2.2905 | 2.2891 | 2.2878 | 2.2817 | 2.2527 | 2.2011 | 2.2242 | 2.2227 | 2.2218 | 2.2178 | 2.2134 | 2.2089 | 2.2041 | 2.2006 | 2.1971 | 2.1937 | 2.1904 | 2.1755 | 2.122 | 2.0679
|  | MALLAIG | FS |  |  |  | 0 | 2.3455 | 2.3443 | 2.3442 | 2.344 | 2.3437 | 2.343 | 2.3423 | 2.3412 | 2.34 | 2.3388 | 2.3375 | 2.3328 | 2.3133 | 2.2751 | 2.3056 | 2.3044 | 2.3043 | 2.3042 | 2.3039 | 2.3035 | 2.303 | 2.3022 | 2.3013 | 2.3003 | 2.2992 | 2.2957 | 2.2848 | 2.2629 | 2.2243 | 2.2231 | 2.2227 | 2.2223 | 2.2215 | 2.2197 | 2.2179 | 2.2156 | 2.2132 | 2.2108 | 2.2083 | 2.1976 | 2.1798 | 2.141
| KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0 | 2.5682 | 2.5315 | 2.4963 | 2.4581 | 2.4183 | 2.3448 | 2.2509 | 2.1575 | 2.0663 | 1.9771 | 1.8941 | 1.4661 | 0.9694 | 0.30103 | 4.532 | 4.3786 | 4.2305 | 4.042 | 3.859 | 3.6835 | 3.5227 | 3.3583 | 3.2001 | 3.0472 | 2.9074 | 2.2284 | 1.509 | 0.63395 | 2.7931 | 2.7564 | 2.7212 | 2.683 | 2.6432 | 2.6011 | 2.5578 | 2.5188 | 2.4795 | 2.4393 | 2.3525 | 2.2242 | 2.0918 | 1.9588
|  | MARNOCH | CT |  |  |  | 0 | 2.5682 | 2.5315 | 2.4963 | 2.4581 | 2.4183 | 2.3762 | 2.3033 | 2.2219 | 2.1413 | 2.0635 | 1.9884 | 1.5973 | 1.1543 | 0.6272 | 4.537 | 4.4296 | 4.3144 | 4.1725 | 4.0262 | 3.8779 | 3.7454 | 3.6146 | 3.4859 | 3.3643 | 3.2487 | 2.6725 | 2.0711 | 1.3955 | 2.7931 | 2.7564 | 2.7212 | 2.683 | 2.6432 | 2.6011 | 2.5578 | 2.5188 | 2.4795 | 2.4393 | 2.399 | 2.3582 | 2.3037 | 2.2238
|  | MARNOCH | LW |  |  |  | 0 | 2.6162 | 2.5798 | 2.5578 | 2.5298 | 2.4445 | 2.3448 | 2.2509 | 2.1575 | 2.0663 | 1.9771 | 1.8941 | 1.4661 | 0.9694 | 0.30103 | 4.532 | 4.3786 | 4.2305 | 4.042 | 3.859 | 3.6835 | 3.5227 | 3.3583 | 3.2001 | 3.0472 | 2.9074 | 2.2284 | 1.509 | 0.63395 | 2.8411 | 2.8047 | 2.7827 | 2.7547 | 2.7227 | 2.6881 | 2.6514 | 2.6189 | 2.5332 | 2.4409 | 2.3525 | 2.2242 | 2.0918 | 1.9588
|  | MARNOCH | ST |  |  |  | 0 | 2.6263 | 2.6159 | 2.6075 | 2.5969 | 2.5836 | 2.5694 | 2.5544 | 2.5441 | 2.5345 | 2.5251 | 2.5158 | 2.3787 | 2.1925 | 2.0369 | 4.6522 | 4.6206 | 4.5864 | 4.522 | 4.4524 | 4.3804 | 4.313 | 4.2441 | 4.1747 | 4.1088 | 4.0454 | 3.7503 | 3.4563 | 3.2015 | 2.8512 | 2.8408 | 2.8324 | 2.8218 | 2.8086 | 2.7943 | 2.7793 | 2.769 | 2.7594 | 2.75 | 2.7407 | 2.6938 | 2.5999 | 2.5052
|  | MARNOCH | FS |  |  |  | 0 | 2.6305 | 2.6239 | 2.6187 | 2.6134 | 2.6081 | 2.6027 | 2.5981 | 2.5925 | 2.5867 | 2.5808 | 2.5747 | 2.5444 | 2.4207 | 2.2676 | 4.6668 | 4.642 | 4.6175 | 4.5893 | 4.5532 | 4.5079 | 4.4645 | 4.4152 | 4.363 | 4.3116 | 4.2611 | 4.0262 | 3.813 | 3.577 | 2.8554 | 2.8488 | 2.8436 | 2.8383 | 2.833 | 2.8276 | 2.8231 | 2.8174 | 2.8116 | 2.8057 | 2.7996 | 2.7693 | 2.7179 | 2.636
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 0 | 4.3613 | 4.3538 | 4.347 | 4.3387 | 4.3284 | 4.3175 | 4.306 | 4.2967 | 4.2872 | 4.2777 | 4.2683 | 4.2085 | 4.0757 | 3.828 | 4.2043 | 4.1833 | 4.1636 | 4.1295 | 4.095 | 4.0609 | 4.0273 | 3.9948 | 3.9626 | 3.9307 | 3.8993 | 3.7324 | 3.5348 | 3.2709 | 4.2049 | 4.1843 | 4.165 | 4.1316 | 4.0978 | 4.0644 | 4.0314 | 3.9995 | 3.9679 | 3.9366 | 3.9059 | 3.8748 | 3.842 | 3.8089
|  | MARYBANK | CT |  |  |  | 0 | 4.3613 | 4.3538 | 4.347 | 4.3389 | 4.3298 | 4.3197 | 4.3091 | 4.3011 | 4.2929 | 4.2847 | 4.2765 | 4.2256 | 4.1526 | 4.05 | 4.2043 | 4.1884 | 4.1722 | 4.1469 | 4.121 | 4.0949 | 4.069 | 4.045 | 4.021 | 3.9973 | 3.9739 | 3.8489 | 3.7019 | 3.5278 | 4.2049 | 4.1893 | 4.1734 | 4.1485 | 4.1231 | 4.0975 | 4.072 | 4.0484 | 4.0249 | 4.0016 | 3.9786 | 3.9557 | 3.9315 | 3.9065
|  | MARYBANK | LW |  |  |  | 0 | 4.3672 | 4.3541 | 4.3479 | 4.3387 | 4.3284 | 4.3175 | 4.306 | 4.2967 | 4.2872 | 4.2777 | 4.2683 | 4.2085 | 4.0757 | 3.828 | 4.2079 | 4.1833 | 4.1636 | 4.1295 | 4.095 | 4.0609 | 4.0273 | 3.9948 | 3.9626 | 3.9307 | 3.8993 | 3.7324 | 3.5348 | 3.2709 | 4.2086 | 4.1843 | 4.165 | 4.1316 | 4.0978 | 4.0644 | 4.0314 | 3.9995 | 3.9679 | 3.9366 | 3.9059 | 3.8748 | 3.842 | 3.8089
|  | MARYBANK | ST |  |  |  | 0 | 4.368 | 4.3656 | 4.3641 | 4.3613 | 4.3581 | 4.3545 | 4.3506 | 4.3486 | 4.3465 | 4.3446 | 4.3427 | 4.3337 | 4.306 | 4.2897 | 4.2252 | 4.2224 | 4.2195 | 4.2052 | 4.1906 | 4.1761 | 4.1617 | 4.1486 | 4.1356 | 4.123 | 4.1107 | 4.0525 | 3.9783 | 3.9177 | 4.2254 | 4.2226 | 4.2198 | 4.2058 | 4.1915 | 4.1774 | 4.1632 | 4.1504 | 4.1378 | 4.1254 | 4.1134 | 4.0566 | 3.9837 | 3.9244
|  | MARYBANK | FS |  |  |  | 0 | 4.3688 | 4.3666 | 4.3657 | 4.3648 | 4.3639 | 4.3629 | 4.3619 | 4.3605 | 4.359 | 4.3574 | 4.3558 | 4.3495 | 4.3346 | 4.3071 | 4.227 | 4.2245 | 4.2232 | 4.2205 | 4.2161 | 4.2077 | 4.1994 | 4.1897 | 4.18 | 4.1703 | 4.1605 | 4.1143 | 4.0622 | 3.9998 | 4.2272 | 4.2247 | 4.2234 | 4.2208 | 4.2165 | 4.2083 | 4.2002 | 4.1908 | 4.1813 | 4.1718 | 4.1622 | 4.1171 | 4.0661 | 4.0047
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0.10211 | 16.0285 | 15.9619 | 15.8998 | 15.8306 | 15.7561 | 15.6767 | 15.5944 | 15.5241 | 15.4518 | 15.3785 | 15.2459 | 14.0823 | 12.7148 | 10.9153 | 14.5523 | 14.3251 | 14.1065 | 13.8023 | 13.5015 | 13.2064 | 12.9259 | 12.6423 | 12.3653 | 12.093 | 11.8334 | 10.5244 | 9.0414 | 7.1233 | 15.4259 | 15.3594 | 15.2973 | 15.0966 | 14.8104 | 14.5291 | 14.2611 | 13.9909 | 13.7268 | 13.467 | 13.2191 | 12.9767 | 12.7132 | 12.4473
|  | MARYTON | CT |  |  |  | 0.10211 | 16.0285 | 15.9619 | 15.8998 | 15.8306 | 15.7561 | 15.6767 | 15.5944 | 15.5241 | 15.4518 | 15.3785 | 15.305 | 14.7532 | 13.6744 | 12.3668 | 14.5523 | 14.3858 | 14.21 | 13.9784 | 13.7399 | 13.4993 | 13.2736 | 13.0527 | 12.834 | 12.6217 | 12.4159 | 11.3547 | 10.1651 | 8.7789 | 15.4259 | 15.3594 | 15.2973 | 15.228 | 15.0282 | 14.7976 | 14.5808 | 14.3694 | 14.1597 | 13.9561 | 13.7585 | 13.561 | 13.3548 | 13.1502
|  | MARYTON | LW |  |  |  | 0.10211 | 16.1026 | 16.0204 | 15.9752 | 15.9162 | 15.8497 | 15.7751 | 15.696 | 15.628 | 15.5585 | 15.4658 | 15.2459 | 14.0823 | 12.7148 | 10.9153 | 14.562 | 14.3251 | 14.1065 | 13.8023 | 13.5015 | 13.2064 | 12.9259 | 12.6423 | 12.3653 | 12.093 | 11.8334 | 10.5244 | 9.0414 | 7.1233 | 15.5001 | 15.4179 | 15.3727 | 15.0966 | 14.8104 | 14.5291 | 14.2611 | 13.9909 | 13.7268 | 13.467 | 13.2191 | 12.9767 | 12.7132 | 12.4473
|  | MARYTON | ST |  |  |  | 0.10211 | 16.1186 | 16.0994 | 16.085 | 16.0632 | 16.0371 | 16.0087 | 15.9783 | 15.9603 | 15.9424 | 15.9247 | 15.9073 | 15.8207 | 15.6158 | 15.4693 | 14.7419 | 14.6975 | 14.6545 | 14.5383 | 14.4158 | 14.292 | 14.1717 | 14.0543 | 13.9372 | 13.8235 | 13.7131 | 13.1945 | 12.6103 | 12.1019 | 15.5161 | 15.4969 | 15.4824 | 15.4606 | 15.4346 | 15.4061 | 15.3757 | 15.3358 | 15.2248 | 15.1171 | 15.0125 | 14.5207 | 13.9602 | 13.4744
|  | MARYTON | FS |  |  |  | 0.10211 | 16.1262 | 16.1125 | 16.1045 | 16.0965 | 16.0882 | 16.0797 | 16.0712 | 16.0607 | 16.0498 | 16.0385 | 16.0267 | 15.973 | 15.864 | 15.6741 | 14.7627 | 14.7282 | 14.6979 | 14.6624 | 14.61 | 14.534 | 14.4592 | 14.3736 | 14.2849 | 14.1977 | 14.1102 | 13.6986 | 13.279 | 12.7903 | 15.5236 | 15.5099 | 15.502 | 15.4939 | 15.4857 | 15.4771 | 15.4686 | 15.4582 | 15.4472 | 15.4359 | 15.3923 | 15.0029 | 14.6027 | 14.1326
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0.12105 | 6.6175 | 6.5814 | 6.5468 | 6.5101 | 6.4707 | 6.4299 | 6.3879 | 6.2992 | 6.186 | 6.0768 | 5.9743 | 5.4611 | 4.8841 | 4.1367 | 6.0969 | 5.9731 | 5.8517 | 5.6946 | 5.5412 | 5.3935 | 5.256 | 5.116 | 4.9804 | 4.85 | 4.7283 | 4.1297 | 3.4755 | 2.6561 | 6.9019 | 6.8624 | 6.8239 | 6.7803 | 6.6268 | 6.4791 | 6.3416 | 6.2015 | 6.0659 | 5.9355 | 5.8138 | 5.698 | 5.578 | 5.4576
|  | MAUD | CT |  |  |  | 0.12105 | 6.6175 | 6.5814 | 6.5468 | 6.5101 | 6.4707 | 6.4299 | 6.3879 | 6.3503 | 6.3116 | 6.2486 | 6.1622 | 5.7152 | 5.2246 | 4.6518 | 6.0969 | 6.0055 | 5.9071 | 5.787 | 5.6627 | 5.5371 | 5.4229 | 5.3114 | 5.2012 | 5.097 | 4.9972 | 4.4882 | 3.9441 | 3.3205 | 6.9019 | 6.8624 | 6.8239 | 6.7822 | 6.7377 | 6.6228 | 6.5086 | 6.3971 | 6.2868 | 6.1827 | 6.0828 | 5.9822 | 5.8798 | 5.7781
|  | MAUD | LW |  |  |  | 0.12105 | 6.6622 | 6.6247 | 6.6022 | 6.5736 | 6.5417 | 6.5062 | 6.4157 | 6.2992 | 6.186 | 6.0768 | 5.9743 | 5.4611 | 4.8841 | 4.1367 | 6.1005 | 5.9731 | 5.8517 | 5.6946 | 5.5412 | 5.3935 | 5.256 | 5.116 | 4.9804 | 4.85 | 4.7283 | 4.1297 | 3.4755 | 2.6561 | 6.944 | 6.9011 | 6.8726 | 6.7803 | 6.6268 | 6.4791 | 6.3416 | 6.2015 | 6.0659 | 5.9355 | 5.8138 | 5.698 | 5.578 | 5.4576
|  | MAUD | ST |  |  |  | 0.12105 | 6.6714 | 6.661 | 6.6533 | 6.6427 | 6.6293 | 6.615 | 6.6007 | 6.5911 | 6.5815 | 6.5721 | 6.5627 | 6.5156 | 6.3388 | 6.1493 | 6.1975 | 6.1713 | 6.1453 | 6.0886 | 6.0277 | 5.9654 | 5.9066 | 5.8491 | 5.7913 | 5.7352 | 5.6816 | 5.4321 | 5.1709 | 4.9478 | 6.9586 | 6.9472 | 6.9384 | 6.925 | 6.9088 | 6.8915 | 6.8745 | 6.8621 | 6.8496 | 6.8209 | 6.7673 | 6.5178 | 6.2565 | 6.0334
|  | MAUD | FS |  |  |  | 0.12105 | 6.6756 | 6.6689 | 6.6637 | 6.6585 | 6.6532 | 6.6486 | 6.644 | 6.6384 | 6.6326 | 6.6266 | 6.6204 | 6.5909 | 6.5391 | 6.4248 | 6.2101 | 6.1898 | 6.17 | 6.1472 | 6.1182 | 6.0799 | 6.0425 | 6 | 5.9565 | 5.9129 | 5.8701 | 5.6695 | 5.4812 | 5.2711 | 6.9633 | 6.9557 | 6.9497 | 6.9434 | 6.9366 | 6.93 | 6.9235 | 6.9156 | 6.9075 | 6.8992 | 6.8909 | 6.7552 | 6.5668 | 6.3568
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.16842 | 1.2533 | 1.2279 | 1.2029 | 1.178 | 1.1524 | 1.1262 | 1.1005 | 1.0748 | 1.0481 | 1.0214 | 0.99467 | 0.84219 | 0.62276 | 0.35998 | 1.2406 | 1.2153 | 1.1903 | 1.1654 | 1.1398 | 1.1135 | 1.0879 | 1.0621 | 1.0354 | 1.0087 | 0.98203 | 0.7968 | 0.55271 | 0.26983 | 1.2385 | 1.2132 | 1.1882 | 1.1633 | 1.1377 | 1.1088 | 1.0722 | 1.0352 | 0.99738 | 0.95974 | 0.92224 | 0.88397 | 0.84409 | 0.80329
|  | MELVICH | CT |  |  |  | 0.16842 | 1.2533 | 1.2279 | 1.2029 | 1.178 | 1.1524 | 1.1262 | 1.1005 | 1.0748 | 1.0481 | 1.0214 | 0.99467 | 0.84219 | 0.62276 | 0.35998 | 1.2406 | 1.2153 | 1.1903 | 1.1654 | 1.1398 | 1.1135 | 1.0879 | 1.0621 | 1.0354 | 1.0087 | 0.98203 | 0.7968 | 0.55271 | 0.26983 | 1.2385 | 1.2132 | 1.1882 | 1.1633 | 1.1377 | 1.1088 | 1.0722 | 1.0352 | 0.99738 | 0.95974 | 0.92224 | 0.88397 | 0.84409 | 0.80329
|  | MELVICH | LW |  |  |  | 0.16842 | 1.2928 | 1.2782 | 1.2672 | 1.253 | 1.2374 | 1.2205 | 1.2024 | 1.1848 | 1.1672 | 1.1486 | 1.1293 | 0.97537 | 0.76305 | 0.47965 | 1.2802 | 1.2656 | 1.2545 | 1.2404 | 1.2248 | 1.2078 | 1.1897 | 1.1721 | 1.1545 | 1.1248 | 1.0895 | 0.89804 | 0.6626 | 0.36219 | 1.2781 | 1.2635 | 1.2524 | 1.2383 | 1.214 | 1.1807 | 1.1468 | 1.1128 | 1.079 | 1.0446 | 1.0097 | 0.97504 | 0.9385 | 0.9001
|  | MELVICH | ST |  |  |  | 0.16842 | 1.3004 | 1.2936 | 1.288 | 1.2817 | 1.2735 | 1.265 | 1.2571 | 1.2504 | 1.2438 | 1.2372 | 1.2306 | 1.1964 | 1.1484 | 1.1036 | 1.2878 | 1.2809 | 1.2754 | 1.2691 | 1.2608 | 1.2523 | 1.2444 | 1.2378 | 1.2312 | 1.2246 | 1.218 | 1.1837 | 1.1358 | 1.058 | 1.2857 | 1.2788 | 1.2733 | 1.267 | 1.2587 | 1.2502 | 1.2423 | 1.2357 | 1.2291 | 1.2211 | 1.2071 | 1.1374 | 1.0556 | 0.97838
|  | MELVICH | FS |  |  |  | 0.16842 | 1.3055 | 1.3021 | 1.2978 | 1.2936 | 1.2893 | 1.285 | 1.2807 | 1.2761 | 1.2715 | 1.2677 | 1.2638 | 1.2406 | 1.2127 | 1.1767 | 1.2928 | 1.2895 | 1.2852 | 1.2809 | 1.2767 | 1.2724 | 1.2681 | 1.2635 | 1.2588 | 1.255 | 1.2512 | 1.2279 | 1.2 | 1.1641 | 1.2907 | 1.2873 | 1.2831 | 1.2788 | 1.2746 | 1.2703 | 1.266 | 1.2614 | 1.2567 | 1.2529 | 1.249 | 1.2159 | 1.1618 | 1.1009
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 0.13895 | 23.4988 | 23.4217 | 23.3866 | 23.337 | 23.2808 | 23.2189 | 23.1534 | 23.1015 | 23.0485 | 22.9943 | 22.9409 | 22.4516 | 21.3342 | 19.6876 | 21.6211 | 21.544 | 21.509 | 21.4594 | 21.4032 | 21.3412 | 21.2757 | 21.2238 | 21.1708 | 21.1167 | 21.0632 | 20.2671 | 19.046 | 17.3003 | 22.4432 | 22.3661 | 22.3311 | 22.2815 | 22.2253 | 22.1633 | 22.0978 | 22.046 | 21.9929 | 21.9388 | 21.8854 | 21.8322 | 21.7438 | 21.5476
|  | MENZIESHILL | CT |  |  |  | 0.13895 | 23.4988 | 23.4715 | 23.4483 | 23.4171 | 23.3791 | 23.3343 | 23.286 | 23.254 | 23.2205 | 23.1865 | 23.1522 | 22.922 | 22.4595 | 21.4646 | 21.6211 | 21.5938 | 21.5706 | 21.5394 | 21.5014 | 21.4566 | 21.4083 | 21.3763 | 21.3428 | 21.3089 | 21.2745 | 21.0443 | 20.2882 | 19.2165 | 22.4432 | 22.4159 | 22.3927 | 22.3615 | 22.3235 | 22.2787 | 22.2304 | 22.1984 | 22.1649 | 22.131 | 22.0966 | 22.0607 | 22.0149 | 21.9678
|  | MENZIESHILL | LW |  |  |  | 0.13895 | 23.5005 | 23.4217 | 23.3866 | 23.337 | 23.2808 | 23.2189 | 23.1534 | 23.1015 | 23.0485 | 22.9943 | 22.9409 | 22.4516 | 21.3342 | 19.6876 | 21.6228 | 21.544 | 21.509 | 21.4594 | 21.4032 | 21.3412 | 21.2757 | 21.2238 | 21.1708 | 21.1167 | 21.0632 | 20.2671 | 19.046 | 17.3003 | 22.4449 | 22.3661 | 22.3311 | 22.2815 | 22.2253 | 22.1633 | 22.0978 | 22.046 | 21.9929 | 21.9388 | 21.8854 | 21.8322 | 21.7438 | 21.5476
|  | MENZIESHILL | ST |  |  |  | 0.13895 | 23.5005 | 23.4898 | 23.4847 | 23.4709 | 23.4542 | 23.4345 | 23.4126 | 23.4044 | 23.3962 | 23.3883 | 23.3807 | 23.3457 | 23.1635 | 23.0682 | 21.6228 | 21.6121 | 21.607 | 21.5932 | 21.5765 | 21.5569 | 21.535 | 21.5268 | 21.5185 | 21.5106 | 21.503 | 21.468 | 21.2858 | 21.1905 | 22.4449 | 22.4342 | 22.4291 | 22.4153 | 22.3986 | 22.379 | 22.3571 | 22.3489 | 22.3406 | 22.3327 | 22.3252 | 22.2901 | 22.1079 | 22.0127
|  | MENZIESHILL | FS |  |  |  | 0.13895 | 23.5013 | 23.4904 | 23.4899 | 23.4893 | 23.4884 | 23.4872 | 23.486 | 23.4813 | 23.476 | 23.4702 | 23.4639 | 23.4471 | 23.3584 | 23.1629 | 21.6236 | 21.6127 | 21.6122 | 21.6116 | 21.6108 | 21.6095 | 21.6083 | 21.6037 | 21.5984 | 21.5925 | 21.5862 | 21.5694 | 21.4808 | 21.2852 | 22.4457 | 22.4348 | 22.4343 | 22.4337 | 22.4329 | 22.4317 | 22.4305 | 22.4258 | 22.4205 | 22.4147 | 22.4083 | 22.3915 | 22.3029 | 22.1073
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.13368 | 2.145 | 3.4205 | 3.3972 | 3.3726 | 3.3463 | 3.3185 | 3.2898 | 3.2645 | 3.2121 | 3.145 | 3.0802 | 2.7525 | 2.3739 | 1.8806 | 1.9062 | 3.1503 | 3.0861 | 2.9986 | 2.9115 | 2.827 | 2.746 | 2.6661 | 2.5876 | 2.5115 | 2.4382 | 2.0722 | 1.6579 | 1.1307 | 1.9677 | 3.2191 | 3.1633 | 3.0856 | 3.0079 | 2.9321 | 2.8591 | 2.7874 | 2.7169 | 2.6484 | 2.5822 | 2.519 | 2.4524 | 2.3852
|  | METHLICK | CT |  |  |  | 0.13368 | 2.145 | 3.4205 | 3.3972 | 3.3726 | 3.3463 | 3.3185 | 3.2898 | 3.2645 | 3.2389 | 3.2125 | 3.1711 | 2.883 | 2.558 | 2.1788 | 1.9062 | 3.1537 | 3.098 | 3.0284 | 2.9569 | 2.8843 | 2.8165 | 2.7509 | 2.6864 | 2.6234 | 2.5617 | 2.2456 | 1.8955 | 1.4924 | 1.9677 | 3.2191 | 3.1681 | 3.1049 | 3.0399 | 2.9737 | 2.9115 | 2.8517 | 2.7928 | 2.735 | 2.6783 | 2.6225 | 2.564 | 2.5052
|  | METHLICK | LW |  |  |  | 0.13368 | 2.1753 | 3.4501 | 3.4352 | 3.416 | 3.3942 | 3.3704 | 3.345 | 3.2811 | 3.2121 | 3.145 | 3.0802 | 2.7525 | 2.3739 | 1.8806 | 1.9191 | 3.1503 | 3.0861 | 2.9986 | 2.9115 | 2.827 | 2.746 | 2.6661 | 2.5876 | 2.5115 | 2.4382 | 2.0722 | 1.6579 | 1.1307 | 1.983 | 3.2205 | 3.1633 | 3.0856 | 3.0079 | 2.9321 | 2.8591 | 2.7874 | 2.7169 | 2.6484 | 2.5822 | 2.519 | 2.4524 | 2.3852
|  | METHLICK | ST |  |  |  | 0.13368 | 2.1812 | 3.4745 | 3.4691 | 3.4617 | 3.4528 | 3.4432 | 3.4331 | 3.4262 | 3.4192 | 3.4132 | 3.4073 | 3.3759 | 3.2784 | 3.1553 | 1.9697 | 3.2559 | 3.2425 | 3.2089 | 3.1731 | 3.1366 | 3.102 | 3.0685 | 3.0345 | 3.0028 | 2.9716 | 2.8251 | 2.6648 | 2.5263 | 2.0272 | 3.3144 | 3.3022 | 3.2723 | 3.2404 | 3.2077 | 3.1767 | 3.147 | 3.1169 | 3.0888 | 3.0612 | 2.9312 | 2.7849 | 2.6594
|  | METHLICK | FS |  |  |  | 0.13368 | 2.1845 | 3.4798 | 3.4763 | 3.4728 | 3.4693 | 3.4657 | 3.4621 | 3.4578 | 3.4542 | 3.4505 | 3.4467 | 3.4273 | 3.393 | 3.3348 | 1.9791 | 3.2684 | 3.2578 | 3.2466 | 3.2306 | 3.2088 | 3.1878 | 3.1629 | 3.1379 | 3.1136 | 3.0894 | 2.9718 | 2.8561 | 2.7276 | 2.0357 | 3.3259 | 3.3164 | 3.3062 | 3.292 | 3.2728 | 3.2543 | 3.2324 | 3.2104 | 3.1891 | 3.1678 | 3.0642 | 2.9602 | 2.8423
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0 | 1.3464 | 1.34 | 1.3371 | 1.3331 | 1.3286 | 1.3236 | 1.3184 | 1.3143 | 1.3102 | 1.306 | 1.3018 | 1.2579 | 1.1731 | 1.0517 | 1.1807 | 1.1743 | 1.1714 | 1.1674 | 1.1629 | 1.158 | 1.1528 | 1.1487 | 1.1445 | 1.1403 | 1.1334 | 1.0608 | 0.97158 | 0.84573 | 1.2395 | 1.233 | 1.2302 | 1.2209 | 1.2068 | 1.1928 | 1.1789 | 1.1649 | 1.151 | 1.1371 | 1.1235 | 1.1101 | 1.0957 | 1.081
|  | MID YELL | CT |  |  |  | 0 | 1.3464 | 1.3441 | 1.3422 | 1.3397 | 1.3365 | 1.3328 | 1.3288 | 1.3262 | 1.3235 | 1.3208 | 1.3181 | 1.3002 | 1.2634 | 1.1906 | 1.1807 | 1.1785 | 1.1766 | 1.174 | 1.1708 | 1.1671 | 1.1631 | 1.1605 | 1.1578 | 1.1551 | 1.1524 | 1.1282 | 1.0674 | 0.9917 | 1.2395 | 1.2372 | 1.2353 | 1.2327 | 1.2244 | 1.2142 | 1.2039 | 1.1946 | 1.1854 | 1.1763 | 1.1673 | 1.1582 | 1.1484 | 1.1385
|  | MID YELL | LW |  |  |  | 0 | 1.3464 | 1.34 | 1.3371 | 1.3331 | 1.3286 | 1.3236 | 1.3184 | 1.3143 | 1.3102 | 1.306 | 1.3018 | 1.2579 | 1.1731 | 1.0517 | 1.1807 | 1.1743 | 1.1714 | 1.1674 | 1.1629 | 1.158 | 1.1528 | 1.1487 | 1.1445 | 1.1403 | 1.1334 | 1.0608 | 0.97158 | 0.84573 | 1.2395 | 1.233 | 1.2302 | 1.2209 | 1.2068 | 1.1928 | 1.1789 | 1.1649 | 1.151 | 1.1371 | 1.1235 | 1.1101 | 1.0957 | 1.081
|  | MID YELL | ST |  |  |  | 0 | 1.3464 | 1.3455 | 1.3451 | 1.344 | 1.3427 | 1.3411 | 1.3394 | 1.3387 | 1.3381 | 1.3374 | 1.3368 | 1.3341 | 1.3204 | 1.3134 | 1.1807 | 1.1799 | 1.1794 | 1.1783 | 1.177 | 1.1754 | 1.1737 | 1.173 | 1.1724 | 1.1717 | 1.1711 | 1.1684 | 1.1547 | 1.1394 | 1.2395 | 1.2386 | 1.2382 | 1.2371 | 1.2358 | 1.2342 | 1.2325 | 1.2291 | 1.2238 | 1.2186 | 1.2136 | 1.1898 | 1.156 | 1.1296
|  | MID YELL | FS |  |  |  | 0 | 1.3464 | 1.3456 | 1.3456 | 1.3455 | 1.3454 | 1.3454 | 1.3453 | 1.3449 | 1.3445 | 1.3441 | 1.3436 | 1.3424 | 1.3359 | 1.3219 | 1.1807 | 1.1799 | 1.1799 | 1.1798 | 1.1798 | 1.1797 | 1.1796 | 1.1792 | 1.1788 | 1.1784 | 1.178 | 1.1767 | 1.1703 | 1.1562 | 1.2395 | 1.2387 | 1.2386 | 1.2386 | 1.2385 | 1.2384 | 1.2384 | 1.238 | 1.2376 | 1.2372 | 1.2352 | 1.215 | 1.1906 | 1.1596
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.096842 | 5.5678 | 5.5361 | 5.5057 | 5.4735 | 5.439 | 5.4024 | 5.2989 | 5.1911 | 5.0875 | 4.9863 | 4.8919 | 4.4234 | 3.903 | 3.2322 | 5.4268 | 5.3744 | 5.2623 | 5.1166 | 4.9755 | 4.84 | 4.7137 | 4.5855 | 4.4624 | 4.3428 | 4.2318 | 3.6896 | 3.1036 | 2.3718 | 5.2579 | 5.2262 | 5.1958 | 5.1636 | 5.1291 | 5.0925 | 5.0548 | 4.9387 | 4.8218 | 4.7054 | 4.5973 | 4.4955 | 4.3892 | 4.2824
|  | MIDMAR | CT |  |  |  | 0.096842 | 5.5678 | 5.5361 | 5.5057 | 5.4735 | 5.439 | 5.4024 | 5.3648 | 5.3256 | 5.2387 | 5.1566 | 5.0778 | 4.6717 | 4.2288 | 3.7174 | 5.4268 | 5.3926 | 5.3189 | 5.2086 | 5.0952 | 4.9797 | 4.8755 | 4.7745 | 4.6738 | 4.5791 | 4.4886 | 4.0289 | 3.5397 | 2.9854 | 5.2579 | 5.2262 | 5.1958 | 5.1636 | 5.1291 | 5.0925 | 5.0548 | 5.0181 | 4.9802 | 4.9213 | 4.8354 | 4.7488 | 4.6605 | 4.5726
|  | MIDMAR | LW |  |  |  | 0.096842 | 5.6074 | 5.5739 | 5.5544 | 5.5286 | 5.4997 | 5.4059 | 5.2989 | 5.1911 | 5.0875 | 4.9863 | 4.8919 | 4.4234 | 3.903 | 3.2322 | 5.4646 | 5.3744 | 5.2623 | 5.1166 | 4.9755 | 4.84 | 4.7137 | 4.5855 | 4.4624 | 4.3428 | 4.2318 | 3.6896 | 3.1036 | 2.3718 | 5.2975 | 5.264 | 5.2445 | 5.2187 | 5.1879 | 5.1506 | 5.059 | 4.9387 | 4.8218 | 4.7054 | 4.5973 | 4.4955 | 4.3892 | 4.2824
|  | MIDMAR | ST |  |  |  | 0.096842 | 5.615 | 5.6058 | 5.5991 | 5.5898 | 5.5779 | 5.5651 | 5.5525 | 5.544 | 5.5356 | 5.5273 | 5.519 | 5.4433 | 5.2396 | 5.0656 | 5.4761 | 5.4662 | 5.4587 | 5.4474 | 5.4276 | 5.3707 | 5.3174 | 5.265 | 5.2122 | 5.161 | 5.1124 | 4.8848 | 4.6499 | 4.4469 | 5.3051 | 5.2959 | 5.2892 | 5.2799 | 5.268 | 5.2552 | 5.2425 | 5.2341 | 5.2257 | 5.2173 | 5.2091 | 5.1617 | 4.9969 | 4.8052
|  | MIDMAR | FS |  |  |  | 0.096842 | 5.62 | 5.6145 | 5.6102 | 5.6058 | 5.6013 | 5.5968 | 5.5923 | 5.5868 | 5.5811 | 5.5761 | 5.571 | 5.5437 | 5.4754 | 5.3109 | 5.4815 | 5.4754 | 5.4704 | 5.4652 | 5.4597 | 5.4537 | 5.4416 | 5.4018 | 5.36 | 5.3198 | 5.2805 | 5.0923 | 4.9197 | 4.7311 | 5.3101 | 5.3046 | 5.3002 | 5.2959 | 5.2914 | 5.2869 | 5.2823 | 5.2768 | 5.2712 | 5.2662 | 5.2611 | 5.2338 | 5.184 | 5.0742
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 0.0052632 | 14.5974 | 14.5591 | 14.5371 | 14.5062 | 14.4715 | 14.4332 | 14.3918 | 14.3584 | 14.324 | 14.289 | 14.2542 | 13.5471 | 12.57 | 11.2423 | 13.3489 | 13.3037 | 13.2756 | 13.235 | 13.1908 | 13.1072 | 12.9144 | 12.7183 | 12.5238 | 12.331 | 12.1427 | 11.1686 | 10.0427 | 8.582 | 13.7361 | 13.6978 | 13.6758 | 13.6449 | 13.6102 | 13.5719 | 13.5305 | 13.4971 | 13.4627 | 13.4276 | 13.3929 | 13.2752 | 13.0869 | 12.8983
|  | MILL RD | CT |  |  |  | 0.0052632 | 14.5974 | 14.5759 | 14.5568 | 14.533 | 14.5051 | 14.4731 | 14.4388 | 14.4143 | 14.3886 | 14.3627 | 14.3364 | 14.1645 | 13.5337 | 12.6828 | 13.3489 | 13.3238 | 13.3006 | 13.2702 | 13.2357 | 13.1972 | 13.1568 | 13.1086 | 12.97 | 12.8342 | 12.7003 | 11.9967 | 11.1858 | 10.2304 | 13.7361 | 13.7146 | 13.6955 | 13.6717 | 13.6438 | 13.6118 | 13.5775 | 13.553 | 13.5273 | 13.5014 | 13.4751 | 13.4478 | 13.4134 | 13.378
|  | MILL RD | LW |  |  |  | 0.0052632 | 14.6067 | 14.5591 | 14.5371 | 14.5062 | 14.4715 | 14.4332 | 14.3918 | 14.3584 | 14.324 | 14.289 | 14.2542 | 13.5471 | 12.57 | 11.2423 | 13.3564 | 13.3037 | 13.2756 | 13.235 | 13.1908 | 13.1072 | 12.9144 | 12.7183 | 12.5238 | 12.331 | 12.1427 | 11.1686 | 10.0427 | 8.582 | 13.7454 | 13.6978 | 13.6758 | 13.6449 | 13.6102 | 13.5719 | 13.5305 | 13.4971 | 13.4627 | 13.4276 | 13.3929 | 13.2752 | 13.0869 | 12.8983
|  | MILL RD | ST |  |  |  | 0.0052632 | 14.6092 | 14.6009 | 14.5961 | 14.5859 | 14.574 | 14.5602 | 14.5451 | 14.5383 | 14.5316 | 14.525 | 14.5187 | 14.4885 | 14.3644 | 14.2951 | 13.3652 | 13.3562 | 13.3505 | 13.3362 | 13.3201 | 13.3022 | 13.283 | 13.2719 | 13.2608 | 13.25 | 13.2394 | 12.9852 | 12.5177 | 12.1054 | 13.7479 | 13.7396 | 13.7348 | 13.7246 | 13.7127 | 13.6989 | 13.6838 | 13.677 | 13.6703 | 13.6637 | 13.6574 | 13.6272 | 13.5031 | 13.4186
|  | MILL RD | FS |  |  |  | 0.0052632 | 14.61 | 14.6021 | 14.601 | 14.5998 | 14.5984 | 14.5967 | 14.5951 | 14.5913 | 14.587 | 14.5824 | 14.5775 | 14.5624 | 14.5007 | 14.3687 | 13.3662 | 13.3577 | 13.3558 | 13.3537 | 13.3506 | 13.346 | 13.3414 | 13.3342 | 13.3265 | 13.3184 | 13.3101 | 13.2784 | 13.0006 | 12.6005 | 13.7487 | 13.7408 | 13.7397 | 13.7384 | 13.737 | 13.7354 | 13.7338 | 13.7299 | 13.7257 | 13.7211 | 13.7162 | 13.7011 | 13.6393 | 13.5074
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 0.38632 | 18.592 | 18.5124 | 18.4393 | 18.3559 | 18.2631 | 18.1626 | 18.0578 | 17.9728 | 17.8856 | 17.7983 | 17.7097 | 17.1008 | 15.5213 | 13.3126 | 16.8431 | 16.7635 | 16.6904 | 16.6071 | 16.5142 | 16.3529 | 16.0618 | 15.778 | 15.4948 | 15.2132 | 14.9355 | 13.4657 | 11.6993 | 9.3072 | 17.2822 | 17.1986 | 17.121 | 17.0295 | 16.9288 | 16.8208 | 16.7088 | 16.6163 | 16.517 | 16.4109 | 16.3055 | 16.1407 | 15.8608 | 15.5768
|  | MILNATHORT | CT |  |  |  | 0.38632 | 18.592 | 18.5124 | 18.4393 | 18.3559 | 18.2631 | 18.1626 | 18.0578 | 17.9728 | 17.8856 | 17.7983 | 17.7097 | 17.1795 | 16.4338 | 15.0275 | 16.8431 | 16.7635 | 16.6904 | 16.6071 | 16.5142 | 16.4137 | 16.3089 | 16.1259 | 15.906 | 15.6883 | 15.4719 | 14.3183 | 12.9452 | 11.3036 | 17.2822 | 17.1986 | 17.121 | 17.0295 | 16.9288 | 16.8208 | 16.7088 | 16.6163 | 16.5216 | 16.4269 | 16.3311 | 16.2338 | 16.1227 | 16.0081
|  | MILNATHORT | LW |  |  |  | 0.38632 | 18.6653 | 18.5441 | 18.4816 | 18.3977 | 18.3029 | 18.1997 | 18.0904 | 17.9992 | 17.9054 | 17.8098 | 17.7147 | 17.1008 | 15.5213 | 13.3126 | 16.9164 | 16.7953 | 16.7328 | 16.6488 | 16.5541 | 16.3529 | 16.0618 | 15.778 | 15.4948 | 15.2132 | 14.9355 | 13.4657 | 11.6993 | 9.3072 | 17.3541 | 17.2277 | 17.1588 | 17.0632 | 16.9571 | 16.8432 | 16.7236 | 16.6215 | 16.517 | 16.4109 | 16.3055 | 16.1407 | 15.8608 | 15.5768
|  | MILNATHORT | ST |  |  |  | 0.38632 | 18.6804 | 18.6567 | 18.64 | 18.6123 | 18.5783 | 18.5415 | 18.5017 | 18.4795 | 18.458 | 18.4369 | 18.4163 | 18.3146 | 18.0389 | 17.8585 | 16.9316 | 16.9078 | 16.8912 | 16.8635 | 16.8295 | 16.7926 | 16.7529 | 16.7306 | 16.7091 | 16.6881 | 16.6675 | 16.2715 | 15.6191 | 15.0792 | 17.3767 | 17.3526 | 17.3356 | 17.3026 | 17.2633 | 17.2215 | 17.1769 | 17.1495 | 17.1229 | 17.0969 | 17.0715 | 16.947 | 16.65 | 16.4493
|  | MILNATHORT | FS |  |  |  | 0.38632 | 18.688 | 18.6703 | 18.6622 | 18.6539 | 18.6453 | 18.6363 | 18.6274 | 18.6144 | 18.6015 | 18.5881 | 18.574 | 18.5134 | 18.3726 | 18.1165 | 16.9391 | 16.9214 | 16.9133 | 16.905 | 16.8965 | 16.8875 | 16.8785 | 16.8655 | 16.8527 | 16.8392 | 16.8252 | 16.7645 | 16.3468 | 15.7908 | 17.3847 | 17.3668 | 17.3583 | 17.3495 | 17.3392 | 17.3268 | 17.3144 | 17.2973 | 17.2805 | 17.263 | 17.245 | 17.1648 | 17.0059 | 16.7329
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 0 | 12.3605 | 12.3146 | 12.2935 | 12.2641 | 12.2307 | 12.1936 | 12.1542 | 12.1231 | 12.091 | 12.0574 | 12.0241 | 11.8114 | 11.4662 | 10.7932 | 11.3829 | 11.3371 | 11.3159 | 11.2865 | 11.2531 | 11.216 | 11.1767 | 11.1455 | 11.1135 | 11.0798 | 11.0465 | 10.8339 | 10.4887 | 9.8157 | 11.2649 | 11.219 | 11.1979 | 11.1685 | 11.1351 | 11.098 | 11.0586 | 11.0275 | 10.9954 | 10.9618 | 10.9285 | 10.8952 | 10.8529 | 10.8088
|  | MILTON OF CRAIGIE | CT |  |  |  | 0 | 12.3605 | 12.3434 | 12.3289 | 12.3095 | 12.2859 | 12.2579 | 12.2277 | 12.2076 | 12.1863 | 12.1648 | 12.1429 | 11.996 | 11.751 | 11.3665 | 11.3829 | 11.3659 | 11.3513 | 11.3319 | 11.3083 | 11.2804 | 11.2502 | 11.23 | 11.2088 | 11.1872 | 11.1653 | 11.0185 | 10.7735 | 10.389 | 11.2649 | 11.2479 | 11.2333 | 11.2139 | 11.1903 | 11.1624 | 11.1322 | 11.112 | 11.0907 | 11.0692 | 11.0473 | 11.0243 | 10.9949 | 10.9645
|  | MILTON OF CRAIGIE | LW |  |  |  | 0 | 12.3621 | 12.3146 | 12.2935 | 12.2641 | 12.2307 | 12.1936 | 12.1542 | 12.1231 | 12.091 | 12.0574 | 12.0241 | 11.8114 | 11.4662 | 10.7932 | 11.3846 | 11.3371 | 11.3159 | 11.2865 | 11.2531 | 11.216 | 11.1767 | 11.1455 | 11.1135 | 11.0798 | 11.0465 | 10.8339 | 10.4887 | 9.8157 | 11.2666 | 11.219 | 11.1979 | 11.1685 | 11.1351 | 11.098 | 11.0586 | 11.0275 | 10.9954 | 10.9618 | 10.9285 | 10.8952 | 10.8529 | 10.8088
|  | MILTON OF CRAIGIE | ST |  |  |  | 0 | 12.363 | 12.3562 | 12.353 | 12.3442 | 12.3336 | 12.3211 | 12.3072 | 12.302 | 12.2968 | 12.2918 | 12.287 | 12.2645 | 12.1455 | 12.083 | 11.3854 | 11.3787 | 11.3754 | 11.3667 | 11.356 | 11.3436 | 11.3297 | 11.3245 | 11.3192 | 11.3142 | 11.3094 | 11.287 | 11.168 | 11.1054 | 11.2674 | 11.2606 | 11.2574 | 11.2486 | 11.238 | 11.2256 | 11.2117 | 11.2065 | 11.2012 | 11.1962 | 11.1914 | 11.169 | 11.05 | 10.9874
|  | MILTON OF CRAIGIE | FS |  |  |  | 0 | 12.363 | 12.3558 | 12.3555 | 12.3551 | 12.3546 | 12.3538 | 12.353 | 12.3499 | 12.3465 | 12.3427 | 12.3385 | 12.3275 | 12.2691 | 12.1393 | 11.3854 | 11.3783 | 11.378 | 11.3776 | 11.377 | 11.3762 | 11.3754 | 11.3724 | 11.3689 | 11.3651 | 11.361 | 11.35 | 11.2915 | 11.1618 | 11.2674 | 11.2603 | 11.2599 | 11.2596 | 11.259 | 11.2582 | 11.2574 | 11.2544 | 11.2509 | 11.2471 | 11.243 | 11.232 | 11.1735 | 11.0438
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 0.33474 | 15.4283 | 15.1284 | 14.8434 | 14.5012 | 14.1742 | 13.8664 | 13.5914 | 13.311 | 13.0456 | 12.7939 | 12.5712 | 11.5473 | 10.523 | 9.2573 | 14.2192 | 13.8721 | 13.537 | 13.1355 | 12.7532 | 12.3945 | 12.0756 | 11.7484 | 11.4394 | 11.1468 | 10.8888 | 9.715 | 8.5661 | 7.1879 | 14.8393 | 14.8032 | 14.6934 | 14.3571 | 14.0355 | 13.7328 | 13.4622 | 13.1865 | 12.9045 | 12.5971 | 12.3263 | 12.081 | 11.8319 | 11.5851
|  | MINTLAW | CT |  |  |  | 0.33474 | 15.5229 | 15.3501 | 15.1615 | 14.9372 | 14.7012 | 14.459 | 14.2532 | 14.0537 | 13.8593 | 13.6815 | 13.5172 | 12.7279 | 11.9639 | 11.1053 | 14.3365 | 14.136 | 13.9161 | 13.6546 | 13.3799 | 13.0986 | 12.861 | 12.6292 | 12.4037 | 12.1979 | 12.0084 | 11.1068 | 10.2537 | 9.3131 | 14.8393 | 14.8085 | 14.7806 | 14.7471 | 14.5526 | 14.3144 | 14.1116 | 13.9154 | 13.7242 | 13.5491 | 13.3873 | 13.2257 | 13.0642 | 12.9102
|  | MINTLAW | LW |  |  |  | 0.33474 | 15.4283 | 15.1284 | 14.8434 | 14.5012 | 14.1742 | 13.8664 | 13.5914 | 13.311 | 13.0456 | 12.7939 | 12.5712 | 11.5473 | 10.523 | 9.2573 | 14.2192 | 13.8721 | 13.537 | 13.1355 | 12.7532 | 12.3945 | 12.0756 | 11.7484 | 11.4394 | 11.1468 | 10.8888 | 9.715 | 8.5661 | 7.1879 | 14.8612 | 14.8032 | 14.6934 | 14.3571 | 14.0355 | 13.7328 | 13.4622 | 13.1865 | 12.9045 | 12.5971 | 12.3263 | 12.081 | 11.8319 | 11.5851
|  | MINTLAW | ST |  |  |  | 0.33474 | 15.6477 | 15.5892 | 15.5258 | 15.4175 | 15.3015 | 15.1806 | 15.0688 | 14.9553 | 14.8391 | 14.7289 | 14.6241 | 14.1507 | 13.7022 | 13.3283 | 14.4806 | 14.4126 | 14.3381 | 14.2111 | 14.0752 | 13.9337 | 13.8034 | 13.6694 | 13.5321 | 13.4021 | 13.2784 | 12.7201 | 12.2077 | 11.7752 | 14.8654 | 14.8553 | 14.8488 | 14.8368 | 14.823 | 14.8073 | 14.7903 | 14.7818 | 14.689 | 14.5809 | 14.478 | 14.013 | 13.5709 | 13.2028
|  | MINTLAW | FS |  |  |  | 0.33474 | 15.6712 | 15.6233 | 15.5773 | 15.5247 | 15.4596 | 15.3827 | 15.308 | 15.2226 | 15.132 | 15.0433 | 14.9575 | 14.5663 | 14.2314 | 13.8624 | 14.5082 | 14.4525 | 14.398 | 14.3357 | 14.2585 | 14.1672 | 14.0785 | 13.9775 | 13.8703 | 13.7654 | 13.6638 | 13.2004 | 12.8119 | 12.3935 | 14.8679 | 14.8602 | 14.8574 | 14.8546 | 14.8516 | 14.8484 | 14.8452 | 14.8401 | 14.8347 | 14.829 | 14.8061 | 14.4222 | 14.0926 | 13.7285
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 0.10632 | 17.3725 | 17.321 | 17.2934 | 17.2556 | 17.213 | 17.1663 | 17.1171 | 17.0771 | 17.0363 | 16.9948 | 16.954 | 16.6391 | 15.6486 | 14.3146 | 16.0821 | 16.0306 | 16.003 | 15.9653 | 15.9227 | 15.8647 | 15.6327 | 15.3972 | 15.1704 | 14.9506 | 14.7472 | 13.7454 | 12.6428 | 11.2006 | 16.1954 | 16.1439 | 16.1163 | 16.0785 | 16.0359 | 15.9892 | 15.94 | 15.9 | 15.7429 | 15.5356 | 15.3436 | 15.1623 | 14.9702 | 14.7785
|  | MONTROSE NORTH | CT |  |  |  | 0.10632 | 17.3725 | 17.3483 | 17.3272 | 17.3001 | 17.2678 | 17.2305 | 17.1915 | 17.164 | 17.1354 | 17.1066 | 17.0775 | 16.8899 | 16.5926 | 15.9968 | 16.0821 | 16.058 | 16.0369 | 16.0097 | 15.9774 | 15.9402 | 15.9012 | 15.8736 | 15.8233 | 15.6724 | 15.5286 | 14.801 | 14.0136 | 13.087 | 16.1954 | 16.1712 | 16.1501 | 16.123 | 16.0907 | 16.0534 | 16.0144 | 15.9869 | 15.9583 | 15.9295 | 15.9004 | 15.8703 | 15.8019 | 15.6636
|  | MONTROSE NORTH | LW |  |  |  | 0.10632 | 17.3801 | 17.321 | 17.2934 | 17.2556 | 17.213 | 17.1663 | 17.1171 | 17.0771 | 17.0363 | 16.9948 | 16.954 | 16.6391 | 15.6486 | 14.3146 | 16.0897 | 16.0306 | 16.003 | 15.9653 | 15.9227 | 15.8647 | 15.6327 | 15.3972 | 15.1704 | 14.9506 | 14.7472 | 13.7454 | 12.6428 | 11.2006 | 16.203 | 16.1439 | 16.1163 | 16.0785 | 16.0359 | 15.9892 | 15.94 | 15.9 | 15.7429 | 15.5356 | 15.3436 | 15.1623 | 14.9702 | 14.7785
|  | MONTROSE NORTH | ST |  |  |  | 0.10632 | 17.3809 | 17.3722 | 17.3676 | 17.3566 | 17.3435 | 17.3282 | 17.3112 | 17.3043 | 17.2974 | 17.2907 | 17.2843 | 17.2545 | 17.1196 | 17.0441 | 16.0906 | 16.0819 | 16.0772 | 16.0663 | 16.0531 | 16.0378 | 16.0208 | 16.014 | 16.007 | 16.0004 | 15.994 | 15.9619 | 15.5085 | 15.1249 | 16.2038 | 16.1951 | 16.1905 | 16.1795 | 16.1664 | 16.1511 | 16.1341 | 16.1272 | 16.1203 | 16.1136 | 16.1072 | 16.0774 | 15.9425 | 15.7011
|  | MONTROSE NORTH | FS |  |  |  | 0.10632 | 17.3818 | 17.3731 | 17.3719 | 17.3707 | 17.3692 | 17.3675 | 17.3658 | 17.3616 | 17.357 | 17.352 | 17.3467 | 17.3305 | 17.2635 | 17.1212 | 16.0914 | 16.0828 | 16.0816 | 16.0803 | 16.0789 | 16.0772 | 16.0755 | 16.0713 | 16.0667 | 16.0617 | 16.0563 | 16.0402 | 15.972 | 15.5964 | 16.2047 | 16.196 | 16.1948 | 16.1936 | 16.1921 | 16.1904 | 16.1887 | 16.1845 | 16.1799 | 16.1749 | 16.1696 | 16.1534 | 16.0864 | 15.9441
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 0.069474 | 2.9521 | 2.915 | 2.8791 | 2.8417 | 2.8024 | 2.7416 | 2.6652 | 2.5889 | 2.5071 | 2.4263 | 2.3477 | 1.9368 | 1.4418 | 0.80425 | 2.6364 | 2.571 | 2.5027 | 2.4181 | 2.3315 | 2.2397 | 2.1471 | 2.0541 | 1.9625 | 1.8722 | 1.7846 | 1.3336 | 0.80668 | 0.13426 | 2.7519 | 2.7149 | 2.679 | 2.6416 | 2.6023 | 2.5621 | 2.4859 | 2.3901 | 2.2958 | 2.2028 | 2.1127 | 2.0253 | 1.9339 | 1.8403
|  | MOSSAT | CT |  |  |  | 0.069474 | 2.9521 | 2.915 | 2.8791 | 2.8417 | 2.8024 | 2.7416 | 2.6652 | 2.59 | 2.5148 | 2.4414 | 2.3689 | 1.9865 | 1.5451 | 1.0248 | 2.6364 | 2.571 | 2.5027 | 2.4181 | 2.3315 | 2.2446 | 2.1613 | 2.0789 | 1.9967 | 1.9166 | 1.8378 | 1.4253 | 0.9559 | 0.41402 | 2.7519 | 2.7149 | 2.679 | 2.6416 | 2.6023 | 2.5621 | 2.5059 | 2.4215 | 2.3373 | 2.2554 | 2.1748 | 2.0944 | 2.0101 | 1.9255
|  | MOSSAT | LW |  |  |  | 0.069474 | 3.0034 | 2.9724 | 2.9523 | 2.9226 | 2.8399 | 2.7545 | 2.6716 | 2.5889 | 2.5071 | 2.4263 | 2.3477 | 1.9368 | 1.4418 | 0.80425 | 2.672 | 2.5977 | 2.5287 | 2.4321 | 2.3356 | 2.2397 | 2.1471 | 2.0541 | 1.9625 | 1.8722 | 1.7846 | 1.3336 | 0.80668 | 0.13426 | 2.8033 | 2.7723 | 2.7522 | 2.7264 | 2.6801 | 2.5813 | 2.4859 | 2.3901 | 2.2958 | 2.2028 | 2.1127 | 2.0253 | 1.9339 | 1.8403
|  | MOSSAT | ST |  |  |  | 0.069474 | 3.0144 | 3.004 | 2.9959 | 2.9856 | 2.9728 | 2.9592 | 2.945 | 2.9345 | 2.9247 | 2.9093 | 2.8788 | 2.7244 | 2.5479 | 2.3896 | 2.7296 | 2.7125 | 2.696 | 2.6578 | 2.6165 | 2.5745 | 2.5343 | 2.4948 | 2.4556 | 2.4178 | 2.3806 | 2.2055 | 2.0112 | 1.8359 | 2.8143 | 2.8039 | 2.7958 | 2.7855 | 2.7726 | 2.7591 | 2.7449 | 2.7344 | 2.7246 | 2.715 | 2.7054 | 2.5459 | 2.3466 | 2.1666
|  | MOSSAT | FS |  |  |  | 0.069474 | 3.0194 | 3.0135 | 3.0084 | 3.0032 | 2.9979 | 2.9926 | 2.9873 | 2.9811 | 2.9748 | 2.9684 | 2.9619 | 2.8884 | 2.7648 | 2.6264 | 2.7378 | 2.7263 | 2.7153 | 2.7019 | 2.6845 | 2.6602 | 2.6359 | 2.6084 | 2.58 | 2.5515 | 2.5229 | 2.3875 | 2.2492 | 2.0972 | 2.8193 | 2.8134 | 2.8082 | 2.8031 | 2.7978 | 2.7925 | 2.7871 | 2.781 | 2.7747 | 2.7683 | 2.7618 | 2.7293 | 2.5906 | 2.4348
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 0 | 15.9464 | 15.9286 | 15.916 | 15.8991 | 15.8802 | 15.8588 | 15.8364 | 15.8183 | 15.7999 | 15.7813 | 15.7621 | 15.6462 | 15.4691 | 15.1457 | 14.8101 | 14.7923 | 14.7797 | 14.7628 | 14.7439 | 14.7225 | 14.7001 | 14.682 | 14.6636 | 14.645 | 14.6258 | 14.5099 | 14.1269 | 13.5783 | 15.1414 | 15.1236 | 15.111 | 15.0941 | 15.0752 | 15.0538 | 15.0314 | 15.0133 | 14.9949 | 14.9763 | 14.9571 | 14.938 | 14.9152 | 14.8916
|  | MOUNT PLEASANT | CT |  |  |  | 0 | 15.9464 | 15.9329 | 15.9207 | 15.906 | 15.8899 | 15.8718 | 15.8527 | 15.8379 | 15.8227 | 15.8075 | 15.7922 | 15.6973 | 15.5572 | 15.3528 | 14.8101 | 14.7966 | 14.7844 | 14.7696 | 14.7536 | 14.7355 | 14.7163 | 14.7016 | 14.6864 | 14.6712 | 14.6559 | 14.561 | 14.4209 | 14.115 | 15.1414 | 15.1279 | 15.1157 | 15.1009 | 15.0849 | 15.0668 | 15.0476 | 15.0329 | 15.0177 | 15.0025 | 14.9872 | 14.9715 | 14.953 | 14.9333
|  | MOUNT PLEASANT | LW |  |  |  | 0 | 15.9548 | 15.9286 | 15.916 | 15.8991 | 15.8802 | 15.8588 | 15.8364 | 15.8183 | 15.7999 | 15.7813 | 15.7621 | 15.6462 | 15.4691 | 15.1457 | 14.8185 | 14.7923 | 14.7797 | 14.7628 | 14.7439 | 14.7225 | 14.7001 | 14.682 | 14.6636 | 14.645 | 14.6258 | 14.5099 | 14.1269 | 13.5783 | 15.1498 | 15.1236 | 15.111 | 15.0941 | 15.0752 | 15.0538 | 15.0314 | 15.0133 | 14.9949 | 14.9763 | 14.9571 | 14.938 | 14.9152 | 14.8916
|  | MOUNT PLEASANT | ST |  |  |  | 0 | 15.9565 | 15.9525 | 15.9501 | 15.9451 | 15.9384 | 15.9308 | 15.9226 | 15.9184 | 15.9143 | 15.9111 | 15.908 | 15.8909 | 15.832 | 15.7971 | 14.8202 | 14.8161 | 14.8138 | 14.8088 | 14.8021 | 14.7945 | 14.7863 | 14.7821 | 14.778 | 14.7747 | 14.7716 | 14.7546 | 14.6956 | 14.6607 | 15.1515 | 15.1474 | 15.1451 | 15.1401 | 15.1334 | 15.1258 | 15.1176 | 15.1134 | 15.1093 | 15.106 | 15.1029 | 15.0859 | 15.0269 | 14.992
|  | MOUNT PLEASANT | FS |  |  |  | 0 | 15.9565 | 15.9527 | 15.9517 | 15.9507 | 15.9496 | 15.9484 | 15.9473 | 15.9451 | 15.9428 | 15.9404 | 15.9378 | 15.929 | 15.9008 | 15.8441 | 14.8202 | 14.8163 | 14.8154 | 14.8144 | 14.8133 | 14.8121 | 14.8109 | 14.8088 | 14.8065 | 14.8041 | 14.8015 | 14.7927 | 14.7645 | 14.7078 | 15.1515 | 15.1476 | 15.1467 | 15.1457 | 15.1446 | 15.1434 | 15.1422 | 15.1401 | 15.1378 | 15.1354 | 15.1328 | 15.124 | 15.0958 | 15.0391
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 0.072632 | 29.1943 | 29.1412 | 29.1008 | 29.0461 | 28.984 | 28.917 | 28.8461 | 28.7879 | 28.7291 | 28.6688 | 28.6094 | 28.2455 | 27.6938 | 26.5328 | 27.8552 | 27.7241 | 27.6093 | 27.4206 | 27.228 | 27.0376 | 26.8486 | 26.6646 | 26.4822 | 26.3005 | 26.1221 | 25.1471 | 23.9664 | 22.3566 | 29.1231 | 29.07 | 29.0296 | 28.9334 | 28.7311 | 28.5317 | 28.334 | 28.1407 | 27.9491 | 27.7585 | 27.5713 | 27.3862 | 27.1891 | 26.9902
|  | MUIR OF ORD | CT |  |  |  | 0.072632 | 29.1943 | 29.1514 | 29.1124 | 29.0664 | 29.0136 | 28.9548 | 28.8929 | 28.8461 | 28.7984 | 28.7496 | 28.7007 | 28.4011 | 27.9648 | 27.3396 | 27.8552 | 27.7661 | 27.6751 | 27.5356 | 27.3918 | 27.247 | 27.1027 | 26.9677 | 26.8333 | 26.6994 | 26.567 | 25.8629 | 24.994 | 23.9449 | 29.1231 | 29.0802 | 29.0412 | 28.9952 | 28.9049 | 28.7537 | 28.6034 | 28.4619 | 28.321 | 28.1809 | 28.0423 | 27.9042 | 27.7573 | 27.6097
|  | MUIR OF ORD | LW |  |  |  | 0.072632 | 29.2238 | 29.1412 | 29.1008 | 29.0461 | 28.984 | 28.917 | 28.8461 | 28.7879 | 28.7291 | 28.6688 | 28.6094 | 28.2455 | 27.6938 | 26.5328 | 27.8676 | 27.7241 | 27.6093 | 27.4206 | 27.228 | 27.0376 | 26.8486 | 26.6646 | 26.4822 | 26.3005 | 26.1221 | 25.1471 | 23.9664 | 22.3566 | 29.1526 | 29.07 | 29.0296 | 28.9334 | 28.7311 | 28.5317 | 28.334 | 28.1407 | 27.9491 | 27.7585 | 27.5713 | 27.3862 | 27.1891 | 26.9902
|  | MUIR OF ORD | ST |  |  |  | 0.072632 | 29.2297 | 29.2158 | 29.2069 | 29.1902 | 29.17 | 29.1471 | 29.123 | 29.1113 | 29.0996 | 29.0883 | 29.0772 | 29.0234 | 28.8464 | 28.7395 | 27.9614 | 27.943 | 27.9299 | 27.8517 | 27.7707 | 27.6903 | 27.6108 | 27.5387 | 27.4679 | 27.399 | 27.3319 | 27.0179 | 26.5965 | 26.2568 | 29.1585 | 29.1446 | 29.1357 | 29.119 | 29.0988 | 29.0759 | 29.0518 | 29.0401 | 28.9803 | 28.9071 | 28.8359 | 28.5027 | 28.0632 | 27.7064
|  | MUIR OF ORD | FS |  |  |  | 0.072632 | 29.2331 | 29.2226 | 29.2188 | 29.215 | 29.2109 | 29.2074 | 29.2039 | 29.1976 | 29.1908 | 29.1835 | 29.1759 | 29.1463 | 29.0592 | 28.8896 | 27.9698 | 27.9564 | 27.9485 | 27.938 | 27.915 | 27.8721 | 27.8295 | 27.7778 | 27.7257 | 27.6734 | 27.6208 | 27.3716 | 27.0809 | 26.7204 | 29.1619 | 29.1513 | 29.1476 | 29.1437 | 29.1397 | 29.1362 | 29.1327 | 29.1264 | 29.1196 | 29.1123 | 29.1047 | 28.8734 | 28.5677 | 28.193
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 0.061053 | 3.6813 | 3.6667 | 3.6533 | 3.6375 | 3.6191 | 3.5979 | 3.5757 | 3.5576 | 3.5138 | 3.4628 | 3.4128 | 3.1479 | 2.824 | 2.3707 | 3.4118 | 3.3922 | 3.3563 | 3.2978 | 3.2386 | 3.1793 | 3.1208 | 3.0645 | 3.0088 | 2.9527 | 2.8977 | 2.6087 | 2.2604 | 1.7834 | 3.4613 | 3.4401 | 3.4047 | 3.3474 | 3.2891 | 3.2308 | 3.1732 | 3.1179 | 3.0631 | 3.0079 | 2.9539 | 2.9007 | 2.8442 | 2.7864
|  | MUIREND | CT |  |  |  | 0.061053 | 3.6813 | 3.6667 | 3.6533 | 3.6375 | 3.6205 | 3.6016 | 3.5819 | 3.5661 | 3.5501 | 3.534 | 3.5179 | 3.3173 | 3.0696 | 2.7674 | 3.4118 | 3.3971 | 3.3718 | 3.3274 | 3.2827 | 3.2377 | 3.193 | 3.15 | 3.1073 | 3.0651 | 3.0233 | 2.8 | 2.5351 | 2.2163 | 3.4613 | 3.4467 | 3.4198 | 3.3762 | 3.3321 | 3.2878 | 3.2437 | 3.2015 | 3.1594 | 3.1178 | 3.0767 | 3.0357 | 2.9916 | 2.9472
|  | MUIREND | LW |  |  |  | 0.061053 | 3.6931 | 3.668 | 3.6551 | 3.6381 | 3.6191 | 3.5979 | 3.5757 | 3.5576 | 3.5138 | 3.4628 | 3.4128 | 3.1479 | 2.824 | 2.3707 | 3.4236 | 3.3922 | 3.3563 | 3.2978 | 3.2386 | 3.1793 | 3.1208 | 3.0645 | 3.0088 | 2.9527 | 2.8977 | 2.6087 | 2.2604 | 1.7834 | 3.4731 | 3.4401 | 3.4047 | 3.3474 | 3.2891 | 3.2308 | 3.1732 | 3.1179 | 3.0631 | 3.0079 | 2.9539 | 2.9007 | 2.8442 | 2.7864
|  | MUIREND | ST |  |  |  | 0.061053 | 3.6956 | 3.691 | 3.688 | 3.6825 | 3.6763 | 3.6692 | 3.6616 | 3.6577 | 3.6537 | 3.6499 | 3.6461 | 3.6284 | 3.5594 | 3.4659 | 3.4261 | 3.4215 | 3.4184 | 3.413 | 3.4067 | 3.3843 | 3.3601 | 3.3383 | 3.317 | 3.2962 | 3.276 | 3.1816 | 3.056 | 2.9532 | 3.4757 | 3.4711 | 3.468 | 3.4625 | 3.4562 | 3.4324 | 3.4086 | 3.3873 | 3.3664 | 3.3461 | 3.3263 | 3.2338 | 3.11 | 3.0089
|  | MUIREND | FS |  |  |  | 0.061053 | 3.6965 | 3.693 | 3.692 | 3.691 | 3.69 | 3.6889 | 3.6877 | 3.6857 | 3.6836 | 3.6814 | 3.679 | 3.6674 | 3.6413 | 3.5847 | 3.4269 | 3.4234 | 3.4225 | 3.4215 | 3.4204 | 3.4193 | 3.4182 | 3.4099 | 3.3936 | 3.3773 | 3.3608 | 3.2805 | 3.1913 | 3.0827 | 3.4765 | 3.473 | 3.4721 | 3.4711 | 3.47 | 3.4689 | 3.4678 | 3.4578 | 3.4419 | 3.4259 | 3.4098 | 3.3312 | 3.2436 | 3.1364
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 0.24842 | 17.6183 | 17.528 | 17.4805 | 17.4153 | 17.3416 | 17.2597 | 17.1736 | 17.1052 | 17.0358 | 16.9653 | 16.8953 | 16.4378 | 15.0085 | 13.0046 | 16.3334 | 16.238 | 16.1855 | 16.1114 | 16.029 | 15.9387 | 15.8446 | 15.7676 | 15.6898 | 15.6111 | 15.5329 | 14.6917 | 13.1338 | 10.9787 | 16.9086 | 16.8183 | 16.7708 | 16.7056 | 16.6319 | 16.55 | 16.4639 | 16.3955 | 16.3261 | 16.2556 | 16.1824 | 16.1028 | 16.0076 | 15.9093
|  | NAIRN CENTRAL | CT |  |  |  | 0.24842 | 17.6183 | 17.5763 | 17.5404 | 17.4942 | 17.4391 | 17.3758 | 17.3083 | 17.2611 | 17.2125 | 17.1635 | 17.1143 | 16.8016 | 16.3154 | 15.1783 | 16.3334 | 16.2884 | 16.249 | 16.1965 | 16.1353 | 16.0662 | 15.9931 | 15.9399 | 15.8854 | 15.8307 | 15.7758 | 15.4351 | 14.7035 | 13.3681 | 16.9086 | 16.8666 | 16.8307 | 16.7845 | 16.7294 | 16.6661 | 16.5986 | 16.5514 | 16.5028 | 16.4538 | 16.4046 | 16.3537 | 16.2918 | 16.2273
|  | NAIRN CENTRAL | LW |  |  |  | 0.24842 | 17.6309 | 17.528 | 17.4805 | 17.4153 | 17.3416 | 17.2597 | 17.1736 | 17.1052 | 17.0358 | 16.9653 | 16.8953 | 16.4378 | 15.0085 | 13.0046 | 16.345 | 16.238 | 16.1855 | 16.1114 | 16.029 | 15.9387 | 15.8446 | 15.7676 | 15.6898 | 15.6111 | 15.5329 | 14.6917 | 13.1338 | 10.9787 | 16.9212 | 16.8183 | 16.7708 | 16.7056 | 16.6319 | 16.55 | 16.4639 | 16.3955 | 16.3261 | 16.2556 | 16.1824 | 16.1028 | 16.0076 | 15.9093
|  | NAIRN CENTRAL | ST |  |  |  | 0.24842 | 17.6343 | 17.6196 | 17.6116 | 17.5932 | 17.5711 | 17.5455 | 17.5172 | 17.5055 | 17.4937 | 17.4824 | 17.4715 | 17.4213 | 17.2045 | 17.0854 | 16.3541 | 16.3391 | 16.3308 | 16.3083 | 16.2822 | 16.2528 | 16.2207 | 16.2049 | 16.1891 | 16.1739 | 16.1592 | 16.0908 | 15.8568 | 15.7209 | 16.9246 | 16.9098 | 16.9019 | 16.8835 | 16.8614 | 16.8358 | 16.8075 | 16.7958 | 16.784 | 16.7727 | 16.7618 | 16.7116 | 16.4948 | 16.3698
|  | NAIRN CENTRAL | FS |  |  |  | 0.24842 | 17.6351 | 17.622 | 17.6207 | 17.6192 | 17.6174 | 17.6152 | 17.613 | 17.6069 | 17.6002 | 17.5928 | 17.5849 | 17.5586 | 17.4569 | 17.2398 | 16.3552 | 16.3419 | 16.3402 | 16.3383 | 16.3352 | 16.3303 | 16.3254 | 16.3162 | 16.3064 | 16.296 | 16.285 | 16.2435 | 16.1277 | 15.8973 | 16.9254 | 16.9123 | 16.911 | 16.9095 | 16.9077 | 16.9055 | 16.9033 | 16.8972 | 16.8905 | 16.8831 | 16.8752 | 16.8489 | 16.7472 | 16.5301
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.10526 | 1.4595 | 5.25 | 5.2414 | 5.2303 | 5.2178 | 5.2035 | 5.1886 | 5.1763 | 5.164 | 5.1515 | 5.1392 | 5.0628 | 4.9469 | 4.7409 | 1.452 | 5.2402 | 5.2298 | 5.216 | 5.2011 | 5.1407 | 5.0778 | 5.0144 | 4.9523 | 4.8923 | 4.8358 | 4.5552 | 4.2454 | 3.8544 | 1.288 | 5.0351 | 4.9858 | 4.9176 | 4.8506 | 4.785 | 4.7235 | 4.6616 | 4.6009 | 4.5424 | 4.4871 | 4.4342 | 4.3782 | 4.3227
|  | NEW PITSLIGO | CT |  |  |  | 0.10526 | 1.4595 | 5.25 | 5.2414 | 5.2311 | 5.2196 | 5.2068 | 5.1933 | 5.1831 | 5.1718 | 5.1606 | 5.1492 | 5.0815 | 4.9849 | 4.8495 | 1.452 | 5.2415 | 5.2316 | 5.2197 | 5.2064 | 5.1919 | 5.1769 | 5.1444 | 5.0983 | 5.0544 | 5.0116 | 4.7972 | 4.5645 | 4.2993 | 1.2956 | 5.0629 | 5.0272 | 4.9796 | 4.9303 | 4.8799 | 4.8333 | 4.788 | 4.743 | 4.7 | 4.6581 | 4.6164 | 4.5739 | 4.5321
|  | NEW PITSLIGO | LW |  |  |  | 0.10526 | 1.467 | 5.25 | 5.2415 | 5.2303 | 5.2178 | 5.2035 | 5.1886 | 5.1763 | 5.164 | 5.1515 | 5.1392 | 5.0628 | 4.9469 | 4.7409 | 1.4589 | 5.2402 | 5.2298 | 5.216 | 5.2011 | 5.1407 | 5.0778 | 5.0144 | 4.9523 | 4.8923 | 4.8358 | 4.5552 | 4.2454 | 3.8544 | 1.288 | 5.0351 | 4.9858 | 4.9176 | 4.8506 | 4.785 | 4.7235 | 4.6616 | 4.6009 | 4.5424 | 4.4871 | 4.4342 | 4.3782 | 4.3227
|  | NEW PITSLIGO | ST |  |  |  | 0.10526 | 1.4687 | 5.2659 | 5.2642 | 5.2608 | 5.2561 | 5.2508 | 5.2459 | 5.2436 | 5.2412 | 5.239 | 5.2367 | 5.2246 | 5.1863 | 5.1621 | 1.4623 | 5.2592 | 5.2572 | 5.2528 | 5.247 | 5.2407 | 5.2349 | 5.2315 | 5.2281 | 5.2248 | 5.2216 | 5.1506 | 5.0236 | 4.9159 | 1.3277 | 5.1191 | 5.1105 | 5.0847 | 5.0576 | 5.0298 | 5.0038 | 4.9785 | 4.9534 | 4.9288 | 4.9054 | 4.7952 | 4.6708 | 4.5655
|  | NEW PITSLIGO | FS |  |  |  | 0.10526 | 1.4687 | 5.2661 | 5.2652 | 5.2643 | 5.2633 | 5.2622 | 5.2612 | 5.2596 | 5.2579 | 5.2561 | 5.2542 | 5.2473 | 5.2289 | 5.1939 | 1.4625 | 5.2597 | 5.2585 | 5.2573 | 5.2558 | 5.254 | 5.2523 | 5.25 | 5.2475 | 5.2449 | 5.2423 | 5.2317 | 5.1743 | 5.0733 | 1.3324 | 5.1249 | 5.1182 | 5.1109 | 5.0996 | 5.0827 | 5.0668 | 5.0482 | 5.0288 | 5.0101 | 4.9914 | 4.9042 | 4.8184 | 4.7193
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0 | 0.36603 | 0.36486 | 0.36397 | 0.36273 | 0.36132 | 0.35979 | 0.35775 | 0.3533 | 0.3489 | 0.34454 | 0.34026 | 0.31792 | 0.29144 | 0.25487 | 0.33319 | 0.33203 | 0.33114 | 0.32989 | 0.32757 | 0.32254 | 0.31757 | 0.3128 | 0.30801 | 0.3032 | 0.29849 | 0.27368 | 0.24456 | 0.20545 | 0.34136 | 0.34019 | 0.3393 | 0.33805 | 0.33304 | 0.32775 | 0.32253 | 0.31751 | 0.31254 | 0.30762 | 0.3028 | 0.29806 | 0.29306 | 0.28803
|  | NEWTON | CT |  |  |  | 0 | 0.36603 | 0.36536 | 0.3648 | 0.36403 | 0.3631 | 0.36201 | 0.36084 | 0.36009 | 0.35881 | 0.35564 | 0.35251 | 0.33604 | 0.31682 | 0.29218 | 0.33319 | 0.33253 | 0.33196 | 0.3312 | 0.33026 | 0.32917 | 0.32553 | 0.32206 | 0.31862 | 0.31521 | 0.31184 | 0.29373 | 0.27248 | 0.24588 | 0.34136 | 0.34069 | 0.34012 | 0.33936 | 0.33842 | 0.33485 | 0.33088 | 0.32722 | 0.32358 | 0.31998 | 0.31643 | 0.31289 | 0.30918 | 0.30545
|  | NEWTON | LW |  |  |  | 0 | 0.36687 | 0.36486 | 0.36397 | 0.36273 | 0.36132 | 0.35979 | 0.35775 | 0.3533 | 0.3489 | 0.34454 | 0.34026 | 0.31792 | 0.29144 | 0.25487 | 0.33404 | 0.33203 | 0.33114 | 0.32989 | 0.32757 | 0.32254 | 0.31757 | 0.3128 | 0.30801 | 0.3032 | 0.29849 | 0.27368 | 0.24456 | 0.20545 | 0.3422 | 0.34019 | 0.3393 | 0.33805 | 0.33304 | 0.32775 | 0.32253 | 0.31751 | 0.31254 | 0.30762 | 0.3028 | 0.29806 | 0.29306 | 0.28803
|  | NEWTON | ST |  |  |  | 0 | 0.36687 | 0.36663 | 0.36651 | 0.3662 | 0.36582 | 0.36538 | 0.36488 | 0.3647 | 0.36451 | 0.36433 | 0.36416 | 0.35807 | 0.34607 | 0.33623 | 0.33404 | 0.33379 | 0.33368 | 0.33337 | 0.33299 | 0.33254 | 0.33205 | 0.33186 | 0.33167 | 0.32985 | 0.32769 | 0.31738 | 0.3042 | 0.29306 | 0.3422 | 0.34195 | 0.34184 | 0.34153 | 0.34115 | 0.3407 | 0.34021 | 0.34002 | 0.33764 | 0.33527 | 0.33296 | 0.32196 | 0.30848 | 0.29721
|  | NEWTON | FS |  |  |  | 0 | 0.36687 | 0.36666 | 0.36665 | 0.36664 | 0.36662 | 0.3666 | 0.36657 | 0.36648 | 0.36638 | 0.36627 | 0.36614 | 0.36582 | 0.36413 | 0.36048 | 0.33404 | 0.33382 | 0.33381 | 0.3338 | 0.33379 | 0.33376 | 0.33374 | 0.33365 | 0.33354 | 0.33343 | 0.33331 | 0.33298 | 0.32979 | 0.32236 | 0.3422 | 0.34198 | 0.34197 | 0.34196 | 0.34195 | 0.34192 | 0.3419 | 0.34181 | 0.3417 | 0.34159 | 0.34147 | 0.34114 | 0.33521 | 0.32751
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 0.32 | 16.9893 | 16.9162 | 31.4224 | 30.5997 | 29.6312 | 28.7326 | 27.9612 | 27.1597 | 26.4158 | 25.7225 | 25.1341 | 22.6301 | 20.3466 | 17.7528 | 15.4144 | 14.2625 | 26.9065 | 25.6133 | 24.4089 | 23.2944 | 22.3412 | 21.3461 | 20.4242 | 19.5661 | 18.8405 | 15.783 | 13.1456 | 10.2832 | 16.7662 | 15.6489 | 28.6968 | 27.4356 | 26.2607 | 25.1731 | 24.2427 | 23.2718 | 22.3721 | 21.5346 | 20.8262 | 20.2134 | 19.5991 | 18.9998
|  | NEWTONHILL | CT |  |  |  | 0.32 | 16.9893 | 16.9473 | 31.46 | 31.4144 | 31.3609 | 30.7594 | 30.1912 | 29.6357 | 29.1008 | 28.6287 | 28.2055 | 26.2789 | 24.6639 | 22.9609 | 15.9002 | 15.2829 | 28.3604 | 27.5572 | 26.7074 | 25.8312 | 25.1309 | 24.4421 | 23.7796 | 23.1963 | 22.6748 | 20.3227 | 18.4027 | 16.4266 | 16.7759 | 16.6437 | 30.1139 | 29.3304 | 28.5012 | 27.6462 | 26.9624 | 26.2903 | 25.6437 | 25.0743 | 24.5651 | 24.0575 | 23.5707 | 23.1194
|  | NEWTONHILL | LW |  |  |  | 0.32 | 17.0087 | 16.9162 | 31.4224 | 30.5997 | 29.6312 | 28.7326 | 27.9612 | 27.1597 | 26.4158 | 25.7225 | 25.1341 | 22.6301 | 20.3466 | 17.7528 | 15.4144 | 14.2625 | 26.9065 | 25.6133 | 24.4089 | 23.2944 | 22.3412 | 21.3461 | 20.4242 | 19.5661 | 18.8405 | 15.783 | 13.1456 | 10.2832 | 16.7662 | 15.6489 | 28.6968 | 27.4356 | 26.2607 | 25.1731 | 24.2427 | 23.2718 | 22.3721 | 21.5346 | 20.8262 | 20.2134 | 19.5991 | 18.9998
|  | NEWTONHILL | ST |  |  |  | 0.32 | 17.0129 | 16.9992 | 31.5413 | 31.5243 | 31.5034 | 31.4794 | 31.4531 | 31.4411 | 31.4291 | 31.4174 | 31.2055 | 29.8614 | 28.7694 | 27.8526 | 16.0722 | 15.9632 | 29.5888 | 29.2138 | 28.806 | 28.3762 | 27.9904 | 27.5774 | 27.1487 | 26.746 | 26.3664 | 24.6841 | 23.3564 | 22.2285 | 16.7995 | 16.7857 | 30.9465 | 30.9088 | 30.5491 | 30.1299 | 29.7534 | 29.3507 | 28.9329 | 28.5403 | 28.1703 | 26.5302 | 25.232 | 24.1305
|  | NEWTONHILL | FS |  |  |  | 0.32 | 17.0154 | 17.0033 | 31.5504 | 31.5481 | 31.5456 | 31.5428 | 31.54 | 31.5338 | 31.5271 | 31.5199 | 31.5122 | 30.9273 | 30.0729 | 29.1746 | 16.1143 | 16.0225 | 29.734 | 29.5621 | 29.2921 | 29.0026 | 28.7224 | 28.4075 | 28.0685 | 27.7401 | 27.4205 | 25.9949 | 24.9417 | 23.8571 | 16.802 | 16.7899 | 30.9619 | 30.9514 | 30.9334 | 30.7416 | 30.4686 | 30.1617 | 29.8313 | 29.5113 | 29.1998 | 27.8104 | 26.782 | 25.7207
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 0 | 1.4259 | 1.4259 | 1.4258 | 1.4258 | 1.4257 | 1.4257 | 1.4256 | 1.4255 | 1.4255 | 1.4254 | 1.4254 | 1.4251 | 1.4247 | 1.4242 | 1.2643 | 1.2643 | 1.2642 | 1.2642 | 1.2641 | 1.2641 | 1.264 | 1.2639 | 1.2639 | 1.2638 | 1.2637 | 1.2634 | 1.263 | 1.2624 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2613 | 1.2613 | 1.2613 | 1.2612 | 1.2612 | 1.2612 | 1.2612 | 1.2611 | 1.2611 | 1.2611
|  | NIGG | CT |  |  |  | 0 | 1.4259 | 1.4259 | 1.4259 | 1.4258 | 1.4258 | 1.4258 | 1.4257 | 1.4257 | 1.4256 | 1.4256 | 1.4256 | 1.4254 | 1.4251 | 1.4248 | 1.2643 | 1.2643 | 1.2643 | 1.2642 | 1.2642 | 1.2642 | 1.2641 | 1.2641 | 1.264 | 1.264 | 1.2639 | 1.2637 | 1.2634 | 1.2631 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2613 | 1.2613 | 1.2613 | 1.2613 | 1.2613 | 1.2613 | 1.2612 | 1.2612
|  | NIGG | LW |  |  |  | 0 | 1.4259 | 1.4259 | 1.4258 | 1.4258 | 1.4257 | 1.4257 | 1.4256 | 1.4255 | 1.4255 | 1.4254 | 1.4254 | 1.4251 | 1.4247 | 1.4242 | 1.2643 | 1.2643 | 1.2642 | 1.2642 | 1.2641 | 1.2641 | 1.264 | 1.2639 | 1.2639 | 1.2638 | 1.2637 | 1.2634 | 1.263 | 1.2624 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2613 | 1.2613 | 1.2613 | 1.2612 | 1.2612 | 1.2612 | 1.2612 | 1.2611 | 1.2611 | 1.2611
|  | NIGG | ST |  |  |  | 0 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4258 | 1.4257 | 1.4256 | 1.4255 | 1.2644 | 1.2644 | 1.2644 | 1.2643 | 1.2643 | 1.2643 | 1.2643 | 1.2642 | 1.2642 | 1.2642 | 1.2642 | 1.2641 | 1.2639 | 1.2638 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2613 | 1.2612
|  | NIGG | FS |  |  |  | 0 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4259 | 1.4258 | 1.4257 | 1.4256 | 1.2644 | 1.2644 | 1.2644 | 1.2644 | 1.2644 | 1.2643 | 1.2643 | 1.2643 | 1.2643 | 1.2643 | 1.2643 | 1.2642 | 1.2641 | 1.264 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2614 | 1.2613
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 0.96632 | 17.7721 | 17.7415 | 17.7271 | 17.7071 | 17.6844 | 17.6594 | 17.6331 | 17.6125 | 17.5914 | 17.57 | 17.5489 | 17.4172 | 17.053 | 16.4242 | 16.3458 | 16.2891 | 16.2449 | 16.1715 | 16.0966 | 16.0223 | 15.9486 | 15.877 | 15.8057 | 15.7349 | 15.6651 | 15.2928 | 14.835 | 14.1838 | 16.9086 | 16.8522 | 16.8084 | 16.7357 | 16.6615 | 16.5879 | 16.5114 | 16.436 | 16.361 | 16.2865 | 16.2132 | 16.1408 | 16.0625 | 15.9834
|  | NINEWELLS | CT |  |  |  | 0.96632 | 17.7721 | 17.7612 | 17.752 | 17.7395 | 17.7242 | 17.7062 | 17.6869 | 17.6742 | 17.661 | 17.6477 | 17.6343 | 17.5458 | 17.4023 | 17.1272 | 16.3498 | 16.3208 | 16.2914 | 16.2417 | 16.19 | 16.1376 | 16.0853 | 16.0369 | 15.9885 | 15.9405 | 15.8929 | 15.6354 | 15.3185 | 14.9199 | 16.9125 | 16.8838 | 16.8547 | 16.8054 | 16.7542 | 16.7023 | 16.6504 | 16.6025 | 16.5521 | 16.5016 | 16.4515 | 16.4014 | 16.3471 | 16.2923
|  | NINEWELLS | LW |  |  |  | 0.96632 | 17.7738 | 17.7415 | 17.7271 | 17.7071 | 17.6844 | 17.6594 | 17.6331 | 17.6125 | 17.5914 | 17.57 | 17.5489 | 17.4172 | 17.053 | 16.4242 | 16.3458 | 16.2891 | 16.2449 | 16.1715 | 16.0966 | 16.0223 | 15.9486 | 15.877 | 15.8057 | 15.7349 | 15.6651 | 15.2928 | 14.835 | 14.1838 | 16.9086 | 16.8522 | 16.8084 | 16.7357 | 16.6615 | 16.5879 | 16.5114 | 16.436 | 16.361 | 16.2865 | 16.2132 | 16.1408 | 16.0625 | 15.9834
|  | NINEWELLS | ST |  |  |  | 0.96632 | 17.7738 | 17.7696 | 17.7675 | 17.7621 | 17.7555 | 17.7477 | 17.7391 | 17.7358 | 17.7325 | 17.7294 | 17.7264 | 17.7127 | 17.6433 | 17.6073 | 16.3809 | 16.3755 | 16.3724 | 16.3425 | 16.3118 | 16.2812 | 16.2504 | 16.2232 | 16.1965 | 16.1705 | 16.1451 | 16.0249 | 15.8531 | 15.7174 | 16.9432 | 16.9379 | 16.9348 | 16.9052 | 16.8748 | 16.8445 | 16.814 | 16.7871 | 16.7607 | 16.735 | 16.71 | 16.5874 | 16.408 | 16.2649
|  | NINEWELLS | FS |  |  |  | 0.96632 | 17.7738 | 17.7697 | 17.7695 | 17.7693 | 17.769 | 17.7685 | 17.7681 | 17.7663 | 17.7643 | 17.7621 | 17.7598 | 17.7535 | 17.7205 | 17.6482 | 16.3819 | 16.3769 | 16.3757 | 16.3733 | 16.3653 | 16.3484 | 16.3316 | 16.3111 | 16.2904 | 16.2697 | 16.2488 | 16.1521 | 16.0336 | 15.8796 | 16.9442 | 16.9393 | 16.938 | 16.9356 | 16.9277 | 16.9111 | 16.8945 | 16.8743 | 16.8539 | 16.8333 | 16.8127 | 16.7172 | 16.5961 | 16.4361
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0 | 0.22306 | 0.22256 | 0.22234 | 0.22203 | 0.22168 | 0.22013 | 0.21837 | 0.21666 | 0.21496 | 0.21326 | 0.21159 | 0.20288 | 0.19295 | 0.18018 | 0.21802 | 0.21718 | 0.21573 | 0.21384 | 0.21194 | 0.21005 | 0.20817 | 0.20634 | 0.20452 | 0.2027 | 0.20091 | 0.19161 | 0.18108 | 0.16771 | 0.21701 | 0.21651 | 0.21629 | 0.21598 | 0.2146 | 0.21267 | 0.21075 | 0.20888 | 0.20702 | 0.20516 | 0.20333 | 0.20151 | 0.19961 | 0.19769
|  | NORTH HOY | CT |  |  |  | 0 | 0.22306 | 0.22289 | 0.22274 | 0.22254 | 0.2223 | 0.22201 | 0.22097 | 0.21957 | 0.21817 | 0.21678 | 0.21539 | 0.20817 | 0.20009 | 0.19085 | 0.21811 | 0.21768 | 0.21724 | 0.2157 | 0.21412 | 0.21253 | 0.21094 | 0.20943 | 0.20793 | 0.20643 | 0.20494 | 0.1972 | 0.1886 | 0.17885 | 0.21701 | 0.21683 | 0.21669 | 0.21649 | 0.21624 | 0.21519 | 0.21357 | 0.21203 | 0.21049 | 0.20895 | 0.20743 | 0.20591 | 0.20432 | 0.20273
|  | NORTH HOY | LW |  |  |  | 0 | 0.22306 | 0.22256 | 0.22234 | 0.22203 | 0.22168 | 0.22013 | 0.21837 | 0.21666 | 0.21496 | 0.21326 | 0.21159 | 0.20288 | 0.19295 | 0.18018 | 0.21802 | 0.21718 | 0.21573 | 0.21384 | 0.21194 | 0.21005 | 0.20817 | 0.20634 | 0.20452 | 0.2027 | 0.20091 | 0.19161 | 0.18108 | 0.16771 | 0.21701 | 0.21651 | 0.21629 | 0.21598 | 0.2146 | 0.21267 | 0.21075 | 0.20888 | 0.20702 | 0.20516 | 0.20333 | 0.20151 | 0.19961 | 0.19769
|  | NORTH HOY | ST |  |  |  | 0 | 0.22306 | 0.223 | 0.22297 | 0.22288 | 0.22278 | 0.22265 | 0.22252 | 0.22247 | 0.22242 | 0.22237 | 0.22232 | 0.22211 | 0.22105 | 0.2194 | 0.21851 | 0.21843 | 0.21838 | 0.21796 | 0.21752 | 0.21708 | 0.21664 | 0.21626 | 0.21589 | 0.21553 | 0.21518 | 0.21355 | 0.21116 | 0.20933 | 0.21701 | 0.21694 | 0.21691 | 0.21683 | 0.21672 | 0.2166 | 0.21646 | 0.21641 | 0.21636 | 0.21631 | 0.21627 | 0.21605 | 0.21381 | 0.21195
|  | NORTH HOY | FS |  |  |  | 0 | 0.22306 | 0.223 | 0.223 | 0.223 | 0.22299 | 0.22298 | 0.22298 | 0.22295 | 0.22292 | 0.22289 | 0.22285 | 0.22275 | 0.22225 | 0.22116 | 0.21854 | 0.21846 | 0.21844 | 0.2184 | 0.21829 | 0.21806 | 0.21783 | 0.21755 | 0.21726 | 0.21697 | 0.21668 | 0.21533 | 0.21368 | 0.2115 | 0.21701 | 0.21695 | 0.21694 | 0.21694 | 0.21694 | 0.21693 | 0.21692 | 0.2169 | 0.21687 | 0.21683 | 0.2168 | 0.2167 | 0.2162 | 0.21416
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 0 | 4.3747 | 4.3629 | 4.353 | 4.3269 | 4.2855 | 4.2445 | 4.2039 | 4.1644 | 4.1253 | 4.0865 | 4.0485 | 3.8472 | 3.5997 | 3.2507 | 4.1986 | 4.1683 | 4.1405 | 4.0946 | 4.0481 | 4.0023 | 3.957 | 3.9127 | 3.8689 | 3.8255 | 3.7829 | 3.5596 | 3.2911 | 2.923 | 4.2109 | 4.1868 | 4.1634 | 4.1176 | 4.0711 | 4.0253 | 3.9802 | 3.9359 | 3.8921 | 3.8488 | 3.8063 | 3.7645 | 3.7202 | 3.6755
|  | NORTH KESSOCK | CT |  |  |  | 0 | 4.3747 | 4.3643 | 4.3548 | 4.3434 | 4.3172 | 4.285 | 4.2538 | 4.2246 | 4.1956 | 4.1669 | 4.1385 | 3.9864 | 3.8024 | 3.5776 | 4.1986 | 4.1773 | 4.1548 | 4.1203 | 4.0849 | 4.0493 | 4.0148 | 3.9822 | 3.9498 | 3.9178 | 3.8862 | 3.7186 | 3.519 | 3.2793 | 4.2109 | 4.1932 | 4.1751 | 4.1432 | 4.1078 | 4.0723 | 4.0378 | 4.0053 | 3.9729 | 3.941 | 3.9094 | 3.8779 | 3.8447 | 3.8113
|  | NORTH KESSOCK | LW |  |  |  | 0 | 4.3823 | 4.3629 | 4.353 | 4.3269 | 4.2855 | 4.2445 | 4.2039 | 4.1644 | 4.1253 | 4.0865 | 4.0485 | 3.8472 | 3.5997 | 3.2507 | 4.2027 | 4.1683 | 4.1405 | 4.0946 | 4.0481 | 4.0023 | 3.957 | 3.9127 | 3.8689 | 3.8255 | 3.7829 | 3.5596 | 3.2911 | 2.923 | 4.2162 | 4.1868 | 4.1634 | 4.1176 | 4.0711 | 4.0253 | 3.9802 | 3.9359 | 3.8921 | 3.8488 | 3.8063 | 3.7645 | 3.7202 | 3.6755
|  | NORTH KESSOCK | ST |  |  |  | 0 | 4.3832 | 4.38 | 4.3781 | 4.3743 | 4.3699 | 4.3648 | 4.3593 | 4.3553 | 4.3408 | 4.3268 | 4.3132 | 4.2495 | 4.161 | 4.0893 | 4.2246 | 4.2207 | 4.2182 | 4.1994 | 4.1802 | 4.1612 | 4.1422 | 4.1252 | 4.1085 | 4.0923 | 4.0765 | 4.0029 | 3.9051 | 3.8245 | 4.2311 | 4.2275 | 4.2251 | 4.2113 | 4.197 | 4.1827 | 4.1651 | 4.1481 | 4.1314 | 4.1152 | 4.0995 | 4.026 | 3.9283 | 3.8478
|  | NORTH KESSOCK | FS |  |  |  | 0 | 4.384 | 4.3811 | 4.3802 | 4.3792 | 4.3782 | 4.3771 | 4.3761 | 4.3743 | 4.3725 | 4.3706 | 4.3685 | 4.322 | 4.2621 | 4.1861 | 4.2267 | 4.2233 | 4.2218 | 4.2196 | 4.2138 | 4.2034 | 4.193 | 4.1807 | 4.1683 | 4.1558 | 4.1432 | 4.0847 | 4.0173 | 3.9343 | 4.2328 | 4.2296 | 4.2282 | 4.2264 | 4.2222 | 4.2149 | 4.2077 | 4.1989 | 4.19 | 4.1787 | 4.1661 | 4.1077 | 4.0404 | 3.9575
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0.035789 | 1.7923 | 1.7538 | 1.7203 | 1.6659 | 1.6104 | 1.5551 | 1.4993 | 1.4447 | 1.3905 | 1.3366 | 1.2835 | 1.0054 | 0.64497 | 0.16047 | 1.5766 | 1.5615 | 1.5501 | 1.5349 | 1.4815 | 1.4114 | 1.3412 | 1.2713 | 1.2019 | 1.133 | 1.0651 | 0.71536 | 0.31117 | -0.21096 | 1.6294 | 1.5818 | 1.5394 | 1.4694 | 1.3987 | 1.3287 | 1.2587 | 1.1889 | 1.1197 | 1.0509 | 0.98318 | 0.91632 | 0.84646 | 0.77618
|  | NOSTIE BRIDGE | CT |  |  |  | 0.035789 | 1.7923 | 1.7671 | 1.7412 | 1.7014 | 1.6602 | 1.6184 | 1.5766 | 1.537 | 1.4976 | 1.4585 | 1.4197 | 1.2154 | 0.97146 | 0.66803 | 1.5766 | 1.5651 | 1.5546 | 1.542 | 1.5275 | 1.4954 | 1.4436 | 1.3933 | 1.3431 | 1.2935 | 1.2443 | 0.99008 | 0.69518 | 0.35366 | 1.6296 | 1.5989 | 1.5669 | 1.5162 | 1.4644 | 1.4125 | 1.3608 | 1.3106 | 1.2606 | 1.211 | 1.1619 | 1.113 | 1.0628 | 1.0116
|  | NOSTIE BRIDGE | LW |  |  |  | 0.035789 | 1.7944 | 1.7538 | 1.7203 | 1.6659 | 1.6104 | 1.5551 | 1.4993 | 1.4447 | 1.3905 | 1.3366 | 1.2835 | 1.0054 | 0.64497 | 0.16047 | 1.5842 | 1.5615 | 1.5501 | 1.5349 | 1.4815 | 1.4114 | 1.3412 | 1.2713 | 1.2019 | 1.133 | 1.0651 | 0.71536 | 0.31117 | -0.21096 | 1.6294 | 1.5818 | 1.5394 | 1.4694 | 1.3987 | 1.3287 | 1.2587 | 1.1889 | 1.1197 | 1.0509 | 0.98318 | 0.91632 | 0.84646 | 0.77618
|  | NOSTIE BRIDGE | ST |  |  |  | 0.035789 | 1.8194 | 1.8143 | 1.8105 | 1.7885 | 1.7652 | 1.7419 | 1.7184 | 1.6975 | 1.6769 | 1.6568 | 1.637 | 1.543 | 1.4189 | 1.3147 | 1.585 | 1.5815 | 1.5794 | 1.575 | 1.57 | 1.5642 | 1.5578 | 1.5549 | 1.5519 | 1.534 | 1.5074 | 1.3807 | 1.2253 | 1.091 | 1.666 | 1.6598 | 1.655 | 1.6249 | 1.5944 | 1.564 | 1.5338 | 1.5057 | 1.4781 | 1.4511 | 1.4246 | 1.2982 | 1.1432 | 1.0091
|  | NOSTIE BRIDGE | FS |  |  |  | 0.035789 | 1.8205 | 1.8163 | 1.8138 | 1.8108 | 1.8046 | 1.7919 | 1.7791 | 1.7639 | 1.7485 | 1.733 | 1.7175 | 1.6441 | 1.5589 | 1.454 | 1.585 | 1.5818 | 1.5808 | 1.5799 | 1.5788 | 1.5777 | 1.5766 | 1.5747 | 1.5727 | 1.5706 | 1.5684 | 1.5117 | 1.4016 | 1.273 | 1.6677 | 1.6629 | 1.6594 | 1.6552 | 1.6459 | 1.6285 | 1.6112 | 1.5906 | 1.5699 | 1.5491 | 1.5282 | 1.4289 | 1.319 | 1.1907
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 0.21579 | 26.8739 | 26.7953 | 26.76 | 26.7108 | 26.6549 | 26.5934 | 26.5283 | 26.477 | 26.4245 | 26.1588 | 25.8802 | 24.4856 | 22.9179 | 20.8609 | 26.1686 | 26.09 | 26.0547 | 26.0055 | 25.9496 | 25.8881 | 25.823 | 25.6198 | 25.277 | 24.9422 | 24.6243 | 23.045 | 21.2977 | 19.0636 | 26.836 | 26.7574 | 26.722 | 26.6729 | 26.617 | 26.5555 | 26.4357 | 26.0881 | 25.7492 | 25.4181 | 25.1038 | 24.8021 | 24.4861 | 24.1709
|  | OBAN | CT |  |  |  | 0.21579 | 26.8739 | 26.8472 | 26.8246 | 26.7939 | 26.7563 | 26.7119 | 26.664 | 26.6326 | 26.5996 | 26.5664 | 26.5327 | 25.9263 | 24.8291 | 23.5352 | 26.1686 | 26.1419 | 26.1193 | 26.0886 | 26.051 | 26.0066 | 25.9587 | 25.9273 | 25.8943 | 25.8611 | 25.798 | 24.6803 | 23.4574 | 22.04 | 26.836 | 26.8093 | 26.7866 | 26.7559 | 26.7183 | 26.6739 | 26.626 | 26.5946 | 26.5617 | 26.4817 | 26.2647 | 26.0473 | 25.8214 | 25.6
|  | OBAN | LW |  |  |  | 0.21579 | 26.8748 | 26.7953 | 26.76 | 26.7108 | 26.6549 | 26.5934 | 26.5283 | 26.477 | 26.4245 | 26.1588 | 25.8802 | 24.4856 | 22.9179 | 20.8609 | 26.1695 | 26.09 | 26.0547 | 26.0055 | 25.9496 | 25.8881 | 25.823 | 25.6198 | 25.277 | 24.9422 | 24.6243 | 23.045 | 21.2977 | 19.0636 | 26.8368 | 26.7574 | 26.722 | 26.6729 | 26.617 | 26.5555 | 26.4357 | 26.0881 | 25.7492 | 25.4181 | 25.1038 | 24.8021 | 24.4861 | 24.1709
|  | OBAN | ST |  |  |  | 0.21579 | 26.8748 | 26.8641 | 26.8589 | 26.8451 | 26.8283 | 26.8087 | 26.7867 | 26.7785 | 26.7702 | 26.7623 | 26.7547 | 26.7197 | 26.5384 | 26.1718 | 26.1695 | 26.1588 | 26.1536 | 26.1398 | 26.123 | 26.1034 | 26.0814 | 26.0732 | 26.0649 | 26.057 | 26.0494 | 26.0144 | 25.5778 | 24.9447 | 26.8368 | 26.8261 | 26.821 | 26.8072 | 26.7904 | 26.7707 | 26.7488 | 26.7406 | 26.7323 | 26.7243 | 26.7168 | 26.6817 | 26.0474 | 25.4216
|  | OBAN | FS |  |  |  | 0.21579 | 26.8748 | 26.864 | 26.8635 | 26.8629 | 26.8621 | 26.8609 | 26.8597 | 26.8551 | 26.8498 | 26.8441 | 26.8378 | 26.8212 | 26.7338 | 26.541 | 26.1695 | 26.1587 | 26.1582 | 26.1576 | 26.1568 | 26.1556 | 26.1544 | 26.1498 | 26.1445 | 26.1388 | 26.1325 | 26.1159 | 26.0285 | 25.7371 | 26.8368 | 26.826 | 26.8256 | 26.825 | 26.8241 | 26.8229 | 26.8217 | 26.8171 | 26.8119 | 26.8061 | 26.7999 | 26.7833 | 26.6959 | 26.2047
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 0.11368 | 12.1269 | 12.0701 | 12.0442 | 12.008 | 11.9669 | 11.9217 | 11.874 | 11.8364 | 11.798 | 11.758 | 11.7186 | 11.4719 | 11.0799 | 10.2766 | 11.6265 | 11.5697 | 11.5437 | 11.5076 | 11.4665 | 11.4213 | 11.3735 | 11.3359 | 11.2976 | 11.2576 | 11.2163 | 10.572 | 9.6869 | 8.4338 | 12.0681 | 12.0114 | 11.9854 | 11.9492 | 11.9081 | 11.8629 | 11.8152 | 11.7776 | 11.7392 | 11.6992 | 11.6599 | 11.615 | 11.4704 | 11.3245
|  | OLD CRAIGIE ROAD | CT |  |  |  | 0.11368 | 12.1269 | 12.1063 | 12.0886 | 12.0651 | 12.0364 | 12.0027 | 11.9665 | 11.9425 | 11.9174 | 11.8921 | 11.8665 | 11.6981 | 11.4249 | 11.0011 | 11.6265 | 11.6058 | 11.5882 | 11.5646 | 11.5359 | 11.5023 | 11.4661 | 11.4421 | 11.417 | 11.3917 | 11.3661 | 11.1931 | 10.5967 | 9.8291 | 12.0681 | 12.0475 | 12.0299 | 12.0063 | 11.9776 | 11.9439 | 11.9077 | 11.8837 | 11.8587 | 11.8334 | 11.8078 | 11.7811 | 11.7474 | 11.7127
|  | OLD CRAIGIE ROAD | LW |  |  |  | 0.11368 | 12.1286 | 12.0701 | 12.0442 | 12.008 | 11.9669 | 11.9217 | 11.874 | 11.8364 | 11.798 | 11.758 | 11.7186 | 11.4719 | 11.0799 | 10.2766 | 11.6282 | 11.5697 | 11.5437 | 11.5076 | 11.4665 | 11.4213 | 11.3735 | 11.3359 | 11.2976 | 11.2576 | 11.2163 | 10.572 | 9.6869 | 8.4338 | 12.0698 | 12.0114 | 11.9854 | 11.9492 | 11.9081 | 11.8629 | 11.8152 | 11.7776 | 11.7392 | 11.6992 | 11.6599 | 11.615 | 11.4704 | 11.3245
|  | OLD CRAIGIE ROAD | ST |  |  |  | 0.11368 | 12.1294 | 12.1216 | 12.1179 | 12.1078 | 12.0955 | 12.0811 | 12.065 | 12.059 | 12.053 | 12.0472 | 12.0416 | 12.0161 | 11.8853 | 11.8172 | 11.629 | 11.6212 | 11.6174 | 11.6073 | 11.5951 | 11.5807 | 11.5646 | 11.5586 | 11.5526 | 11.5468 | 11.5412 | 11.5157 | 11.3849 | 11.3134 | 12.0707 | 12.0628 | 12.0591 | 12.049 | 12.0367 | 12.0223 | 12.0063 | 12.0003 | 11.9942 | 11.9884 | 11.9829 | 11.9574 | 11.8265 | 11.7585
|  | OLD CRAIGIE ROAD | FS |  |  |  | 0.11368 | 12.1294 | 12.1217 | 12.1214 | 12.121 | 12.1203 | 12.1195 | 12.1186 | 12.1153 | 12.1116 | 12.1075 | 12.103 | 12.0911 | 12.0287 | 11.8913 | 11.629 | 11.6213 | 11.6209 | 11.6205 | 11.6199 | 11.6191 | 11.6182 | 11.6149 | 11.6112 | 11.6071 | 11.6026 | 11.5907 | 11.5283 | 11.3909 | 12.0707 | 12.0629 | 12.0626 | 12.0622 | 12.0616 | 12.0607 | 12.0599 | 12.0566 | 12.0528 | 12.0487 | 12.0442 | 12.0324 | 11.9699 | 11.8325
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 0.40842 | 8.9703 | 8.9351 | 8.9081 | 8.7001 | 8.4757 | 8.2621 | 8.0661 | 7.8683 | 7.6564 | 7.453 | 7.269 | 6.4007 | 5.4915 | 4.3399 | 8.4196 | 8.2374 | 7.9899 | 7.6807 | 7.3833 | 7.1025 | 6.8472 | 6.5876 | 6.3403 | 6.1033 | 5.8896 | 4.892 | 3.8704 | 2.6153 | 8.7411 | 8.7059 | 8.5216 | 8.2222 | 7.9341 | 7.6619 | 7.4141 | 7.1626 | 6.9228 | 6.6929 | 6.4855 | 6.2951 | 6.0986 | 5.9027
|  | OLDMELDRUM | CT |  |  |  | 0.40842 | 8.9703 | 8.9421 | 8.9167 | 8.886 | 8.8063 | 8.6384 | 8.4907 | 8.3501 | 8.2114 | 8.0827 | 7.9618 | 7.3225 | 6.6479 | 5.8791 | 8.4196 | 8.3846 | 8.2565 | 8.0515 | 7.8375 | 7.6184 | 7.4283 | 7.244 | 7.063 | 6.8958 | 6.7397 | 5.9821 | 5.2274 | 4.3841 | 8.7411 | 8.7129 | 8.6874 | 8.5801 | 8.3725 | 8.16 | 7.9753 | 7.7966 | 7.621 | 7.4587 | 7.3071 | 7.1559 | 7.0042 | 6.858
|  | OLDMELDRUM | LW |  |  |  | 0.40842 | 8.9896 | 8.9351 | 8.9081 | 8.7001 | 8.4757 | 8.2621 | 8.0661 | 7.8683 | 7.6564 | 7.453 | 7.269 | 6.4007 | 5.4915 | 4.3399 | 8.4337 | 8.2374 | 7.9899 | 7.6807 | 7.3833 | 7.1025 | 6.8472 | 6.5876 | 6.3403 | 6.1033 | 5.8896 | 4.892 | 3.8704 | 2.6153 | 8.7604 | 8.7059 | 8.5216 | 8.2222 | 7.9341 | 7.6619 | 7.4141 | 7.1626 | 6.9228 | 6.6929 | 6.4855 | 6.2951 | 6.0986 | 5.9027
|  | OLDMELDRUM | ST |  |  |  | 0.40842 | 8.993 | 8.9842 | 8.9786 | 8.968 | 8.9547 | 8.9397 | 8.9234 | 8.9152 | 8.8994 | 8.8233 | 8.751 | 8.42 | 8.0723 | 7.7811 | 8.4478 | 8.4367 | 8.4286 | 8.4128 | 8.3793 | 8.2666 | 8.1615 | 8.0542 | 7.9452 | 7.8421 | 7.7438 | 7.2954 | 6.8549 | 6.488 | 8.7638 | 8.755 | 8.7494 | 8.7388 | 8.7255 | 8.7105 | 8.6875 | 8.5838 | 8.4785 | 8.3788 | 8.2838 | 7.8503 | 7.4217 | 7.0656
|  | OLDMELDRUM | FS |  |  |  | 0.40842 | 8.9947 | 8.9873 | 8.9854 | 8.9834 | 8.9813 | 8.979 | 8.9767 | 8.9725 | 8.9681 | 8.9634 | 8.9584 | 8.7322 | 8.4837 | 8.1985 | 8.4505 | 8.4413 | 8.4374 | 8.4332 | 8.428 | 8.4218 | 8.3956 | 8.3162 | 8.2329 | 8.1512 | 8.0703 | 7.6994 | 7.3744 | 7.018 | 8.7655 | 8.7581 | 8.7562 | 8.7542 | 8.7521 | 8.7498 | 8.7474 | 8.7433 | 8.7389 | 8.679 | 8.6009 | 8.2426 | 7.9273 | 7.58
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 0.031579 | 9.0074 | 16.0145 | 15.9838 | 15.9417 | 15.8947 | 15.8429 | 15.7885 | 15.7437 | 15.6983 | 15.6474 | 15.5052 | 14.7488 | 13.8267 | 12.5444 | 8.5825 | 14.8396 | 14.8089 | 14.7669 | 14.7198 | 14.5956 | 14.4293 | 14.2653 | 14.1023 | 13.9403 | 13.7798 | 12.933 | 11.9183 | 10.5437 | 8.5689 | 15.201 | 15.1703 | 15.1283 | 15.0813 | 15.0294 | 14.9751 | 14.8256 | 14.67 | 14.5152 | 14.3618 | 14.2102 | 14.0474 | 13.8833
|  | ORMLIE | CT |  |  |  | 0.031579 | 9.0074 | 16.0251 | 15.9959 | 15.9605 | 15.9199 | 15.8742 | 15.8269 | 15.7914 | 15.7541 | 15.7166 | 15.6789 | 15.2953 | 14.6103 | 13.7724 | 8.5825 | 14.8502 | 14.821 | 14.7857 | 14.745 | 14.6994 | 14.6521 | 14.5435 | 14.4239 | 14.3054 | 14.1878 | 13.5605 | 12.811 | 11.9096 | 8.5689 | 15.2116 | 15.1824 | 15.1471 | 15.1064 | 15.0608 | 15.0135 | 14.9779 | 14.9406 | 14.8616 | 14.7489 | 14.6363 | 14.5154 | 14.3938
|  | ORMLIE | LW |  |  |  | 0.031579 | 9.0276 | 16.0145 | 15.9838 | 15.9417 | 15.8947 | 15.8429 | 15.7885 | 15.7437 | 15.6983 | 15.6474 | 15.5052 | 14.7488 | 13.8267 | 12.5444 | 8.6027 | 14.8396 | 14.8089 | 14.7669 | 14.7198 | 14.5956 | 14.4293 | 14.2653 | 14.1023 | 13.9403 | 13.7798 | 12.933 | 11.9183 | 10.5437 | 8.5891 | 15.201 | 15.1703 | 15.1283 | 15.0813 | 15.0294 | 14.9751 | 14.8256 | 14.67 | 14.5152 | 14.3618 | 14.2102 | 14.0474 | 13.8833
|  | ORMLIE | ST |  |  |  | 0.031579 | 9.0318 | 16.0714 | 16.0651 | 16.0525 | 16.0368 | 16.0189 | 15.9994 | 15.99 | 15.9806 | 15.9714 | 15.9625 | 15.9203 | 15.777 | 15.5578 | 8.6069 | 14.8965 | 14.8902 | 14.8776 | 14.8619 | 14.8441 | 14.8246 | 14.8152 | 14.8057 | 14.7965 | 14.7876 | 14.5341 | 14.1481 | 13.8261 | 8.5934 | 15.258 | 15.2517 | 15.239 | 15.2233 | 15.2055 | 15.186 | 15.1766 | 15.1671 | 15.1579 | 15.149 | 15.0887 | 14.7179 | 14.4105
|  | ORMLIE | FS |  |  |  | 0.031579 | 9.0343 | 16.0752 | 16.0724 | 16.0695 | 16.0663 | 16.0638 | 16.0613 | 16.0565 | 16.0512 | 16.0456 | 16.0396 | 16.0164 | 15.9442 | 15.8011 | 8.6095 | 14.9004 | 14.8975 | 14.8946 | 14.8915 | 14.889 | 14.8865 | 14.8816 | 14.8763 | 14.8707 | 14.8647 | 14.8415 | 14.5859 | 14.2527 | 8.5959 | 15.2618 | 15.2589 | 15.256 | 15.2529 | 15.2504 | 15.2479 | 15.243 | 15.2377 | 15.2321 | 15.2261 | 15.2029 | 15.1308 | 14.8174
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0 | 1.1398 | 1.1296 | 1.1188 | 1.104 | 1.0889 | 1.0713 | 1.0529 | 1.0353 | 1.0177 | 1.0001 | 0.98281 | 0.89062 | 0.77323 | 0.6204 | 1.2688 | 1.2572 | 1.2447 | 1.2271 | 1.2055 | 1.1841 | 1.162 | 1.1404 | 1.119 | 1.0977 | 1.0767 | 0.96621 | 0.83852 | 0.67769 | 1.1057 | 1.0997 | 1.0939 | 1.0875 | 1.0806 | 1.0734 | 1.0659 | 1.0595 | 1.0531 | 1.0467 | 1.0402 | 1.0337 | 1.0215 | 0.99948
|  | OTTER FERRY | CT |  |  |  | 0 | 1.1398 | 1.1296 | 1.1188 | 1.104 | 1.089 | 1.0737 | 1.0585 | 1.0435 | 1.0286 | 1.0137 | 0.99894 | 0.92031 | 0.8271 | 0.71422 | 1.2688 | 1.2572 | 1.2447 | 1.2272 | 1.2094 | 1.1915 | 1.1738 | 1.1559 | 1.1382 | 1.1205 | 1.103 | 1.0112 | 0.90443 | 0.78252 | 1.1057 | 1.0997 | 1.0939 | 1.0875 | 1.0806 | 1.0734 | 1.0659 | 1.0595 | 1.0531 | 1.0467 | 1.0402 | 1.0337 | 1.0258 | 1.0177
|  | OTTER FERRY | LW |  |  |  | 0 | 1.1467 | 1.1348 | 1.1238 | 1.1065 | 1.0889 | 1.0713 | 1.0529 | 1.0353 | 1.0177 | 1.0001 | 0.98281 | 0.89062 | 0.77323 | 0.6204 | 1.2754 | 1.2616 | 1.2485 | 1.2271 | 1.2055 | 1.1841 | 1.162 | 1.1404 | 1.119 | 1.0977 | 1.0767 | 0.96621 | 0.83852 | 0.67769 | 1.1133 | 1.1069 | 1.1027 | 1.0976 | 1.092 | 1.0861 | 1.0791 | 1.073 | 1.067 | 1.0608 | 1.0548 | 1.0422 | 1.0215 | 0.99948
|  | OTTER FERRY | ST |  |  |  | 0 | 1.1552 | 1.1528 | 1.1508 | 1.1436 | 1.1363 | 1.1289 | 1.1215 | 1.1141 | 1.1068 | 1.0996 | 1.0925 | 1.0595 | 1.0207 | 0.98455 | 1.2861 | 1.2835 | 1.2813 | 1.2722 | 1.2631 | 1.254 | 1.2449 | 1.2355 | 1.2262 | 1.2171 | 1.208 | 1.1662 | 1.1196 | 1.0759 | 1.115 | 1.1135 | 1.1123 | 1.1106 | 1.1086 | 1.1065 | 1.1043 | 1.1029 | 1.1015 | 1.1002 | 1.0988 | 1.0924 | 1.0774 | 1.0614
|  | OTTER FERRY | FS |  |  |  | 0 | 1.1568 | 1.1553 | 1.1536 | 1.1518 | 1.1488 | 1.1441 | 1.1395 | 1.1344 | 1.1292 | 1.1241 | 1.1189 | 1.0941 | 1.0662 | 1.0333 | 1.2883 | 1.2867 | 1.2848 | 1.2827 | 1.279 | 1.2731 | 1.2672 | 1.2608 | 1.2543 | 1.2478 | 1.2413 | 1.21 | 1.1759 | 1.137 | 1.115 | 1.1136 | 1.1127 | 1.1118 | 1.1109 | 1.11 | 1.1091 | 1.108 | 1.1069 | 1.1057 | 1.1045 | 1.0993 | 1.0903 | 1.0755
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 0.35789 | 42.276 | 42.2571 | 42.2463 | 42.2299 | 42.2122 | 42.1401 | 42.0489 | 41.9538 | 41.8581 | 41.7618 | 41.6652 | 41.1553 | 40.5638 | 39.8131 | 39.6092 | 39.5515 | 39.4934 | 39.3926 | 39.2903 | 39.1872 | 39.0836 | 38.9751 | 38.866 | 38.7562 | 38.6461 | 38.0677 | 37.4041 | 36.5786 | 40.6095 | 40.5516 | 40.4933 | 40.3922 | 40.2896 | 40.1862 | 40.0822 | 39.9734 | 39.8639 | 39.7538 | 39.6434 | 39.5327 | 39.4151 | 39.2979
|  | OVERGATE | CT |  |  |  | 0.35789 | 42.276 | 42.2689 | 42.2623 | 42.2521 | 42.2407 | 42.2277 | 42.2029 | 42.1376 | 42.0717 | 42.0055 | 41.9388 | 41.5862 | 41.1742 | 40.6922 | 39.6182 | 39.5823 | 39.5426 | 39.473 | 39.402 | 39.3299 | 39.2573 | 39.1826 | 39.1072 | 39.0315 | 38.9554 | 38.5548 | 38.0922 | 37.558 | 40.6185 | 40.5825 | 40.5427 | 40.4728 | 40.4016 | 40.3293 | 40.2564 | 40.1815 | 40.1059 | 40.0299 | 39.9535 | 39.8765 | 39.7948 | 39.7137
|  | OVERGATE | LW |  |  |  | 0.35789 | 42.2761 | 42.2571 | 42.2463 | 42.2299 | 42.2122 | 42.1401 | 42.0489 | 41.9538 | 41.8581 | 41.7618 | 41.6652 | 41.1553 | 40.5638 | 39.8131 | 39.6092 | 39.5515 | 39.4934 | 39.3926 | 39.2903 | 39.1872 | 39.0836 | 38.9751 | 38.866 | 38.7562 | 38.6461 | 38.0677 | 37.4041 | 36.5786 | 40.6095 | 40.5516 | 40.4933 | 40.3922 | 40.2896 | 40.1862 | 40.0822 | 39.9734 | 39.8639 | 39.7538 | 39.6434 | 39.5327 | 39.4151 | 39.2979
|  | OVERGATE | ST |  |  |  | 0.35789 | 42.28 | 42.2771 | 42.2755 | 42.2692 | 42.2623 | 42.2548 | 42.2467 | 42.2415 | 42.2363 | 42.2311 | 42.212 | 42.0018 | 41.7481 | 41.5123 | 39.6635 | 39.6552 | 39.6472 | 39.6011 | 39.5542 | 39.507 | 39.4594 | 39.4109 | 39.3625 | 39.3141 | 39.2658 | 39.0234 | 38.7372 | 38.468 | 40.664 | 40.6556 | 40.6476 | 40.6014 | 40.5543 | 40.507 | 40.4592 | 40.4105 | 40.3619 | 40.3134 | 40.2649 | 40.0217 | 39.7346 | 39.4645
|  | OVERGATE | FS |  |  |  | 0.35789 | 42.2799 | 42.2765 | 42.276 | 42.2753 | 42.2739 | 42.2713 | 42.2687 | 42.2648 | 42.2607 | 42.2565 | 42.2521 | 42.1812 | 41.9979 | 41.783 | 39.6626 | 39.6553 | 39.65 | 39.6421 | 39.6258 | 39.5936 | 39.5614 | 39.524 | 39.4865 | 39.4489 | 39.4111 | 39.2282 | 39.0198 | 38.7799 | 40.663 | 40.6557 | 40.6504 | 40.6425 | 40.6262 | 40.5938 | 40.5615 | 40.524 | 40.4864 | 40.4486 | 40.4107 | 40.2271 | 40.0181 | 39.7776
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0 | 0.1503 | 0.14856 | 0.14682 | 0.14506 | 0.14329 | 0.1415 | 0.1397 | 0.13795 | 0.13619 | 0.13443 | 0.13267 | 0.12124 | 0.10787 | 0.091833 | 0.14948 | 0.14774 | 0.146 | 0.14424 | 0.14247 | 0.14068 | 0.13888 | 0.13713 | 0.13537 | 0.13361 | 0.13185 | 0.12042 | 0.10628 | 0.090049 | 0.14877 | 0.14703 | 0.14529 | 0.14353 | 0.14176 | 0.13997 | 0.13817 | 0.13642 | 0.13466 | 0.1329 | 0.13114 | 0.12938 | 0.1276 | 0.12497
|  | OVERSCAIG | CT |  |  |  | 0 | 0.1503 | 0.14856 | 0.14682 | 0.14506 | 0.14329 | 0.1415 | 0.1397 | 0.13795 | 0.13619 | 0.13443 | 0.13267 | 0.12124 | 0.10787 | 0.091833 | 0.14948 | 0.14774 | 0.146 | 0.14424 | 0.14247 | 0.14068 | 0.13888 | 0.13713 | 0.13537 | 0.13361 | 0.13185 | 0.12042 | 0.10628 | 0.090049 | 0.14877 | 0.14703 | 0.14529 | 0.14353 | 0.14176 | 0.13997 | 0.13817 | 0.13642 | 0.13466 | 0.1329 | 0.13114 | 0.12938 | 0.1276 | 0.12497
|  | OVERSCAIG | LW |  |  |  | 0 | 0.15283 | 0.15179 | 0.15087 | 0.1499 | 0.14892 | 0.14793 | 0.14694 | 0.14597 | 0.14501 | 0.14404 | 0.14308 | 0.13542 | 0.12487 | 0.11085 | 0.15201 | 0.15097 | 0.15005 | 0.14908 | 0.1481 | 0.14711 | 0.14612 | 0.14515 | 0.14419 | 0.14322 | 0.14226 | 0.13372 | 0.12297 | 0.10875 | 0.1513 | 0.15026 | 0.14934 | 0.14837 | 0.14739 | 0.1464 | 0.14541 | 0.14444 | 0.14348 | 0.14251 | 0.14155 | 0.14059 | 0.1396 | 0.13776
|  | OVERSCAIG | ST |  |  |  | 0 | 0.15451 | 0.15365 | 0.1528 | 0.15192 | 0.15105 | 0.15016 | 0.14927 | 0.14841 | 0.14755 | 0.14669 | 0.14584 | 0.14155 | 0.13699 | 0.1326 | 0.15369 | 0.15283 | 0.15198 | 0.1511 | 0.15023 | 0.14934 | 0.14845 | 0.14759 | 0.14673 | 0.14587 | 0.14502 | 0.14073 | 0.13617 | 0.13178 | 0.15298 | 0.15212 | 0.15127 | 0.15039 | 0.14952 | 0.14863 | 0.14774 | 0.14688 | 0.14602 | 0.14516 | 0.14431 | 0.14002 | 0.13546 | 0.13107
|  | OVERSCAIG | FS |  |  |  | 0 | 0.15451 | 0.15449 | 0.15449 | 0.15449 | 0.15449 | 0.15449 | 0.15449 | 0.15448 | 0.15447 | 0.15446 | 0.15445 | 0.15442 | 0.15426 | 0.15392 | 0.15369 | 0.15367 | 0.15367 | 0.15367 | 0.15367 | 0.15367 | 0.15367 | 0.15366 | 0.15365 | 0.15364 | 0.15363 | 0.1536 | 0.15344 | 0.1531 | 0.15298 | 0.15296 | 0.15296 | 0.15296 | 0.15296 | 0.15296 | 0.15296 | 0.15295 | 0.15294 | 0.15293 | 0.15292 | 0.15288 | 0.15273 | 0.15239
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0.022105 | 1.6218 | 1.6031 | 1.5855 | 1.5657 | 1.5442 | 1.5211 | 1.498 | 1.4783 | 1.4338 | 1.3641 | 1.2984 | 0.97357 | 0.60765 | 0.12771 | 1.3271 | 1.2618 | 1.1992 | 1.1077 | 1.017 | 0.92987 | 0.8472 | 0.76468 | 0.68368 | 0.60502 | 0.531 | 0.16942 | -0.23037 | -0.74243 | 1.36 | 1.296 | 1.2325 | 1.1468 | 1.062 | 0.98036 | 0.90267 | 0.82542 | 0.74947 | 0.67566 | 0.60611 | 0.54154 | 0.47338 | 0.40391
|  | PARK | CT |  |  |  | 0.022105 | 1.6218 | 1.6031 | 1.5855 | 1.5657 | 1.5442 | 1.5211 | 1.498 | 1.4783 | 1.4575 | 1.4368 | 1.4159 | 1.1793 | 0.88029 | 0.53517 | 1.3271 | 1.2802 | 1.2306 | 1.1662 | 1.0961 | 1.0239 | 0.95821 | 0.89479 | 0.83166 | 0.77174 | 0.71408 | 0.41733 | 0.094321 | -0.27303 | 1.36 | 1.3148 | 1.2647 | 1.1997 | 1.1326 | 1.0645 | 1.0024 | 0.94262 | 0.88304 | 0.8264 | 0.77184 | 0.71742 | 0.66107 | 0.60448
|  | PARK | LW |  |  |  | 0.022105 | 1.6429 | 1.6187 | 1.6053 | 1.5874 | 1.5669 | 1.5452 | 1.5218 | 1.502 | 1.4338 | 1.3641 | 1.2984 | 0.97357 | 0.60765 | 0.12771 | 1.3299 | 1.2618 | 1.1992 | 1.1077 | 1.017 | 0.92987 | 0.8472 | 0.76468 | 0.68368 | 0.60502 | 0.531 | 0.16942 | -0.23037 | -0.74243 | 1.3639 | 1.296 | 1.2325 | 1.1468 | 1.062 | 0.98036 | 0.90267 | 0.82542 | 0.74947 | 0.67566 | 0.60611 | 0.54154 | 0.47338 | 0.40391
|  | PARK | ST |  |  |  | 0.022105 | 1.6463 | 1.6412 | 1.6375 | 1.6317 | 1.6243 | 1.6163 | 1.6077 | 1.6024 | 1.5971 | 1.5927 | 1.5884 | 1.5652 | 1.5099 | 1.4148 | 1.3774 | 1.3651 | 1.3533 | 1.3226 | 1.2897 | 1.2562 | 1.2244 | 1.1939 | 1.1602 | 1.1288 | 1.0978 | 0.95472 | 0.79626 | 0.66272 | 1.4088 | 1.3969 | 1.3856 | 1.3564 | 1.3243 | 1.2903 | 1.2581 | 1.2272 | 1.1958 | 1.1666 | 1.1378 | 1.0048 | 0.85501 | 0.72958
|  | PARK | FS |  |  |  | 0.022105 | 1.6488 | 1.6448 | 1.643 | 1.6412 | 1.6393 | 1.6374 | 1.6355 | 1.6328 | 1.63 | 1.6271 | 1.6241 | 1.6088 | 1.5797 | 1.5321 | 1.3853 | 1.375 | 1.3668 | 1.3572 | 1.3431 | 1.3234 | 1.3046 | 1.2821 | 1.2586 | 1.2359 | 1.213 | 1.0921 | 0.97664 | 0.85328 | 1.4164 | 1.4065 | 1.3987 | 1.3895 | 1.3761 | 1.3575 | 1.3392 | 1.3163 | 1.2925 | 1.2695 | 1.2463 | 1.1343 | 1.0261 | 0.9091
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 0.0063158 | 2.9377 | 2.9303 | 2.9234 | 2.9153 | 2.9055 | 2.8946 | 2.8833 | 2.874 | 2.8646 | 2.8543 | 2.8441 | 2.701 | 2.5034 | 2.2348 | 2.8183 | 2.8104 | 2.8031 | 2.7935 | 2.7822 | 2.7702 | 2.7578 | 2.7473 | 2.7345 | 2.6987 | 2.6633 | 2.4794 | 2.2623 | 1.9744 | 2.8127 | 2.8052 | 2.7984 | 2.7903 | 2.7804 | 2.7696 | 2.7582 | 2.749 | 2.7396 | 2.7292 | 2.719 | 2.6927 | 2.6577 | 2.6225
|  | PEDDIESTON | CT |  |  |  | 0.0063158 | 2.9377 | 2.9303 | 2.9234 | 2.9153 | 2.9062 | 2.8961 | 2.8855 | 2.8774 | 2.8691 | 2.8608 | 2.8525 | 2.7999 | 2.6658 | 2.4862 | 2.8183 | 2.8104 | 2.8031 | 2.7942 | 2.7842 | 2.7733 | 2.7619 | 2.7531 | 2.744 | 2.7349 | 2.7258 | 2.611 | 2.4488 | 2.2561 | 2.8127 | 2.8052 | 2.7984 | 2.7903 | 2.7811 | 2.771 | 2.7604 | 2.7523 | 2.7441 | 2.7358 | 2.7274 | 2.7189 | 2.7082 | 2.6973
|  | PEDDIESTON | LW |  |  |  | 0.0063158 | 2.9436 | 2.9308 | 2.9247 | 2.9156 | 2.9055 | 2.8946 | 2.8833 | 2.874 | 2.8646 | 2.8543 | 2.8441 | 2.701 | 2.5034 | 2.2348 | 2.824 | 2.8107 | 2.8038 | 2.7935 | 2.7822 | 2.7702 | 2.7578 | 2.7473 | 2.7345 | 2.6987 | 2.6633 | 2.4794 | 2.2623 | 1.9744 | 2.8186 | 2.8058 | 2.7996 | 2.7905 | 2.7804 | 2.7696 | 2.7582 | 2.749 | 2.7396 | 2.7292 | 2.719 | 2.6927 | 2.6577 | 2.6225
|  | PEDDIESTON | ST |  |  |  | 0.0063158 | 2.9445 | 2.9421 | 2.9405 | 2.9376 | 2.9344 | 2.9307 | 2.9267 | 2.9246 | 2.9226 | 2.9206 | 2.9187 | 2.9095 | 2.8806 | 2.8637 | 2.8257 | 2.8232 | 2.8216 | 2.8182 | 2.8144 | 2.8102 | 2.8056 | 2.8031 | 2.8005 | 2.798 | 2.7955 | 2.7839 | 2.7487 | 2.6806 | 2.8194 | 2.817 | 2.8154 | 2.8126 | 2.8093 | 2.8056 | 2.8016 | 2.7996 | 2.7976 | 2.7956 | 2.7936 | 2.7844 | 2.7555 | 2.7386
|  | PEDDIESTON | FS |  |  |  | 0.0063158 | 2.9453 | 2.943 | 2.9421 | 2.9412 | 2.9402 | 2.9392 | 2.9382 | 2.9368 | 2.9352 | 2.9336 | 2.9319 | 2.9255 | 2.9097 | 2.8802 | 2.8265 | 2.8242 | 2.8233 | 2.8223 | 2.8212 | 2.8198 | 2.8184 | 2.8165 | 2.8146 | 2.8125 | 2.8104 | 2.802 | 2.7843 | 2.753 | 2.8203 | 2.818 | 2.8171 | 2.8161 | 2.8152 | 2.8142 | 2.8132 | 2.8117 | 2.8102 | 2.8086 | 2.8069 | 2.8004 | 2.7847 | 2.7552
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 0.84947 | 27.4326 | 27.3145 | 27.2523 | 27.1669 | 26.6033 | 25.9499 | 25.3599 | 24.7609 | 24.1905 | 23.6457 | 23.1559 | 20.8534 | 18.4474 | 15.3488 | 25.9799 | 25.3164 | 24.6452 | 23.8147 | 23.0199 | 22.269 | 21.594 | 20.9043 | 20.2488 | 19.6236 | 19.0629 | 16.4523 | 13.7772 | 10.4273 | 26.5726 | 26.4544 | 26.0938 | 25.285 | 24.5106 | 23.7786 | 23.1201 | 22.4479 | 21.8088 | 21.1992 | 20.6522 | 20.1511 | 19.6316 | 19.1179
|  | PETERHEAD GRANGE | CT |  |  |  | 0.84947 | 27.4326 | 27.3781 | 27.3305 | 27.2692 | 27.1963 | 27.1124 | 26.8158 | 26.4013 | 25.996 | 25.6227 | 25.2742 | 23.5702 | 21.8408 | 19.8404 | 25.9799 | 25.8775 | 25.4465 | 24.9114 | 24.3494 | 23.7733 | 23.2785 | 22.8012 | 22.3353 | 21.9071 | 21.5082 | 19.5758 | 17.6553 | 15.475 | 26.5726 | 26.518 | 26.4704 | 26.3527 | 25.8049 | 25.2433 | 24.7603 | 24.2952 | 23.841 | 23.4234 | 23.0343 | 22.6462 | 22.2546 | 21.8791
|  | PETERHEAD GRANGE | LW |  |  |  | 0.84947 | 27.4495 | 27.3145 | 27.2523 | 27.1669 | 26.6033 | 25.9499 | 25.3599 | 24.7609 | 24.1905 | 23.6457 | 23.1559 | 20.8534 | 18.4474 | 15.3488 | 25.984 | 25.3164 | 24.6452 | 23.8147 | 23.0199 | 22.269 | 21.594 | 20.9043 | 20.2488 | 19.6236 | 19.0629 | 16.4523 | 13.7772 | 10.4273 | 26.5894 | 26.4544 | 26.0938 | 25.285 | 24.5106 | 23.7786 | 23.1201 | 22.4479 | 21.8088 | 21.1992 | 20.6522 | 20.1511 | 19.6316 | 19.1179
|  | PETERHEAD GRANGE | ST |  |  |  | 0.84947 | 27.4528 | 27.4329 | 27.422 | 27.397 | 27.3671 | 27.3326 | 27.2943 | 27.2784 | 27.2624 | 27.247 | 27.2321 | 26.4778 | 25.438 | 24.5838 | 26.0122 | 25.9871 | 25.9701 | 25.9334 | 25.7178 | 25.4205 | 25.1424 | 24.8609 | 24.5736 | 24.3003 | 24.0393 | 22.8553 | 21.6832 | 20.7059 | 26.5928 | 26.5728 | 26.5619 | 26.5369 | 26.5071 | 26.4725 | 26.4342 | 26.304 | 26.0246 | 25.7589 | 25.505 | 24.3536 | 23.2071 | 22.2536
|  | PETERHEAD GRANGE | FS |  |  |  | 0.84947 | 27.4545 | 27.4369 | 27.4345 | 27.4319 | 27.4289 | 27.4254 | 27.4218 | 27.413 | 27.4032 | 27.3926 | 27.3812 | 27.347 | 26.6023 | 25.7112 | 26.016 | 25.9941 | 25.987 | 25.979 | 25.9689 | 25.9219 | 25.7364 | 25.5223 | 25.2966 | 25.0749 | 24.8572 | 23.8726 | 22.9947 | 21.9989 | 26.5945 | 26.5769 | 26.5744 | 26.5719 | 26.5688 | 26.5653 | 26.5618 | 26.5529 | 26.5431 | 26.515 | 26.3034 | 25.3465 | 24.4901 | 23.5145
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 0.50737 | 26.5018 | 26.4825 | 26.4739 | 26.462 | 26.4484 | 26.4332 | 26.4169 | 26.404 | 26.3905 | 26.3242 | 26.2236 | 25.7197 | 25.1547 | 24.4356 | 25.0197 | 24.9971 | 24.9847 | 24.8684 | 24.7355 | 24.606 | 24.4826 | 24.3548 | 24.2293 | 24.1062 | 23.9878 | 23.399 | 22.7492 | 21.9484 | 25.4664 | 25.4428 | 25.4294 | 25.4104 | 25.3901 | 25.3684 | 25.3461 | 25.3267 | 25.3069 | 25.2869 | 25.2672 | 25.2477 | 25.224 | 25.1996
|  | PETERHEAD NORTH STREET | CT |  |  |  | 0.50737 | 26.5018 | 26.4954 | 26.49 | 26.4826 | 26.4735 | 26.4626 | 26.4507 | 26.4428 | 26.4344 | 26.4258 | 26.4169 | 26.2206 | 25.826 | 25.3666 | 25.0211 | 25.0125 | 25.0045 | 24.9935 | 24.9243 | 24.8308 | 24.7432 | 24.6552 | 24.5686 | 24.4846 | 24.4032 | 23.9856 | 23.532 | 23.0136 | 25.4681 | 25.4588 | 25.4502 | 25.4382 | 25.4245 | 25.4089 | 25.3927 | 25.3803 | 25.3675 | 25.3546 | 25.3416 | 25.3282 | 25.3118 | 25.2951
|  | PETERHEAD NORTH STREET | LW |  |  |  | 0.50737 | 26.5018 | 26.4825 | 26.4739 | 26.462 | 26.4484 | 26.4332 | 26.4169 | 26.404 | 26.3905 | 26.3242 | 26.2236 | 25.7197 | 25.1547 | 24.4356 | 25.0197 | 24.9971 | 24.9847 | 24.8684 | 24.7355 | 24.606 | 24.4826 | 24.3548 | 24.2293 | 24.1062 | 23.9878 | 23.399 | 22.7492 | 21.9484 | 25.4664 | 25.4428 | 25.4294 | 25.4104 | 25.3901 | 25.3684 | 25.3461 | 25.3267 | 25.3069 | 25.2869 | 25.2672 | 25.2477 | 25.224 | 25.1996
|  | PETERHEAD NORTH STREET | ST |  |  |  | 0.50737 | 26.5018 | 26.4989 | 26.4975 | 26.4938 | 26.4892 | 26.4839 | 26.478 | 26.4758 | 26.4735 | 26.4714 | 26.4693 | 26.4595 | 26.4055 | 26.2358 | 25.0233 | 25.0198 | 25.0177 | 25.0118 | 25.005 | 24.9974 | 24.9893 | 24.9659 | 24.91 | 24.8552 | 24.8016 | 24.5427 | 24.2579 | 23.9996 | 25.4709 | 25.4672 | 25.4649 | 25.4585 | 25.4511 | 25.4429 | 25.4342 | 25.4289 | 25.4237 | 25.4186 | 25.4136 | 25.3897 | 25.3227 | 25.281
|  | PETERHEAD NORTH STREET | FS |  |  |  | 0.50737 | 26.5018 | 26.4986 | 26.4984 | 26.4982 | 26.498 | 26.4976 | 26.4973 | 26.4959 | 26.4943 | 26.4926 | 26.4907 | 26.4857 | 26.4586 | 26.3981 | 25.0234 | 25.0197 | 25.019 | 25.0182 | 25.0169 | 25.015 | 25.013 | 25.0098 | 25.0064 | 25.0029 | 24.9696 | 24.7686 | 24.5606 | 24.3227 | 25.4711 | 25.4672 | 25.4664 | 25.4653 | 25.4638 | 25.4614 | 25.4591 | 25.4554 | 25.4515 | 25.4474 | 25.4432 | 25.4271 | 25.3899 | 25.3193
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 0.0052632 | 12.6887 | 12.6606 | 12.6474 | 12.6289 | 12.608 | 12.5849 | 12.5605 | 12.5413 | 12.5216 | 12.5007 | 12.4801 | 12.3509 | 11.9102 | 11.2149 | 12.1601 | 12.13 | 12.1148 | 12.093 | 12.0686 | 12.0423 | 12.0147 | 11.9649 | 11.8766 | 11.7878 | 11.6999 | 11.2378 | 10.6845 | 9.9384 | 12.3388 | 12.3107 | 12.2974 | 12.279 | 12.2581 | 12.235 | 12.2106 | 12.1914 | 12.1717 | 12.1508 | 12.1302 | 12.1097 | 12.084 | 12.0448
|  | PINEGROVE | CT |  |  |  | 0.0052632 | 12.6887 | 12.6777 | 12.6683 | 12.6558 | 12.6406 | 12.6229 | 12.6039 | 12.5911 | 12.5778 | 12.5643 | 12.5507 | 12.4612 | 12.3167 | 11.9962 | 12.1601 | 12.1479 | 12.1372 | 12.1223 | 12.1048 | 12.0848 | 12.0635 | 12.0484 | 12.0327 | 12.0169 | 11.9653 | 11.6429 | 11.2583 | 10.7939 | 12.3388 | 12.3278 | 12.3183 | 12.3058 | 12.2907 | 12.273 | 12.254 | 12.2412 | 12.2278 | 12.2144 | 12.2007 | 12.1865 | 12.1686 | 12.1502
|  | PINEGROVE | LW |  |  |  | 0.0052632 | 12.6904 | 12.6606 | 12.6474 | 12.6289 | 12.608 | 12.5849 | 12.5605 | 12.5413 | 12.5216 | 12.5007 | 12.4801 | 12.3509 | 11.9102 | 11.2149 | 12.1614 | 12.13 | 12.1148 | 12.093 | 12.0686 | 12.0423 | 12.0147 | 11.9649 | 11.8766 | 11.7878 | 11.6999 | 11.2378 | 10.6845 | 9.9384 | 12.3405 | 12.3107 | 12.2974 | 12.279 | 12.2581 | 12.235 | 12.2106 | 12.1914 | 12.1717 | 12.1508 | 12.1302 | 12.1097 | 12.084 | 12.0448
|  | PINEGROVE | ST |  |  |  | 0.0052632 | 12.6913 | 12.6872 | 12.6853 | 12.68 | 12.6737 | 12.6662 | 12.6579 | 12.6548 | 12.6516 | 12.6486 | 12.6457 | 12.6325 | 12.564 | 12.5284 | 12.1644 | 12.1602 | 12.1581 | 12.1513 | 12.1434 | 12.1344 | 12.1246 | 12.1199 | 12.1152 | 12.1106 | 12.1062 | 12.0855 | 11.884 | 11.7001 | 12.3413 | 12.3373 | 12.3353 | 12.3301 | 12.3237 | 12.3163 | 12.3079 | 12.3048 | 12.3017 | 12.2987 | 12.2958 | 12.2825 | 12.2141 | 12.1784
|  | PINEGROVE | FS |  |  |  | 0.0052632 | 12.6913 | 12.6872 | 12.687 | 12.6868 | 12.6865 | 12.686 | 12.6856 | 12.6838 | 12.6818 | 12.6796 | 12.6773 | 12.671 | 12.6379 | 12.565 | 12.1644 | 12.1602 | 12.1599 | 12.1595 | 12.1587 | 12.1571 | 12.1556 | 12.1526 | 12.1494 | 12.146 | 12.1424 | 12.1299 | 12.0909 | 11.9178 | 12.3413 | 12.3372 | 12.337 | 12.3368 | 12.3365 | 12.3361 | 12.3356 | 12.3339 | 12.3319 | 12.3297 | 12.3273 | 12.3211 | 12.288 | 12.2151
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 0.11895 | 6.5617 | 6.5402 | 6.522 | 6.4979 | 6.4703 | 6.4405 | 6.4085 | 6.3399 | 6.2699 | 6.1885 | 6.1 | 5.6338 | 5.0782 | 4.327 | 6.59 | 6.5684 | 6.5502 | 6.5262 | 6.4986 | 6.4688 | 6.3816 | 6.2829 | 6.1849 | 6.0874 | 5.9905 | 5.4826 | 4.8847 | 4.0917 | 6.4181 | 6.3965 | 6.3783 | 6.3543 | 6.2822 | 6.1818 | 6.0816 | 5.9825 | 5.8841 | 5.7864 | 5.6891 | 5.5931 | 5.4917 | 5.3887
|  | PITLOCHRY | CT |  |  |  | 0.11895 | 6.5617 | 6.5412 | 6.5224 | 6.5002 | 6.4759 | 6.4489 | 6.4206 | 6.3984 | 6.3757 | 6.3325 | 6.2798 | 5.952 | 5.5338 | 5.0328 | 6.59 | 6.5695 | 6.5507 | 6.5285 | 6.5042 | 6.4772 | 6.4489 | 6.4267 | 6.3624 | 6.2898 | 6.2178 | 5.8375 | 5.3896 | 4.8595 | 6.4181 | 6.3976 | 6.3788 | 6.3565 | 6.3323 | 6.2853 | 6.2094 | 6.1358 | 6.0624 | 5.9896 | 5.9174 | 5.8453 | 5.7686 | 5.6915
|  | PITLOCHRY | LW |  |  |  | 0.11895 | 6.5761 | 6.5402 | 6.522 | 6.4979 | 6.4703 | 6.4405 | 6.4085 | 6.3399 | 6.2699 | 6.1885 | 6.1 | 5.6338 | 5.0782 | 4.327 | 6.6043 | 6.5684 | 6.5502 | 6.5262 | 6.4986 | 6.4688 | 6.3816 | 6.2829 | 6.1849 | 6.0874 | 5.9905 | 5.4826 | 4.8847 | 4.0917 | 6.4324 | 6.3965 | 6.3783 | 6.3543 | 6.2822 | 6.1818 | 6.0816 | 5.9825 | 5.8841 | 5.7864 | 5.6891 | 5.5931 | 5.4917 | 5.3887
|  | PITLOCHRY | ST |  |  |  | 0.11895 | 6.5794 | 6.5727 | 6.5681 | 6.5601 | 6.5509 | 6.5406 | 6.5293 | 6.5235 | 6.5177 | 6.512 | 6.5065 | 6.4652 | 6.293 | 6.1151 | 6.6077 | 6.6009 | 6.5964 | 6.5884 | 6.5792 | 6.5688 | 6.5576 | 6.5518 | 6.546 | 6.5403 | 6.5348 | 6.426 | 6.1966 | 6.0011 | 6.4358 | 6.429 | 6.4245 | 6.4165 | 6.4073 | 6.3969 | 6.3857 | 6.3799 | 6.3741 | 6.3492 | 6.3103 | 6.1258 | 5.8957 | 5.6996
|  | PITLOCHRY | FS |  |  |  | 0.11895 | 6.582 | 6.5772 | 6.5753 | 6.5734 | 6.5714 | 6.5693 | 6.5672 | 6.5638 | 6.5602 | 6.5565 | 6.5525 | 6.538 | 6.4946 | 6.3464 | 6.6102 | 6.6055 | 6.6036 | 6.6017 | 6.5997 | 6.5976 | 6.5955 | 6.5921 | 6.5885 | 6.5847 | 6.5808 | 6.5663 | 6.4627 | 6.2686 | 6.4383 | 6.4336 | 6.4317 | 6.4298 | 6.4278 | 6.4257 | 6.4236 | 6.4202 | 6.4166 | 6.4128 | 6.4089 | 6.325 | 6.1626 | 5.968
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0 | 4.6789 | 4.6527 | 4.641 | 4.6248 | 4.6063 | 4.5862 | 4.5649 | 4.5482 | 4.5313 | 4.514 | 4.4971 | 4.3872 | 4.0102 | 3.4839 | 4.615 | 4.5676 | 4.5295 | 4.4656 | 4.4007 | 4.3362 | 4.2712 | 4.204 | 4.1372 | 4.071 | 4.0058 | 3.6669 | 3.2596 | 2.7031 | 4.06 | 4.0337 | 4.0221 | 4.0058 | 3.9874 | 3.9672 | 3.946 | 3.9293 | 3.9123 | 3.8951 | 3.8782 | 3.8614 | 3.8406 | 3.7934
|  | POLLACHAR | CT |  |  |  | 0 | 4.6789 | 4.6698 | 4.662 | 4.6514 | 4.6385 | 4.6234 | 4.6072 | 4.5966 | 4.5856 | 4.5746 | 4.5634 | 4.4905 | 4.3739 | 4.0823 | 4.6158 | 4.5958 | 4.5694 | 4.5259 | 4.4807 | 4.435 | 4.3893 | 4.3469 | 4.3047 | 4.2595 | 4.2146 | 3.976 | 3.6914 | 3.3467 | 4.06 | 4.0508 | 4.043 | 4.0325 | 4.0196 | 4.0045 | 3.9883 | 3.9777 | 3.9667 | 3.9556 | 3.9445 | 3.9329 | 3.9183 | 3.9033
|  | POLLACHAR | LW |  |  |  | 0 | 4.6789 | 4.6527 | 4.641 | 4.6248 | 4.6063 | 4.5862 | 4.5649 | 4.5482 | 4.5313 | 4.514 | 4.4971 | 4.3872 | 4.0102 | 3.4839 | 4.615 | 4.5676 | 4.5295 | 4.4656 | 4.4007 | 4.3362 | 4.2712 | 4.204 | 4.1372 | 4.071 | 4.0058 | 3.6669 | 3.2596 | 2.7031 | 4.06 | 4.0337 | 4.0221 | 4.0058 | 3.9874 | 3.9672 | 3.946 | 3.9293 | 3.9123 | 3.8951 | 3.8782 | 3.8614 | 3.8406 | 3.7934
|  | POLLACHAR | ST |  |  |  | 0 | 4.6789 | 4.6755 | 4.6738 | 4.6693 | 4.6638 | 4.6574 | 4.6503 | 4.6476 | 4.6449 | 4.6424 | 4.6399 | 4.6287 | 4.573 | 4.5444 | 4.6158 | 4.6123 | 4.6106 | 4.6061 | 4.5826 | 4.5555 | 4.5283 | 4.5041 | 4.4804 | 4.4572 | 4.4346 | 4.3254 | 4.1678 | 4.0406 | 4.06 | 4.0565 | 4.0548 | 4.0504 | 4.0449 | 4.0385 | 4.0314 | 4.0287 | 4.026 | 4.0234 | 4.0209 | 4.0097 | 3.9541 | 3.9254
|  | POLLACHAR | FS |  |  |  | 0 | 4.6789 | 4.6757 | 4.6756 | 4.6754 | 4.6752 | 4.6748 | 4.6745 | 4.6731 | 4.6715 | 4.6698 | 4.6679 | 4.663 | 4.6372 | 4.5808 | 4.6158 | 4.6126 | 4.6124 | 4.6123 | 4.612 | 4.6116 | 4.6032 | 4.586 | 4.5686 | 4.5512 | 4.5336 | 4.4519 | 4.353 | 4.2192 | 4.06 | 4.0568 | 4.0566 | 4.0565 | 4.0562 | 4.0559 | 4.0555 | 4.0541 | 4.0526 | 4.0509 | 4.049 | 4.0441 | 4.0183 | 3.9618
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0 | 0.10973 | 0.10962 | 0.10956 | 0.10949 | 0.10942 | 0.10933 | 0.10924 | 0.10917 | 0.10909 | 0.10902 | 0.10895 | 0.1085 | 0.10781 | 0.10597 | 0.10495 | 0.10484 | 0.10479 | 0.10472 | 0.10464 | 0.10455 | 0.10446 | 0.10439 | 0.10432 | 0.10424 | 0.10417 | 0.10351 | 0.1021 | 0.10008 | 0.10614 | 0.10603 | 0.10598 | 0.10591 | 0.10583 | 0.10574 | 0.10565 | 0.10558 | 0.1055 | 0.10543 | 0.10536 | 0.10528 | 0.10504 | 0.10479
|  | POOR HOUSE | CT |  |  |  | 0 | 0.10973 | 0.10969 | 0.10966 | 0.10961 | 0.10956 | 0.10949 | 0.10943 | 0.10938 | 0.10934 | 0.10929 | 0.10924 | 0.10894 | 0.10847 | 0.10774 | 0.10495 | 0.10491 | 0.10488 | 0.10484 | 0.10478 | 0.10472 | 0.10465 | 0.10461 | 0.10456 | 0.10451 | 0.10447 | 0.10417 | 0.10363 | 0.10242 | 0.10614 | 0.1061 | 0.10607 | 0.10602 | 0.10597 | 0.10591 | 0.10584 | 0.10579 | 0.10575 | 0.1057 | 0.10566 | 0.10561 | 0.10555 | 0.10549
|  | POOR HOUSE | LW |  |  |  | 0 | 0.10973 | 0.10962 | 0.10956 | 0.10949 | 0.10942 | 0.10933 | 0.10924 | 0.10917 | 0.10909 | 0.10902 | 0.10895 | 0.1085 | 0.10781 | 0.10597 | 0.10495 | 0.10484 | 0.10479 | 0.10472 | 0.10464 | 0.10455 | 0.10446 | 0.10439 | 0.10432 | 0.10424 | 0.10417 | 0.10351 | 0.1021 | 0.10008 | 0.10614 | 0.10603 | 0.10598 | 0.10591 | 0.10583 | 0.10574 | 0.10565 | 0.10558 | 0.1055 | 0.10543 | 0.10536 | 0.10528 | 0.10504 | 0.10479
|  | POOR HOUSE | ST |  |  |  | 0 | 0.10973 | 0.10971 | 0.10971 | 0.10969 | 0.10967 | 0.10964 | 0.10961 | 0.1096 | 0.10959 | 0.10958 | 0.10957 | 0.10952 | 0.1093 | 0.10918 | 0.10495 | 0.10494 | 0.10493 | 0.10491 | 0.10489 | 0.10486 | 0.10483 | 0.10482 | 0.10481 | 0.1048 | 0.10479 | 0.10474 | 0.10452 | 0.1044 | 0.10614 | 0.10612 | 0.10612 | 0.1061 | 0.10608 | 0.10605 | 0.10602 | 0.10601 | 0.106 | 0.10599 | 0.10598 | 0.10593 | 0.10571 | 0.10559
|  | POOR HOUSE | FS |  |  |  | 0 | 0.10973 | 0.10972 | 0.10971 | 0.10971 | 0.10971 | 0.10971 | 0.10971 | 0.1097 | 0.1097 | 0.10969 | 0.10968 | 0.10966 | 0.10956 | 0.10933 | 0.10495 | 0.10494 | 0.10494 | 0.10494 | 0.10494 | 0.10493 | 0.10493 | 0.10493 | 0.10492 | 0.10491 | 0.10491 | 0.10489 | 0.10478 | 0.10455 | 0.10614 | 0.10613 | 0.10612 | 0.10612 | 0.10612 | 0.10612 | 0.10612 | 0.10611 | 0.10611 | 0.1061 | 0.10609 | 0.10607 | 0.10597 | 0.10574
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | YES | 0 | 1.7005 | 1.6926 | 1.6882 | 1.6815 | 1.6743 | 1.6505 | 1.6264 | 1.6013 | 1.5765 | 1.5517 | 1.5272 | 1.4034 | 1.2624 | 1.0859 | 1.5294 | 1.5227 | 1.5197 | 1.5156 | 1.5109 | 1.5057 | 1.5003 | 1.4961 | 1.4917 | 1.465 | 1.4387 | 1.3012 | 1.1427 | 0.94887 | 1.6557 | 1.649 | 1.6461 | 1.6419 | 1.6252 | 1.5984 | 1.5726 | 1.5457 | 1.519 | 1.4925 | 1.4662 | 1.4401 | 1.4131 | 1.3868
|  | PORT ASKAIG | CT |  |  |  | 0 | 1.7009 | 1.6978 | 1.6949 | 1.6906 | 1.6857 | 1.6803 | 1.6733 | 1.6563 | 1.6394 | 1.6225 | 1.6058 | 1.519 | 1.422 | 1.3112 | 1.5294 | 1.5271 | 1.5252 | 1.5226 | 1.5194 | 1.5157 | 1.5117 | 1.5091 | 1.5064 | 1.5037 | 1.501 | 1.4296 | 1.3232 | 1.2006 | 1.6557 | 1.6535 | 1.6515 | 1.6489 | 1.6457 | 1.6411 | 1.6227 | 1.6044 | 1.5862 | 1.5681 | 1.5501 | 1.5322 | 1.5136 | 1.4949
|  | PORT ASKAIG | LW |  |  |  | 0 | 1.7005 | 1.6926 | 1.6882 | 1.6815 | 1.6743 | 1.6505 | 1.6264 | 1.6013 | 1.5765 | 1.5517 | 1.5272 | 1.4034 | 1.2624 | 1.0859 | 1.5294 | 1.5227 | 1.5197 | 1.5156 | 1.5109 | 1.5057 | 1.5003 | 1.4961 | 1.4917 | 1.465 | 1.4387 | 1.3012 | 1.1427 | 0.94887 | 1.6557 | 1.649 | 1.6461 | 1.6419 | 1.6252 | 1.5984 | 1.5726 | 1.5457 | 1.519 | 1.4925 | 1.4662 | 1.4401 | 1.4131 | 1.3868
|  | PORT ASKAIG | ST |  |  |  | 0 | 1.7021 | 1.7011 | 1.7006 | 1.6984 | 1.6959 | 1.6933 | 1.6904 | 1.6886 | 1.6867 | 1.6849 | 1.6819 | 1.6344 | 1.5784 | 1.5298 | 1.5294 | 1.5285 | 1.5281 | 1.5271 | 1.5257 | 1.5242 | 1.5225 | 1.5218 | 1.5212 | 1.5205 | 1.5199 | 1.5173 | 1.4927 | 1.4402 | 1.6557 | 1.6549 | 1.6545 | 1.6534 | 1.6521 | 1.6505 | 1.6488 | 1.6482 | 1.6475 | 1.6426 | 1.6313 | 1.5799 | 1.5201 | 1.4678
|  | PORT ASKAIG | FS |  |  |  | 0 | 1.7022 | 1.7013 | 1.7011 | 1.701 | 1.7005 | 1.6996 | 1.6987 | 1.6976 | 1.6964 | 1.6952 | 1.6939 | 1.6867 | 1.6481 | 1.6033 | 1.5294 | 1.5286 | 1.5286 | 1.5286 | 1.5285 | 1.5284 | 1.5283 | 1.528 | 1.5276 | 1.5272 | 1.5268 | 1.5256 | 1.5196 | 1.5065 | 1.6557 | 1.655 | 1.6549 | 1.6549 | 1.6548 | 1.6548 | 1.6547 | 1.6544 | 1.654 | 1.6536 | 1.6532 | 1.636 | 1.5945 | 1.547
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 0 | 5.4868 | 5.4728 | 5.4638 | 5.4515 | 5.4384 | 5.4249 | 5.4113 | 5.3759 | 5.3255 | 5.2765 | 5.2312 | 5.012 | 4.776 | 4.4757 | 4.8854 | 4.8737 | 4.8685 | 4.8613 | 4.853 | 4.844 | 4.8345 | 4.827 | 4.8193 | 4.7953 | 4.7356 | 4.451 | 4.154 | 3.7949 | 4.9423 | 4.9305 | 4.9253 | 4.9181 | 4.9098 | 4.9008 | 4.8913 | 4.8838 | 4.8761 | 4.8669 | 4.8563 | 4.846 | 4.8337 | 4.7922
|  | PORT ELLEN | CT |  |  |  | 0 | 5.4868 | 5.4828 | 5.4774 | 5.4694 | 5.4603 | 5.4502 | 5.44 | 5.4323 | 5.4243 | 5.4166 | 5.409 | 5.2518 | 5.0861 | 4.8946 | 4.8854 | 4.8814 | 4.8779 | 4.8732 | 4.8675 | 4.8607 | 4.8535 | 4.8487 | 4.8438 | 4.8388 | 4.8338 | 4.7653 | 4.5568 | 4.3241 | 4.9423 | 4.9382 | 4.9347 | 4.93 | 4.9243 | 4.9175 | 4.9103 | 4.9055 | 4.9006 | 4.8956 | 4.8906 | 4.8853 | 4.8787 | 4.8719
|  | PORT ELLEN | LW |  |  |  | 0 | 5.4868 | 5.4728 | 5.4638 | 5.4515 | 5.4384 | 5.4249 | 5.4113 | 5.3759 | 5.3255 | 5.2765 | 5.2312 | 5.012 | 4.776 | 4.4757 | 4.8854 | 4.8737 | 4.8685 | 4.8613 | 4.853 | 4.844 | 4.8345 | 4.827 | 4.8193 | 4.7953 | 4.7356 | 4.451 | 4.154 | 3.7949 | 4.9423 | 4.9305 | 4.9253 | 4.9181 | 4.9098 | 4.9008 | 4.8913 | 4.8838 | 4.8761 | 4.8669 | 4.8563 | 4.846 | 4.8337 | 4.7922
|  | PORT ELLEN | ST |  |  |  | 0 | 5.4868 | 5.4853 | 5.4845 | 5.4825 | 5.4793 | 5.4745 | 5.4694 | 5.4662 | 5.4629 | 5.4598 | 5.4568 | 5.4431 | 5.392 | 5.3081 | 4.8854 | 4.8839 | 4.8831 | 4.8811 | 4.8786 | 4.8757 | 4.8724 | 4.8712 | 4.87 | 4.8688 | 4.8677 | 4.8626 | 4.8368 | 4.8235 | 4.9423 | 4.9407 | 4.9399 | 4.9379 | 4.9354 | 4.9325 | 4.9293 | 4.928 | 4.9268 | 4.9256 | 4.9245 | 4.9194 | 4.8936 | 4.8803
|  | PORT ELLEN | FS |  |  |  | 0 | 5.4868 | 5.4853 | 5.4852 | 5.4852 | 5.485 | 5.4849 | 5.484 | 5.4819 | 5.4796 | 5.4772 | 5.4748 | 5.4653 | 5.4469 | 5.4141 | 4.8854 | 4.8839 | 4.8838 | 4.8838 | 4.8836 | 4.8835 | 4.8833 | 4.8826 | 4.8819 | 4.8811 | 4.8802 | 4.8779 | 4.8656 | 4.8386 | 4.9423 | 4.9407 | 4.9407 | 4.9406 | 4.9405 | 4.9403 | 4.9401 | 4.9395 | 4.9387 | 4.9379 | 4.937 | 4.9347 | 4.9224 | 4.8954
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 0.061053 | 9.0467 | 9.0157 | 8.9973 | 8.9722 | 8.944 | 8.9126 | 8.8796 | 8.8532 | 8.8265 | 8.7994 | 8.7727 | 8.606 | 8.1702 | 7.4167 | 8.7059 | 8.6749 | 8.6565 | 8.6314 | 8.6032 | 8.5718 | 8.5388 | 8.5124 | 8.4857 | 8.4586 | 8.4319 | 8.2652 | 7.6216 | 6.7093 | 8.5297 | 8.4987 | 8.4802 | 8.4552 | 8.427 | 8.3955 | 8.3626 | 8.3361 | 8.3094 | 8.2823 | 8.2557 | 8.2284 | 8.1956 | 8.1615
|  | PORTREE | CT |  |  |  | 0.061053 | 9.0467 | 9.0289 | 9.013 | 8.9941 | 8.9719 | 8.9466 | 8.9199 | 8.9002 | 8.8799 | 8.8595 | 8.8391 | 8.7118 | 8.5195 | 8.1918 | 8.7059 | 8.6881 | 8.6722 | 8.6533 | 8.6311 | 8.6059 | 8.5791 | 8.5594 | 8.5391 | 8.5188 | 8.4983 | 8.371 | 8.1787 | 7.7366 | 8.5297 | 8.5118 | 8.4959 | 8.477 | 8.4548 | 8.4296 | 8.4028 | 8.3831 | 8.3628 | 8.3425 | 8.322 | 8.301 | 8.2759 | 8.2502
|  | PORTREE | LW |  |  |  | 0.061053 | 9.0551 | 9.0157 | 8.9973 | 8.9722 | 8.944 | 8.9126 | 8.8796 | 8.8532 | 8.8265 | 8.7994 | 8.7727 | 8.606 | 8.1702 | 7.4167 | 8.7143 | 8.6749 | 8.6565 | 8.6314 | 8.6032 | 8.5718 | 8.5388 | 8.5124 | 8.4857 | 8.4586 | 8.4319 | 8.2652 | 7.6216 | 6.7093 | 8.5381 | 8.4987 | 8.4802 | 8.4552 | 8.427 | 8.3955 | 8.3626 | 8.3361 | 8.3094 | 8.2823 | 8.2557 | 8.2284 | 8.1956 | 8.1615
|  | PORTREE | ST |  |  |  | 0.061053 | 9.0568 | 9.0512 | 9.048 | 9.041 | 9.0318 | 9.0213 | 9.0098 | 9.0044 | 8.9999 | 8.9955 | 8.9912 | 8.9691 | 8.8853 | 8.8377 | 8.716 | 8.7104 | 8.7072 | 8.7002 | 8.691 | 8.6805 | 8.669 | 8.6636 | 8.6591 | 8.6547 | 8.6504 | 8.6283 | 8.5445 | 8.4969 | 8.5398 | 8.5341 | 8.531 | 8.5239 | 8.5147 | 8.5042 | 8.4927 | 8.4874 | 8.4828 | 8.4784 | 8.4742 | 8.452 | 8.3683 | 8.3206
|  | PORTREE | FS |  |  |  | 0.061053 | 9.0568 | 9.0516 | 9.0505 | 9.0495 | 9.0483 | 9.0469 | 9.0456 | 9.0429 | 9.0399 | 9.0367 | 9.0333 | 9.0224 | 8.983 | 8.9021 | 8.716 | 8.7108 | 8.7097 | 8.7087 | 8.7075 | 8.7061 | 8.7048 | 8.7021 | 8.6991 | 8.6959 | 8.6925 | 8.6816 | 8.6422 | 8.5613 | 8.5398 | 8.5345 | 8.5335 | 8.5324 | 8.5312 | 8.5299 | 8.5286 | 8.5258 | 8.5228 | 8.5197 | 8.5163 | 8.5053 | 8.4659 | 8.3851
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 0.17895 | 2.0063 | 1.9901 | 1.9749 | 1.9576 | 1.9385 | 1.9177 | 1.8961 | 1.8788 | 1.8596 | 1.8403 | 1.8209 | 1.7074 | 1.5485 | 1.071 | 2.4624 | 2.4447 | 2.4279 | 2.4081 | 2.3857 | 2.3071 | 2.231 | 2.154 | 2.0784 | 2.0043 | 1.9328 | 1.5736 | 1.1625 | 0.63261 | 2.6368 | 2.5951 | 2.5531 | 2.4934 | 2.4329 | 2.3738 | 2.3157 | 2.2583 | 2.2018 | 2.1458 | 2.0917 | 2.0394 | 1.9838 | 1.9277
|  | PORTSOY | CT |  |  |  | 0.17895 | 2.0063 | 1.9901 | 1.9749 | 1.9576 | 1.9385 | 1.9177 | 1.8961 | 1.8788 | 1.8596 | 1.8403 | 1.8209 | 1.7074 | 1.5503 | 1.3377 | 2.4624 | 2.4447 | 2.4279 | 2.4081 | 2.3864 | 2.3632 | 2.3298 | 2.2717 | 2.212 | 2.1546 | 2.0984 | 1.8108 | 1.4872 | 1.1143 | 2.6368 | 2.6034 | 2.569 | 2.5225 | 2.474 | 2.4243 | 2.3768 | 2.3322 | 2.286 | 2.2412 | 2.1972 | 2.1533 | 2.1071 | 2.0611
|  | PORTSOY | LW |  |  |  | 0.17895 | 2.0232 | 2 | 1.9875 | 1.9714 | 1.9527 | 1.9327 | 1.911 | 1.893 | 1.8747 | 1.8554 | 1.8364 | 1.721 | 1.5485 | 1.071 | 2.4784 | 2.4531 | 2.4381 | 2.4182 | 2.3857 | 2.3071 | 2.231 | 2.154 | 2.0784 | 2.0043 | 1.9328 | 1.5736 | 1.1625 | 0.63261 | 2.6438 | 2.5951 | 2.5531 | 2.4934 | 2.4329 | 2.3738 | 2.3157 | 2.2583 | 2.2018 | 2.1458 | 2.0917 | 2.0394 | 1.9838 | 1.9277
|  | PORTSOY | ST |  |  |  | 0.17895 | 2.0266 | 2.0214 | 2.0176 | 2.0117 | 2.0051 | 1.9978 | 1.9899 | 1.9854 | 1.9809 | 1.9764 | 1.972 | 1.951 | 1.8973 | 1.8601 | 2.4842 | 2.4788 | 2.4746 | 2.4673 | 2.4592 | 2.4504 | 2.4411 | 2.435 | 2.4289 | 2.423 | 2.4172 | 2.2983 | 2.1374 | 1.9973 | 2.6755 | 2.6668 | 2.6589 | 2.6359 | 2.6117 | 2.5874 | 2.5629 | 2.5404 | 2.5175 | 2.4956 | 2.4741 | 2.374 | 2.2486 | 2.1427
|  | PORTSOY | FS |  |  |  | 0.17895 | 2.0282 | 2.025 | 2.0232 | 2.0214 | 2.0196 | 2.0176 | 2.0157 | 2.013 | 2.0102 | 2.0072 | 2.0042 | 1.9921 | 1.9649 | 1.9155 | 2.4861 | 2.4826 | 2.4805 | 2.4784 | 2.4758 | 2.4729 | 2.4699 | 2.466 | 2.462 | 2.4579 | 2.4537 | 2.4361 | 2.322 | 2.1876 | 2.6795 | 2.6729 | 2.6676 | 2.6619 | 2.6523 | 2.6381 | 2.6245 | 2.608 | 2.5914 | 2.5747 | 2.5579 | 2.48 | 2.3944 | 2.2882
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0.067368 | 15.2147 | 15.1431 | 32.086 | 32.0412 | 31.9903 | 31.9334 | 31.8728 | 31.8247 | 31.7749 | 31.7238 | 31.6731 | 31.3433 | 30.1178 | 28.2261 | 14.0949 | 14.0233 | 30.0911 | 30.0463 | 29.9954 | 29.9385 | 29.8779 | 29.8182 | 29.5658 | 29.317 | 29.0792 | 27.8436 | 26.3736 | 24.3457 | 14.4358 | 14.3643 | 30.8696 | 30.8248 | 30.7739 | 30.717 | 30.6564 | 30.6083 | 30.5586 | 30.4791 | 30.2557 | 30.0395 | 29.8027 | 29.5656
|  | QUEENS LANE NORTH | CT |  |  |  | 0.067368 | 15.2147 | 15.1897 | 32.1434 | 32.1148 | 32.08 | 32.0384 | 31.9932 | 31.963 | 31.9309 | 31.8983 | 31.8649 | 31.6375 | 31.2483 | 30.4086 | 14.0949 | 14.0699 | 30.1486 | 30.12 | 30.0852 | 30.0436 | 29.9984 | 29.9682 | 29.9361 | 29.9034 | 29.8701 | 29.0484 | 28.0141 | 26.7409 | 14.4358 | 14.4108 | 30.927 | 30.8985 | 30.8636 | 30.822 | 30.7768 | 30.7467 | 30.7146 | 30.6819 | 30.6486 | 30.6135 | 30.5678 | 30.5207
|  | QUEENS LANE NORTH | LW |  |  |  | 0.067368 | 15.2156 | 15.1431 | 32.086 | 32.0412 | 31.9903 | 31.9334 | 31.8728 | 31.8247 | 31.7749 | 31.7238 | 31.6731 | 31.3433 | 30.1178 | 28.2261 | 14.0957 | 14.0233 | 30.0911 | 30.0463 | 29.9954 | 29.9385 | 29.8779 | 29.8182 | 29.5658 | 29.317 | 29.0792 | 27.8436 | 26.3736 | 24.3457 | 14.4367 | 14.3643 | 30.8696 | 30.8248 | 30.7739 | 30.717 | 30.6564 | 30.6083 | 30.5586 | 30.4791 | 30.2557 | 30.0395 | 29.8027 | 29.5656
|  | QUEENS LANE NORTH | ST |  |  |  | 0.067368 | 15.2156 | 15.205 | 32.1749 | 32.1612 | 32.1447 | 32.1252 | 32.1035 | 32.0954 | 32.0872 | 32.0794 | 32.0719 | 32.0364 | 31.8434 | 31.7411 | 14.0957 | 14.0851 | 30.1801 | 30.1664 | 30.1498 | 30.1304 | 30.1087 | 30.1005 | 30.0924 | 30.0845 | 30.077 | 30.0415 | 29.7195 | 29.206 | 14.4367 | 14.4261 | 30.9585 | 30.9449 | 30.9283 | 30.9088 | 30.8871 | 30.879 | 30.8708 | 30.863 | 30.8555 | 30.82 | 30.627 | 30.3779
|  | QUEENS LANE NORTH | FS |  |  |  | 0.067368 | 15.2156 | 15.2033 | 32.1778 | 32.1771 | 32.1762 | 32.1748 | 32.1735 | 32.1683 | 32.1624 | 32.1559 | 32.1488 | 32.13 | 32.0302 | 31.8084 | 14.0957 | 14.0835 | 30.183 | 30.1823 | 30.1813 | 30.18 | 30.1787 | 30.1734 | 30.1675 | 30.161 | 30.154 | 30.1352 | 30.0353 | 29.6704 | 14.4367 | 14.4245 | 30.9614 | 30.9608 | 30.9598 | 30.9585 | 30.9571 | 30.9519 | 30.946 | 30.9395 | 30.9324 | 30.9137 | 30.8138 | 30.592
| QUOICH | QUOICH | MINIMUM HEADROOM | NH 11700 01900 | YES | YES | 0 | -1.9606 | -1.9632 | -1.9658 | -1.9685 | -1.9711 | -1.9738 | -1.9765 | -1.9792 | -1.9818 | -1.9845 | -1.9871 | -2.0014 | -2.0194 | -2.0398 | -1.8945 | -1.8971 | -1.8998 | -1.9024 | -1.9051 | -1.9078 | -1.9105 | -1.9131 | -1.9158 | -1.9184 | -1.9211 | -1.9353 | -1.9534 | -1.9737 | -1.9248 | -1.9275 | -1.9302 | -1.9329 | -1.9357 | -1.9385 | -1.9413 | -1.9441 | -1.9468 | -1.9496 | -1.9523 | -1.9551 | -1.9579 | -1.9606
|  | QUOICH | CT |  |  |  | 0 | -1.9606 | -1.9632 | -1.9658 | -1.9685 | -1.9711 | -1.9738 | -1.9765 | -1.9792 | -1.9818 | -1.9845 | -1.9871 | -2.0014 | -2.0194 | -2.0398 | -1.8945 | -1.8971 | -1.8998 | -1.9024 | -1.9051 | -1.9078 | -1.9105 | -1.9131 | -1.9158 | -1.9184 | -1.9211 | -1.9353 | -1.9534 | -1.9737 | -1.9248 | -1.9275 | -1.9302 | -1.9329 | -1.9357 | -1.9385 | -1.9413 | -1.9441 | -1.9468 | -1.9496 | -1.9523 | -1.9551 | -1.9579 | -1.9606
|  | QUOICH | LW |  |  |  | 0 | -1.9572 | -1.9584 | -1.9593 | -1.9604 | -1.9614 | -1.9625 | -1.9636 | -1.9655 | -1.9674 | -1.9693 | -1.9712 | -1.9808 | -1.9944 | -2.0113 | -1.8911 | -1.8923 | -1.8933 | -1.8943 | -1.8954 | -1.8965 | -1.8975 | -1.8994 | -1.9013 | -1.9032 | -1.9051 | -1.9147 | -1.9283 | -1.9453 | -1.9214 | -1.9227 | -1.9237 | -1.925 | -1.9262 | -1.9274 | -1.9287 | -1.9307 | -1.9327 | -1.9348 | -1.9368 | -1.9388 | -1.9409 | -1.9429
|  | QUOICH | ST |  |  |  | 0 | -1.9564 | -1.9572 | -1.9581 | -1.959 | -1.9599 | -1.9608 | -1.9617 | -1.9626 | -1.9635 | -1.9643 | -1.9652 | -1.9695 | -1.9743 | -1.9788 | -1.8903 | -1.8912 | -1.892 | -1.8929 | -1.8938 | -1.8947 | -1.8957 | -1.8965 | -1.8974 | -1.8983 | -1.8991 | -1.9035 | -1.9083 | -1.9128 | -1.9205 | -1.9214 | -1.9222 | -1.9232 | -1.9242 | -1.9252 | -1.9261 | -1.9271 | -1.928 | -1.929 | -1.9299 | -1.9345 | -1.9396 | -1.9444
|  | QUOICH | FS |  |  |  | 0 | -1.9555 | -1.9556 | -1.9564 | -1.9572 | -1.9581 | -1.9581 | -1.9581 | -1.9581 | -1.9581 | -1.9581 | -1.9582 | -1.9616 | -1.9661 | -1.9708 | -1.8895 | -1.8895 | -1.8903 | -1.8912 | -1.892 | -1.892 | -1.892 | -1.892 | -1.8921 | -1.8921 | -1.8921 | -1.8955 | -1.9 | -1.9048 | -1.9196 | -1.9197 | -1.9205 | -1.9214 | -1.9222 | -1.9223 | -1.9223 | -1.9224 | -1.9225 | -1.9225 | -1.9226 | -1.9263 | -1.931 | -1.936
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0 | 0.11301 | 0.11271 | 0.11257 | 0.11238 | 0.11193 | 0.11055 | 0.10919 | 0.10785 | 0.10652 | 0.10519 | 0.10387 | 0.097089 | 0.08956 | 0.080296 | 0.11013 | 0.10962 | 0.10923 | 0.10776 | 0.10628 | 0.10481 | 0.10334 | 0.1019 | 0.10047 | 0.099043 | 0.097627 | 0.09035 | 0.082324 | 0.072565 | 0.1096 | 0.10929 | 0.10916 | 0.10897 | 0.10777 | 0.10626 | 0.10477 | 0.10329 | 0.10183 | 0.10037 | 0.09892 | 0.097481 | 0.095992 | 0.094496
|  | RACKWICK | CT |  |  |  | 0 | 0.11301 | 0.1129 | 0.11281 | 0.11269 | 0.11254 | 0.11237 | 0.11218 | 0.11206 | 0.11193 | 0.1118 | 0.11167 | 0.10968 | 0.10705 | 0.10373 | 0.11018 | 0.10992 | 0.10965 | 0.10921 | 0.10875 | 0.10828 | 0.10782 | 0.1074 | 0.10698 | 0.10657 | 0.10616 | 0.10396 | 0.10122 | 0.097778 | 0.1096 | 0.10949 | 0.1094 | 0.10928 | 0.10913 | 0.10895 | 0.10876 | 0.10864 | 0.1085 | 0.10808 | 0.10766 | 0.10725 | 0.1068 | 0.10634
|  | RACKWICK | LW |  |  |  | 0 | 0.11301 | 0.11271 | 0.11257 | 0.11238 | 0.11193 | 0.11055 | 0.10919 | 0.10785 | 0.10652 | 0.10519 | 0.10387 | 0.097089 | 0.08956 | 0.080296 | 0.11013 | 0.10962 | 0.10923 | 0.10776 | 0.10628 | 0.10481 | 0.10334 | 0.1019 | 0.10047 | 0.099043 | 0.097627 | 0.09035 | 0.082324 | 0.072565 | 0.1096 | 0.10929 | 0.10916 | 0.10897 | 0.10777 | 0.10626 | 0.10477 | 0.10329 | 0.10183 | 0.10037 | 0.09892 | 0.097481 | 0.095992 | 0.094496
|  | RACKWICK | ST |  |  |  | 0 | 0.11301 | 0.11297 | 0.11295 | 0.1129 | 0.11284 | 0.11276 | 0.11268 | 0.11265 | 0.11262 | 0.11259 | 0.11256 | 0.11243 | 0.11158 | 0.11053 | 0.11043 | 0.11038 | 0.11035 | 0.11009 | 0.10982 | 0.10956 | 0.10929 | 0.10906 | 0.10883 | 0.10861 | 0.1084 | 0.1074 | 0.10594 | 0.10483 | 0.1096 | 0.10955 | 0.10954 | 0.10948 | 0.10942 | 0.10935 | 0.10926 | 0.10923 | 0.1092 | 0.10917 | 0.10914 | 0.10891 | 0.10743 | 0.1063
|  | RACKWICK | FS |  |  |  | 0 | 0.11301 | 0.11297 | 0.11297 | 0.11297 | 0.11297 | 0.11296 | 0.11296 | 0.11294 | 0.11292 | 0.1129 | 0.11288 | 0.11282 | 0.11252 | 0.11178 | 0.11044 | 0.1104 | 0.11038 | 0.11036 | 0.1103 | 0.11015 | 0.11001 | 0.10984 | 0.10966 | 0.10949 | 0.10931 | 0.10849 | 0.10748 | 0.10616 | 0.1096 | 0.10956 | 0.10956 | 0.10955 | 0.10955 | 0.10955 | 0.10954 | 0.10953 | 0.10951 | 0.10949 | 0.10946 | 0.10941 | 0.10899 | 0.10765
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 0 | 1.0153 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.015 | 1.015 | 1.015 | 1.0149 | 1.0149 | 1.0148 | 1.0145 | 1.0141 | 1.0133 | 1.0078 | 1.0077 | 1.0077 | 1.0076 | 1.0076 | 1.0075 | 1.0075 | 1.0074 | 1.0074 | 1.0074 | 1.0073 | 1.007 | 1.0066 | 1.0058 | 1.0096 | 1.0096 | 1.0095 | 1.0095 | 1.0095 | 1.0094 | 1.0094 | 1.0093 | 1.0093 | 1.0092 | 1.0092 | 1.0091 | 1.0091 | 1.009
|  | RAHOY | CT |  |  |  | 0 | 1.0153 | 1.0153 | 1.0152 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151 | 1.015 | 1.015 | 1.015 | 1.0148 | 1.0145 | 1.014 | 1.0078 | 1.0078 | 1.0077 | 1.0077 | 1.0077 | 1.0076 | 1.0076 | 1.0076 | 1.0075 | 1.0075 | 1.0075 | 1.0073 | 1.007 | 1.0065 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0095 | 1.0095 | 1.0095 | 1.0094 | 1.0094 | 1.0094 | 1.0093 | 1.0093 | 1.0093 | 1.0092
|  | RAHOY | LW |  |  |  | 0 | 1.0153 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.015 | 1.015 | 1.015 | 1.0149 | 1.0149 | 1.0148 | 1.0145 | 1.0141 | 1.0133 | 1.0078 | 1.0077 | 1.0077 | 1.0076 | 1.0076 | 1.0075 | 1.0075 | 1.0074 | 1.0074 | 1.0074 | 1.0073 | 1.007 | 1.0066 | 1.0058 | 1.0096 | 1.0096 | 1.0095 | 1.0095 | 1.0095 | 1.0094 | 1.0094 | 1.0093 | 1.0093 | 1.0092 | 1.0092 | 1.0091 | 1.0091 | 1.009
|  | RAHOY | ST |  |  |  | 0 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.015 | 1.0149 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0077 | 1.0077 | 1.0077 | 1.0077 | 1.0077 | 1.0077 | 1.0077 | 1.0077 | 1.0075 | 1.0074 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0095 | 1.0095 | 1.0094 | 1.0093
|  | RAHOY | FS |  |  |  | 0 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0153 | 1.0152 | 1.0152 | 1.015 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0078 | 1.0077 | 1.0077 | 1.0075 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0096 | 1.0095 | 1.0094
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 0.75789 | 28.1469 | 28.153 | 28.1533 | 28.1536 | 28.154 | 28.1546 | 28.1552 | 28.1576 | 28.1602 | 28.1631 | 28.1663 | 28.1747 | 28.2186 | 28.3147 | 24.4498 | 24.4045 | 24.3822 | 24.3499 | 24.2273 | 24.1054 | 23.9846 | 23.8655 | 23.747 | 23.6292 | 23.513 | 22.9057 | 22.1841 | 21.2022 | 27.098 | 27.1041 | 27.1044 | 27.1047 | 27.1051 | 27.1057 | 27.1063 | 27.1086 | 27.1113 | 27.1142 | 27.1174 | 27.1258 | 27.1697 | 27.2658
|  | RAIGMORE | CT |  |  |  | 0.75789 | 28.1469 | 28.1617 | 28.1742 | 28.1912 | 28.2119 | 28.2363 | 28.2625 | 28.2796 | 28.2974 | 28.3153 | 28.3334 | 28.455 | 28.6502 | 28.951 | 24.4498 | 24.4664 | 24.4809 | 24.5016 | 24.526 | 24.6099 | 24.6955 | 24.7761 | 24.8567 | 24.9365 | 25.0157 | 25.4389 | 25.9418 | 25.337 | 27.098 | 27.1128 | 27.1253 | 27.1422 | 27.163 | 27.1874 | 27.2136 | 27.2307 | 27.2485 | 27.2664 | 27.2845 | 27.3034 | 27.3278 | 27.353
|  | RAIGMORE | LW |  |  |  | 0.75789 | 28.1476 | 28.1911 | 28.2105 | 28.2375 | 28.2681 | 28.3016 | 28.337 | 28.3648 | 28.3931 | 28.4218 | 28.4501 | 28.6264 | 28.9996 | 29.9125 | 24.4504 | 24.4045 | 24.3822 | 24.3499 | 24.2273 | 24.1054 | 23.9846 | 23.8655 | 23.747 | 23.6292 | 23.513 | 22.9057 | 22.1841 | 21.2022 | 27.0986 | 27.1422 | 27.1616 | 27.1885 | 27.2192 | 27.2527 | 27.2881 | 27.3159 | 27.3441 | 27.3729 | 27.4012 | 27.4292 | 27.4642 | 27.5005
|  | RAIGMORE | ST |  |  |  | 0.75789 | 28.1476 | 28.1533 | 28.156 | 28.1633 | 28.1722 | 28.1827 | 28.1943 | 28.1987 | 28.2031 | 28.2073 | 28.2113 | 28.2297 | 28.3223 | 28.3702 | 24.4505 | 24.4564 | 24.4593 | 24.469 | 24.4804 | 24.4931 | 24.507 | 24.5138 | 24.5314 | 24.5774 | 24.6225 | 24.8378 | 25.1173 | 25.3477 | 27.0986 | 27.1043 | 27.107 | 27.1144 | 27.1233 | 27.1337 | 27.1454 | 27.1497 | 27.1541 | 27.1583 | 27.1624 | 27.1807 | 27.2733 | 27.3213
|  | RAIGMORE | FS |  |  |  | 0.75789 | 28.1476 | 28.153 | 28.1533 | 28.1536 | 28.154 | 28.1546 | 28.1552 | 28.1576 | 28.1602 | 28.1631 | 28.1663 | 28.1747 | 28.2186 | 28.3147 | 24.4505 | 24.4561 | 24.4565 | 24.4571 | 24.4583 | 24.4606 | 24.4628 | 24.467 | 24.4715 | 24.4763 | 24.4814 | 24.6186 | 24.8181 | 25.0637 | 27.0986 | 27.1041 | 27.1044 | 27.1047 | 27.1051 | 27.1057 | 27.1063 | 27.1086 | 27.1113 | 27.1142 | 27.1174 | 27.1258 | 27.1697 | 27.2658
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0.078947 | 1.4121 | 1.3877 | 1.3645 | 1.3391 | 1.3116 | 1.2833 | 1.2541 | 1.2279 | 1.2013 | 1.1748 | 1.1482 | 0.98939 | 0.77928 | 0.48027 | 1.5733 | 1.5475 | 1.5227 | 1.4949 | 1.4652 | 1.4346 | 1.3741 | 1.2901 | 1.2085 | 1.1291 | 1.0535 | 0.66759 | 0.23098 | -0.33167 | 1.6222 | 1.5978 | 1.5746 | 1.5491 | 1.5217 | 1.4934 | 1.4588 | 1.3775 | 1.2984 | 1.2214 | 1.1446 | 1.071 | 0.99438 | 0.91645
|  | REDFORD | CT |  |  |  | 0.078947 | 1.4121 | 1.3877 | 1.3645 | 1.3391 | 1.3116 | 1.2833 | 1.2541 | 1.2279 | 1.2013 | 1.1748 | 1.1482 | 0.98939 | 0.77928 | 0.50262 | 1.5733 | 1.5475 | 1.5227 | 1.4949 | 1.4652 | 1.4346 | 1.4035 | 1.3751 | 1.323 | 1.2586 | 1.1965 | 0.8716 | 0.50845 | 0.086001 | 1.6222 | 1.5978 | 1.5746 | 1.5491 | 1.5217 | 1.4934 | 1.4642 | 1.4379 | 1.4055 | 1.3428 | 1.2822 | 1.221 | 1.1575 | 1.0939
|  | REDFORD | LW |  |  |  | 0.078947 | 1.4424 | 1.4149 | 1.399 | 1.3783 | 1.3549 | 1.3293 | 1.3019 | 1.2785 | 1.2541 | 1.2295 | 1.2044 | 1.0541 | 0.83678 | 0.48027 | 1.6027 | 1.5729 | 1.5544 | 1.5302 | 1.5035 | 1.4576 | 1.3741 | 1.2901 | 1.2085 | 1.1291 | 1.0535 | 0.66759 | 0.23098 | -0.33167 | 1.6525 | 1.6249 | 1.609 | 1.5883 | 1.5649 | 1.5393 | 1.4588 | 1.3775 | 1.2984 | 1.2214 | 1.1446 | 1.071 | 0.99438 | 0.91645
|  | REDFORD | ST |  |  |  | 0.078947 | 1.4475 | 1.4405 | 1.435 | 1.4272 | 1.4178 | 1.4077 | 1.397 | 1.3898 | 1.3835 | 1.3772 | 1.371 | 1.3386 | 1.2712 | 1.2205 | 1.6102 | 1.6029 | 1.5969 | 1.5878 | 1.5771 | 1.5657 | 1.5537 | 1.5452 | 1.5375 | 1.53 | 1.5226 | 1.4736 | 1.3102 | 1.17 | 1.6575 | 1.6505 | 1.645 | 1.6372 | 1.6279 | 1.6177 | 1.607 | 1.5998 | 1.5935 | 1.5872 | 1.5811 | 1.5487 | 1.3963 | 1.2601
|  | REDFORD | FS |  |  |  | 0.078947 | 1.4509 | 1.4458 | 1.4424 | 1.4389 | 1.4353 | 1.4317 | 1.428 | 1.4244 | 1.4207 | 1.4168 | 1.4129 | 1.3931 | 1.3565 | 1.297 | 1.6137 | 1.6084 | 1.6046 | 1.6007 | 1.5965 | 1.592 | 1.5875 | 1.5829 | 1.5781 | 1.5732 | 1.5683 | 1.5437 | 1.5033 | 1.3764 | 1.6609 | 1.6559 | 1.6524 | 1.6489 | 1.6453 | 1.6417 | 1.638 | 1.6345 | 1.6307 | 1.6269 | 1.6229 | 1.6031 | 1.5666 | 1.4608
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 0.34947 | 16.3527 | 16.3036 | 16.2584 | 16.2072 | 16.151 | 16.0909 | 16.0284 | 15.9763 | 15.9225 | 15.8686 | 15.8144 | 15.2274 | 14.3392 | 13.0546 | 14.9647 | 14.9126 | 14.8639 | 14.8066 | 14.6646 | 14.5048 | 14.3451 | 14.1875 | 14.0302 | 13.873 | 13.7174 | 12.8923 | 11.8923 | 10.5316 | 15.3883 | 15.3392 | 15.2939 | 15.2428 | 15.1865 | 15.1145 | 14.9573 | 14.8024 | 14.6478 | 14.4933 | 14.3402 | 14.1891 | 14.0276 | 13.8639
|  | REDGORTON | CT |  |  |  | 0.34947 | 16.3527 | 16.3036 | 16.2584 | 16.2072 | 16.151 | 16.0909 | 16.0284 | 15.9763 | 15.9225 | 15.8686 | 15.8144 | 15.489 | 14.803 | 13.9383 | 14.9647 | 14.9126 | 14.8639 | 14.8066 | 14.7253 | 14.5938 | 14.4628 | 14.3376 | 14.2119 | 14.0872 | 13.9635 | 13.2959 | 12.4956 | 11.5341 | 15.3883 | 15.3392 | 15.2939 | 15.2428 | 15.1865 | 15.1264 | 15.064 | 14.9472 | 14.8234 | 14.7005 | 14.5786 | 14.4559 | 14.3256 | 14.1929
|  | REDGORTON | LW |  |  |  | 0.34947 | 16.4024 | 16.3369 | 16.3014 | 16.2542 | 16.2015 | 16.1441 | 16.0827 | 16.0303 | 15.9766 | 15.9214 | 15.8661 | 15.2274 | 14.3392 | 13.0546 | 15.0133 | 14.9437 | 14.9033 | 14.8253 | 14.6646 | 14.5048 | 14.3451 | 14.1875 | 14.0302 | 13.873 | 13.7174 | 12.8923 | 11.8923 | 10.5316 | 15.4379 | 15.3724 | 15.3369 | 15.2898 | 15.237 | 15.1145 | 14.9573 | 14.8024 | 14.6478 | 14.4933 | 14.3402 | 14.1891 | 14.0276 | 13.8639
|  | REDGORTON | ST |  |  |  | 0.34947 | 16.4134 | 16.3983 | 16.388 | 16.3717 | 16.3516 | 16.3294 | 16.3057 | 16.2924 | 16.2791 | 16.266 | 16.2531 | 16.1895 | 16.0285 | 15.9179 | 15.03 | 15.0147 | 15.004 | 14.9837 | 14.9596 | 14.9337 | 14.9064 | 14.8891 | 14.8451 | 14.7841 | 14.7244 | 14.4386 | 14.0651 | 13.7492 | 15.4489 | 15.4338 | 15.4235 | 15.4072 | 15.3871 | 15.365 | 15.3412 | 15.3279 | 15.3146 | 15.3015 | 15.2886 | 15.0511 | 14.6831 | 14.3726
|  | REDGORTON | FS |  |  |  | 0.34947 | 16.4184 | 16.408 | 16.4026 | 16.3972 | 16.3916 | 16.3857 | 16.3799 | 16.3718 | 16.3633 | 16.3545 | 16.3454 | 16.3059 | 16.2216 | 16.0728 | 15.0352 | 15.0246 | 15.019 | 15.0131 | 15.0062 | 14.9977 | 14.9892 | 14.9781 | 14.9665 | 14.9546 | 14.9424 | 14.7385 | 14.4781 | 14.1623 | 15.4539 | 15.4435 | 15.4381 | 15.4327 | 15.4271 | 15.4213 | 15.4154 | 15.4073 | 15.3989 | 15.3901 | 15.3809 | 15.3414 | 15.0905 | 14.779
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 1.1484 | 44.0637 | 43.9866 | 43.948 | 43.1072 | 42.2807 | 41.5105 | 40.8408 | 40.1469 | 39.499 | 38.8901 | 38.3662 | 36.0798 | 33.9811 | 31.5715 | 42.7117 | 42.2881 | 41.4188 | 40.42 | 39.4833 | 38.6118 | 37.8557 | 37.0698 | 36.3367 | 35.6484 | 35.0571 | 32.492 | 30.1663 | 27.5022 | 43.9332 | 43.5748 | 42.7017 | 41.6987 | 40.7581 | 39.8829 | 39.1237 | 38.3346 | 37.5984 | 36.8925 | 36.2843 | 35.7482 | 35.2078 | 34.6782
|  | REDMOSS | CT |  |  |  | 1.1484 | 44.0637 | 44.0301 | 44.0009 | 43.963 | 43.8172 | 43.2186 | 42.7297 | 42.2517 | 41.7892 | 41.3767 | 41.0031 | 39.278 | 37.7708 | 36.1552 | 42.7268 | 42.6668 | 42.5109 | 41.8874 | 41.2289 | 40.5516 | 40.0002 | 39.4588 | 38.9354 | 38.4691 | 38.0475 | 36.1107 | 34.4434 | 32.6813 | 43.9332 | 43.8995 | 43.7985 | 43.1724 | 42.5112 | 41.831 | 41.2774 | 40.7337 | 40.2081 | 39.7399 | 39.3165 | 38.8944 | 38.4837 | 38.1015
|  | REDMOSS | LW |  |  |  | 1.1484 | 44.0713 | 43.9866 | 43.948 | 43.1072 | 42.2807 | 41.5105 | 40.8408 | 40.1469 | 39.499 | 38.8901 | 38.3662 | 36.0798 | 33.9811 | 31.5715 | 42.7117 | 42.2881 | 41.4188 | 40.42 | 39.4833 | 38.6118 | 37.8557 | 37.0698 | 36.3367 | 35.6484 | 35.0571 | 32.492 | 30.1663 | 27.5022 | 43.9408 | 43.5748 | 42.7017 | 41.6987 | 40.7581 | 39.8829 | 39.1237 | 38.3346 | 37.5984 | 36.8925 | 36.2843 | 35.7482 | 35.2078 | 34.6782
|  | REDMOSS | ST |  |  |  | 1.1484 | 44.0739 | 44.0613 | 44.0545 | 44.0389 | 44.0202 | 43.9987 | 43.9748 | 43.9648 | 43.9548 | 43.7958 | 43.531 | 42.3438 | 41.3316 | 40.4766 | 42.7532 | 42.7312 | 42.7131 | 42.6809 | 42.6445 | 42.4912 | 42.1831 | 41.8566 | 41.5192 | 41.2006 | 40.899 | 39.5471 | 38.4152 | 37.4512 | 43.9433 | 43.9308 | 43.9239 | 43.9083 | 43.8897 | 43.7787 | 43.4694 | 43.1414 | 42.8026 | 42.4826 | 42.1796 | 40.8219 | 39.6857 | 38.7177
|  | REDMOSS | FS |  |  |  | 1.1484 | 44.0755 | 44.0652 | 44.0639 | 44.0625 | 44.0608 | 44.0588 | 44.0568 | 44.0516 | 44.0457 | 44.0393 | 44.0325 | 43.292 | 42.5078 | 41.6698 | 42.7587 | 42.7404 | 42.7305 | 42.7193 | 42.706 | 42.6909 | 42.6763 | 42.5343 | 42.2673 | 42.008 | 41.7537 | 40.6146 | 39.7299 | 38.7978 | 43.945 | 43.9346 | 43.9333 | 43.9319 | 43.9302 | 43.9282 | 43.9263 | 43.8218 | 43.5537 | 43.2932 | 43.0377 | 41.8936 | 41.0053 | 40.0698
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 0.15263 | 1.5846 | 1.5696 | 1.5629 | 1.5537 | 1.5431 | 1.5317 | 1.5197 | 1.5103 | 1.5008 | 1.4692 | 1.4303 | 1.2284 | 0.99467 | 0.68434 | 1.5185 | 1.5035 | 1.4968 | 1.4875 | 1.477 | 1.4656 | 1.4536 | 1.4223 | 1.3763 | 1.3306 | 1.2857 | 1.0541 | 0.79078 | 0.45141 | 1.4612 | 1.4462 | 1.4395 | 1.4302 | 1.4197 | 1.4083 | 1.3963 | 1.3869 | 1.3774 | 1.348 | 1.304 | 1.2605 | 1.2151 | 1.1694
|  | RHICONICH | CT |  |  |  | 0.15263 | 1.5846 | 1.5796 | 1.5753 | 1.5696 | 1.5625 | 1.5543 | 1.5456 | 1.5399 | 1.534 | 1.5281 | 1.5222 | 1.4164 | 1.2555 | 1.0658 | 1.5185 | 1.5135 | 1.5092 | 1.5035 | 1.4964 | 1.4882 | 1.4795 | 1.4738 | 1.4679 | 1.4598 | 1.4289 | 1.2684 | 1.0868 | 0.87688 | 1.4612 | 1.4562 | 1.4519 | 1.4462 | 1.4391 | 1.4309 | 1.4222 | 1.4165 | 1.4106 | 1.4047 | 1.3988 | 1.3926 | 1.3829 | 1.3512
|  | RHICONICH | LW |  |  |  | 0.15263 | 1.5846 | 1.5696 | 1.5629 | 1.5537 | 1.5431 | 1.5317 | 1.5197 | 1.5103 | 1.5008 | 1.4692 | 1.4303 | 1.2284 | 0.99467 | 0.68434 | 1.5185 | 1.5035 | 1.4968 | 1.4875 | 1.477 | 1.4656 | 1.4536 | 1.4223 | 1.3763 | 1.3306 | 1.2857 | 1.0541 | 0.79078 | 0.45141 | 1.4612 | 1.4462 | 1.4395 | 1.4302 | 1.4197 | 1.4083 | 1.3963 | 1.3869 | 1.3774 | 1.348 | 1.304 | 1.2605 | 1.2151 | 1.1694
|  | RHICONICH | ST |  |  |  | 0.15263 | 1.5846 | 1.5827 | 1.5819 | 1.5795 | 1.5766 | 1.5733 | 1.5695 | 1.5681 | 1.5667 | 1.5653 | 1.564 | 1.5582 | 1.5263 | 1.4511 | 1.5185 | 1.5166 | 1.5158 | 1.5134 | 1.5105 | 1.5072 | 1.5034 | 1.502 | 1.5006 | 1.4992 | 1.4979 | 1.4921 | 1.3915 | 1.3038 | 1.4612 | 1.4593 | 1.4585 | 1.4561 | 1.4532 | 1.4499 | 1.4461 | 1.4447 | 1.4433 | 1.4419 | 1.4406 | 1.4348 | 1.4064 | 1.3225
|  | RHICONICH | FS |  |  |  | 0.15263 | 1.5846 | 1.583 | 1.5829 | 1.5828 | 1.5827 | 1.5825 | 1.5823 | 1.5816 | 1.5808 | 1.58 | 1.579 | 1.5765 | 1.5637 | 1.5358 | 1.5185 | 1.5168 | 1.5168 | 1.5167 | 1.5166 | 1.5164 | 1.5162 | 1.5155 | 1.5147 | 1.5139 | 1.5129 | 1.5104 | 1.4976 | 1.4269 | 1.4612 | 1.4595 | 1.4595 | 1.4594 | 1.4593 | 1.4591 | 1.4589 | 1.4582 | 1.4574 | 1.4566 | 1.4556 | 1.4531 | 1.4403 | 1.4124
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 0 | 26.1165 | 26.0307 | 25.9918 | 25.9377 | 25.8762 | 25.8065 | 25.7318 | 25.6723 | 25.6099 | 25.5456 | 25.4805 | 25.0487 | 24.089 | 21.551 | 23.837 | 23.7385 | 23.686 | 23.6069 | 23.5204 | 23.4264 | 23.3279 | 23.2423 | 23.154 | 23.0161 | 22.7483 | 21.2597 | 19.3564 | 16.6319 | 24.9753 | 24.8895 | 24.8506 | 24.7965 | 24.735 | 24.6653 | 24.5906 | 24.5311 | 24.4687 | 24.4044 | 24.3393 | 24.2738 | 23.986 | 23.6873
|  | ROSEBANK STREET | CT |  |  |  | 0 | 26.1165 | 26.0882 | 26.064 | 26.0316 | 25.9921 | 25.9439 | 25.8911 | 25.8557 | 25.8173 | 25.778 | 25.7375 | 25.4534 | 24.9462 | 24.1285 | 23.8383 | 23.8016 | 23.7679 | 23.718 | 23.661 | 23.5958 | 23.5263 | 23.4727 | 23.4161 | 23.3586 | 23.2998 | 22.5274 | 21.207 | 19.5248 | 24.9753 | 24.947 | 24.9228 | 24.8904 | 24.8509 | 24.8027 | 24.7499 | 24.7145 | 24.6761 | 24.6368 | 24.5963 | 24.5535 | 24.4962 | 24.437
|  | ROSEBANK STREET | LW |  |  |  | 0 | 26.1182 | 26.0307 | 25.9918 | 25.9377 | 25.8762 | 25.8065 | 25.7318 | 25.6723 | 25.6099 | 25.5456 | 25.4805 | 25.0487 | 24.089 | 21.551 | 23.837 | 23.7385 | 23.686 | 23.6069 | 23.5204 | 23.4264 | 23.3279 | 23.2423 | 23.154 | 23.0161 | 22.7483 | 21.2597 | 19.3564 | 16.6319 | 24.977 | 24.8895 | 24.8506 | 24.7965 | 24.735 | 24.6653 | 24.5906 | 24.5311 | 24.4687 | 24.4044 | 24.3393 | 24.2738 | 23.986 | 23.6873
|  | ROSEBANK STREET | ST |  |  |  | 0 | 26.1191 | 26.1058 | 26.0995 | 26.0824 | 26.0617 | 26.0374 | 26.0103 | 26.0001 | 25.9899 | 25.9801 | 25.9708 | 25.9253 | 25.6664 | 25.5274 | 23.8532 | 23.839 | 23.8316 | 23.803 | 23.7707 | 23.7351 | 23.6969 | 23.6744 | 23.652 | 23.63 | 23.6085 | 23.5012 | 23.0877 | 22.4255 | 24.9778 | 24.9646 | 24.9583 | 24.9412 | 24.9205 | 24.8962 | 24.8691 | 24.8589 | 24.8487 | 24.8389 | 24.8296 | 24.7841 | 24.5252 | 24.2326
|  | ROSEBANK STREET | FS |  |  |  | 0 | 26.1191 | 26.1032 | 26.1025 | 26.1017 | 26.1004 | 26.0987 | 26.097 | 26.0902 | 26.0825 | 26.0741 | 26.065 | 26.0407 | 25.9088 | 25.6115 | 23.8522 | 23.8356 | 23.8338 | 23.8313 | 23.8258 | 23.8152 | 23.8046 | 23.7877 | 23.7699 | 23.7513 | 23.732 | 23.6582 | 23.4744 | 23.0381 | 24.9778 | 24.962 | 24.9613 | 24.9605 | 24.9592 | 24.9575 | 24.9558 | 24.949 | 24.9413 | 24.9329 | 24.9238 | 24.8995 | 24.7676 | 24.4703
| KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 0.078947 | 7.0671 | 7.0392 | 7.0132 | 6.985 | 6.9547 | 6.9235 | 6.8913 | 6.8622 | 6.8327 | 6.8033 | 6.7729 | 6.5983 | 6.3625 | 6.0068 | 6.2013 | 6.1733 | 6.1474 | 6.1179 | 6.0521 | 5.9791 | 5.9031 | 5.8273 | 5.752 | 5.6763 | 5.6008 | 5.2013 | 4.7254 | 4.1031 | 6.9026 | 6.8746 | 6.8487 | 6.8204 | 6.7902 | 6.7589 | 6.7267 | 6.6976 | 6.6682 | 6.6387 | 6.6083 | 6.5776 | 6.5435 | 6.5082
|  | ROTHES | CT |  |  |  | 0.078947 | 7.0671 | 7.0392 | 7.0132 | 6.985 | 6.9547 | 6.9235 | 6.8913 | 6.8622 | 6.8327 | 6.8033 | 6.7729 | 6.5983 | 6.3625 | 6.0533 | 6.2013 | 6.1733 | 6.1474 | 6.1179 | 6.0521 | 5.9869 | 5.9219 | 5.8577 | 5.7937 | 5.73 | 5.666 | 5.3258 | 4.9232 | 4.4506 | 6.9026 | 6.8746 | 6.8487 | 6.8204 | 6.7902 | 6.7589 | 6.7267 | 6.6976 | 6.6682 | 6.6387 | 6.6083 | 6.5776 | 6.5435 | 6.5082
|  | ROTHES | LW |  |  |  | 0.078947 | 7.1008 | 7.0723 | 7.0555 | 7.034 | 7.0097 | 6.9831 | 6.9547 | 6.9294 | 6.904 | 6.8774 | 6.8504 | 6.6893 | 6.4548 | 6.0068 | 6.2349 | 6.2064 | 6.1897 | 6.1308 | 6.055 | 5.9791 | 5.9031 | 5.8273 | 5.752 | 5.6763 | 5.6008 | 5.2013 | 4.7254 | 4.1031 | 6.9362 | 6.9078 | 6.891 | 6.8694 | 6.8451 | 6.8185 | 6.7902 | 6.7649 | 6.7394 | 6.7129 | 6.6858 | 6.6588 | 6.6276 | 6.5949
|  | ROTHES | ST |  |  |  | 0.078947 | 7.1084 | 7.1004 | 7.094 | 7.0852 | 7.0747 | 7.0635 | 7.0524 | 7.0452 | 7.0379 | 7.0306 | 7.0235 | 6.9872 | 6.9124 | 6.8558 | 6.2425 | 6.2346 | 6.2281 | 6.2193 | 6.2089 | 6.1976 | 6.1866 | 6.1568 | 6.1259 | 6.0956 | 6.0658 | 5.921 | 5.7419 | 5.5843 | 6.9438 | 6.9359 | 6.9294 | 6.9206 | 6.9102 | 6.8989 | 6.8879 | 6.8806 | 6.8733 | 6.8661 | 6.859 | 6.8227 | 6.7478 | 6.6912
|  | ROTHES | FS |  |  |  | 0.078947 | 7.1117 | 7.1065 | 7.103 | 7.0995 | 7.0959 | 7.0923 | 7.0886 | 7.0841 | 7.0794 | 7.0746 | 7.0697 | 7.0453 | 7.0053 | 6.9416 | 6.2459 | 6.2407 | 6.2372 | 6.2337 | 6.2301 | 6.2264 | 6.2228 | 6.2182 | 6.2136 | 6.2088 | 6.1856 | 6.0707 | 5.9446 | 5.803 | 6.9472 | 6.942 | 6.9385 | 6.935 | 6.9314 | 6.9277 | 6.9241 | 6.9195 | 6.9149 | 6.9101 | 6.9051 | 6.8808 | 6.8408 | 6.777
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0 | 24.9096 | 16.1328 | 16.1121 | 16.0831 | 16.0503 | 16.0137 | 15.973 | 15.9332 | 15.7994 | 15.6598 | 15.5209 | 14.7767 | 13.8672 | 12.605 | 23.6264 | 15.2996 | 15.2788 | 15.2499 | 15.217 | 15.1804 | 15.0995 | 14.9497 | 14.7995 | 14.6499 | 14.501 | 13.6857 | 12.681 | 11.3176 | 23.9971 | 16.0453 | 16.0246 | 15.9956 | 15.9628 | 15.8807 | 15.7231 | 15.5645 | 15.4055 | 15.2472 | 15.0897 | 14.9337 | 14.7644 | 14.5948
|  | ROTHESAY | CT |  |  |  | 0 | 24.9096 | 16.1637 | 16.1502 | 16.1319 | 16.1094 | 16.0827 | 16.0536 | 16.0344 | 16.014 | 15.9873 | 15.9489 | 15.4298 | 14.7906 | 13.9981 | 23.6264 | 15.3304 | 15.3169 | 15.2986 | 15.2762 | 15.2494 | 15.2203 | 15.2011 | 15.1628 | 15.0601 | 14.9574 | 14.4027 | 13.709 | 12.8518 | 23.9971 | 16.0761 | 16.0627 | 16.0444 | 16.0219 | 15.9951 | 15.9661 | 15.8978 | 15.7881 | 15.6794 | 15.5706 | 15.4611 | 15.3423 | 15.2237
|  | ROTHESAY | LW |  |  |  | 0 | 24.9096 | 16.1328 | 16.1121 | 16.0831 | 16.0503 | 16.0137 | 15.973 | 15.9332 | 15.7994 | 15.6598 | 15.5209 | 14.7767 | 13.8672 | 12.605 | 23.6264 | 15.2996 | 15.2788 | 15.2499 | 15.217 | 15.1804 | 15.0995 | 14.9497 | 14.7995 | 14.6499 | 14.501 | 13.6857 | 12.681 | 11.3176 | 23.9971 | 16.0453 | 16.0246 | 15.9956 | 15.9628 | 15.8807 | 15.7231 | 15.5645 | 15.4055 | 15.2472 | 15.0897 | 14.9337 | 14.7644 | 14.5948
|  | ROTHESAY | ST |  |  |  | 0 | 24.9096 | 16.1728 | 16.1695 | 16.1607 | 16.15 | 16.1375 | 16.1235 | 16.1182 | 16.113 | 16.1079 | 16.1031 | 16.0741 | 15.7629 | 15.451 | 23.6264 | 15.3395 | 15.3363 | 15.3275 | 15.3168 | 15.3042 | 15.2902 | 15.285 | 15.2797 | 15.2747 | 15.2698 | 15.1441 | 14.7552 | 14.4179 | 23.9971 | 16.0853 | 16.082 | 16.0732 | 16.0625 | 16.05 | 16.036 | 16.0307 | 16.0254 | 16.0204 | 16.0156 | 15.7631 | 15.3545 | 14.9995
|  | ROTHESAY | FS |  |  |  | 0 | 24.9096 | 16.1722 | 16.1718 | 16.1714 | 16.1709 | 16.17 | 16.1692 | 16.166 | 16.1624 | 16.1585 | 16.1542 | 16.1428 | 16.0748 | 15.7887 | 23.6264 | 15.3389 | 15.3386 | 15.3382 | 15.3376 | 15.3368 | 15.336 | 15.3328 | 15.3292 | 15.3252 | 15.3209 | 15.3095 | 15.1345 | 14.7846 | 23.9971 | 16.0847 | 16.0843 | 16.0839 | 16.0833 | 16.0825 | 16.0817 | 16.0785 | 16.0749 | 16.071 | 16.0667 | 16.047 | 15.7527 | 15.387
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0 | 0.26603 | 0.26287 | 0.26147 | 0.25951 | 0.25729 | 0.25487 | 0.25232 | 0.25032 | 0.24829 | 0.24623 | 0.24421 | 0.2317 | 0.21212 | 0.17474 | 0.51705 | 0.51268 | 0.50954 | 0.50463 | 0.49952 | 0.49432 | 0.48908 | 0.48429 | 0.4795 | 0.47472 | 0.47001 | 0.4443 | 0.41135 | 0.36076 | 0.25778 | 0.25462 | 0.25322 | 0.25126 | 0.24904 | 0.24662 | 0.24407 | 0.24207 | 0.24004 | 0.23798 | 0.23596 | 0.23395 | 0.23148 | 0.2289
|  | ROUSAY | CT |  |  |  | 0 | 0.26603 | 0.26494 | 0.26402 | 0.26276 | 0.26123 | 0.25944 | 0.25752 | 0.25626 | 0.25497 | 0.25366 | 0.25235 | 0.24378 | 0.23016 | 0.20919 | 0.51728 | 0.51519 | 0.51319 | 0.50991 | 0.50638 | 0.50268 | 0.49891 | 0.49574 | 0.49254 | 0.48937 | 0.48621 | 0.46856 | 0.4458 | 0.41588 | 0.25778 | 0.25669 | 0.25576 | 0.25451 | 0.25298 | 0.25119 | 0.24927 | 0.24801 | 0.24671 | 0.24541 | 0.2441 | 0.24273 | 0.24102 | 0.23926
|  | ROUSAY | LW |  |  |  | 0 | 0.26603 | 0.26287 | 0.26147 | 0.25951 | 0.25729 | 0.25487 | 0.25232 | 0.25032 | 0.24829 | 0.24623 | 0.24421 | 0.2317 | 0.21212 | 0.17474 | 0.51705 | 0.51268 | 0.50954 | 0.50463 | 0.49952 | 0.49432 | 0.48908 | 0.48429 | 0.4795 | 0.47472 | 0.47001 | 0.4443 | 0.41135 | 0.36076 | 0.25778 | 0.25462 | 0.25322 | 0.25126 | 0.24904 | 0.24662 | 0.24407 | 0.24207 | 0.24004 | 0.23798 | 0.23596 | 0.23395 | 0.23148 | 0.2289
|  | ROUSAY | ST |  |  |  | 0 | 0.26603 | 0.26562 | 0.26543 | 0.2649 | 0.26426 | 0.2635 | 0.26266 | 0.26235 | 0.26203 | 0.26173 | 0.26144 | 0.26013 | 0.25364 | 0.2503 | 0.519 | 0.51855 | 0.51831 | 0.51657 | 0.51473 | 0.51282 | 0.51087 | 0.50903 | 0.50722 | 0.50544 | 0.50369 | 0.49538 | 0.48211 | 0.47217 | 0.25778 | 0.25737 | 0.25717 | 0.25664 | 0.256 | 0.25525 | 0.25441 | 0.2541 | 0.25378 | 0.25348 | 0.25319 | 0.25187 | 0.24538 | 0.24205
|  | ROUSAY | FS |  |  |  | 0 | 0.26603 | 0.26566 | 0.26564 | 0.26562 | 0.26559 | 0.26555 | 0.26551 | 0.26535 | 0.26517 | 0.26497 | 0.26475 | 0.26418 | 0.26119 | 0.25466 | 0.51909 | 0.51869 | 0.51863 | 0.51853 | 0.5179 | 0.51697 | 0.51603 | 0.5149 | 0.51374 | 0.51256 | 0.51138 | 0.50603 | 0.49849 | 0.4876 | 0.25778 | 0.2574 | 0.25739 | 0.25737 | 0.25734 | 0.2573 | 0.25726 | 0.2571 | 0.25691 | 0.25672 | 0.2565 | 0.25592 | 0.25294 | 0.24641
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 0.2 | 24.9068 | 24.8279 | 24.7921 | 24.7422 | 24.6856 | 24.6229 | 24.5564 | 24.5038 | 24.4499 | 24.3947 | 24.3402 | 23.7857 | 22.5698 | 20.809 | 24.6219 | 24.543 | 24.5072 | 24.4573 | 24.4007 | 24.338 | 24.2715 | 24.2189 | 24.0821 | 23.8476 | 23.6233 | 22.4578 | 21.0701 | 19.1363 | 24.8254 | 24.7465 | 24.7107 | 24.6608 | 24.6042 | 24.5415 | 24.475 | 24.2968 | 24.063 | 23.8338 | 23.6145 | 23.4021 | 23.1709 | 22.9386
|  | RUTHRIESTON | CT |  |  |  | 0.2 | 24.9068 | 24.8785 | 24.8545 | 24.8222 | 24.7828 | 24.7362 | 24.6858 | 24.6525 | 24.6173 | 24.5818 | 24.5456 | 24.3037 | 23.9013 | 22.8253 | 24.6219 | 24.5937 | 24.5696 | 24.5373 | 24.4979 | 24.4513 | 24.401 | 24.3676 | 24.3325 | 24.2969 | 24.2607 | 23.6092 | 22.6352 | 21.4327 | 24.8254 | 24.7971 | 24.7731 | 24.7408 | 24.7014 | 24.6548 | 24.6045 | 24.5711 | 24.5359 | 24.5004 | 24.406 | 24.2532 | 24.0883 | 23.925
|  | RUTHRIESTON | LW |  |  |  | 0.2 | 24.9085 | 24.8279 | 24.7921 | 24.7422 | 24.6856 | 24.6229 | 24.5564 | 24.5038 | 24.4499 | 24.3947 | 24.3402 | 23.7857 | 22.5698 | 20.809 | 24.6236 | 24.543 | 24.5072 | 24.4573 | 24.4007 | 24.338 | 24.2715 | 24.2189 | 24.0821 | 23.8476 | 23.6233 | 22.4578 | 21.0701 | 19.1363 | 24.8271 | 24.7465 | 24.7107 | 24.6608 | 24.6042 | 24.5415 | 24.475 | 24.2968 | 24.063 | 23.8338 | 23.6145 | 23.4021 | 23.1709 | 22.9386
|  | RUTHRIESTON | ST |  |  |  | 0.2 | 24.9093 | 24.898 | 24.8926 | 24.878 | 24.8603 | 24.8395 | 24.8163 | 24.8076 | 24.7989 | 24.7905 | 24.7825 | 24.7453 | 24.5493 | 24.4465 | 24.6244 | 24.6131 | 24.6077 | 24.5931 | 24.5754 | 24.5546 | 24.5314 | 24.5228 | 24.514 | 24.5057 | 24.4977 | 24.4604 | 24.2644 | 23.8549 | 24.8279 | 24.8166 | 24.8112 | 24.7966 | 24.7789 | 24.7581 | 24.7349 | 24.7263 | 24.7175 | 24.7091 | 24.7011 | 24.6639 | 24.286 | 23.8425
|  | RUTHRIESTON | FS |  |  |  | 0.2 | 24.9093 | 24.8973 | 24.8968 | 24.8962 | 24.8952 | 24.8939 | 24.8926 | 24.8875 | 24.8817 | 24.8753 | 24.8684 | 24.85 | 24.7527 | 24.5377 | 24.6244 | 24.6124 | 24.6119 | 24.6113 | 24.6103 | 24.609 | 24.6077 | 24.6026 | 24.5968 | 24.5904 | 24.5835 | 24.5651 | 24.4678 | 24.2528 | 24.8279 | 24.8159 | 24.8154 | 24.8148 | 24.8138 | 24.8125 | 24.8112 | 24.8061 | 24.8003 | 24.7939 | 24.787 | 24.7686 | 24.6713 | 24.2863
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 0 | 6.8108 | 6.797 | 6.7909 | 6.7824 | 6.7727 | 6.7621 | 6.751 | 6.7124 | 6.6532 | 6.5951 | 6.539 | 6.2629 | 5.9622 | 5.589 | 6.7671 | 6.7533 | 6.7472 | 6.7387 | 6.729 | 6.6918 | 6.6232 | 6.554 | 6.486 | 6.4192 | 6.3548 | 6.0394 | 5.7007 | 5.2902 | 6.7066 | 6.6928 | 6.6867 | 6.6782 | 6.6685 | 6.6567 | 6.589 | 6.5207 | 6.4536 | 6.3877 | 6.3242 | 6.2629 | 6.1995 | 6.1376
|  | SALEN | CT |  |  |  | 0 | 6.8108 | 6.8061 | 6.8022 | 6.7968 | 6.7903 | 6.7826 | 6.7744 | 6.7691 | 6.7635 | 6.7579 | 6.7353 | 6.541 | 6.3314 | 6.0947 | 6.7671 | 6.7624 | 6.7585 | 6.7531 | 6.7466 | 6.7389 | 6.7307 | 6.7164 | 6.6695 | 6.6238 | 6.5792 | 6.357 | 6.1208 | 5.858 | 6.7066 | 6.7019 | 6.698 | 6.6926 | 6.6861 | 6.6784 | 6.6702 | 6.6649 | 6.6347 | 6.5896 | 6.5457 | 6.5018 | 6.4573 | 6.4127
|  | SALEN | LW |  |  |  | 0 | 6.8108 | 6.797 | 6.7909 | 6.7824 | 6.7727 | 6.7621 | 6.751 | 6.7124 | 6.6532 | 6.5951 | 6.539 | 6.2629 | 5.9622 | 5.589 | 6.7671 | 6.7533 | 6.7472 | 6.7387 | 6.729 | 6.6918 | 6.6232 | 6.554 | 6.486 | 6.4192 | 6.3548 | 6.0394 | 5.7007 | 5.2902 | 6.7066 | 6.6928 | 6.6867 | 6.6782 | 6.6685 | 6.6567 | 6.589 | 6.5207 | 6.4536 | 6.3877 | 6.3242 | 6.2629 | 6.1995 | 6.1376
|  | SALEN | ST |  |  |  | 0 | 6.8108 | 6.809 | 6.8082 | 6.8059 | 6.8032 | 6.8 | 6.7964 | 6.795 | 6.7937 | 6.7924 | 6.7912 | 6.7855 | 6.6938 | 6.5823 | 6.7671 | 6.7653 | 6.7645 | 6.7622 | 6.7595 | 6.7563 | 6.7527 | 6.7514 | 6.75 | 6.7487 | 6.7475 | 6.6736 | 6.5295 | 6.4008 | 6.7066 | 6.7048 | 6.704 | 6.7017 | 6.699 | 6.6958 | 6.6922 | 6.6909 | 6.6895 | 6.6882 | 6.687 | 6.6391 | 6.4968 | 6.3699
|  | SALEN | FS |  |  |  | 0 | 6.8108 | 6.8091 | 6.8091 | 6.809 | 6.8088 | 6.8087 | 6.8085 | 6.8078 | 6.807 | 6.8061 | 6.8052 | 6.8027 | 6.7898 | 6.7387 | 6.7671 | 6.7654 | 6.7654 | 6.7653 | 6.7652 | 6.765 | 6.7648 | 6.7641 | 6.7633 | 6.7625 | 6.7615 | 6.759 | 6.6956 | 6.5816 | 6.7066 | 6.705 | 6.7049 | 6.7048 | 6.7047 | 6.7045 | 6.7043 | 6.7036 | 6.7028 | 6.702 | 6.701 | 6.6985 | 6.6608 | 6.5482
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | YES | 0.018947 | 2.7878 | 2.772 | 2.7639 | 2.7521 | 2.7391 | 2.7056 | 2.6649 | 2.625 | 2.5855 | 2.5462 | 2.5076 | 2.3073 | 2.0758 | 1.7688 | 2.9205 | 2.8891 | 2.862 | 2.8168 | 2.7711 | 2.7259 | 2.6812 | 2.6371 | 2.5934 | 2.55 | 2.5074 | 2.2872 | 2.0359 | 1.7095 | 2.7217 | 2.7068 | 2.7002 | 2.691 | 2.6805 | 2.6692 | 2.6572 | 2.6457 | 2.6009 | 2.5565 | 2.5127 | 2.4696 | 2.4245 | 2.3792
|  | SALEN 2 | CT |  |  |  | 0.018947 | 2.7878 | 2.7826 | 2.7774 | 2.7698 | 2.761 | 2.7512 | 2.7389 | 2.712 | 2.6853 | 2.6588 | 2.6326 | 2.4954 | 2.3373 | 2.1511 | 2.9249 | 2.9078 | 2.8895 | 2.8582 | 2.8261 | 2.7939 | 2.7619 | 2.7321 | 2.7024 | 2.6731 | 2.6441 | 2.4931 | 2.3213 | 2.1218 | 2.7217 | 2.7167 | 2.7125 | 2.7068 | 2.6999 | 2.6918 | 2.6831 | 2.6774 | 2.6716 | 2.6658 | 2.6525 | 2.6229 | 2.5919 | 2.5608
|  | SALEN 2 | LW |  |  |  | 0.018947 | 2.7878 | 2.772 | 2.7639 | 2.7521 | 2.7391 | 2.7056 | 2.6649 | 2.625 | 2.5855 | 2.5462 | 2.5076 | 2.3073 | 2.0758 | 1.7688 | 2.9205 | 2.8891 | 2.862 | 2.8168 | 2.7711 | 2.7259 | 2.6812 | 2.6371 | 2.5934 | 2.55 | 2.5074 | 2.2872 | 2.0359 | 1.7095 | 2.7217 | 2.7068 | 2.7002 | 2.691 | 2.6805 | 2.6692 | 2.6572 | 2.6457 | 2.6009 | 2.5565 | 2.5127 | 2.4696 | 2.4245 | 2.3792
|  | SALEN 2 | ST |  |  |  | 0.018947 | 2.7878 | 2.786 | 2.7851 | 2.7828 | 2.7793 | 2.7748 | 2.77 | 2.7674 | 2.7648 | 2.7623 | 2.7599 | 2.6929 | 2.6008 | 2.5246 | 2.9426 | 2.9393 | 2.9371 | 2.9183 | 2.8991 | 2.8802 | 2.8612 | 2.8429 | 2.8249 | 2.8073 | 2.79 | 2.7078 | 2.6068 | 2.5221 | 2.7217 | 2.7199 | 2.719 | 2.7167 | 2.7139 | 2.7105 | 2.7068 | 2.7054 | 2.704 | 2.7027 | 2.7014 | 2.6957 | 2.6138 | 2.5269
|  | SALEN 2 | FS |  |  |  | 0.018947 | 2.7878 | 2.7862 | 2.7861 | 2.7861 | 2.7859 | 2.7857 | 2.7853 | 2.7837 | 2.782 | 2.7802 | 2.7784 | 2.7682 | 2.7039 | 2.6311 | 2.9438 | 2.9409 | 2.9395 | 2.9375 | 2.9318 | 2.9207 | 2.9098 | 2.8963 | 2.8828 | 2.8693 | 2.8557 | 2.791 | 2.7196 | 2.6405 | 2.7217 | 2.7201 | 2.72 | 2.7199 | 2.7198 | 2.7196 | 2.7195 | 2.7188 | 2.718 | 2.7171 | 2.7162 | 2.7138 | 2.7011 | 2.6483
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0 | 1.2595 | 1.2541 | 1.249 | 1.2402 | 1.2233 | 1.2065 | 1.1898 | 1.1737 | 1.1576 | 1.1417 | 1.1251 | 1.0382 | 0.93285 | 0.78778 | 1.1873 | 1.1773 | 1.1671 | 1.1493 | 1.1308 | 1.1125 | 1.0944 | 1.0767 | 1.0592 | 1.0418 | 1.0237 | 0.92978 | 0.8172 | 0.66714 | 1.2337 | 1.2275 | 1.2215 | 1.2138 | 1.1983 | 1.1789 | 1.1596 | 1.1409 | 1.1223 | 1.1037 | 1.0846 | 1.0657 | 1.0458 | 1.0257
|  | SANDAY | CT |  |  |  | 0 | 1.2595 | 1.2541 | 1.249 | 1.2425 | 1.2289 | 1.215 | 1.2012 | 1.1883 | 1.1755 | 1.1627 | 1.15 | 1.0797 | 0.99516 | 0.89367 | 1.1873 | 1.1773 | 1.1671 | 1.1528 | 1.1381 | 1.1233 | 1.1085 | 1.0946 | 1.0808 | 1.067 | 1.0534 | 0.97842 | 0.88905 | 0.78287 | 1.2337 | 1.2275 | 1.2215 | 1.2143 | 1.2021 | 1.1895 | 1.1759 | 1.1612 | 1.1467 | 1.1322 | 1.1178 | 1.1034 | 1.0875 | 1.0715
|  | SANDAY | LW |  |  |  | 0 | 1.2654 | 1.2587 | 1.2552 | 1.2402 | 1.2233 | 1.2065 | 1.1898 | 1.1737 | 1.1576 | 1.1417 | 1.1251 | 1.0382 | 0.93285 | 0.78778 | 1.1905 | 1.1782 | 1.1675 | 1.1493 | 1.1308 | 1.1125 | 1.0944 | 1.0767 | 1.0592 | 1.0418 | 1.0237 | 0.92978 | 0.8172 | 0.66714 | 1.2391 | 1.2315 | 1.2268 | 1.2138 | 1.1983 | 1.1789 | 1.1596 | 1.1409 | 1.1223 | 1.1037 | 1.0846 | 1.0657 | 1.0458 | 1.0257
|  | SANDAY | ST |  |  |  | 0 | 1.2662 | 1.2646 | 1.2634 | 1.2615 | 1.2595 | 1.2572 | 1.2548 | 1.25 | 1.2438 | 1.2378 | 1.2318 | 1.2033 | 1.1658 | 1.1348 | 1.2004 | 1.1986 | 1.1972 | 1.1897 | 1.1821 | 1.1745 | 1.1669 | 1.1599 | 1.1531 | 1.1464 | 1.1398 | 1.1083 | 1.0678 | 1.034 | 1.2415 | 1.2399 | 1.2386 | 1.2358 | 1.2328 | 1.2296 | 1.2263 | 1.2225 | 1.2171 | 1.2118 | 1.2066 | 1.1738 | 1.1311 | 1.0952
|  | SANDAY | FS |  |  |  | 0 | 1.267 | 1.2655 | 1.2646 | 1.2637 | 1.2628 | 1.2619 | 1.261 | 1.2598 | 1.2586 | 1.2574 | 1.2524 | 1.227 | 1.1979 | 1.1625 | 1.2015 | 1.1998 | 1.1987 | 1.1974 | 1.1945 | 1.1901 | 1.1858 | 1.1799 | 1.1741 | 1.1682 | 1.1623 | 1.1341 | 1.1023 | 1.0644 | 1.2424 | 1.2408 | 1.2399 | 1.2389 | 1.2377 | 1.2362 | 1.2347 | 1.2327 | 1.2307 | 1.2287 | 1.2249 | 1.2013 | 1.1674 | 1.1276
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.50947 | 9.0199 | 8.9915 | 8.9789 | 8.9072 | 8.8272 | 8.7487 | 8.6724 | 8.5974 | 8.5233 | 8.4509 | 8.3807 | 8.0038 | 7.5379 | 6.918 | 8.4415 | 8.4131 | 8.4005 | 8.3829 | 8.2927 | 8.1915 | 8.0939 | 7.996 | 7.8996 | 7.8056 | 7.7145 | 7.2535 | 6.7349 | 6.0636 | 8.6335 | 8.6051 | 8.5925 | 8.575 | 8.5349 | 8.4397 | 8.3452 | 8.2475 | 8.1512 | 8.0574 | 7.9665 | 7.8784 | 7.7859 | 7.6926
|  | SANDBANK | CT |  |  |  | 0.50947 | 9.0199 | 9.0102 | 9.002 | 8.9908 | 8.9372 | 8.8801 | 8.8254 | 8.7748 | 8.7242 | 8.6752 | 8.6272 | 8.375 | 8.0822 | 7.6994 | 8.4415 | 8.4318 | 8.4236 | 8.4125 | 8.3988 | 8.3588 | 8.2891 | 8.2227 | 8.1564 | 8.0925 | 8.03 | 7.7074 | 7.3483 | 6.9299 | 8.6335 | 8.6238 | 8.6156 | 8.6045 | 8.5909 | 8.5749 | 8.5318 | 8.4695 | 8.4066 | 8.3439 | 8.2815 | 8.2192 | 8.1537 | 8.0887
|  | SANDBANK | LW |  |  |  | 0.50947 | 9.0199 | 8.9915 | 8.9789 | 8.9072 | 8.8272 | 8.7487 | 8.6724 | 8.5974 | 8.5233 | 8.4509 | 8.3807 | 8.0038 | 7.5379 | 6.918 | 8.4415 | 8.4131 | 8.4005 | 8.3829 | 8.2927 | 8.1915 | 8.0939 | 7.996 | 7.8996 | 7.8056 | 7.7145 | 7.2535 | 6.7349 | 6.0636 | 8.6335 | 8.6051 | 8.5925 | 8.575 | 8.5349 | 8.4397 | 8.3452 | 8.2475 | 8.1512 | 8.0574 | 7.9665 | 7.8784 | 7.7859 | 7.6926
|  | SANDBANK | ST |  |  |  | 0.50947 | 9.0199 | 9.0162 | 9.0145 | 9.0097 | 9.004 | 8.9973 | 8.9898 | 8.97 | 8.9401 | 8.9114 | 8.8831 | 8.7528 | 8.5867 | 8.4523 | 8.4415 | 8.4378 | 8.4361 | 8.4314 | 8.4256 | 8.4189 | 8.4114 | 8.4086 | 8.4058 | 8.3945 | 8.356 | 8.1782 | 7.969 | 7.7929 | 8.6335 | 8.6299 | 8.6281 | 8.6234 | 8.6177 | 8.6109 | 8.6034 | 8.6006 | 8.5978 | 8.5951 | 8.5925 | 8.4293 | 8.2206 | 8.0448
|  | SANDBANK | FS |  |  |  | 0.50947 | 9.0199 | 9.0165 | 9.0163 | 9.0161 | 9.0158 | 9.0155 | 9.0151 | 9.0136 | 9.012 | 9.0102 | 8.9927 | 8.8897 | 8.7739 | 8.6285 | 8.4415 | 8.4381 | 8.4379 | 8.4378 | 8.4375 | 8.4371 | 8.4367 | 8.4353 | 8.4336 | 8.4318 | 8.4298 | 8.3556 | 8.2043 | 8.0245 | 8.6335 | 8.6301 | 8.6299 | 8.6298 | 8.6295 | 8.6291 | 8.6287 | 8.6273 | 8.6256 | 8.6238 | 8.6218 | 8.5977 | 8.4548 | 8.2761
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0 | 3.8223 | 3.8046 | 3.7947 | 8.7414 | 8.7263 | 8.7099 | 8.6927 | 8.679 | 8.6651 | 8.651 | 8.6372 | 8.497 | 8.2358 | 7.8604 | 3.523 | 3.5052 | 3.4954 | 8.442 | 8.427 | 8.4106 | 8.3724 | 8.3267 | 8.2814 | 8.2365 | 8.1924 | 7.9585 | 7.6719 | 7.2655 | 3.4866 | 3.4689 | 3.4591 | 8.4057 | 8.3906 | 8.3742 | 8.357 | 8.3433 | 8.3294 | 8.3153 | 8.2925 | 8.2487 | 8.2016 | 8.1541
|  | SANDWICK | CT |  |  |  | 0 | 3.8223 | 3.8136 | 3.8059 | 8.7561 | 8.7445 | 8.7312 | 8.7171 | 8.7073 | 8.6972 | 8.6871 | 8.6768 | 8.6126 | 8.4821 | 8.2472 | 3.523 | 3.5142 | 3.5066 | 8.4568 | 8.4452 | 8.4319 | 8.4178 | 8.408 | 8.3846 | 8.353 | 8.3217 | 8.1542 | 7.9486 | 7.6965 | 3.4866 | 3.4779 | 3.4702 | 8.4204 | 8.4088 | 8.3956 | 8.3814 | 8.3716 | 8.3615 | 8.3514 | 8.3411 | 8.3306 | 8.3178 | 8.3046
|  | SANDWICK | LW |  |  |  | 0 | 3.8257 | 3.8046 | 3.7947 | 8.7414 | 8.7263 | 8.7099 | 8.6927 | 8.679 | 8.6651 | 8.651 | 8.6372 | 8.497 | 8.2358 | 7.8604 | 3.5263 | 3.5052 | 3.4954 | 8.442 | 8.427 | 8.4106 | 8.3724 | 8.3267 | 8.2814 | 8.2365 | 8.1924 | 7.9585 | 7.6719 | 7.2655 | 3.49 | 3.4689 | 3.4591 | 8.4057 | 8.3906 | 8.3742 | 8.357 | 8.3433 | 8.3294 | 8.3153 | 8.2925 | 8.2487 | 8.2016 | 8.1541
|  | SANDWICK | ST |  |  |  | 0 | 3.8257 | 3.823 | 3.8217 | 8.7783 | 8.7733 | 8.7675 | 8.7612 | 8.7583 | 8.7554 | 8.7534 | 8.7516 | 8.7405 | 8.6946 | 8.6685 | 3.5263 | 3.5237 | 3.5224 | 8.4789 | 8.4739 | 8.4682 | 8.4619 | 8.459 | 8.4561 | 8.4541 | 8.4522 | 8.4252 | 8.3185 | 8.2342 | 3.49 | 3.4873 | 3.486 | 8.4426 | 8.4376 | 8.4318 | 8.4255 | 8.4226 | 8.4197 | 8.4178 | 8.4159 | 8.4048 | 8.3589 | 8.3329
|  | SANDWICK | FS |  |  |  | 0 | 3.8257 | 3.8231 | 3.823 | 8.7829 | 8.7827 | 8.7824 | 8.7822 | 8.7811 | 8.7799 | 8.7785 | 8.7771 | 8.7732 | 8.7532 | 8.7095 | 3.5263 | 3.5238 | 3.5237 | 8.4836 | 8.4834 | 8.4831 | 8.4828 | 8.4817 | 8.4805 | 8.4792 | 8.4777 | 8.4739 | 8.4347 | 8.341 | 3.49 | 3.4875 | 3.4873 | 8.4472 | 8.447 | 8.4467 | 8.4465 | 8.4454 | 8.4442 | 8.4428 | 8.4414 | 8.4375 | 8.4175 | 8.3738
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0 | 2.6062 | 2.5865 | 2.5727 | 9.3141 | 9.2924 | 9.2639 | 9.2042 | 9.1465 | 9.0884 | 9.0306 | 8.9738 | 8.6712 | 8.2977 | 7.7658 | 2.1317 | 2.1119 | 2.0981 | 8.4395 | 8.4162 | 8.3907 | 8.3641 | 8.3421 | 8.3191 | 8.2692 | 8.2036 | 7.8575 | 7.4397 | 6.8641 | 2.1082 | 2.0884 | 2.0746 | 8.616 | 8.5943 | 8.5708 | 8.5462 | 8.5264 | 8.4986 | 8.433 | 8.3685 | 8.3049 | 8.237 | 8.1685
|  | SCALLOWAY | CT |  |  |  | 0 | 2.6062 | 2.5917 | 2.5786 | 9.3227 | 9.3043 | 9.2837 | 9.262 | 9.2378 | 9.1953 | 9.1533 | 9.1116 | 8.8842 | 8.6043 | 8.2582 | 2.1317 | 2.1171 | 2.1041 | 8.4481 | 8.4298 | 8.4082 | 8.385 | 8.3676 | 8.3498 | 8.3319 | 8.314 | 8.1087 | 7.7979 | 7.4218 | 2.1082 | 2.0936 | 2.0806 | 8.6246 | 8.6063 | 8.5857 | 8.5639 | 8.548 | 8.5316 | 8.5152 | 8.4987 | 8.4814 | 8.4304 | 8.379
|  | SCALLOWAY | LW |  |  |  | 0 | 2.6155 | 2.5865 | 2.5727 | 9.3141 | 9.2924 | 9.2639 | 9.2042 | 9.1465 | 9.0884 | 9.0306 | 8.9738 | 8.6712 | 8.2977 | 7.7658 | 2.1409 | 2.1119 | 2.0981 | 8.4395 | 8.4162 | 8.3907 | 8.3641 | 8.3421 | 8.3191 | 8.2692 | 8.2036 | 7.8575 | 7.4397 | 6.8641 | 2.1174 | 2.0884 | 2.0746 | 8.616 | 8.5943 | 8.5708 | 8.5462 | 8.5264 | 8.4986 | 8.433 | 8.3685 | 8.3049 | 8.237 | 8.1685
|  | SCALLOWAY | ST |  |  |  | 0 | 2.6172 | 2.6119 | 2.6094 | 9.3639 | 9.3566 | 9.3484 | 9.3394 | 9.335 | 9.3305 | 9.3262 | 9.322 | 9.2614 | 9.1227 | 9.0146 | 2.1426 | 2.1374 | 2.1348 | 8.4894 | 8.4821 | 8.4738 | 8.4648 | 8.4604 | 8.456 | 8.4512 | 8.4461 | 8.4219 | 8.3526 | 8.245 | 2.1191 | 2.1139 | 2.1113 | 8.6659 | 8.6586 | 8.6503 | 8.6413 | 8.6369 | 8.6325 | 8.6282 | 8.6239 | 8.6041 | 8.5332 | 8.4098
|  | SCALLOWAY | FS |  |  |  | 0 | 2.618 | 2.6138 | 2.6128 | 9.3718 | 9.3707 | 9.3695 | 9.3683 | 9.366 | 9.3635 | 9.3609 | 9.3581 | 9.3488 | 9.2811 | 9.1608 | 2.1435 | 2.1393 | 2.1383 | 8.4973 | 8.4961 | 8.4949 | 8.4937 | 8.4915 | 8.489 | 8.4864 | 8.4836 | 8.4722 | 8.4379 | 8.3722 | 2.12 | 2.1158 | 2.1148 | 8.6737 | 8.6726 | 8.6714 | 8.6702 | 8.6679 | 8.6655 | 8.6629 | 8.6601 | 8.6507 | 8.6198 | 8.5574
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.11752 | 0.11691 | 0.11664 | 0.11626 | 0.11583 | 0.11536 | 0.11487 | 0.11449 | 0.1141 | 0.11371 | 0.11332 | 0.11096 | 0.10647 | 0.096332 | 0.11737 | 0.11676 | 0.11649 | 0.11611 | 0.11568 | 0.11521 | 0.11472 | 0.11434 | 0.11395 | 0.11356 | 0.11317 | 0.10827 | 0.10066 | 0.08995 | 0.11771 | 0.1171 | 0.11683 | 0.11645 | 0.11602 | 0.11555 | 0.11506 | 0.11468 | 0.11429 | 0.1139 | 0.11326 | 0.11209 | 0.11084 | 0.10958
|  | SCAMMADALE | CT |  |  |  | 0 | 0.11752 | 0.11732 | 0.11715 | 0.11691 | 0.11662 | 0.11629 | 0.11593 | 0.1157 | 0.11546 | 0.11522 | 0.11498 | 0.11341 | 0.11097 | 0.10723 | 0.11737 | 0.11717 | 0.11699 | 0.11676 | 0.11647 | 0.11614 | 0.11578 | 0.11555 | 0.11531 | 0.11506 | 0.11482 | 0.11326 | 0.10919 | 0.10284 | 0.11771 | 0.11751 | 0.11734 | 0.1171 | 0.11681 | 0.11648 | 0.11612 | 0.11589 | 0.11565 | 0.11541 | 0.11517 | 0.11491 | 0.1146 | 0.11428
|  | SCAMMADALE | LW |  |  |  | 0 | 0.11752 | 0.11691 | 0.11664 | 0.11626 | 0.11583 | 0.11536 | 0.11487 | 0.11449 | 0.1141 | 0.11371 | 0.11332 | 0.11096 | 0.10647 | 0.096332 | 0.11737 | 0.11676 | 0.11649 | 0.11611 | 0.11568 | 0.11521 | 0.11472 | 0.11434 | 0.11395 | 0.11356 | 0.11317 | 0.10827 | 0.10066 | 0.08995 | 0.11771 | 0.1171 | 0.11683 | 0.11645 | 0.11602 | 0.11555 | 0.11506 | 0.11468 | 0.11429 | 0.1139 | 0.11326 | 0.11209 | 0.11084 | 0.10958
|  | SCAMMADALE | ST |  |  |  | 0 | 0.11752 | 0.11745 | 0.11741 | 0.11732 | 0.1172 | 0.11706 | 0.11691 | 0.11685 | 0.11679 | 0.11674 | 0.11669 | 0.11645 | 0.11529 | 0.11469 | 0.11737 | 0.1173 | 0.11726 | 0.11716 | 0.11705 | 0.11691 | 0.11676 | 0.1167 | 0.11664 | 0.11659 | 0.11653 | 0.11629 | 0.11513 | 0.11454 | 0.11771 | 0.11764 | 0.1176 | 0.11751 | 0.11739 | 0.11725 | 0.1171 | 0.11704 | 0.11698 | 0.11693 | 0.11688 | 0.11664 | 0.11548 | 0.11488
|  | SCAMMADALE | FS |  |  |  | 0 | 0.11752 | 0.11746 | 0.11746 | 0.11745 | 0.11745 | 0.11744 | 0.11743 | 0.11741 | 0.11737 | 0.11734 | 0.1173 | 0.1172 | 0.11669 | 0.11556 | 0.11737 | 0.11731 | 0.1173 | 0.1173 | 0.1173 | 0.11729 | 0.11728 | 0.11725 | 0.11722 | 0.11719 | 0.11715 | 0.11705 | 0.11653 | 0.11541 | 0.11771 | 0.11765 | 0.11765 | 0.11764 | 0.11764 | 0.11763 | 0.11762 | 0.1176 | 0.11756 | 0.11753 | 0.11749 | 0.11739 | 0.11688 | 0.11576
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 1.3484 | 17.1821 | 17.1207 | 17.0915 | 17.051 | 17.0053 | 16.9553 | 16.9026 | 16.8027 | 16.6672 | 16.5317 | 16.3983 | 15.6895 | 14.8178 | 13.574 | 15.9596 | 15.8412 | 15.746 | 15.5869 | 15.4253 | 15.2654 | 15.1074 | 14.953 | 14.7996 | 14.6465 | 14.4958 | 13.7023 | 12.7433 | 11.4126 | 16.5104 | 16.449 | 16.4198 | 16.3793 | 16.3336 | 16.2836 | 16.2085 | 16.0527 | 15.8981 | 15.7436 | 15.5917 | 15.442 | 15.2811 | 15.1189
|  | SCONE | CT |  |  |  | 1.3484 | 17.1821 | 17.1578 | 17.1377 | 17.111 | 17.0786 | 17.0411 | 17.0008 | 16.9731 | 16.9444 | 16.9081 | 16.8158 | 16.318 | 15.7062 | 14.9441 | 15.9701 | 15.9056 | 15.8398 | 15.7297 | 15.6159 | 15.5011 | 15.3867 | 15.28 | 15.1735 | 15.0681 | 14.9636 | 14.4064 | 13.7339 | 12.9122 | 16.5104 | 16.4861 | 16.466 | 16.4393 | 16.4069 | 16.3694 | 16.3291 | 16.3014 | 16.2727 | 16.1686 | 16.0632 | 15.9581 | 15.845 | 15.7312
|  | SCONE | LW |  |  |  | 1.3484 | 17.1855 | 17.1207 | 17.0915 | 17.051 | 17.0053 | 16.9553 | 16.9026 | 16.8027 | 16.6672 | 16.5317 | 16.3983 | 15.6895 | 14.8178 | 13.574 | 15.9596 | 15.8412 | 15.746 | 15.5869 | 15.4253 | 15.2654 | 15.1074 | 14.953 | 14.7996 | 14.6465 | 14.4958 | 13.7023 | 12.7433 | 11.4126 | 16.5138 | 16.449 | 16.4198 | 16.3793 | 16.3336 | 16.2836 | 16.2085 | 16.0527 | 15.8981 | 15.7436 | 15.5917 | 15.442 | 15.2811 | 15.1189
|  | SCONE | ST |  |  |  | 1.3484 | 17.1872 | 17.178 | 17.1732 | 17.1616 | 17.1477 | 17.1315 | 17.1136 | 17.1064 | 17.0991 | 17.0921 | 17.0854 | 17.0543 | 16.7479 | 16.4906 | 16.0375 | 16.025 | 16.0161 | 15.9501 | 15.8824 | 15.8151 | 15.7478 | 15.6864 | 15.6261 | 15.5673 | 15.51 | 15.242 | 14.8773 | 14.5849 | 16.5155 | 16.5063 | 16.5015 | 16.4899 | 16.476 | 16.4598 | 16.4419 | 16.4347 | 16.4274 | 16.4204 | 16.4137 | 16.343 | 15.9755 | 15.6805
|  | SCONE | FS |  |  |  | 1.3484 | 17.1872 | 17.1793 | 17.1789 | 17.1785 | 17.1779 | 17.177 | 17.1761 | 17.1727 | 17.1689 | 17.1647 | 17.1601 | 17.1446 | 17.0812 | 16.8185 | 16.0406 | 16.03 | 16.0265 | 16.0197 | 16.0022 | 15.9653 | 15.9286 | 15.8835 | 15.8382 | 15.7926 | 15.7467 | 15.5297 | 15.276 | 14.9561 | 16.5155 | 16.5076 | 16.5072 | 16.5068 | 16.5062 | 16.5053 | 16.5044 | 16.501 | 16.4972 | 16.493 | 16.4884 | 16.4729 | 16.377 | 16.055
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0 | 1.0431 | 1.0349 | 1.0267 | 1.0168 | 1.0068 | 0.99663 | 0.98645 | 0.97675 | 0.96705 | 0.95737 | 0.94772 | 0.89375 | 0.82866 | 0.75167 | 1.0321 | 1.023 | 1.0139 | 1.0024 | 0.99073 | 0.979 | 0.96729 | 0.95599 | 0.94471 | 0.93348 | 0.92229 | 0.86076 | 0.78806 | 0.70237 | 1.0928 | 1.086 | 1.0793 | 1.0723 | 1.0635 | 1.0521 | 1.0408 | 1.0298 | 1.0189 | 1.008 | 0.99713 | 0.98628 | 0.97429 | 0.96227
|  | SHAPINSAY | CT |  |  |  | 0 | 1.0431 | 1.0349 | 1.0267 | 1.0168 | 1.0068 | 0.99663 | 0.98645 | 0.97675 | 0.96705 | 0.95737 | 0.94772 | 0.89375 | 0.82866 | 0.75167 | 1.0321 | 1.023 | 1.0139 | 1.0024 | 0.99073 | 0.979 | 0.96729 | 0.95599 | 0.94471 | 0.93348 | 0.92229 | 0.86076 | 0.78806 | 0.7036 | 1.0928 | 1.086 | 1.0793 | 1.0723 | 1.0635 | 1.0521 | 1.0408 | 1.0298 | 1.0189 | 1.008 | 0.99713 | 0.98628 | 0.97429 | 0.96227
|  | SHAPINSAY | LW |  |  |  | 0 | 1.0521 | 1.046 | 1.0406 | 1.0322 | 1.0237 | 1.0151 | 1.0057 | 0.99666 | 0.98763 | 0.97861 | 0.96967 | 0.91904 | 0.85543 | 0.76988 | 1.0409 | 1.0338 | 1.027 | 1.0161 | 1.0052 | 0.99434 | 0.98271 | 0.97132 | 0.95999 | 0.9487 | 0.93753 | 0.87588 | 0.80088 | 0.70237 | 1.1021 | 1.0977 | 1.0948 | 1.0889 | 1.0785 | 1.0682 | 1.057 | 1.0461 | 1.0353 | 1.0245 | 1.0138 | 1.0032 | 0.99138 | 0.97946
|  | SHAPINSAY | ST |  |  |  | 0 | 1.0574 | 1.0553 | 1.0534 | 1.0495 | 1.0456 | 1.0417 | 1.0377 | 1.0341 | 1.0305 | 1.0269 | 1.0234 | 1.0063 | 0.98518 | 0.96693 | 1.0478 | 1.0457 | 1.0437 | 1.0389 | 1.034 | 1.0291 | 1.0242 | 1.0196 | 1.0151 | 1.0106 | 1.0062 | 0.98472 | 0.95935 | 0.93703 | 1.1046 | 1.1026 | 1.1007 | 1.0986 | 1.0963 | 1.094 | 1.0916 | 1.0897 | 1.0877 | 1.0834 | 1.0792 | 1.0587 | 1.0343 | 1.0128
|  | SHAPINSAY | FS |  |  |  | 0 | 1.0583 | 1.0571 | 1.0562 | 1.0552 | 1.054 | 1.0519 | 1.0497 | 1.0474 | 1.045 | 1.0426 | 1.0402 | 1.0286 | 1.0154 | 0.99935 | 1.0488 | 1.0476 | 1.0467 | 1.0456 | 1.0442 | 1.0413 | 1.0384 | 1.0352 | 1.032 | 1.0288 | 1.0256 | 1.0101 | 0.9931 | 0.97343 | 1.1054 | 1.1043 | 1.1034 | 1.1026 | 1.1017 | 1.1008 | 1.0999 | 1.099 | 1.098 | 1.0969 | 1.0959 | 1.0835 | 1.0673 | 1.0484
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0 | 1.1477 | 1.1437 | 1.1407 | 1.1358 | 1.1298 | 1.1238 | 1.1178 | 1.1121 | 1.1065 | 1.1008 | 1.0921 | 1.0473 | 0.99673 | 0.93217 | 1.1506 | 1.1479 | 1.1466 | 1.1449 | 1.14 | 1.13 | 1.1201 | 1.1105 | 1.1009 | 1.0914 | 1.082 | 1.0338 | 0.97988 | 0.91198 | 1.1525 | 1.1468 | 1.1404 | 1.1299 | 1.1192 | 1.1086 | 1.0982 | 1.088 | 1.0778 | 1.0678 | 1.0578 | 1.048 | 1.0378 | 1.0275
|  | SHIELDAIG | CT |  |  |  | 0 | 1.1485 | 1.1465 | 1.1445 | 1.1415 | 1.1383 | 1.1343 | 1.1302 | 1.1266 | 1.123 | 1.1195 | 1.1159 | 1.0946 | 1.0616 | 1.0235 | 1.1506 | 1.1497 | 1.1489 | 1.1479 | 1.1466 | 1.1451 | 1.1403 | 1.1341 | 1.128 | 1.1219 | 1.1159 | 1.0847 | 1.0496 | 1.0093 | 1.154 | 1.1509 | 1.1472 | 1.1404 | 1.1334 | 1.1264 | 1.1195 | 1.113 | 1.1065 | 1.1 | 1.0936 | 1.0873 | 1.0807 | 1.074
|  | SHIELDAIG | LW |  |  |  | 0 | 1.1477 | 1.1437 | 1.1407 | 1.1358 | 1.1298 | 1.1238 | 1.1178 | 1.1121 | 1.1065 | 1.1008 | 1.0921 | 1.0473 | 0.99673 | 0.93217 | 1.1506 | 1.1479 | 1.1466 | 1.1449 | 1.14 | 1.13 | 1.1201 | 1.1105 | 1.1009 | 1.0914 | 1.082 | 1.0338 | 0.97988 | 0.91198 | 1.1525 | 1.1468 | 1.1404 | 1.1299 | 1.1192 | 1.1086 | 1.0982 | 1.088 | 1.0778 | 1.0678 | 1.0578 | 1.048 | 1.0378 | 1.0275
|  | SHIELDAIG | ST |  |  |  | 0 | 1.15 | 1.1496 | 1.1494 | 1.1477 | 1.1459 | 1.144 | 1.1421 | 1.1406 | 1.1391 | 1.1372 | 1.1354 | 1.1264 | 1.1137 | 1.1023 | 1.1506 | 1.1503 | 1.1501 | 1.1497 | 1.1491 | 1.1485 | 1.1478 | 1.1476 | 1.1473 | 1.1471 | 1.1468 | 1.1304 | 1.11 | 1.0926 | 1.1568 | 1.1564 | 1.1561 | 1.1532 | 1.1502 | 1.1464 | 1.1422 | 1.1382 | 1.1343 | 1.1305 | 1.1267 | 1.1087 | 1.0872 | 1.0687
|  | SHIELDAIG | FS |  |  |  | 0 | 1.1501 | 1.1497 | 1.1497 | 1.1496 | 1.1491 | 1.1483 | 1.1475 | 1.1463 | 1.1451 | 1.1438 | 1.1425 | 1.1351 | 1.1257 | 1.1138 | 1.1506 | 1.1503 | 1.1503 | 1.1503 | 1.1502 | 1.1502 | 1.1502 | 1.1501 | 1.1499 | 1.1497 | 1.1496 | 1.1445 | 1.1279 | 1.109 | 1.1569 | 1.1566 | 1.1565 | 1.1563 | 1.1553 | 1.1539 | 1.1525 | 1.1502 | 1.1468 | 1.1434 | 1.14 | 1.1236 | 1.106 | 1.0861
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | YES | 0 | 2.5857 | 2.5816 | 2.5778 | 2.5735 | 2.5688 | 2.5622 | 2.5511 | 2.5406 | 2.5301 | 2.5197 | 2.5095 | 2.4526 | 2.3802 | 2.2813 | 2.5522 | 2.5448 | 2.5373 | 2.527 | 2.5143 | 2.5007 | 2.4874 | 2.4744 | 2.4616 | 2.4489 | 2.4364 | 2.3695 | 2.2904 | 2.185 | 2.5543 | 2.5474 | 2.5404 | 2.531 | 2.5204 | 2.5081 | 2.4959 | 2.4841 | 2.4725 | 2.461 | 2.4497 | 2.4385 | 2.4268 | 2.4141
|  | SHIN | CT |  |  |  | 0 | 2.5857 | 2.5816 | 2.5778 | 2.5735 | 2.5688 | 2.5638 | 2.5552 | 2.5464 | 2.5367 | 2.5271 | 2.5176 | 2.468 | 2.4078 | 2.334 | 2.5522 | 2.5448 | 2.5373 | 2.527 | 2.5166 | 2.5061 | 2.4956 | 2.4849 | 2.4735 | 2.4621 | 2.4508 | 2.3928 | 2.325 | 2.2462 | 2.5543 | 2.5474 | 2.5404 | 2.531 | 2.5214 | 2.5117 | 2.502 | 2.4923 | 2.4817 | 2.4713 | 2.4609 | 2.4505 | 2.4398 | 2.429
|  | SHIN | LW |  |  |  | 0 | 2.5916 | 2.5861 | 2.5833 | 2.5796 | 2.5733 | 2.5622 | 2.5511 | 2.5406 | 2.5301 | 2.5197 | 2.5095 | 2.4526 | 2.3802 | 2.2813 | 2.5573 | 2.5477 | 2.5399 | 2.5272 | 2.5143 | 2.5007 | 2.4874 | 2.4744 | 2.4616 | 2.4489 | 2.4364 | 2.3695 | 2.2904 | 2.185 | 2.5595 | 2.5504 | 2.5434 | 2.532 | 2.5204 | 2.5081 | 2.4959 | 2.4841 | 2.4725 | 2.461 | 2.4497 | 2.4385 | 2.4268 | 2.4141
|  | SHIN | ST |  |  |  | 0 | 2.5924 | 2.591 | 2.5899 | 2.5883 | 2.5866 | 2.5848 | 2.5828 | 2.5815 | 2.5802 | 2.579 | 2.5767 | 2.5582 | 2.5336 | 2.5138 | 2.5647 | 2.5632 | 2.5619 | 2.5561 | 2.5503 | 2.5445 | 2.5387 | 2.5334 | 2.5282 | 2.5231 | 2.5181 | 2.4945 | 2.4652 | 2.4409 | 2.5659 | 2.5644 | 2.5631 | 2.558 | 2.5528 | 2.5476 | 2.5423 | 2.5376 | 2.533 | 2.5284 | 2.524 | 2.503 | 2.4761 | 2.4541
|  | SHIN | FS |  |  |  | 0 | 2.5932 | 2.5927 | 2.5919 | 2.591 | 2.5901 | 2.5892 | 2.5883 | 2.5873 | 2.5862 | 2.5851 | 2.584 | 2.5752 | 2.5566 | 2.534 | 2.566 | 2.5654 | 2.5643 | 2.5632 | 2.5613 | 2.5575 | 2.5537 | 2.5493 | 2.545 | 2.5407 | 2.5363 | 2.5154 | 2.4926 | 2.4661 | 2.5671 | 2.5665 | 2.5655 | 2.5644 | 2.5627 | 2.5593 | 2.5559 | 2.5521 | 2.5482 | 2.5443 | 2.5404 | 2.5219 | 2.5012 | 2.4767
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0 | 0.10492 | 0.10475 | 0.10467 | 0.10456 | 0.10444 | 0.1043 | 0.10416 | 0.10405 | 0.10394 | 0.10382 | 0.10371 | 0.10302 | 0.10193 | 0.098911 | 0.10526 | 0.10507 | 0.10499 | 0.10487 | 0.10473 | 0.10458 | 0.10443 | 0.10431 | 0.10415 | 0.10379 | 0.10344 | 0.10156 | 0.099268 | 0.095997 | 0.10469 | 0.10451 | 0.10443 | 0.10433 | 0.1042 | 0.10407 | 0.10393 | 0.10382 | 0.1037 | 0.10359 | 0.10348 | 0.10337 | 0.10323 | 0.10308
|  | SHONA BEG | CT |  |  |  | 0 | 0.10492 | 0.10486 | 0.10481 | 0.10474 | 0.10465 | 0.10455 | 0.10445 | 0.10438 | 0.10431 | 0.10423 | 0.10416 | 0.10368 | 0.10292 | 0.10174 | 0.10526 | 0.10519 | 0.10514 | 0.10506 | 0.10496 | 0.10485 | 0.10474 | 0.10466 | 0.10458 | 0.1045 | 0.10441 | 0.10331 | 0.10171 | 0.099717 | 0.10469 | 0.10463 | 0.10457 | 0.1045 | 0.10442 | 0.10432 | 0.10421 | 0.10414 | 0.10407 | 0.104 | 0.10392 | 0.10385 | 0.10375 | 0.10365
|  | SHONA BEG | LW |  |  |  | 0 | 0.10492 | 0.10475 | 0.10467 | 0.10456 | 0.10444 | 0.1043 | 0.10416 | 0.10405 | 0.10394 | 0.10382 | 0.10371 | 0.10302 | 0.10193 | 0.098911 | 0.10526 | 0.10507 | 0.10499 | 0.10487 | 0.10473 | 0.10458 | 0.10443 | 0.10431 | 0.10415 | 0.10379 | 0.10344 | 0.10156 | 0.099268 | 0.095997 | 0.10469 | 0.10451 | 0.10443 | 0.10433 | 0.1042 | 0.10407 | 0.10393 | 0.10382 | 0.1037 | 0.10359 | 0.10348 | 0.10337 | 0.10323 | 0.10308
|  | SHONA BEG | ST |  |  |  | 0 | 0.10492 | 0.1049 | 0.10489 | 0.10486 | 0.10482 | 0.10478 | 0.10473 | 0.10472 | 0.1047 | 0.10468 | 0.10466 | 0.10459 | 0.10423 | 0.10404 | 0.10526 | 0.10524 | 0.10523 | 0.10519 | 0.10515 | 0.1051 | 0.10505 | 0.10503 | 0.10501 | 0.10498 | 0.10496 | 0.10486 | 0.10447 | 0.10383 | 0.10469 | 0.10466 | 0.10465 | 0.10462 | 0.10459 | 0.10455 | 0.1045 | 0.10448 | 0.10446 | 0.10445 | 0.10443 | 0.10436 | 0.10399 | 0.10381
|  | SHONA BEG | FS |  |  |  | 0 | 0.10492 | 0.1049 | 0.1049 | 0.1049 | 0.1049 | 0.10489 | 0.10489 | 0.10488 | 0.10487 | 0.10486 | 0.10485 | 0.10482 | 0.10464 | 0.10427 | 0.10527 | 0.10524 | 0.10524 | 0.10524 | 0.10524 | 0.10523 | 0.10522 | 0.10521 | 0.1052 | 0.10518 | 0.10516 | 0.10511 | 0.10491 | 0.10452 | 0.10469 | 0.10466 | 0.10466 | 0.10466 | 0.10466 | 0.10466 | 0.10466 | 0.10465 | 0.10464 | 0.10463 | 0.10461 | 0.10458 | 0.10441 | 0.10404
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 0.14316 | 32.9232 | 32.8337 | 32.7855 | 32.7184 | 32.6427 | 32.5598 | 32.472 | 32.4021 | 32.3306 | 32.2582 | 32.1871 | 31.7518 | 31.0856 | 29.7826 | 30.8674 | 30.7779 | 30.7256 | 30.6424 | 30.5513 | 30.2925 | 29.9692 | 29.6489 | 29.3365 | 29.033 | 28.745 | 27.3022 | 25.6753 | 23.524 | 31.7184 | 31.629 | 31.5807 | 31.5137 | 31.438 | 31.3551 | 31.2673 | 31.1973 | 31.119 | 31.0318 | 30.912 | 30.6663 | 30.4059 | 30.1438
|  | SKENE | CT |  |  |  | 0.14316 | 32.9232 | 32.8793 | 32.8408 | 32.7918 | 32.734 | 32.6689 | 32.5999 | 32.5511 | 32.501 | 32.4508 | 32.4003 | 32.0818 | 31.5988 | 30.8796 | 30.8674 | 30.8235 | 30.785 | 30.7322 | 30.6636 | 30.588 | 30.5096 | 30.3863 | 30.1659 | 29.955 | 29.7507 | 28.7098 | 27.5537 | 26.1936 | 31.7184 | 31.6746 | 31.6361 | 31.5871 | 31.5292 | 31.4642 | 31.3951 | 31.3463 | 31.2963 | 31.2461 | 31.1956 | 31.1435 | 31.0762 | 31.002
|  | SKENE | LW |  |  |  | 0.14316 | 32.9392 | 32.8337 | 32.7855 | 32.7184 | 32.6427 | 32.5598 | 32.472 | 32.4021 | 32.3306 | 32.2582 | 32.1871 | 31.7518 | 31.0856 | 29.7826 | 30.8834 | 30.7779 | 30.7256 | 30.6424 | 30.5513 | 30.2925 | 29.9692 | 29.6489 | 29.3365 | 29.033 | 28.745 | 27.3022 | 25.6753 | 23.524 | 31.7344 | 31.629 | 31.5807 | 31.5137 | 31.438 | 31.3551 | 31.2673 | 31.1973 | 31.119 | 31.0318 | 30.912 | 30.6663 | 30.4059 | 30.1438
|  | SKENE | ST |  |  |  | 0.14316 | 32.9434 | 32.9289 | 32.9211 | 32.9029 | 32.8804 | 32.8544 | 32.8256 | 32.8133 | 32.8009 | 32.7889 | 32.7773 | 32.7239 | 32.5117 | 32.3963 | 30.8876 | 30.8731 | 30.8653 | 30.8471 | 30.8246 | 30.7986 | 30.7693 | 30.7505 | 30.7316 | 30.7134 | 30.6958 | 30.3947 | 29.7576 | 29.2436 | 31.7386 | 31.7242 | 31.7164 | 31.6982 | 31.6756 | 31.6496 | 31.6209 | 31.6086 | 31.5962 | 31.5842 | 31.5726 | 31.5191 | 31.307 | 31.1746
|  | SKENE | FS |  |  |  | 0.14316 | 32.9451 | 32.9324 | 32.9302 | 32.9279 | 32.9253 | 32.9223 | 32.9193 | 32.9126 | 32.9052 | 32.8973 | 32.8888 | 32.8623 | 32.7606 | 32.5497 | 30.8893 | 30.8766 | 30.8744 | 30.8721 | 30.8695 | 30.8665 | 30.8635 | 30.8568 | 30.8494 | 30.839 | 30.8255 | 30.7754 | 30.4716 | 29.9262 | 31.7403 | 31.7277 | 31.7255 | 31.7232 | 31.7206 | 31.7176 | 31.7146 | 31.7079 | 31.7005 | 31.6925 | 31.6841 | 31.6575 | 31.5558 | 31.3449
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 0.018947 | 1.6661 | 1.6255 | 1.591 | 1.5348 | 1.4766 | 1.4186 | 1.361 | 1.3056 | 1.2497 | 1.1925 | 1.134 | 0.82722 | 0.46313 | -0.031001 | 1.5682 | 1.5518 | 1.5394 | 1.5228 | 1.5034 | 1.4825 | 1.4135 | 1.3429 | 1.2721 | 1.2018 | 1.1327 | 0.77422 | 0.35825 | -0.18661 | 1.616 | 1.5995 | 1.5871 | 1.5706 | 1.5512 | 1.481 | 1.4099 | 1.3401 | 1.2701 | 1.2007 | 1.1323 | 1.0649 | 0.99434 | 0.9232
|  | SKULAMUS | CT |  |  |  | 0.018947 | 1.6661 | 1.6391 | 1.6115 | 1.5697 | 1.5264 | 1.4824 | 1.4384 | 1.3977 | 1.3571 | 1.3169 | 1.277 | 1.0551 | 0.78583 | 0.46452 | 1.5682 | 1.5551 | 1.5433 | 1.529 | 1.5126 | 1.4944 | 1.4752 | 1.461 | 1.4137 | 1.3632 | 1.3132 | 1.049 | 0.74361 | 0.38726 | 1.616 | 1.6029 | 1.591 | 1.5767 | 1.5604 | 1.5421 | 1.5111 | 1.4604 | 1.4099 | 1.3599 | 1.3105 | 1.2612 | 1.2088 | 1.1562
|  | SKULAMUS | LW |  |  |  | 0.018947 | 1.6695 | 1.6255 | 1.591 | 1.5348 | 1.4766 | 1.4186 | 1.361 | 1.3056 | 1.2497 | 1.1925 | 1.134 | 0.82722 | 0.46313 | -0.031001 | 1.5775 | 1.5518 | 1.5394 | 1.5228 | 1.5034 | 1.4825 | 1.4135 | 1.3429 | 1.2721 | 1.2018 | 1.1327 | 0.77422 | 0.35825 | -0.18661 | 1.6253 | 1.5995 | 1.5871 | 1.5706 | 1.5512 | 1.481 | 1.4099 | 1.3401 | 1.2701 | 1.2007 | 1.1323 | 1.0649 | 0.99434 | 0.9232
|  | SKULAMUS | ST |  |  |  | 0.018947 | 1.697 | 1.6911 | 1.6869 | 1.6641 | 1.6398 | 1.6154 | 1.591 | 1.5687 | 1.5467 | 1.5253 | 1.5042 | 1.4043 | 1.275 | 1.1649 | 1.5792 | 1.5745 | 1.5723 | 1.5676 | 1.5613 | 1.5542 | 1.5465 | 1.5425 | 1.5386 | 1.5347 | 1.5309 | 1.453 | 1.2937 | 1.1612 | 1.6269 | 1.6223 | 1.62 | 1.6154 | 1.6091 | 1.602 | 1.5943 | 1.5903 | 1.5863 | 1.5825 | 1.5787 | 1.4496 | 1.292 | 1.161
|  | SKULAMUS | FS |  |  |  | 0.018947 | 1.6992 | 1.6946 | 1.6925 | 1.689 | 1.6824 | 1.6696 | 1.6568 | 1.6414 | 1.6257 | 1.61 | 1.5942 | 1.5201 | 1.4331 | 1.325 | 1.58 | 1.5765 | 1.5756 | 1.5746 | 1.5735 | 1.5724 | 1.5713 | 1.5693 | 1.5672 | 1.565 | 1.5626 | 1.5543 | 1.487 | 1.3554 | 1.6278 | 1.6243 | 1.6233 | 1.6224 | 1.6213 | 1.6202 | 1.619 | 1.6171 | 1.615 | 1.6127 | 1.6104 | 1.5937 | 1.4833 | 1.3529
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 0.58421 | 24.7921 | 42.3709 | 42.2984 | 40.9146 | 39.106 | 37.4289 | 35.9903 | 34.4941 | 33.1067 | 31.8128 | 30.7174 | 26.0388 | 21.8562 | 17.0516 | 23.2944 | 40.6232 | 38.6679 | 36.4171 | 34.3214 | 32.3815 | 30.7217 | 28.9898 | 27.3856 | 25.891 | 24.6285 | 19.2725 | 14.5651 | 9.2999 | 23.9359 | 41.7397 | 40.3334 | 38.2486 | 36.1764 | 34.2537 | 32.6084 | 30.8708 | 29.2602 | 27.7597 | 26.4922 | 25.3949 | 24.2868 | 23.2068
|  | SPRINGHILL | CT |  |  |  | 0.58421 | 24.7921 | 42.4624 | 42.411 | 42.3432 | 42.2612 | 41.312 | 40.2618 | 39.2352 | 38.2468 | 37.3755 | 36.5954 | 33.0367 | 30.0276 | 26.802 | 23.2944 | 40.7147 | 40.6633 | 39.8747 | 38.4049 | 36.8872 | 35.6764 | 34.4876 | 33.3438 | 32.3372 | 31.4375 | 27.3581 | 23.9715 | 20.4029 | 23.9359 | 41.8311 | 41.7798 | 41.4505 | 40.0879 | 38.6799 | 37.5183 | 36.3401 | 35.2066 | 34.2088 | 33.317 | 32.4265 | 31.5567 | 30.7519
|  | SPRINGHILL | LW |  |  |  | 0.58421 | 24.8023 | 42.3709 | 42.2984 | 40.9146 | 39.106 | 37.4289 | 35.9903 | 34.4941 | 33.1067 | 31.8128 | 30.7174 | 26.0388 | 21.8562 | 17.0516 | 23.3045 | 40.6232 | 38.6679 | 36.4171 | 34.3214 | 32.3815 | 30.7217 | 28.9898 | 27.3856 | 25.891 | 24.6285 | 19.2725 | 14.5651 | 9.2999 | 23.946 | 41.7397 | 40.3334 | 38.2486 | 36.1764 | 34.2537 | 32.6084 | 30.8708 | 29.2602 | 27.7597 | 26.4922 | 25.3949 | 24.2868 | 23.2068
|  | SPRINGHILL | ST |  |  |  | 0.58421 | 24.8039 | 42.5114 | 42.5003 | 42.4715 | 42.436 | 42.3946 | 42.3486 | 42.3303 | 42.3119 | 42.2942 | 42.071 | 39.5582 | 37.4768 | 35.7291 | 23.3062 | 40.7637 | 40.7525 | 40.7238 | 40.6882 | 40.6468 | 40.5695 | 39.8546 | 39.1114 | 38.4134 | 37.756 | 34.8304 | 32.4588 | 30.4482 | 23.9477 | 41.8802 | 41.869 | 41.8403 | 41.8047 | 41.7633 | 41.7173 | 41.431 | 40.7437 | 40.0983 | 39.4903 | 36.6817 | 34.3291 | 32.3357
|  | SPRINGHILL | FS |  |  |  | 0.58421 | 24.8039 | 42.5114 | 42.5096 | 42.5076 | 42.5051 | 42.5018 | 42.4986 | 42.4885 | 42.4772 | 42.4648 | 42.4515 | 41.4891 | 39.859 | 38.1082 | 23.3062 | 40.7637 | 40.7619 | 40.7599 | 40.7573 | 40.7541 | 40.7509 | 40.7408 | 40.6739 | 40.0989 | 39.5386 | 37.0524 | 35.1764 | 33.1947 | 23.9477 | 41.8802 | 41.8784 | 41.8764 | 41.8738 | 41.8706 | 41.8674 | 41.8573 | 41.8459 | 41.6668 | 41.1487 | 38.8515 | 37.0247 | 35.0581
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 0.031579 | 6.7637 | 6.7484 | 6.7342 | 6.6612 | 6.574 | 6.4891 | 6.4105 | 6.3318 | 6.2549 | 6.1811 | 6.1125 | 5.7735 | 5.3906 | 4.9022 | 6.6981 | 6.6189 | 6.5365 | 6.427 | 6.3214 | 6.2193 | 6.1252 | 6.0302 | 5.9376 | 5.8492 | 5.7671 | 5.3737 | 4.9518 | 4.4266 | 6.2545 | 6.2393 | 6.225 | 6.2088 | 6.1916 | 6.1728 | 6.1532 | 6.137 | 6.1205 | 6.1039 | 6.0874 | 6.0705 | 6.0506 | 6.0083
|  | ST CYRUS | CT |  |  |  | 0.031579 | 6.7637 | 6.7484 | 6.7342 | 6.7179 | 6.6751 | 6.6075 | 6.5465 | 6.4879 | 6.4301 | 6.3755 | 6.3234 | 6.0599 | 5.7776 | 5.4466 | 6.6981 | 6.6661 | 6.6066 | 6.5302 | 6.4517 | 6.3712 | 6.2992 | 6.2294 | 6.1606 | 6.096 | 6.0345 | 5.7277 | 5.4079 | 5.0469 | 6.2545 | 6.2393 | 6.225 | 6.2088 | 6.1916 | 6.1728 | 6.1532 | 6.137 | 6.1205 | 6.1039 | 6.0874 | 6.0705 | 6.0507 | 6.0306
|  | ST CYRUS | LW |  |  |  | 0.031579 | 6.778 | 6.7552 | 6.7437 | 6.6612 | 6.574 | 6.4891 | 6.4105 | 6.3318 | 6.2549 | 6.1811 | 6.1125 | 5.7735 | 5.3906 | 4.9022 | 6.7075 | 6.6189 | 6.5365 | 6.427 | 6.3214 | 6.2193 | 6.1252 | 6.0302 | 5.9376 | 5.8492 | 5.7671 | 5.3737 | 4.9518 | 4.4266 | 6.2688 | 6.246 | 6.2345 | 6.2186 | 6.201 | 6.1813 | 6.1608 | 6.1438 | 6.1258 | 6.1077 | 6.0898 | 6.0721 | 6.0506 | 6.0083
|  | ST CYRUS | ST |  |  |  | 0.031579 | 6.7814 | 6.7771 | 6.7742 | 6.7693 | 6.7628 | 6.7557 | 6.7479 | 6.7435 | 6.7227 | 6.6912 | 6.6609 | 6.5224 | 6.3756 | 6.255 | 6.7158 | 6.7115 | 6.7087 | 6.7037 | 6.6631 | 6.6213 | 6.5815 | 6.5419 | 6.5018 | 6.4632 | 6.4259 | 6.2563 | 6.0842 | 5.9403 | 6.2722 | 6.268 | 6.2651 | 6.2602 | 6.2537 | 6.2465 | 6.2388 | 6.2343 | 6.2299 | 6.2255 | 6.2212 | 6.2005 | 6.1492 | 6.1163
|  | ST CYRUS | FS |  |  |  | 0.031579 | 6.783 | 6.7799 | 6.7781 | 6.7763 | 6.7744 | 6.7725 | 6.7706 | 6.7679 | 6.7651 | 6.7622 | 6.7592 | 6.6548 | 6.5475 | 6.4219 | 6.7174 | 6.7143 | 6.7125 | 6.7107 | 6.7089 | 6.6967 | 6.6718 | 6.6419 | 6.611 | 6.5809 | 6.5507 | 6.4138 | 6.2851 | 6.1389 | 6.2739 | 6.2708 | 6.269 | 6.2672 | 6.2653 | 6.2634 | 6.2614 | 6.2588 | 6.256 | 6.2531 | 6.2501 | 6.2381 | 6.2116 | 6.1638
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 0 | 22.8291 | 22.7892 | 22.7492 | 22.6977 | 22.6461 | 22.596 | 22.5477 | 22.5009 | 22.4545 | 22.4093 | 22.3673 | 22.153 | 21.9046 | 21.5663 | 29.0684 | 29.0272 | 28.9862 | 28.9334 | 28.8805 | 28.8292 | 28.78 | 28.7321 | 28.6847 | 28.6385 | 28.5956 | 28.3773 | 28.1254 | 27.7837 | 25.9055 | 25.8901 | 25.8763 | 25.8609 | 25.8441 | 25.8261 | 25.8075 | 25.7913 | 25.7749 | 25.7584 | 25.7419 | 25.7252 | 25.706 | 25.6865
|  | ST FERGUS GAS TERM | CT |  |  |  | 0 | 22.8291 | 22.7974 | 22.7644 | 22.7236 | 22.6812 | 22.6377 | 22.5972 | 22.5586 | 22.5205 | 22.4842 | 22.4491 | 22.2654 | 22.0566 | 21.8073 | 29.0684 | 29.0361 | 29.0025 | 28.9608 | 28.9175 | 28.8731 | 28.8319 | 28.7925 | 28.7537 | 28.7168 | 28.6811 | 28.4944 | 28.2831 | 28.0314 | 25.9055 | 25.8901 | 25.8763 | 25.8609 | 25.8441 | 25.8261 | 25.8075 | 25.7913 | 25.7749 | 25.7584 | 25.7419 | 25.7252 | 25.706 | 25.6865
|  | ST FERGUS GAS TERM | LW |  |  |  | 0 | 22.8346 | 22.7892 | 22.7492 | 22.6977 | 22.6461 | 22.596 | 22.5477 | 22.5009 | 22.4545 | 22.4093 | 22.3673 | 22.153 | 21.9046 | 21.5663 | 29.0734 | 29.0272 | 28.9862 | 28.9334 | 28.8805 | 28.8292 | 28.78 | 28.7321 | 28.6847 | 28.6385 | 28.5956 | 28.3773 | 28.1254 | 27.7837 | 25.9224 | 25.9041 | 25.8938 | 25.8807 | 25.8655 | 25.8493 | 25.8316 | 25.8167 | 25.8007 | 25.7847 | 25.7688 | 25.7531 | 25.7342 | 25.7148
|  | ST FERGUS GAS TERM | ST |  |  |  | 0 | 22.8649 | 22.8552 | 22.846 | 22.8272 | 22.8075 | 22.787 | 22.7675 | 22.7495 | 22.7311 | 22.7135 | 22.6961 | 22.6169 | 22.524 | 22.4464 | 29.1047 | 29.0948 | 29.0854 | 29.0662 | 29.0459 | 29.025 | 29.0051 | 28.9866 | 28.9677 | 28.9496 | 28.9318 | 28.8506 | 28.756 | 28.6769 | 25.9257 | 25.9212 | 25.9177 | 25.9127 | 25.907 | 25.9009 | 25.8943 | 25.8902 | 25.8862 | 25.8822 | 25.8782 | 25.8593 | 25.8155 | 25.7835
|  | ST FERGUS GAS TERM | FS |  |  |  | 0 | 22.8684 | 22.8623 | 22.8564 | 22.8492 | 22.84 | 22.8285 | 22.8171 | 22.8038 | 22.7899 | 22.7765 | 22.763 | 22.702 | 22.6394 | 22.561 | 29.1082 | 29.102 | 29.096 | 29.0886 | 29.0792 | 29.0674 | 29.0556 | 29.0419 | 29.0277 | 29.0139 | 29.0001 | 28.9373 | 28.8734 | 28.7937 | 25.9274 | 25.9248 | 25.923 | 25.9212 | 25.9194 | 25.9175 | 25.9156 | 25.9132 | 25.9106 | 25.908 | 25.9053 | 25.8941 | 25.8714 | 25.8319
| ST FILLANS | ST FILLANS | MINIMUM HEADROOM | NN 6942 2464 | YES | NO | 0 | 7.4959 | 7.4937 | 7.4916 | 7.4883 | 7.4851 | 7.4818 | 7.4793 | 7.4761 | 7.473 | 7.4698 | 7.4666 | 7.4506 | 7.4336 | 7.4131 | 7.4957 | 7.4935 | 7.4913 | 7.4879 | 7.4843 | 7.4808 | 7.4782 | 7.4748 | 7.4714 | 7.468 | 7.4646 | 7.4474 | 7.4294 | 7.4078 | 7.4957 | 7.4935 | 7.4913 | 7.4879 | 7.4844 | 7.4809 | 7.4782 | 7.4748 | 7.4714 | 7.468 | 7.4646 | 7.4612 | 7.4578 | 7.4544
|  | ST FILLANS | CT |  |  |  | 0 | 7.4959 | 7.4937 | 7.4916 | 7.4883 | 7.4851 | 7.4818 | 7.4793 | 7.4761 | 7.473 | 7.4698 | 7.4666 | 7.4506 | 7.4336 | 7.4131 | 7.4957 | 7.4935 | 7.4913 | 7.4879 | 7.4843 | 7.4808 | 7.4782 | 7.4748 | 7.4714 | 7.468 | 7.4646 | 7.4474 | 7.4294 | 7.4078 | 7.4957 | 7.4935 | 7.4913 | 7.4879 | 7.4844 | 7.4809 | 7.4782 | 7.4748 | 7.4714 | 7.468 | 7.4646 | 7.4612 | 7.4578 | 7.4544
|  | ST FILLANS | LW |  |  |  | 0 | 7.4983 | 7.4974 | 7.4958 | 7.493 | 7.4902 | 7.4875 | 7.4847 | 7.482 | 7.4793 | 7.4766 | 7.4739 | 7.4603 | 7.4429 | 7.4208 | 7.4982 | 7.4971 | 7.4955 | 7.4925 | 7.4894 | 7.4863 | 7.4833 | 7.4803 | 7.4774 | 7.4744 | 7.4715 | 7.4566 | 7.438 | 7.4146 | 7.4982 | 7.4971 | 7.4955 | 7.4925 | 7.4894 | 7.4864 | 7.4833 | 7.4804 | 7.4774 | 7.4745 | 7.4716 | 7.4687 | 7.4657 | 7.4627
|  | ST FILLANS | ST |  |  |  | 0 | 7.4988 | 7.4987 | 7.4987 | 7.4982 | 7.4978 | 7.4973 | 7.4968 | 7.4964 | 7.4961 | 7.4957 | 7.4953 | 7.4936 | 7.4912 | 7.486 | 7.4988 | 7.4987 | 7.4986 | 7.4981 | 7.4976 | 7.4971 | 7.4965 | 7.4961 | 7.4956 | 7.4952 | 7.4948 | 7.4929 | 7.4902 | 7.4848 | 7.4988 | 7.4987 | 7.4986 | 7.4981 | 7.4976 | 7.4971 | 7.4965 | 7.4961 | 7.4956 | 7.4952 | 7.4948 | 7.4929 | 7.4902 | 7.4848
|  | ST FILLANS | FS |  |  |  | 0 | 7.4997 | 7.4996 | 7.4996 | 7.4996 | 7.4995 | 7.4992 | 7.499 | 7.4987 | 7.4984 | 7.4981 | 7.4978 | 7.4965 | 7.4948 | 7.4927 | 7.4997 | 7.4996 | 7.4996 | 7.4995 | 7.4994 | 7.4991 | 7.4988 | 7.4985 | 7.4982 | 7.4978 | 7.4975 | 7.4959 | 7.494 | 7.4917 | 7.4997 | 7.4996 | 7.4996 | 7.4995 | 7.4994 | 7.4991 | 7.4988 | 7.4985 | 7.4982 | 7.4978 | 7.4975 | 7.4959 | 7.4941 | 7.4917
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | YES | 0.030526 | 24.1509 | 24.0934 | 24.0671 | 24.0305 | 23.989 | 23.9418 | 23.8913 | 23.851 | 23.8089 | 23.7653 | 23.7219 | 22.8308 | 21.5782 | 19.8092 | 23.7825 | 23.6832 | 23.6135 | 23.5209 | 23.3639 | 23.1198 | 22.8929 | 22.6629 | 22.4393 | 22.2215 | 22.0186 | 20.98 | 19.7467 | 17.9976 | 24.401 | 24.3435 | 24.3172 | 24.2806 | 24.2339 | 24.1715 | 24.1074 | 23.8509 | 23.5901 | 23.3365 | 23.1009 | 22.8782 | 22.6344 | 22.3925
|  | ST MACHAR | CT |  |  |  | 0.030526 | 24.1509 | 24.1315 | 24.1149 | 24.0927 | 24.0656 | 24.0328 | 23.9968 | 23.9725 | 23.9463 | 23.9194 | 23.8917 | 23.698 | 23.0939 | 21.9955 | 23.7989 | 23.7551 | 23.7108 | 23.6526 | 23.5884 | 23.5181 | 23.4351 | 23.2793 | 23.1245 | 22.9778 | 22.8377 | 22.097 | 21.2343 | 20.1499 | 24.401 | 24.3815 | 24.3649 | 24.3427 | 24.3157 | 24.2828 | 24.2466 | 24.2122 | 24.176 | 24.1399 | 24.053 | 23.8881 | 23.7116 | 23.5397
|  | ST MACHAR | LW |  |  |  | 0.030526 | 24.1526 | 24.0934 | 24.0671 | 24.0305 | 23.989 | 23.9418 | 23.8913 | 23.851 | 23.8089 | 23.7653 | 23.7219 | 22.8308 | 21.5782 | 19.8092 | 23.7825 | 23.6832 | 23.6135 | 23.5209 | 23.3639 | 23.1198 | 22.8929 | 22.6629 | 22.4393 | 22.2215 | 22.0186 | 20.98 | 19.7467 | 17.9976 | 24.4027 | 24.3435 | 24.3172 | 24.2806 | 24.2339 | 24.1715 | 24.1074 | 23.8509 | 23.5901 | 23.3365 | 23.1009 | 22.8782 | 22.6344 | 22.3925
|  | ST MACHAR | ST |  |  |  | 0.030526 | 24.1526 | 24.1437 | 24.1394 | 24.1278 | 24.1138 | 24.0973 | 24.079 | 24.0721 | 24.0652 | 24.0586 | 24.0522 | 24.0215 | 23.8461 | 23.752 | 23.8207 | 23.8044 | 23.7915 | 23.7608 | 23.7266 | 23.6895 | 23.652 | 23.6238 | 23.5951 | 23.5674 | 23.5407 | 23.2122 | 22.6946 | 22.256 | 24.4027 | 24.3937 | 24.3894 | 24.3779 | 24.3638 | 24.3474 | 24.329 | 24.3222 | 24.3152 | 24.3086 | 24.3023 | 24.2522 | 23.8901 | 23.3808
|  | ST MACHAR | FS |  |  |  | 0.030526 | 24.1526 | 24.1419 | 24.1414 | 24.1408 | 24.14 | 24.1388 | 24.1376 | 24.133 | 24.1278 | 24.1221 | 24.1158 | 24.0993 | 24.0096 | 23.8076 | 23.822 | 23.805 | 23.7977 | 23.789 | 23.7769 | 23.76 | 23.7433 | 23.7213 | 23.698 | 23.6746 | 23.6509 | 23.5374 | 23.164 | 22.6751 | 24.4027 | 24.3919 | 24.3914 | 24.3908 | 24.39 | 24.3888 | 24.3876 | 24.383 | 24.3778 | 24.3721 | 24.3659 | 24.3491 | 24.2375 | 23.8746
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 0 | 1.2189 | 1.1954 | 1.185 | 1.1705 | 1.1541 | 1.1361 | 1.1172 | 1.1023 | 1.0872 | 1.0719 | 1.0569 | 0.96372 | 0.8176 | 0.53835 | 1.0306 | 0.98428 | 0.94553 | 0.88083 | 0.81525 | 0.75047 | 0.68644 | 0.62351 | 0.56106 | 0.49907 | 0.43808 | 0.1192 | -0.25627 | -0.76224 | 1.1136 | 1.075 | 1.0458 | 0.99801 | 0.94898 | 0.89996 | 0.85113 | 0.80439 | 0.7579 | 0.71163 | 0.66612 | 0.62122 | 0.57262 | 0.52343
|  | ST MARYS | CT |  |  |  | 0 | 1.2189 | 1.2107 | 1.2038 | 1.1945 | 1.1831 | 1.1697 | 1.1554 | 1.146 | 1.1363 | 1.1266 | 1.1168 | 1.0527 | 0.95049 | 0.793 | 1.0369 | 1.0112 | 0.98499 | 0.94061 | 0.89488 | 0.84885 | 0.80304 | 0.75986 | 0.71682 | 0.67422 | 0.63204 | 0.40892 | 0.14618 | -0.16843 | 1.1178 | 1.098 | 1.0783 | 1.0457 | 1.0115 | 0.97653 | 0.94132 | 0.90954 | 0.87773 | 0.8462 | 0.81492 | 0.78358 | 0.74957 | 0.71524
|  | ST MARYS | LW |  |  |  | 0 | 1.2189 | 1.1954 | 1.185 | 1.1705 | 1.1541 | 1.1361 | 1.1172 | 1.1023 | 1.0872 | 1.0719 | 1.0569 | 0.96372 | 0.8176 | 0.53835 | 1.0306 | 0.98428 | 0.94553 | 0.88083 | 0.81525 | 0.75047 | 0.68644 | 0.62351 | 0.56106 | 0.49907 | 0.43808 | 0.1192 | -0.25627 | -0.76224 | 1.1136 | 1.075 | 1.0458 | 0.99801 | 0.94898 | 0.89996 | 0.85113 | 0.80439 | 0.7579 | 0.71163 | 0.66612 | 0.62122 | 0.57262 | 0.52343
|  | ST MARYS | ST |  |  |  | 0 | 1.2189 | 1.2158 | 1.2143 | 1.2104 | 1.2056 | 1.1999 | 1.1937 | 1.1913 | 1.1889 | 1.1867 | 1.1845 | 1.1747 | 1.1259 | 1.1009 | 1.0631 | 1.0582 | 1.055 | 1.0282 | 1.0008 | 0.97366 | 0.94651 | 0.92095 | 0.89584 | 0.87131 | 0.84735 | 0.7336 | 0.58535 | 0.46403 | 1.1352 | 1.1309 | 1.1283 | 1.1092 | 1.0894 | 1.0695 | 1.0493 | 1.0316 | 1.0142 | 0.99713 | 0.98051 | 0.90177 | 0.78705 | 0.69816
|  | ST MARYS | FS |  |  |  | 0 | 1.2189 | 1.216 | 1.2158 | 1.2157 | 1.2155 | 1.2151 | 1.2148 | 1.2136 | 1.2122 | 1.2107 | 1.209 | 1.2046 | 1.1817 | 1.1316 | 1.0643 | 1.0599 | 1.058 | 1.0552 | 1.0479 | 1.0325 | 1.0171 | 0.99813 | 0.97901 | 0.95981 | 0.94052 | 0.84981 | 0.74553 | 0.61814 | 1.136 | 1.132 | 1.1308 | 1.1289 | 1.1239 | 1.1136 | 1.1033 | 1.0903 | 1.0772 | 1.0639 | 1.0506 | 0.98891 | 0.91204 | 0.81072
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 0.0094737 | 18.2162 | 18.1813 | 18.1658 | 18.1442 | 18.1197 | 18.0918 | 18.062 | 17.935 | 17.6802 | 17.4379 | 17.2227 | 16.2147 | 15.172 | 13.8589 | 17.7941 | 17.7451 | 17.625 | 17.3408 | 17.0326 | 16.7409 | 16.4822 | 16.1823 | 15.8804 | 15.5937 | 15.3396 | 14.1729 | 13 | 11.5611 | 17.8584 | 17.8068 | 17.7737 | 17.7314 | 17.6875 | 17.5504 | 17.2519 | 16.9406 | 16.6459 | 16.366 | 16.1178 | 15.8931 | 15.6591 | 15.4285
|  | ST NICHOLAS | CT |  |  |  | 0.0094737 | 18.2162 | 18.2052 | 18.1959 | 18.1833 | 18.1679 | 18.149 | 18.1282 | 18.1143 | 18.0993 | 18.0838 | 18.0679 | 17.5084 | 16.7881 | 15.9438 | 17.8009 | 17.7818 | 17.7631 | 17.7365 | 17.5733 | 17.3772 | 17.1916 | 17.0087 | 16.8298 | 16.6669 | 16.5171 | 15.6852 | 14.8588 | 13.9187 | 17.8665 | 17.8458 | 17.8255 | 17.8 | 17.771 | 17.7383 | 17.7063 | 17.6809 | 17.6534 | 17.465 | 17.2918 | 17.1175 | 16.9417 | 16.7751
|  | ST NICHOLAS | LW |  |  |  | 0.0094737 | 18.2162 | 18.1813 | 18.1658 | 18.1442 | 18.1197 | 18.0918 | 18.062 | 17.935 | 17.6802 | 17.4379 | 17.2227 | 16.2147 | 15.172 | 13.8589 | 17.7941 | 17.7451 | 17.625 | 17.3408 | 17.0326 | 16.7409 | 16.4822 | 16.1823 | 15.8804 | 15.5937 | 15.3396 | 14.1729 | 13 | 11.5611 | 17.8584 | 17.8068 | 17.7737 | 17.7314 | 17.6875 | 17.5504 | 17.2519 | 16.9406 | 16.6459 | 16.366 | 16.1178 | 15.8931 | 15.6591 | 15.4285
|  | ST NICHOLAS | ST |  |  |  | 0.0094737 | 18.2162 | 18.2109 | 18.2083 | 18.2015 | 18.1931 | 18.1833 | 18.1724 | 18.1683 | 18.1642 | 18.1603 | 18.1565 | 18.1382 | 18.0334 | 17.7882 | 17.8063 | 17.798 | 17.7921 | 17.7797 | 17.7655 | 17.7497 | 17.7332 | 17.7054 | 17.6151 | 17.5291 | 17.4403 | 16.9546 | 16.4798 | 16.0179 | 17.8728 | 17.8641 | 17.8575 | 17.8441 | 17.8288 | 17.8119 | 17.7944 | 17.783 | 17.7713 | 17.7602 | 17.7496 | 17.6995 | 17.2541 | 16.7789
|  | ST NICHOLAS | FS |  |  |  | 0.0094737 | 18.2162 | 18.2097 | 18.2094 | 18.209 | 18.2085 | 18.2078 | 18.2071 | 18.2043 | 18.2011 | 18.1977 | 18.1939 | 18.1839 | 18.1295 | 18.0072 | 17.8071 | 17.7982 | 17.7952 | 17.7918 | 17.7876 | 17.7824 | 17.7773 | 17.7697 | 17.7614 | 17.7415 | 17.6731 | 17.3201 | 16.9605 | 16.5383 | 17.8738 | 17.8645 | 17.8611 | 17.8571 | 17.8521 | 17.8461 | 17.8402 | 17.8317 | 17.8225 | 17.8131 | 17.8035 | 17.7669 | 17.6918 | 17.3273
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0 | 1.2031 | 1.1965 | 1.1935 | 1.1894 | 1.1847 | 1.1783 | 1.1718 | 1.1662 | 1.159 | 1.1409 | 1.1231 | 1.0296 | 0.91988 | 0.77251 | 1.0617 | 1.0551 | 1.0521 | 1.048 | 1.0434 | 1.0383 | 1.0329 | 1.0287 | 1.0245 | 1.0201 | 1.001 | 0.8956 | 0.77379 | 0.61439 | 1.1902 | 1.1836 | 1.1807 | 1.1766 | 1.1719 | 1.1668 | 1.1615 | 1.1573 | 1.1484 | 1.1283 | 1.1085 | 1.089 | 1.0683 | 1.0475
|  | STOCKINISH | CT |  |  |  | 0 | 1.2031 | 1.2008 | 1.1988 | 1.1961 | 1.1929 | 1.1891 | 1.1845 | 1.1809 | 1.1772 | 1.1735 | 1.1698 | 1.1124 | 1.0352 | 0.94278 | 1.0617 | 1.0594 | 1.0574 | 1.0548 | 1.0515 | 1.0477 | 1.0436 | 1.0409 | 1.0382 | 1.0354 | 1.0326 | 0.98872 | 0.90304 | 0.80223 | 1.1902 | 1.1879 | 1.1859 | 1.1833 | 1.18 | 1.1762 | 1.1721 | 1.1695 | 1.1667 | 1.1639 | 1.1611 | 1.1553 | 1.1407 | 1.1261
|  | STOCKINISH | LW |  |  |  | 0 | 1.2031 | 1.1965 | 1.1935 | 1.1894 | 1.1847 | 1.1783 | 1.1718 | 1.1662 | 1.159 | 1.1409 | 1.1231 | 1.0296 | 0.91988 | 0.77251 | 1.0617 | 1.0551 | 1.0521 | 1.048 | 1.0434 | 1.0383 | 1.0329 | 1.0287 | 1.0245 | 1.0201 | 1.001 | 0.8956 | 0.77379 | 0.61439 | 1.1902 | 1.1836 | 1.1807 | 1.1766 | 1.1719 | 1.1668 | 1.1615 | 1.1573 | 1.1484 | 1.1283 | 1.1085 | 1.089 | 1.0683 | 1.0475
|  | STOCKINISH | ST |  |  |  | 0 | 1.2031 | 1.2022 | 1.2018 | 1.2006 | 1.1993 | 1.1977 | 1.1958 | 1.1952 | 1.1945 | 1.1938 | 1.1931 | 1.1875 | 1.1659 | 1.1311 | 1.0617 | 1.0608 | 1.0604 | 1.0593 | 1.0579 | 1.0563 | 1.0545 | 1.0538 | 1.0531 | 1.0525 | 1.0518 | 1.049 | 1.035 | 1.0083 | 1.1902 | 1.1893 | 1.1889 | 1.1878 | 1.1864 | 1.1848 | 1.183 | 1.1823 | 1.1816 | 1.181 | 1.1804 | 1.1776 | 1.1548 | 1.116
|  | STOCKINISH | FS |  |  |  | 0 | 1.2031 | 1.2022 | 1.2022 | 1.2022 | 1.2021 | 1.202 | 1.2019 | 1.2016 | 1.2012 | 1.2007 | 1.2002 | 1.1986 | 1.1899 | 1.1734 | 1.0617 | 1.0609 | 1.0608 | 1.0608 | 1.0607 | 1.0606 | 1.0605 | 1.0602 | 1.0598 | 1.0593 | 1.0589 | 1.0576 | 1.0509 | 1.0365 | 1.1902 | 1.1894 | 1.1894 | 1.1893 | 1.1892 | 1.1891 | 1.1891 | 1.1887 | 1.1883 | 1.1879 | 1.1874 | 1.1861 | 1.1795 | 1.165
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.33553 | 0.33544 | 0.33535 | 0.33524 | 0.3351 | 0.33485 | 0.3335 | 0.33218 | 0.33087 | 0.32956 | 0.32826 | 0.32001 | 0.30954 | 0.29845 | 0.32581 | 0.32571 | 0.32562 | 0.32551 | 0.32537 | 0.32521 | 0.32504 | 0.3249 | 0.32339 | 0.32189 | 0.3204 | 0.31145 | 0.3001 | 0.28814 | 0.32673 | 0.32663 | 0.32654 | 0.32643 | 0.32629 | 0.32613 | 0.32504 | 0.32352 | 0.32201 | 0.3205 | 0.31901 | 0.31753 | 0.316 | 0.31444
|  | STONEFIELD | CT |  |  |  | 0 | 0.33553 | 0.33544 | 0.33535 | 0.33524 | 0.3351 | 0.33492 | 0.33373 | 0.33259 | 0.33145 | 0.33031 | 0.32918 | 0.32001 | 0.30954 | 0.29845 | 0.32581 | 0.32571 | 0.32562 | 0.32551 | 0.32537 | 0.32521 | 0.32504 | 0.32493 | 0.32412 | 0.3228 | 0.3215 | 0.31145 | 0.3001 | 0.28814 | 0.32673 | 0.32663 | 0.32654 | 0.32643 | 0.32629 | 0.32613 | 0.32537 | 0.32405 | 0.32273 | 0.32142 | 0.32011 | 0.3188 | 0.31662 | 0.31444
|  | STONEFIELD | LW |  |  |  | 0 | 0.33638 | 0.33609 | 0.33596 | 0.33579 | 0.33559 | 0.33485 | 0.3335 | 0.33218 | 0.33087 | 0.32956 | 0.32826 | 0.3216 | 0.31428 | 0.30204 | 0.32665 | 0.32636 | 0.32624 | 0.32606 | 0.32586 | 0.32564 | 0.32541 | 0.3249 | 0.32339 | 0.32189 | 0.3204 | 0.31278 | 0.30449 | 0.29129 | 0.32757 | 0.32728 | 0.32716 | 0.32698 | 0.32678 | 0.32656 | 0.32504 | 0.32352 | 0.32201 | 0.3205 | 0.31901 | 0.31753 | 0.316 | 0.31447
|  | STONEFIELD | ST |  |  |  | 0 | 0.33638 | 0.33634 | 0.33632 | 0.33627 | 0.33622 | 0.33615 | 0.33607 | 0.33605 | 0.33602 | 0.33599 | 0.33596 | 0.33585 | 0.33527 | 0.33497 | 0.32665 | 0.32661 | 0.32659 | 0.32655 | 0.32649 | 0.32642 | 0.32635 | 0.32632 | 0.32629 | 0.32626 | 0.32624 | 0.32612 | 0.32554 | 0.32524 | 0.32757 | 0.32753 | 0.32751 | 0.32747 | 0.32741 | 0.32734 | 0.32727 | 0.32724 | 0.32721 | 0.32718 | 0.32716 | 0.32704 | 0.32646 | 0.32616
|  | STONEFIELD | FS |  |  |  | 0 | 0.33638 | 0.33634 | 0.33634 | 0.33634 | 0.33634 | 0.33633 | 0.33633 | 0.33631 | 0.3363 | 0.33628 | 0.33626 | 0.33621 | 0.33594 | 0.33535 | 0.32665 | 0.32661 | 0.32661 | 0.32661 | 0.32661 | 0.3266 | 0.3266 | 0.32659 | 0.32657 | 0.32655 | 0.32653 | 0.32648 | 0.32621 | 0.32562 | 0.32757 | 0.32753 | 0.32753 | 0.32753 | 0.32753 | 0.32752 | 0.32752 | 0.3275 | 0.32749 | 0.32747 | 0.32745 | 0.3274 | 0.32713 | 0.32654
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 0.32632 | 25.432 | 25.3609 | 25.2958 | 25.2205 | 25.1373 | 25.0458 | 24.9509 | 24.8745 | 24.7956 | 24.7073 | 24.6193 | 24.0781 | 23.0657 | 20.6567 | 23.858 | 23.4764 | 23.122 | 22.6457 | 22.1799 | 21.7309 | 21.3112 | 20.8864 | 20.4752 | 20.0757 | 19.7022 | 17.86 | 15.8269 | 13.2176 | 24.7439 | 24.6727 | 24.6077 | 24.5324 | 24.4491 | 24.3577 | 24.2628 | 24.1864 | 24.1075 | 23.9856 | 23.62 | 23.2729 | 22.91 | 22.5458
|  | STONEHAVEN | CT |  |  |  | 0.32632 | 25.432 | 25.3609 | 25.2958 | 25.2205 | 25.1373 | 25.0458 | 24.9509 | 24.8745 | 24.7956 | 24.7165 | 24.6361 | 24.1514 | 23.4565 | 22.4818 | 23.9106 | 23.6712 | 23.4153 | 23.0795 | 22.7305 | 22.3754 | 22.0529 | 21.7397 | 21.4305 | 21.1367 | 20.8546 | 19.4259 | 17.8759 | 16.0797 | 24.7439 | 24.6727 | 24.6077 | 24.5324 | 24.4491 | 24.3577 | 24.2628 | 24.1864 | 24.1075 | 24.0284 | 23.948 | 23.8659 | 23.7709 | 23.6725
|  | STONEHAVEN | LW |  |  |  | 0.32632 | 25.4951 | 25.3833 | 25.3258 | 25.2491 | 25.1622 | 25.0669 | 24.9665 | 24.882 | 24.7956 | 24.7073 | 24.6193 | 24.0781 | 23.0657 | 20.6567 | 23.858 | 23.4764 | 23.122 | 22.6457 | 22.1799 | 21.7309 | 21.3112 | 20.8864 | 20.4752 | 20.0757 | 19.7022 | 17.86 | 15.8269 | 13.2176 | 24.807 | 24.6951 | 24.6377 | 24.5609 | 24.474 | 24.3787 | 24.2784 | 24.1939 | 24.1075 | 23.9856 | 23.62 | 23.2729 | 22.91 | 22.5458
|  | STONEHAVEN | ST |  |  |  | 0.32632 | 25.5078 | 25.4854 | 25.4708 | 25.4455 | 25.4141 | 25.38 | 25.3432 | 25.3231 | 25.3029 | 25.2831 | 25.2646 | 25.1728 | 24.9078 | 24.7367 | 24.1414 | 24.0733 | 24.0039 | 23.8321 | 23.6498 | 23.4654 | 23.2882 | 23.1144 | 22.9386 | 22.7698 | 22.6077 | 21.8502 | 21.0238 | 20.3207 | 24.8196 | 24.7973 | 24.7827 | 24.7574 | 24.726 | 24.6919 | 24.6551 | 24.6349 | 24.6147 | 24.595 | 24.5765 | 24.4846 | 24.2197 | 24.0486
|  | STONEHAVEN | FS |  |  |  | 0.32632 | 25.5145 | 25.4977 | 25.4904 | 25.483 | 25.4753 | 25.4671 | 25.459 | 25.4477 | 25.4358 | 25.4232 | 25.41 | 25.3544 | 25.2192 | 24.9653 | 24.169 | 24.1136 | 24.0644 | 24.0057 | 23.9239 | 23.8086 | 23.6955 | 23.5648 | 23.4291 | 23.2948 | 23.162 | 22.5425 | 21.9371 | 21.2393 | 24.8264 | 24.8096 | 24.8023 | 24.7949 | 24.7871 | 24.779 | 24.7709 | 24.7596 | 24.7476 | 24.735 | 24.7219 | 24.6663 | 24.531 | 24.2771
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | 2.9663 | 2.9662 | 2.9661 | 2.966 | 2.9659 | 2.9659 | 2.9658 | 2.9657 | 2.9656 | 2.9655 | 2.9654 | 2.965 | 2.9645 | 2.9638 | 4.0105 | 4.0104 | 4.0103 | 4.0102 | 4.0101 | 4.01 | 4.0099 | 4.0098 | 4.0098 | 4.0097 | 4.0096 | 4.0091 | 4.0086 | 4.0079 | 3.101 | 3.1009 | 3.1009 | 3.1008 | 3.1008 | 3.1007 | 3.1006 | 3.1006 | 3.1005 | 3.1004 | 3.1004 | 3.1003 | 3.1003 | 3.1002
|  | STONEYHILL | CT |  |  |  | 0 | 2.9663 | 2.9662 | 2.9662 | 2.9661 | 2.9661 | 2.966 | 2.9659 | 2.9659 | 2.9658 | 2.9658 | 2.9657 | 2.9654 | 2.9651 | 2.9647 | 4.0105 | 4.0104 | 4.0104 | 4.0103 | 4.0103 | 4.0102 | 4.0101 | 4.0101 | 4.01 | 4.0099 | 4.0099 | 4.0096 | 4.0092 | 4.0088 | 3.101 | 3.101 | 3.101 | 3.1009 | 3.1009 | 3.1008 | 3.1008 | 3.1007 | 3.1007 | 3.1006 | 3.1006 | 3.1006 | 3.1005 | 3.1005
|  | STONEYHILL | LW |  |  |  | 0 | 2.9663 | 2.9662 | 2.9661 | 2.966 | 2.9659 | 2.9659 | 2.9658 | 2.9657 | 2.9656 | 2.9655 | 2.9654 | 2.965 | 2.9645 | 2.9638 | 4.0105 | 4.0104 | 4.0103 | 4.0102 | 4.0101 | 4.01 | 4.0099 | 4.0098 | 4.0098 | 4.0097 | 4.0096 | 4.0091 | 4.0086 | 4.0079 | 3.101 | 3.1009 | 3.1009 | 3.1008 | 3.1008 | 3.1007 | 3.1006 | 3.1006 | 3.1005 | 3.1004 | 3.1004 | 3.1003 | 3.1003 | 3.1002
|  | STONEYHILL | ST |  |  |  | 0 | 2.9663 | 2.9663 | 2.9663 | 2.9662 | 2.9662 | 2.9662 | 2.9661 | 2.9661 | 2.9661 | 2.9661 | 2.966 | 2.9659 | 2.9657 | 2.9656 | 4.0105 | 4.0105 | 4.0105 | 4.0104 | 4.0104 | 4.0104 | 4.0103 | 4.0103 | 4.0103 | 4.0102 | 4.0102 | 4.0101 | 4.0099 | 4.0097 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.1009 | 3.1009 | 3.1009 | 3.1009 | 3.1008 | 3.1008 | 3.1006 | 3.1005
|  | STONEYHILL | FS |  |  |  | 0 | 2.9663 | 2.9663 | 2.9663 | 2.9663 | 2.9663 | 2.9663 | 2.9662 | 2.9662 | 2.9662 | 2.9662 | 2.9662 | 2.9661 | 2.9659 | 2.9658 | 4.0105 | 4.0105 | 4.0105 | 4.0105 | 4.0105 | 4.0105 | 4.0104 | 4.0104 | 4.0104 | 4.0104 | 4.0103 | 4.0102 | 4.0101 | 4.0099 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.101 | 3.1009 | 3.1009 | 3.1008 | 3.1007
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0.21053 | 24.8376 | 24.4637 | 23.5688 | 22.5255 | 21.5601 | 20.6716 | 19.9224 | 19.1316 | 18.4038 | 17.7306 | 17.1724 | 14.8985 | 13.0688 | 11.2232 | 23.2756 | 22.1889 | 21.0679 | 19.8453 | 18.7165 | 17.6787 | 16.8047 | 15.8808 | 15.031 | 14.2453 | 13.5947 | 10.9541 | 8.8523 | 6.7738 | 24.0233 | 23.0985 | 21.9735 | 20.7505 | 19.6214 | 18.5833 | 17.709 | 16.7848 | 15.9347 | 15.1487 | 14.4979 | 13.9456 | 13.398 | 12.8695
|  | STONEYWOOD T1&T2 | CT |  |  |  | 0.21053 | 24.8376 | 24.8219 | 24.7293 | 24.1335 | 23.4982 | 22.7957 | 22.2465 | 21.7024 | 21.1814 | 20.7282 | 20.3289 | 18.5689 | 17.2414 | 15.9311 | 23.3855 | 23.2033 | 22.5187 | 21.7788 | 20.9855 | 20.165 | 19.5247 | 18.8891 | 18.2806 | 17.7518 | 17.2863 | 15.2414 | 13.717 | 12.2309 | 24.0233 | 24.0076 | 23.4321 | 22.6847 | 21.8911 | 21.0703 | 20.4299 | 19.794 | 19.1854 | 18.6564 | 18.1907 | 17.7258 | 17.287 | 16.8879
|  | STONEYWOOD T1&T2 | LW |  |  |  | 0.21053 | 24.8409 | 24.4637 | 23.5688 | 22.5255 | 21.5601 | 20.6716 | 19.9224 | 19.1316 | 18.4038 | 17.7306 | 17.1724 | 14.8985 | 13.0688 | 11.2232 | 23.2756 | 22.1889 | 21.0679 | 19.8453 | 18.7165 | 17.6787 | 16.8047 | 15.8808 | 15.031 | 14.2453 | 13.5947 | 10.9541 | 8.8523 | 6.7738 | 24.0266 | 23.0985 | 21.9735 | 20.7505 | 19.6214 | 18.5833 | 17.709 | 16.7848 | 15.9347 | 15.1487 | 14.4979 | 13.9456 | 13.398 | 12.8695
|  | STONEYWOOD T1&T2 | ST |  |  |  | 0.21053 | 24.8418 | 24.8357 | 24.8324 | 24.8248 | 24.8124 | 24.7266 | 24.4437 | 24.1359 | 23.8141 | 23.5104 | 23.2059 | 21.8581 | 20.859 | 19.9932 | 23.4037 | 23.3875 | 23.372 | 23.2808 | 22.9101 | 22.516 | 22.1659 | 21.7822 | 21.3775 | 20.9981 | 20.6415 | 19.0628 | 17.9057 | 16.8979 | 24.0275 | 24.0214 | 24.0181 | 24.0105 | 23.8194 | 23.4294 | 23.0753 | 22.6881 | 22.2832 | 21.9037 | 21.547 | 19.9678 | 18.8103 | 17.8022
|  | STONEYWOOD T1&T2 | FS |  |  |  | 0.21053 | 24.8426 | 24.8373 | 24.8362 | 24.8351 | 24.8339 | 24.8333 | 24.8194 | 24.7138 | 24.4584 | 24.2114 | 23.9715 | 22.8579 | 22.052 | 21.2369 | 23.4087 | 23.3948 | 23.3846 | 23.3732 | 23.3214 | 23.0497 | 22.7873 | 22.4938 | 22.1758 | 21.8681 | 21.5662 | 20.2266 | 19.2888 | 18.3488 | 24.0283 | 24.023 | 24.022 | 24.0208 | 24.0196 | 23.9505 | 23.7036 | 23.4066 | 23.0849 | 22.774 | 22.472 | 21.132 | 20.1938 | 19.2535
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | YES | YES | 0 | 14.9764 | 14.9668 | 14.9625 | 14.9566 | 14.9499 | 14.9425 | 14.9348 | 14.9287 | 14.9225 | 14.9162 | 14.91 | 14.8717 | 14.8113 | 14.6958 | 13.8991 | 13.8895 | 13.8852 | 13.8793 | 13.8726 | 13.8652 | 13.8575 | 13.8514 | 13.8452 | 13.8389 | 13.8327 | 13.7944 | 13.734 | 13.6185 | 14.2541 | 14.2446 | 14.2403 | 14.2344 | 14.2277 | 14.2203 | 14.2125 | 14.2065 | 14.2003 | 14.194 | 14.1878 | 14.1817 | 14.1741 | 14.1662
|  | STONEYWOOD T3 | CT |  |  |  | 0 | 14.9764 | 14.973 | 14.9702 | 14.9663 | 14.9616 | 14.9561 | 14.9502 | 14.9463 | 14.9423 | 14.9383 | 14.9342 | 14.9076 | 14.8651 | 14.7994 | 13.8991 | 13.8957 | 13.8929 | 13.889 | 13.8843 | 13.8788 | 13.8729 | 13.869 | 13.865 | 13.861 | 13.8569 | 13.8303 | 13.7878 | 13.7221 | 14.2541 | 14.2508 | 14.248 | 14.2441 | 14.2394 | 14.2339 | 14.228 | 14.2241 | 14.2201 | 14.2161 | 14.212 | 14.2078 | 14.2025 | 14.197
|  | STONEYWOOD T3 | LW |  |  |  | 0 | 14.9764 | 14.9668 | 14.9625 | 14.9566 | 14.9499 | 14.9425 | 14.9348 | 14.9287 | 14.9225 | 14.9162 | 14.91 | 14.8717 | 14.8113 | 14.6958 | 13.8991 | 13.8895 | 13.8852 | 13.8793 | 13.8726 | 13.8652 | 13.8575 | 13.8514 | 13.8452 | 13.8389 | 13.8327 | 13.7944 | 13.734 | 13.6185 | 14.2541 | 14.2446 | 14.2403 | 14.2344 | 14.2277 | 14.2203 | 14.2125 | 14.2065 | 14.2003 | 14.194 | 14.1878 | 14.1817 | 14.1741 | 14.1662
|  | STONEYWOOD T3 | ST |  |  |  | 0 | 14.9764 | 14.9751 | 14.9745 | 14.9728 | 14.9709 | 14.9685 | 14.9659 | 14.9649 | 14.964 | 14.963 | 14.9621 | 14.958 | 14.9377 | 14.9273 | 13.8991 | 13.8978 | 13.8972 | 13.8955 | 13.8935 | 13.8912 | 13.8886 | 13.8876 | 13.8866 | 13.8857 | 13.8848 | 13.8807 | 13.8604 | 13.85 | 14.2541 | 14.2529 | 14.2523 | 14.2506 | 14.2486 | 14.2463 | 14.2437 | 14.2427 | 14.2417 | 14.2408 | 14.2399 | 14.2358 | 14.2155 | 14.2051
|  | STONEYWOOD T3 | FS |  |  |  | 0 | 14.9764 | 14.9752 | 14.9751 | 14.975 | 14.9749 | 14.9748 | 14.9747 | 14.9742 | 14.9736 | 14.9729 | 14.9723 | 14.9704 | 14.9608 | 14.9399 | 13.8991 | 13.8978 | 13.8978 | 13.8977 | 13.8976 | 13.8975 | 13.8974 | 13.8969 | 13.8963 | 13.8956 | 13.8949 | 13.8931 | 13.8835 | 13.8626 | 14.2541 | 14.2529 | 14.2529 | 14.2528 | 14.2527 | 14.2526 | 14.2525 | 14.252 | 14.2514 | 14.2507 | 14.25 | 14.2482 | 14.2386 | 14.2176
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0 | 1.1138 | 1.1085 | 1.1058 | 1.1021 | 1.0978 | 1.0932 | 1.0883 | 1.0845 | 1.0806 | 1.0767 | 1.0728 | 1.0134 | 0.92588 | 0.80605 | 1.2389 | 1.2337 | 1.231 | 1.2272 | 1.223 | 1.2183 | 1.2134 | 1.2096 | 1.2057 | 1.2018 | 1.1979 | 1.1734 | 1.1309 | 1.0134 | 1.1035 | 1.0982 | 1.0956 | 1.0918 | 1.0875 | 1.0829 | 1.078 | 1.0742 | 1.0636 | 1.0486 | 1.0338 | 1.0193 | 1.0039 | 0.98831
|  | STRACHUR | CT |  |  |  | 0 | 1.1138 | 1.1109 | 1.1083 | 1.1051 | 1.1013 | 1.0971 | 1.0927 | 1.0895 | 1.0862 | 1.0829 | 1.0796 | 1.0595 | 1.0059 | 0.93212 | 1.2389 | 1.236 | 1.2334 | 1.2302 | 1.2265 | 1.2223 | 1.2178 | 1.2146 | 1.2113 | 1.2081 | 1.2048 | 1.1846 | 1.1552 | 1.1124 | 1.1035 | 1.1006 | 1.098 | 1.0948 | 1.0911 | 1.0868 | 1.0824 | 1.0792 | 1.0759 | 1.0726 | 1.0693 | 1.0627 | 1.0513 | 1.0398
|  | STRACHUR | LW |  |  |  | 0 | 1.1146 | 1.1085 | 1.1058 | 1.1021 | 1.0978 | 1.0932 | 1.0883 | 1.0845 | 1.0806 | 1.0767 | 1.0728 | 1.0134 | 0.92588 | 0.80605 | 1.2397 | 1.2337 | 1.231 | 1.2272 | 1.223 | 1.2183 | 1.2134 | 1.2096 | 1.2057 | 1.2018 | 1.1979 | 1.1734 | 1.1309 | 1.0134 | 1.1043 | 1.0982 | 1.0956 | 1.0918 | 1.0875 | 1.0829 | 1.078 | 1.0742 | 1.0636 | 1.0486 | 1.0338 | 1.0193 | 1.0039 | 0.98831
|  | STRACHUR | ST |  |  |  | 0 | 1.1146 | 1.1138 | 1.1135 | 1.1125 | 1.1113 | 1.1099 | 1.1083 | 1.1077 | 1.1072 | 1.1066 | 1.106 | 1.1036 | 1.0916 | 1.0855 | 1.2397 | 1.239 | 1.2386 | 1.2376 | 1.2364 | 1.235 | 1.2335 | 1.2329 | 1.2323 | 1.2317 | 1.2312 | 1.2288 | 1.2168 | 1.2106 | 1.1043 | 1.1036 | 1.1032 | 1.1022 | 1.101 | 1.0996 | 1.098 | 1.0975 | 1.0969 | 1.0963 | 1.0958 | 1.0933 | 1.0688 | 1.0381
|  | STRACHUR | FS |  |  |  | 0 | 1.1146 | 1.1139 | 1.1139 | 1.1138 | 1.1138 | 1.1137 | 1.1136 | 1.1133 | 1.113 | 1.1126 | 1.1122 | 1.1112 | 1.1057 | 1.0938 | 1.2397 | 1.2391 | 1.239 | 1.239 | 1.2389 | 1.2389 | 1.2388 | 1.2385 | 1.2381 | 1.2378 | 1.2374 | 1.2363 | 1.2308 | 1.2189 | 1.1043 | 1.1036 | 1.1036 | 1.1036 | 1.1035 | 1.1034 | 1.1034 | 1.1031 | 1.1027 | 1.1024 | 1.102 | 1.1009 | 1.0954 | 1.0835
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0.0052632 | 1.1376 | 1.1311 | 1.1098 | 1.0793 | 1.0492 | 1.0192 | 0.99092 | 0.96265 | 0.93368 | 0.90559 | 0.87855 | 0.74342 | 0.59562 | 0.41134 | 1.1571 | 1.1455 | 1.1209 | 1.0855 | 1.0508 | 1.0163 | 0.98388 | 0.95122 | 0.91789 | 0.88563 | 0.8546 | 0.70051 | 0.53471 | 0.33311 | 1.1243 | 1.1181 | 1.113 | 1.106 | 1.0985 | 1.0906 | 1.0756 | 1.0447 | 1.013 | 0.98219 | 0.95152 | 0.92202 | 0.89155 | 0.86091
|  | STRATHDON | CT |  |  |  | 0.0052632 | 1.1376 | 1.1327 | 1.127 | 1.1046 | 1.081 | 1.0572 | 1.0358 | 1.0147 | 0.99365 | 0.97348 | 0.95343 | 0.853 | 0.74329 | 0.61865 | 1.1571 | 1.1512 | 1.1416 | 1.1159 | 1.0889 | 1.0618 | 1.0374 | 1.0133 | 0.98925 | 0.96624 | 0.94338 | 0.82967 | 0.70757 | 0.57077 | 1.1243 | 1.1186 | 1.1133 | 1.1069 | 1.0998 | 1.0921 | 1.0852 | 1.0788 | 1.0724 | 1.0581 | 1.0363 | 1.0146 | 0.99301 | 0.97136
|  | STRATHDON | LW |  |  |  | 0.0052632 | 1.141 | 1.1311 | 1.1098 | 1.0793 | 1.0492 | 1.0192 | 0.99092 | 0.96265 | 0.93368 | 0.90559 | 0.87855 | 0.74342 | 0.59562 | 0.41134 | 1.1598 | 1.1455 | 1.1209 | 1.0855 | 1.0508 | 1.0163 | 0.98388 | 0.95122 | 0.91789 | 0.88563 | 0.8546 | 0.70051 | 0.53471 | 0.33311 | 1.1271 | 1.1181 | 1.113 | 1.106 | 1.0985 | 1.0906 | 1.0756 | 1.0447 | 1.013 | 0.98219 | 0.95152 | 0.92202 | 0.89155 | 0.86091
|  | STRATHDON | ST |  |  |  | 0.0052632 | 1.1427 | 1.141 | 1.1397 | 1.1377 | 1.1355 | 1.1265 | 1.1141 | 1.1016 | 1.0893 | 1.0772 | 1.0652 | 1.0093 | 0.94899 | 0.89647 | 1.1631 | 1.1611 | 1.1596 | 1.1566 | 1.1534 | 1.1401 | 1.1257 | 1.1112 | 1.0969 | 1.0827 | 1.0687 | 1.0034 | 0.935 | 0.87458 | 1.13 | 1.1281 | 1.1266 | 1.1239 | 1.121 | 1.1178 | 1.1145 | 1.1123 | 1.11 | 1.1078 | 1.1056 | 1.0947 | 1.0295 | 0.97132
|  | STRATHDON | FS |  |  |  | 0.0052632 | 1.1427 | 1.1419 | 1.1419 | 1.1418 | 1.1418 | 1.1417 | 1.1416 | 1.14 | 1.1313 | 1.1225 | 1.1145 | 1.0725 | 1.0307 | 0.98589 | 1.1634 | 1.1624 | 1.1621 | 1.1618 | 1.1613 | 1.1605 | 1.1598 | 1.1546 | 1.1442 | 1.1339 | 1.1244 | 1.0753 | 1.0271 | 0.97633 | 1.1302 | 1.1292 | 1.129 | 1.1288 | 1.1284 | 1.1279 | 1.1273 | 1.1264 | 1.1255 | 1.1245 | 1.1235 | 1.1164 | 1.1054 | 1.0691
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.86316 | 9.6298 | 9.5909 | 9.5542 | 9.5147 | 9.4736 | 9.4303 | 9.3867 | 9.3463 | 9.2606 | 9.0974 | 8.9515 | 8.2677 | 7.5667 | 6.7177 | 9.8226 | 9.6748 | 9.5326 | 9.3493 | 9.1728 | 9.0047 | 8.8262 | 8.6322 | 8.4482 | 8.2723 | 8.1155 | 7.3853 | 6.6454 | 5.7609 | 9.8325 | 9.7935 | 9.7569 | 9.5862 | 9.3593 | 9.1447 | 8.9522 | 8.7526 | 8.5634 | 8.3827 | 8.2217 | 8.074 | 7.9224 | 7.7728
|  | STRICHEN | CT |  |  |  | 0.86316 | 9.6298 | 9.5909 | 9.5542 | 9.5147 | 9.4736 | 9.4303 | 9.3867 | 9.3463 | 9.3057 | 9.2641 | 9.2225 | 8.7717 | 8.1772 | 7.5104 | 9.8255 | 9.7208 | 9.61 | 9.4819 | 9.3434 | 9.1971 | 9.0704 | 8.9458 | 8.8239 | 8.7081 | 8.5803 | 7.9542 | 7.3322 | 6.64 | 9.8325 | 9.7935 | 9.7569 | 9.7173 | 9.62 | 9.4377 | 9.282 | 9.128 | 8.9777 | 8.8377 | 8.707 | 8.5764 | 8.4457 | 8.3183
|  | STRICHEN | LW |  |  |  | 0.86316 | 9.6804 | 9.644 | 9.6215 | 9.5933 | 9.561 | 9.5262 | 9.4885 | 9.4312 | 9.2606 | 9.0974 | 8.9515 | 8.2677 | 7.5667 | 6.7177 | 9.8226 | 9.6748 | 9.5326 | 9.3493 | 9.1728 | 9.0047 | 8.8262 | 8.6322 | 8.4482 | 8.2723 | 8.1155 | 7.3853 | 6.6454 | 5.7609 | 9.883 | 9.8466 | 9.8236 | 9.5862 | 9.3593 | 9.1447 | 8.9522 | 8.7526 | 8.5634 | 8.3827 | 8.2217 | 8.074 | 7.9224 | 7.7728
|  | STRICHEN | ST |  |  |  | 0.86316 | 9.6905 | 9.6802 | 9.6718 | 9.6605 | 9.6466 | 9.6317 | 9.6169 | 9.6067 | 9.5964 | 9.5862 | 9.5761 | 9.5253 | 9.4298 | 9.3468 | 9.9313 | 9.8991 | 9.8642 | 9.808 | 9.747 | 9.6836 | 9.6248 | 9.5654 | 9.5028 | 9.4398 | 9.3792 | 9.1054 | 8.8288 | 8.5496 | 9.8931 | 9.8829 | 9.8744 | 9.8632 | 9.8492 | 9.8344 | 9.8196 | 9.8093 | 9.7921 | 9.7107 | 9.6325 | 9.2809 | 8.9569 | 8.6706
|  | STRICHEN | FS |  |  |  | 0.86316 | 9.6955 | 9.689 | 9.6838 | 9.6785 | 9.6732 | 9.6678 | 9.6624 | 9.656 | 9.6494 | 9.6426 | 9.6357 | 9.603 | 9.5498 | 9.4693 | 9.9464 | 9.9211 | 9.8959 | 9.8676 | 9.8337 | 9.7946 | 9.7561 | 9.7123 | 9.6666 | 9.6214 | 9.5773 | 9.3573 | 9.1627 | 8.9502 | 9.8982 | 9.8916 | 9.8864 | 9.8812 | 9.8759 | 9.8705 | 9.8651 | 9.8586 | 9.852 | 9.8453 | 9.8384 | 9.5936 | 9.3496 | 9.0909
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 0 | 9.2996 | 9.2582 | 9.2398 | 9.2141 | 9.185 | 9.1532 | 9.1197 | 9.0934 | 9.0667 | 9.0395 | 9.0129 | 8.7323 | 8.1524 | 7.327 | 8.8938 | 8.8524 | 8.834 | 8.7516 | 8.6418 | 8.5331 | 8.4254 | 8.3199 | 8.2151 | 8.111 | 8.0085 | 7.4455 | 6.7664 | 5.8548 | 8.8733 | 8.8295 | 8.8083 | 8.7775 | 8.7266 | 8.6118 | 8.4983 | 8.3866 | 8.2757 | 8.1656 | 8.0571 | 7.9502 | 7.8365 | 7.7219
|  | STROMNESS | CT |  |  |  | 0 | 9.2996 | 9.2852 | 9.273 | 9.2564 | 9.2361 | 9.2124 | 9.187 | 9.1704 | 9.1532 | 9.1358 | 9.1184 | 9.0043 | 8.7575 | 8.2682 | 8.8938 | 8.8794 | 8.8672 | 8.8506 | 8.7746 | 8.6966 | 8.6188 | 8.5467 | 8.4747 | 8.4034 | 8.3328 | 7.958 | 7.4921 | 6.9247 | 8.874 | 8.8578 | 8.8436 | 8.8234 | 8.7995 | 8.7724 | 8.7016 | 8.6252 | 8.5489 | 8.4734 | 8.3986 | 8.324 | 8.2444 | 8.1644
|  | STROMNESS | LW |  |  |  | 0 | 9.2996 | 9.2582 | 9.2398 | 9.2141 | 9.185 | 9.1532 | 9.1197 | 9.0934 | 9.0667 | 9.0395 | 9.0129 | 8.7323 | 8.1524 | 7.327 | 8.8938 | 8.8524 | 8.834 | 8.7516 | 8.6418 | 8.5331 | 8.4254 | 8.3199 | 8.2151 | 8.111 | 8.0085 | 7.4455 | 6.7664 | 5.8548 | 8.8733 | 8.8295 | 8.8083 | 8.7775 | 8.7266 | 8.6118 | 8.4983 | 8.3866 | 8.2757 | 8.1656 | 8.0571 | 7.9502 | 7.8365 | 7.7219
|  | STROMNESS | ST |  |  |  | 0 | 9.2996 | 9.2942 | 9.2916 | 9.2845 | 9.276 | 9.266 | 9.2548 | 9.2506 | 9.2464 | 9.2424 | 9.2385 | 9.221 | 9.1342 | 9.0896 | 8.8938 | 8.8884 | 8.8857 | 8.8787 | 8.8702 | 8.8602 | 8.849 | 8.8179 | 8.7766 | 8.7362 | 8.6968 | 8.5093 | 8.2595 | 8.057 | 8.8767 | 8.8711 | 8.8683 | 8.8589 | 8.848 | 8.8357 | 8.8224 | 8.8158 | 8.8093 | 8.803 | 8.7817 | 8.5809 | 8.3184 | 8.1034
|  | STROMNESS | FS |  |  |  | 0 | 9.2996 | 9.2945 | 9.2943 | 9.294 | 9.2936 | 9.293 | 9.2925 | 9.2903 | 9.2878 | 9.2851 | 9.2822 | 9.2743 | 9.2335 | 9.1445 | 8.8938 | 8.8887 | 8.8885 | 8.8882 | 8.8878 | 8.8872 | 8.8867 | 8.8845 | 8.882 | 8.8793 | 8.8565 | 8.7098 | 8.5377 | 8.3235 | 8.8768 | 8.8716 | 8.8712 | 8.8706 | 8.8695 | 8.8674 | 8.8653 | 8.8613 | 8.857 | 8.8525 | 8.8478 | 8.7929 | 8.6105 | 8.3865
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0 | 1.1111 | 1.1024 | 1.094 | 1.086 | 1.0778 | 1.0693 | 1.0607 | 1.0518 | 1.042 | 1.0297 | 1.0176 | 0.95072 | 0.87018 | 0.77503 | 1.0809 | 1.0699 | 1.0589 | 1.0469 | 1.0347 | 1.0225 | 1.0103 | 0.9977 | 0.98513 | 0.9726 | 0.96013 | 0.89185 | 0.80985 | 0.71327 | 1.0766 | 1.068 | 1.0595 | 1.0515 | 1.0433 | 1.0348 | 1.0255 | 1.0128 | 1.0002 | 0.98756 | 0.97499 | 0.96243 | 0.94866 | 0.93485
|  | STRONSAY | CT |  |  |  | 0 | 1.1111 | 1.1024 | 1.094 | 1.086 | 1.0778 | 1.0693 | 1.0607 | 1.0518 | 1.042 | 1.0297 | 1.0176 | 0.95072 | 0.87018 | 0.77503 | 1.0809 | 1.0699 | 1.0589 | 1.0469 | 1.0347 | 1.0225 | 1.0103 | 0.9977 | 0.98513 | 0.9726 | 0.96013 | 0.89185 | 0.80985 | 0.71327 | 1.0766 | 1.068 | 1.0595 | 1.0515 | 1.0433 | 1.0348 | 1.0255 | 1.0128 | 1.0002 | 0.98756 | 0.97499 | 0.96243 | 0.94866 | 0.93485
|  | STRONSAY | LW |  |  |  | 0 | 1.1246 | 1.119 | 1.1151 | 1.1107 | 1.1052 | 1.0995 | 1.0901 | 1.0786 | 1.0671 | 1.0556 | 1.0443 | 0.97976 | 0.89935 | 0.79488 | 1.0939 | 1.0854 | 1.0782 | 1.0676 | 1.056 | 1.0445 | 1.033 | 1.021 | 1.0091 | 0.99716 | 0.98537 | 0.91858 | 0.83588 | 0.72914 | 1.0901 | 1.0845 | 1.0806 | 1.0762 | 1.0707 | 1.0596 | 1.048 | 1.0358 | 1.0237 | 1.0117 | 0.99974 | 0.98707 | 0.97388 | 0.96063
|  | STRONSAY | ST |  |  |  | 0 | 1.1262 | 1.1241 | 1.1223 | 1.1201 | 1.1177 | 1.1153 | 1.1128 | 1.1108 | 1.1088 | 1.1068 | 1.1049 | 1.0903 | 1.0625 | 1.0356 | 1.1002 | 1.098 | 1.096 | 1.0909 | 1.0858 | 1.0806 | 1.0754 | 1.0706 | 1.0658 | 1.0611 | 1.0565 | 1.0332 | 1.0044 | 0.9765 | 1.0918 | 1.0897 | 1.0878 | 1.0856 | 1.0833 | 1.0809 | 1.0783 | 1.0764 | 1.0744 | 1.0724 | 1.0704 | 1.0481 | 1.019 | 0.99083
|  | STRONSAY | FS |  |  |  | 0 | 1.1279 | 1.1267 | 1.125 | 1.1233 | 1.1216 | 1.1198 | 1.1181 | 1.1171 | 1.1161 | 1.115 | 1.114 | 1.1058 | 1.0879 | 1.063 | 1.102 | 1.1007 | 1.0989 | 1.097 | 1.0947 | 1.0907 | 1.0868 | 1.0834 | 1.08 | 1.0766 | 1.0731 | 1.0533 | 1.0306 | 1.0049 | 1.0935 | 1.0922 | 1.0905 | 1.0888 | 1.0871 | 1.0854 | 1.0837 | 1.0827 | 1.0816 | 1.0806 | 1.0795 | 1.0684 | 1.0455 | 1.0195
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 0.011579 | 1.1328 | 1.1271 | 1.1246 | 1.1211 | 1.1172 | 1.1128 | 1.1083 | 1.1048 | 1.1012 | 1.0975 | 1.094 | 1.0722 | 1.0304 | 0.92148 | 1.1395 | 1.1335 | 1.1257 | 1.1105 | 1.0951 | 1.0798 | 1.0648 | 1.0503 | 1.0359 | 1.0217 | 1.0077 | 0.93504 | 0.85044 | 0.73705 | 1.1269 | 1.1213 | 1.1187 | 1.1152 | 1.1113 | 1.107 | 1.1024 | 1.0989 | 1.0953 | 1.0917 | 1.0881 | 1.0846 | 1.0803 | 1.0687
|  | STRONTIAN | CT |  |  |  | 0.011579 | 1.1328 | 1.1309 | 1.1293 | 1.1271 | 1.1245 | 1.1214 | 1.1181 | 1.1159 | 1.1137 | 1.1115 | 1.1092 | 1.0948 | 1.0723 | 1.0378 | 1.1396 | 1.1374 | 1.1354 | 1.1249 | 1.114 | 1.1031 | 1.0923 | 1.0823 | 1.0723 | 1.0625 | 1.0528 | 1.0019 | 0.943 | 0.87336 | 1.1269 | 1.125 | 1.1234 | 1.1213 | 1.1186 | 1.1155 | 1.1122 | 1.11 | 1.1078 | 1.1056 | 1.1034 | 1.1011 | 1.0982 | 1.0952
|  | STRONTIAN | LW |  |  |  | 0.011579 | 1.1328 | 1.1271 | 1.1246 | 1.1211 | 1.1172 | 1.1128 | 1.1083 | 1.1048 | 1.1012 | 1.0975 | 1.094 | 1.0722 | 1.0304 | 0.92148 | 1.1395 | 1.1335 | 1.1257 | 1.1105 | 1.0951 | 1.0798 | 1.0648 | 1.0503 | 1.0359 | 1.0217 | 1.0077 | 0.93504 | 0.85044 | 0.73705 | 1.1269 | 1.1213 | 1.1187 | 1.1152 | 1.1113 | 1.107 | 1.1024 | 1.0989 | 1.0953 | 1.0917 | 1.0881 | 1.0846 | 1.0803 | 1.0687
|  | STRONTIAN | ST |  |  |  | 0.011579 | 1.1328 | 1.1321 | 1.1318 | 1.1309 | 1.1298 | 1.1285 | 1.1271 | 1.1266 | 1.126 | 1.1255 | 1.125 | 1.1228 | 1.1121 | 1.1067 | 1.1399 | 1.1392 | 1.1389 | 1.1377 | 1.1363 | 1.1322 | 1.1257 | 1.1199 | 1.1142 | 1.1086 | 1.1031 | 1.0774 | 1.0443 | 1.0174 | 1.1269 | 1.1262 | 1.1259 | 1.125 | 1.1239 | 1.1226 | 1.1212 | 1.1207 | 1.1202 | 1.1197 | 1.1192 | 1.117 | 1.1063 | 1.1008
|  | STRONTIAN | FS |  |  |  | 0.011579 | 1.1328 | 1.1322 | 1.1321 | 1.1321 | 1.1321 | 1.132 | 1.1319 | 1.1317 | 1.1314 | 1.131 | 1.1307 | 1.1297 | 1.1248 | 1.1142 | 1.14 | 1.1393 | 1.1393 | 1.1392 | 1.1391 | 1.1388 | 1.1385 | 1.1381 | 1.1355 | 1.1316 | 1.1277 | 1.1092 | 1.0881 | 1.0623 | 1.1269 | 1.1263 | 1.1263 | 1.1262 | 1.1262 | 1.1261 | 1.126 | 1.1258 | 1.1255 | 1.1252 | 1.1248 | 1.1238 | 1.119 | 1.1084
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0 | 1.5368 | 1.5279 | 1.524 | 1.5185 | 1.5122 | 1.5054 | 1.4982 | 1.4926 | 1.4868 | 1.481 | 1.4753 | 1.4397 | 1.3838 | 1.236 | 1.4308 | 1.4216 | 1.4172 | 1.4109 | 1.4039 | 1.3964 | 1.3885 | 1.3821 | 1.3757 | 1.3691 | 1.3627 | 1.3103 | 1.1801 | 0.99819 | 1.3837 | 1.3677 | 1.3554 | 1.3337 | 1.3117 | 1.2898 | 1.2682 | 1.2474 | 1.2268 | 1.2063 | 1.1861 | 1.1663 | 1.1449 | 1.1234
|  | SUMBURGH | CT |  |  |  | 0 | 1.5368 | 1.5337 | 1.5311 | 1.5275 | 1.5232 | 1.5181 | 1.5126 | 1.509 | 1.5053 | 1.5015 | 1.4978 | 1.4731 | 1.4337 | 1.3729 | 1.4309 | 1.4275 | 1.4246 | 1.4205 | 1.4156 | 1.41 | 1.404 | 1.3999 | 1.3957 | 1.3915 | 1.3872 | 1.3603 | 1.3184 | 1.2085 | 1.3853 | 1.3767 | 1.368 | 1.3531 | 1.3378 | 1.3222 | 1.3067 | 1.2926 | 1.2786 | 1.2647 | 1.2509 | 1.2371 | 1.2223 | 1.2074
|  | SUMBURGH | LW |  |  |  | 0 | 1.5368 | 1.5279 | 1.524 | 1.5185 | 1.5122 | 1.5054 | 1.4982 | 1.4926 | 1.4868 | 1.481 | 1.4753 | 1.4397 | 1.3838 | 1.236 | 1.4308 | 1.4216 | 1.4172 | 1.4109 | 1.4039 | 1.3964 | 1.3885 | 1.3821 | 1.3757 | 1.3691 | 1.3627 | 1.3103 | 1.1801 | 0.99819 | 1.3837 | 1.3677 | 1.3554 | 1.3337 | 1.3117 | 1.2898 | 1.2682 | 1.2474 | 1.2268 | 1.2063 | 1.1861 | 1.1663 | 1.1449 | 1.1234
|  | SUMBURGH | ST |  |  |  | 0 | 1.5368 | 1.5357 | 1.5351 | 1.5336 | 1.5317 | 1.5296 | 1.5272 | 1.5263 | 1.5253 | 1.5245 | 1.5236 | 1.5199 | 1.5011 | 1.4914 | 1.4313 | 1.4301 | 1.4295 | 1.4277 | 1.4255 | 1.423 | 1.4203 | 1.4191 | 1.4178 | 1.4167 | 1.4155 | 1.4103 | 1.3901 | 1.3791 | 1.3944 | 1.3929 | 1.392 | 1.3834 | 1.3746 | 1.3659 | 1.3571 | 1.3494 | 1.3418 | 1.3344 | 1.3272 | 1.2933 | 1.246 | 1.2088
|  | SUMBURGH | FS |  |  |  | 0 | 1.5368 | 1.5357 | 1.5357 | 1.5356 | 1.5355 | 1.5354 | 1.5353 | 1.5348 | 1.5343 | 1.5337 | 1.533 | 1.5313 | 1.5225 | 1.5031 | 1.4313 | 1.4302 | 1.4301 | 1.4301 | 1.4299 | 1.4295 | 1.4292 | 1.4284 | 1.4276 | 1.4268 | 1.4259 | 1.4229 | 1.4128 | 1.3922 | 1.3948 | 1.3934 | 1.3931 | 1.3924 | 1.3904 | 1.3854 | 1.3803 | 1.3743 | 1.3682 | 1.362 | 1.3559 | 1.3272 | 1.2931 | 1.2498
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 0 | 16.4927 | 16.4661 | 16.4469 | 16.4212 | 16.3915 | 16.3593 | 16.3256 | 16.2975 | 16.2691 | 16.2402 | 16.2118 | 16.0346 | 15.7311 | 14.95 | 15.3078 | 15.2812 | 15.262 | 15.2363 | 15.2066 | 15.1744 | 15.1407 | 15.1126 | 15.0842 | 15.0553 | 15.027 | 14.7366 | 14.1064 | 13.2547 | 15.7974 | 15.7708 | 15.7516 | 15.7259 | 15.6962 | 15.664 | 15.6303 | 15.6022 | 15.5738 | 15.5449 | 15.5166 | 15.4875 | 15.4527 | 15.4167
|  | TAIN | CT |  |  |  | 0 | 16.4927 | 16.4723 | 16.4539 | 16.4316 | 16.4069 | 16.3791 | 16.3497 | 16.3274 | 16.3045 | 16.2815 | 16.2583 | 16.1143 | 15.9004 | 15.589 | 15.3078 | 15.2874 | 15.269 | 15.2467 | 15.222 | 15.1942 | 15.1649 | 15.1425 | 15.1196 | 15.0966 | 15.0735 | 14.9294 | 14.662 | 14.1042 | 15.7974 | 15.777 | 15.7586 | 15.7363 | 15.7116 | 15.6838 | 15.6544 | 15.6321 | 15.6092 | 15.5862 | 15.563 | 15.5393 | 15.5105 | 15.4811
|  | TAIN | LW |  |  |  | 0 | 16.5061 | 16.4661 | 16.4469 | 16.4212 | 16.3915 | 16.3593 | 16.3256 | 16.2975 | 16.2691 | 16.2402 | 16.2118 | 16.0346 | 15.7311 | 14.95 | 15.3212 | 15.2812 | 15.262 | 15.2363 | 15.2066 | 15.1744 | 15.1407 | 15.1126 | 15.0842 | 15.0553 | 15.027 | 14.7366 | 14.1064 | 13.2547 | 15.8108 | 15.7708 | 15.7516 | 15.7259 | 15.6962 | 15.664 | 15.6303 | 15.6022 | 15.5738 | 15.5449 | 15.5166 | 15.4875 | 15.4527 | 15.4167
|  | TAIN | ST |  |  |  | 0 | 16.5078 | 16.5013 | 16.4972 | 16.4893 | 16.4791 | 16.4685 | 16.4568 | 16.4514 | 16.446 | 16.4407 | 16.4355 | 16.4106 | 16.3204 | 16.2673 | 15.3229 | 15.3164 | 15.3124 | 15.3044 | 15.2942 | 15.2836 | 15.2719 | 15.2665 | 15.2611 | 15.2558 | 15.2506 | 15.2257 | 15.1355 | 15.0824 | 15.8125 | 15.806 | 15.802 | 15.794 | 15.7838 | 15.7732 | 15.7615 | 15.7561 | 15.7507 | 15.7454 | 15.7402 | 15.7153 | 15.6251 | 15.572
|  | TAIN | FS |  |  |  | 0 | 16.5095 | 16.5041 | 16.5022 | 16.5003 | 16.4982 | 16.496 | 16.4938 | 16.491 | 16.488 | 16.4847 | 16.4812 | 16.4666 | 16.4215 | 16.3328 | 15.3246 | 15.3192 | 15.3173 | 15.3154 | 15.3133 | 15.3111 | 15.3089 | 15.3061 | 15.3031 | 15.2998 | 15.2963 | 15.2817 | 15.2366 | 15.148 | 15.8142 | 15.8088 | 15.8069 | 15.805 | 15.8029 | 15.8007 | 15.7985 | 15.7957 | 15.7927 | 15.7894 | 15.7859 | 15.7713 | 15.7262 | 15.6376
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 1.0516 | 2.3447 | 1.4983 | 1.494 | 1.4881 | 1.4809 | 1.4725 | 1.4635 | 1.4576 | 1.4514 | 1.4453 | 1.4391 | 1.3426 | 1.2025 | 1.0285 | 2.2485 | 1.4018 | 1.3969 | 1.39 | 1.3818 | 1.3724 | 1.3624 | 1.3556 | 1.3485 | 1.3241 | 1.2998 | 1.1706 | 1.0158 | 0.82686 | 2.2653 | 1.419 | 1.4146 | 1.4088 | 1.4016 | 1.3932 | 1.3841 | 1.3782 | 1.3721 | 1.3659 | 1.3597 | 1.3533 | 1.3412 | 1.3143
|  | TARBERT | CT |  |  |  | 1.0516 | 2.3447 | 1.4983 | 1.494 | 1.4881 | 1.4809 | 1.4725 | 1.4635 | 1.4576 | 1.4514 | 1.4453 | 1.4391 | 1.3426 | 1.2025 | 1.0285 | 2.2486 | 1.4018 | 1.3969 | 1.39 | 1.3818 | 1.3724 | 1.3624 | 1.3556 | 1.3485 | 1.3241 | 1.2998 | 1.1706 | 1.0158 | 0.82686 | 2.2653 | 1.419 | 1.4146 | 1.4088 | 1.4016 | 1.3932 | 1.3841 | 1.3782 | 1.3721 | 1.3659 | 1.3597 | 1.3533 | 1.3412 | 1.3143
|  | TARBERT | LW |  |  |  | 1.0516 | 2.3447 | 2.3301 | 2.3236 | 2.3145 | 2.3042 | 2.293 | 2.2812 | 2.2719 | 2.262 | 2.2307 | 2.1998 | 2.0358 | 1.8362 | 1.5532 | 2.2485 | 2.2332 | 2.2259 | 2.2154 | 2.2037 | 2.1911 | 2.1728 | 2.1367 | 2.1008 | 2.0652 | 2.0301 | 1.8456 | 1.6219 | 1.3121 | 2.2653 | 2.2507 | 2.2442 | 2.2352 | 2.2249 | 2.2137 | 2.2018 | 2.1925 | 2.1831 | 2.1561 | 2.1199 | 2.0842 | 2.046 | 2.0076
|  | TARBERT | ST |  |  |  | 1.0516 | 2.3447 | 2.3427 | 2.3418 | 2.3393 | 2.3363 | 2.3327 | 2.3287 | 2.3272 | 2.3257 | 2.3243 | 2.3229 | 2.3167 | 2.2803 | 2.2214 | 2.2494 | 2.2474 | 2.2464 | 2.2433 | 2.2396 | 2.2354 | 2.2308 | 2.2287 | 2.2265 | 2.2244 | 2.2224 | 2.2022 | 2.1181 | 2.0508 | 2.2653 | 2.2634 | 2.2625 | 2.26 | 2.2569 | 2.2534 | 2.2494 | 2.2479 | 2.2464 | 2.245 | 2.2436 | 2.2374 | 2.2063 | 2.1404
|  | TARBERT | FS |  |  |  | 1.0516 | 2.3447 | 2.3429 | 2.3428 | 2.3427 | 2.3425 | 2.3423 | 2.3421 | 2.3413 | 2.3404 | 2.3395 | 2.3384 | 2.3356 | 2.3209 | 2.2889 | 2.2495 | 2.2476 | 2.2475 | 2.2473 | 2.247 | 2.2463 | 2.2457 | 2.2444 | 2.243 | 2.2415 | 2.2399 | 2.2345 | 2.2059 | 2.1328 | 2.2653 | 2.2635 | 2.2634 | 2.2633 | 2.2632 | 2.263 | 2.2628 | 2.262 | 2.2611 | 2.2601 | 2.2591 | 2.2563 | 2.2416 | 2.2096
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0 | 0.16125 | 0.16112 | 0.16106 | 0.16098 | 0.16061 | 0.15958 | 0.15855 | 0.15753 | 0.15652 | 0.15551 | 0.1545 | 0.14942 | 0.14406 | 0.13805 | 0.15613 | 0.156 | 0.15594 | 0.15586 | 0.15577 | 0.15567 | 0.1546 | 0.15342 | 0.15225 | 0.15107 | 0.14991 | 0.14403 | 0.13787 | 0.13107 | 0.15661 | 0.15648 | 0.15642 | 0.15634 | 0.15625 | 0.15506 | 0.15387 | 0.15269 | 0.15152 | 0.15034 | 0.14918 | 0.14802 | 0.14684 | 0.14566
|  | TARBERT JURA | CT |  |  |  | 0 | 0.16125 | 0.16121 | 0.16117 | 0.16112 | 0.16106 | 0.16099 | 0.16091 | 0.16086 | 0.16081 | 0.16076 | 0.16071 | 0.16038 | 0.15969 | 0.15845 | 0.15613 | 0.15609 | 0.15605 | 0.156 | 0.15594 | 0.15587 | 0.15579 | 0.15574 | 0.15569 | 0.15564 | 0.15559 | 0.15526 | 0.15475 | 0.15397 | 0.15661 | 0.15657 | 0.15653 | 0.15648 | 0.15642 | 0.15635 | 0.15628 | 0.15623 | 0.15618 | 0.15613 | 0.15607 | 0.15602 | 0.15596 | 0.15589
|  | TARBERT JURA | LW |  |  |  | 0 | 0.16125 | 0.16112 | 0.16106 | 0.16098 | 0.16061 | 0.15958 | 0.15855 | 0.15753 | 0.15652 | 0.15551 | 0.1545 | 0.14942 | 0.14406 | 0.13805 | 0.15613 | 0.156 | 0.15594 | 0.15586 | 0.15577 | 0.15567 | 0.1546 | 0.15342 | 0.15225 | 0.15107 | 0.14991 | 0.14403 | 0.13787 | 0.13107 | 0.15661 | 0.15648 | 0.15642 | 0.15634 | 0.15625 | 0.15506 | 0.15387 | 0.15269 | 0.15152 | 0.15034 | 0.14918 | 0.14802 | 0.14684 | 0.14566
|  | TARBERT JURA | ST |  |  |  | 0 | 0.16125 | 0.16123 | 0.16123 | 0.16121 | 0.16118 | 0.16115 | 0.16112 | 0.16111 | 0.1611 | 0.16108 | 0.16107 | 0.16102 | 0.16078 | 0.16066 | 0.15613 | 0.15611 | 0.15611 | 0.15609 | 0.15606 | 0.15603 | 0.156 | 0.15599 | 0.15598 | 0.15596 | 0.15595 | 0.1559 | 0.15566 | 0.15554 | 0.15661 | 0.1566 | 0.15659 | 0.15657 | 0.15655 | 0.15652 | 0.15648 | 0.15647 | 0.15646 | 0.15645 | 0.15644 | 0.15639 | 0.15614 | 0.15602
|  | TARBERT JURA | FS |  |  |  | 0 | 0.16125 | 0.16124 | 0.16124 | 0.16124 | 0.16123 | 0.16123 | 0.16123 | 0.16123 | 0.16122 | 0.16121 | 0.1612 | 0.16118 | 0.16108 | 0.16084 | 0.15613 | 0.15612 | 0.15612 | 0.15612 | 0.15611 | 0.15611 | 0.15611 | 0.15611 | 0.1561 | 0.15609 | 0.15608 | 0.15606 | 0.15596 | 0.15572 | 0.15661 | 0.1566 | 0.1566 | 0.1566 | 0.1566 | 0.1566 | 0.1566 | 0.15659 | 0.15658 | 0.15658 | 0.15657 | 0.15655 | 0.15644 | 0.15621
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 0 | 5.1725 | 5.1521 | 5.1334 | 5.1131 | 5.0915 | 5.0686 | 5.045 | 5.0237 | 4.9664 | 4.9101 | 4.8541 | 4.5607 | 4.2115 | 3.754 | 3.7194 | 3.699 | 3.6803 | 3.66 | 3.6384 | 3.6138 | 3.5583 | 3.5012 | 3.4449 | 3.3895 | 3.3345 | 3.0455 | 2.6787 | 2.1897 | 3.9773 | 3.9569 | 3.9382 | 3.9179 | 3.8963 | 3.8734 | 3.8498 | 3.8286 | 3.7742 | 3.7179 | 3.662 | 3.6073 | 3.5487 | 3.4897
|  | TARBERT LOCH FYNE | CT |  |  |  | 0 | 5.1725 | 5.1521 | 5.1334 | 5.1131 | 5.0915 | 5.0686 | 5.045 | 5.0238 | 5.0023 | 4.9589 | 4.9117 | 4.6593 | 4.3643 | 4.0147 | 3.7194 | 3.699 | 3.6803 | 3.66 | 3.6384 | 3.6155 | 3.5774 | 3.5298 | 3.4822 | 3.4355 | 3.389 | 3.1398 | 2.848 | 2.5004 | 3.9773 | 3.9569 | 3.9382 | 3.9179 | 3.8963 | 3.8734 | 3.8498 | 3.8286 | 3.8072 | 3.7664 | 3.7193 | 3.6712 | 3.6218 | 3.5714
|  | TARBERT LOCH FYNE | LW |  |  |  | 0 | 5.1977 | 5.1783 | 5.1664 | 5.1511 | 5.1336 | 5.1151 | 5.0819 | 5.0237 | 4.9664 | 4.9101 | 4.8541 | 4.5607 | 4.2115 | 3.754 | 3.7446 | 3.7252 | 3.7133 | 3.698 | 3.6701 | 3.6138 | 3.5583 | 3.5012 | 3.4449 | 3.3895 | 3.3345 | 3.0455 | 2.6787 | 2.1897 | 4.0025 | 3.9831 | 3.9712 | 3.9559 | 3.9384 | 3.9199 | 3.8894 | 3.8313 | 3.7742 | 3.7179 | 3.662 | 3.6073 | 3.5487 | 3.4897
|  | TARBERT LOCH FYNE | ST |  |  |  | 0 | 5.2028 | 5.1974 | 5.193 | 5.187 | 5.1796 | 5.1716 | 5.1632 | 5.1575 | 5.1517 | 5.146 | 5.1403 | 5.1001 | 4.9687 | 4.8525 | 3.7497 | 3.7443 | 3.7399 | 3.7339 | 3.7265 | 3.7186 | 3.7102 | 3.7044 | 3.6986 | 3.6929 | 3.6856 | 3.5766 | 3.4471 | 3.3328 | 4.0076 | 4.0022 | 3.9978 | 3.9918 | 3.9844 | 3.9765 | 3.9681 | 3.9623 | 3.9565 | 3.9508 | 3.9451 | 3.9076 | 3.7764 | 3.6604
|  | TARBERT LOCH FYNE | FS |  |  |  | 0 | 5.2061 | 5.2024 | 5.1998 | 5.1972 | 5.1945 | 5.1918 | 5.189 | 5.1856 | 5.1821 | 5.1785 | 5.1748 | 5.1558 | 5.1246 | 5.0163 | 3.7531 | 3.7494 | 3.7467 | 3.7441 | 3.7414 | 3.7387 | 3.7359 | 3.7325 | 3.729 | 3.7254 | 3.7218 | 3.6902 | 3.6008 | 3.494 | 4.0109 | 4.0073 | 4.0046 | 4.002 | 3.9993 | 3.9966 | 3.9938 | 3.9904 | 3.9869 | 3.9833 | 3.9797 | 3.9606 | 3.9317 | 3.824
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0 | 2.7723 | 2.7652 | 2.7613 | 2.7558 | 2.7497 | 2.7429 | 2.7358 | 2.7302 | 2.7246 | 2.7189 | 2.7133 | 2.638 | 2.497 | 2.3083 | 2.7699 | 2.7628 | 2.7589 | 2.7535 | 2.7473 | 2.7405 | 2.7334 | 2.7279 | 2.7222 | 2.6968 | 2.6716 | 2.5426 | 2.3871 | 2.1839 | 2.7753 | 2.7682 | 2.7643 | 2.7588 | 2.7526 | 2.7459 | 2.7388 | 2.7277 | 2.7022 | 2.6769 | 2.652 | 2.6274 | 2.6024 | 2.5772
|  | TAYNUILT | CT |  |  |  | 0 | 2.7723 | 2.7685 | 2.7651 | 2.7608 | 2.7557 | 2.7499 | 2.7438 | 2.7395 | 2.7351 | 2.7306 | 2.7262 | 2.6984 | 2.6381 | 2.5227 | 2.7699 | 2.7661 | 2.7627 | 2.7584 | 2.7533 | 2.7475 | 2.7414 | 2.7371 | 2.7327 | 2.7282 | 2.7238 | 2.6528 | 2.5463 | 2.4213 | 2.7753 | 2.7715 | 2.7681 | 2.7638 | 2.7587 | 2.7529 | 2.7468 | 2.7425 | 2.738 | 2.7336 | 2.7247 | 2.7073 | 2.689 | 2.6706
|  | TAYNUILT | LW |  |  |  | 0 | 2.774 | 2.7652 | 2.7613 | 2.7558 | 2.7497 | 2.7429 | 2.7358 | 2.7302 | 2.7246 | 2.7189 | 2.7133 | 2.638 | 2.497 | 2.3083 | 2.7716 | 2.7628 | 2.7589 | 2.7535 | 2.7473 | 2.7405 | 2.7334 | 2.7279 | 2.7222 | 2.6968 | 2.6716 | 2.5426 | 2.3871 | 2.1839 | 2.777 | 2.7682 | 2.7643 | 2.7588 | 2.7526 | 2.7459 | 2.7388 | 2.7277 | 2.7022 | 2.6769 | 2.652 | 2.6274 | 2.6024 | 2.5772
|  | TAYNUILT | ST |  |  |  | 0 | 2.774 | 2.7729 | 2.7724 | 2.7709 | 2.7691 | 2.7671 | 2.7648 | 2.7639 | 2.763 | 2.7622 | 2.7614 | 2.7578 | 2.7401 | 2.7309 | 2.7716 | 2.7705 | 2.77 | 2.7685 | 2.7668 | 2.7647 | 2.7624 | 2.7615 | 2.7606 | 2.7598 | 2.759 | 2.7554 | 2.7351 | 2.6889 | 2.777 | 2.7759 | 2.7753 | 2.7739 | 2.7721 | 2.77 | 2.7677 | 2.7669 | 2.766 | 2.7652 | 2.7644 | 2.7608 | 2.715 | 2.6693
|  | TAYNUILT | FS |  |  |  | 0 | 2.774 | 2.773 | 2.7729 | 2.7729 | 2.7728 | 2.7727 | 2.7726 | 2.7721 | 2.7716 | 2.7711 | 2.7705 | 2.7689 | 2.7607 | 2.7428 | 2.7716 | 2.7706 | 2.7706 | 2.7705 | 2.7704 | 2.7703 | 2.7702 | 2.7697 | 2.7692 | 2.7687 | 2.7681 | 2.7665 | 2.7583 | 2.7404 | 2.777 | 2.776 | 2.7759 | 2.7759 | 2.7758 | 2.7757 | 2.7756 | 2.7751 | 2.7746 | 2.7741 | 2.7735 | 2.7719 | 2.7637 | 2.7261
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 0.23684 | 25.4382 | 25.3685 | 25.3375 | 25.2944 | 25.2454 | 25.1904 | 25.1317 | 25.0851 | 25.0366 | 24.9867 | 24.9372 | 24.6122 | 24.0677 | 22.9848 | 24.5938 | 24.5241 | 24.4931 | 24.45 | 24.401 | 24.346 | 24.2873 | 24.2407 | 24.1922 | 24.1424 | 24.0928 | 23.7679 | 23.2233 | 21.7091 | 24.6276 | 24.5579 | 24.5269 | 24.4838 | 24.4348 | 24.3798 | 24.3211 | 24.2745 | 24.226 | 24.1762 | 24.1266 | 24.0769 | 24.012 | 23.9444
|  | THIMBLEROW | CT |  |  |  | 0.23684 | 25.4382 | 25.4157 | 25.3968 | 25.3711 | 25.3395 | 25.3015 | 25.2599 | 25.2323 | 25.2028 | 25.1726 | 25.1417 | 24.9271 | 24.551 | 23.9482 | 24.5938 | 24.5714 | 24.5524 | 24.5267 | 24.4952 | 24.4571 | 24.4155 | 24.388 | 24.3584 | 24.3282 | 24.2973 | 24.0827 | 23.7066 | 23.1038 | 24.6276 | 24.6052 | 24.5862 | 24.5605 | 24.5289 | 24.4909 | 24.4493 | 24.4217 | 24.3922 | 24.362 | 24.3311 | 24.2985 | 24.2553 | 24.2107
|  | THIMBLEROW | LW |  |  |  | 0.23684 | 25.4382 | 25.3685 | 25.3375 | 25.2944 | 25.2454 | 25.1904 | 25.1317 | 25.0851 | 25.0366 | 24.9867 | 24.9372 | 24.6122 | 24.0677 | 22.9848 | 24.5938 | 24.5241 | 24.4931 | 24.45 | 24.401 | 24.346 | 24.2873 | 24.2407 | 24.1922 | 24.1424 | 24.0928 | 23.7679 | 23.2233 | 21.7091 | 24.6276 | 24.5579 | 24.5269 | 24.4838 | 24.4348 | 24.3798 | 24.3211 | 24.2745 | 24.226 | 24.1762 | 24.1266 | 24.0769 | 24.012 | 23.9444
|  | THIMBLEROW | ST |  |  |  | 0.23684 | 25.4382 | 25.428 | 25.4231 | 25.41 | 25.3941 | 25.3754 | 25.3546 | 25.3468 | 25.3389 | 25.3314 | 25.3242 | 25.2898 | 25.0989 | 24.9972 | 24.5938 | 24.5836 | 24.5787 | 24.5656 | 24.5497 | 24.531 | 24.5102 | 24.5024 | 24.4945 | 24.487 | 24.4798 | 24.4454 | 24.2545 | 24.1528 | 24.6276 | 24.6174 | 24.6125 | 24.5994 | 24.5835 | 24.5648 | 24.544 | 24.5362 | 24.5283 | 24.5208 | 24.5136 | 24.4792 | 24.2883 | 24.1866
|  | THIMBLEROW | FS |  |  |  | 0.23684 | 25.4382 | 25.4264 | 25.4259 | 25.4253 | 25.4244 | 25.4231 | 25.4218 | 25.4168 | 25.4111 | 25.4049 | 25.3981 | 25.3801 | 25.2833 | 25.0667 | 24.5938 | 24.5821 | 24.5815 | 24.5809 | 24.58 | 24.5787 | 24.5774 | 24.5724 | 24.5667 | 24.5605 | 24.5537 | 24.5357 | 24.4389 | 24.2223 | 24.6276 | 24.6158 | 24.6153 | 24.6147 | 24.6138 | 24.6125 | 24.6112 | 24.6062 | 24.6005 | 24.5943 | 24.5875 | 24.5695 | 24.4727 | 24.2561
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.21168 | 0.2113 | 0.21114 | 0.2109 | 0.21064 | 0.21035 | 0.21004 | 0.2098 | 0.20956 | 0.20843 | 0.20695 | 0.19937 | 0.1909 | 0.18034 | 0.21158 | 0.2112 | 0.21103 | 0.2108 | 0.21053 | 0.21024 | 0.20964 | 0.20792 | 0.2062 | 0.2045 | 0.20281 | 0.19415 | 0.18459 | 0.17296 | 0.21181 | 0.21143 | 0.21126 | 0.21103 | 0.21076 | 0.21047 | 0.20878 | 0.20709 | 0.20539 | 0.20371 | 0.20204 | 0.20039 | 0.19868 | 0.19696
|  | TIRORAN BRIDGE | CT |  |  |  | 0 | 0.21168 | 0.21155 | 0.21144 | 0.21129 | 0.21111 | 0.21089 | 0.21066 | 0.21051 | 0.21036 | 0.2102 | 0.2093 | 0.20285 | 0.19578 | 0.18788 | 0.21158 | 0.21145 | 0.21134 | 0.21119 | 0.21101 | 0.21079 | 0.21056 | 0.20974 | 0.20829 | 0.20684 | 0.20539 | 0.19798 | 0.18995 | 0.18111 | 0.21181 | 0.21168 | 0.21157 | 0.21142 | 0.21124 | 0.21102 | 0.21034 | 0.2089 | 0.20746 | 0.20603 | 0.2046 | 0.20318 | 0.20172 | 0.20025
|  | TIRORAN BRIDGE | LW |  |  |  | 0 | 0.21168 | 0.2113 | 0.21114 | 0.2109 | 0.21064 | 0.21035 | 0.21004 | 0.2098 | 0.20956 | 0.20843 | 0.20695 | 0.19937 | 0.1909 | 0.18034 | 0.21158 | 0.2112 | 0.21103 | 0.2108 | 0.21053 | 0.21024 | 0.20964 | 0.20792 | 0.2062 | 0.2045 | 0.20281 | 0.19415 | 0.18459 | 0.17296 | 0.21181 | 0.21143 | 0.21126 | 0.21103 | 0.21076 | 0.21047 | 0.20878 | 0.20709 | 0.20539 | 0.20371 | 0.20204 | 0.20039 | 0.19868 | 0.19696
|  | TIRORAN BRIDGE | ST |  |  |  | 0 | 0.21168 | 0.21163 | 0.21161 | 0.21155 | 0.21147 | 0.21138 | 0.21128 | 0.21124 | 0.21121 | 0.21117 | 0.21113 | 0.21098 | 0.2102 | 0.20981 | 0.21158 | 0.21153 | 0.21151 | 0.21145 | 0.21137 | 0.21128 | 0.21118 | 0.21114 | 0.2111 | 0.21107 | 0.21103 | 0.21088 | 0.2101 | 0.2097 | 0.21181 | 0.21176 | 0.21174 | 0.21167 | 0.2116 | 0.21151 | 0.21141 | 0.21137 | 0.21133 | 0.2113 | 0.21126 | 0.2111 | 0.21033 | 0.20993
|  | TIRORAN BRIDGE | FS |  |  |  | 0 | 0.21168 | 0.21164 | 0.21164 | 0.21163 | 0.21163 | 0.21162 | 0.21162 | 0.2116 | 0.21158 | 0.21155 | 0.21153 | 0.21146 | 0.2111 | 0.21031 | 0.21158 | 0.21154 | 0.21153 | 0.21153 | 0.21153 | 0.21152 | 0.21152 | 0.2115 | 0.21148 | 0.21145 | 0.21143 | 0.21136 | 0.211 | 0.21021 | 0.21181 | 0.21176 | 0.21176 | 0.21176 | 0.21176 | 0.21175 | 0.21175 | 0.21173 | 0.21171 | 0.21168 | 0.21165 | 0.21159 | 0.21122 | 0.21044
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0.061053 | 1.3234 | 1.3097 | 1.2962 | 1.2831 | 1.2694 | 1.2553 | 1.2409 | 1.2269 | 1.2128 | 1.1988 | 1.1847 | 1.0882 | 0.96279 | 0.81436 | 1.2607 | 1.2469 | 1.2335 | 1.2203 | 1.2066 | 1.1925 | 1.1782 | 1.1642 | 1.1483 | 1.1278 | 1.1075 | 0.99492 | 0.86077 | 0.70398 | 1.2811 | 1.2673 | 1.2539 | 1.2407 | 1.227 | 1.2129 | 1.1985 | 1.1845 | 1.1705 | 1.1564 | 1.1423 | 1.1273 | 1.1117 | 1.0952
|  | TOMATIN | CT |  |  |  | 0.061053 | 1.3234 | 1.3097 | 1.2962 | 1.2831 | 1.2694 | 1.2553 | 1.2409 | 1.2269 | 1.2128 | 1.1988 | 1.1847 | 1.0882 | 0.96279 | 0.81436 | 1.2607 | 1.2469 | 1.2335 | 1.2203 | 1.2066 | 1.1925 | 1.1782 | 1.1642 | 1.1483 | 1.1278 | 1.1075 | 0.99492 | 0.86077 | 0.70398 | 1.2811 | 1.2673 | 1.2539 | 1.2407 | 1.227 | 1.2129 | 1.1985 | 1.1845 | 1.1705 | 1.1564 | 1.1423 | 1.1273 | 1.1117 | 1.0952
|  | TOMATIN | LW |  |  |  | 0.061053 | 1.3428 | 1.3336 | 1.3268 | 1.3189 | 1.3098 | 1.2994 | 1.2889 | 1.2785 | 1.2672 | 1.2498 | 1.2318 | 1.1347 | 1.0119 | 0.84383 | 1.28 | 1.2708 | 1.264 | 1.2562 | 1.247 | 1.2367 | 1.2202 | 1.1997 | 1.1794 | 1.1593 | 1.1385 | 1.0281 | 0.89192 | 0.71371 | 1.3004 | 1.2912 | 1.2844 | 1.2766 | 1.2674 | 1.2571 | 1.2465 | 1.2361 | 1.2257 | 1.2152 | 1.2039 | 1.1927 | 1.1729 | 1.1509
|  | TOMATIN | ST |  |  |  | 0.061053 | 1.347 | 1.3438 | 1.3409 | 1.3375 | 1.333 | 1.3283 | 1.3235 | 1.3196 | 1.3156 | 1.3118 | 1.3079 | 1.2888 | 1.2617 | 1.2228 | 1.2842 | 1.281 | 1.2781 | 1.2747 | 1.2702 | 1.2656 | 1.2607 | 1.2568 | 1.2529 | 1.249 | 1.2451 | 1.2208 | 1.1743 | 1.1299 | 1.3046 | 1.3014 | 1.2985 | 1.2951 | 1.2906 | 1.2859 | 1.2811 | 1.2772 | 1.2733 | 1.2694 | 1.2655 | 1.2464 | 1.2194 | 1.1936
|  | TOMATIN | FS |  |  |  | 0.061053 | 1.3495 | 1.3472 | 1.3447 | 1.3429 | 1.3412 | 1.3395 | 1.3377 | 1.3357 | 1.3338 | 1.3317 | 1.3297 | 1.317 | 1.2994 | 1.2802 | 1.2868 | 1.2845 | 1.2819 | 1.2802 | 1.2785 | 1.2767 | 1.275 | 1.273 | 1.271 | 1.269 | 1.267 | 1.2542 | 1.231 | 1.1956 | 1.3072 | 1.3048 | 1.3023 | 1.3006 | 1.2988 | 1.2971 | 1.2953 | 1.2934 | 1.2914 | 1.2894 | 1.2873 | 1.2746 | 1.257 | 1.2379
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0 | 1.6712 | 1.6712 | 1.6712 | 1.6711 | 1.6711 | 1.6711 | 1.671 | 1.671 | 1.671 | 1.671 | 1.6709 | 1.6708 | 1.6705 | 1.6676 | 1.1239 | 1.1239 | 1.1239 | 1.1239 | 1.1238 | 1.1238 | 1.1238 | 1.1237 | 1.1237 | 1.1237 | 1.1237 | 1.1235 | 1.1232 | 1.1203 | 1.1092 | 1.1092 | 1.1092 | 1.1092 | 1.1091 | 1.1091 | 1.1091 | 1.109 | 1.109 | 1.109 | 1.109 | 1.1089 | 1.1089 | 1.1089
|  | TORBOLL | CT |  |  |  | 0 | 1.6712 | 1.6712 | 1.6712 | 1.6711 | 1.6711 | 1.6711 | 1.671 | 1.671 | 1.671 | 1.671 | 1.6709 | 1.6708 | 1.6705 | 1.6676 | 1.1239 | 1.1239 | 1.1239 | 1.1239 | 1.1238 | 1.1238 | 1.1238 | 1.1237 | 1.1237 | 1.1237 | 1.1237 | 1.1235 | 1.1232 | 1.1203 | 1.1092 | 1.1092 | 1.1092 | 1.1092 | 1.1091 | 1.1091 | 1.1091 | 1.109 | 1.109 | 1.109 | 1.109 | 1.1089 | 1.1089 | 1.1089
|  | TORBOLL | LW |  |  |  | 0 | 1.6721 | 1.672 | 1.672 | 1.6719 | 1.6719 | 1.6718 | 1.6718 | 1.6717 | 1.6717 | 1.6716 | 1.6716 | 1.6713 | 1.6709 | 1.6702 | 1.1248 | 1.1247 | 1.1247 | 1.1246 | 1.1246 | 1.1245 | 1.1245 | 1.1244 | 1.1244 | 1.1243 | 1.1243 | 1.124 | 1.1236 | 1.1229 | 1.1101 | 1.11 | 1.11 | 1.1099 | 1.1099 | 1.1098 | 1.1098 | 1.1097 | 1.1097 | 1.1097 | 1.1096 | 1.1096 | 1.1095 | 1.1095
|  | TORBOLL | ST |  |  |  | 0 | 1.6721 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.6719 | 1.6718 | 1.6718 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1247 | 1.1245 | 1.1245 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.1098 | 1.1098
|  | TORBOLL | FS |  |  |  | 0 | 1.6721 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.672 | 1.6718 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 1.1247 | 1.1247 | 1.1247 | 1.1246 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.1101 | 1.11 | 1.11 | 1.1099
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 1.3211 | 27.1055 | 27.0521 | 26.9225 | 26.2614 | 25.637 | 25.052 | 24.5374 | 24.0079 | 23.5107 | 23.0419 | 22.6334 | 20.8132 | 19.0809 | 17.0375 | 24.0455 | 23.3788 | 22.721 | 21.9536 | 21.2306 | 20.555 | 19.9628 | 19.3506 | 18.7766 | 18.2362 | 17.7664 | 15.6912 | 13.7521 | 11.5241 | 25.4113 | 24.7501 | 24.0982 | 23.3298 | 22.6039 | 21.9257 | 21.3312 | 20.7167 | 20.1405 | 19.598 | 19.1265 | 18.7073 | 18.2827 | 17.8638
|  | TORRYBURN | CT |  |  |  | 1.3211 | 27.1055 | 27.0626 | 27.0237 | 26.9769 | 26.7114 | 26.2513 | 25.8687 | 25.4959 | 25.1351 | 24.8097 | 24.5117 | 23.1125 | 21.8341 | 20.4432 | 24.3008 | 23.9194 | 23.4966 | 23.0055 | 22.4885 | 21.9581 | 21.5193 | 21.0894 | 20.6739 | 20.3 | 19.9584 | 18.3663 | 16.9399 | 15.4138 | 25.6639 | 25.2856 | 24.8665 | 24.3796 | 23.867 | 23.3346 | 22.8942 | 22.4627 | 22.0456 | 21.6703 | 21.3275 | 20.9862 | 20.6518 | 20.3368
|  | TORRYBURN | LW |  |  |  | 1.3211 | 27.135 | 27.0521 | 26.9225 | 26.2614 | 25.637 | 25.052 | 24.5374 | 24.0079 | 23.5107 | 23.0419 | 22.6334 | 20.8132 | 19.0809 | 17.0375 | 24.0455 | 23.3788 | 22.721 | 21.9536 | 21.2306 | 20.555 | 19.9628 | 19.3506 | 18.7766 | 18.2362 | 17.7664 | 15.6912 | 13.7521 | 11.5241 | 25.4113 | 24.7501 | 24.0982 | 23.3298 | 22.6039 | 21.9257 | 21.3312 | 20.7167 | 20.1405 | 19.598 | 19.1265 | 18.7073 | 18.2827 | 17.8638
|  | TORRYBURN | ST |  |  |  | 1.3211 | 27.1409 | 27.127 | 27.1182 | 27.1016 | 27.0815 | 27.0596 | 27.0357 | 27.0241 | 26.9586 | 26.747 | 26.5464 | 25.6467 | 24.849 | 24.1805 | 24.5561 | 24.4232 | 24.2729 | 24.0373 | 23.7838 | 23.5201 | 23.2784 | 23.0246 | 22.7633 | 22.5167 | 22.2828 | 21.2349 | 20.3281 | 19.5605 | 25.9171 | 25.7853 | 25.6363 | 25.4028 | 25.1515 | 24.8901 | 24.6505 | 24.399 | 24.1401 | 23.895 | 23.6602 | 22.608 | 21.6981 | 20.9277
|  | TORRYBURN | FS |  |  |  | 1.3211 | 27.1443 | 27.1338 | 27.13 | 27.127 | 27.1238 | 27.1203 | 27.1168 | 27.1105 | 27.1038 | 27.0966 | 27.089 | 26.4024 | 25.7942 | 25.1414 | 24.6097 | 24.5 | 24.3893 | 24.263 | 24.1107 | 23.9369 | 23.7679 | 23.5767 | 23.3724 | 23.1734 | 22.9786 | 22.1015 | 21.4019 | 20.6635 | 25.9702 | 25.8615 | 25.7518 | 25.6266 | 25.4757 | 25.3035 | 25.1361 | 24.9467 | 24.7443 | 24.547 | 24.354 | 23.4778 | 22.7756 | 22.0348
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0 | 0.58453 | 0.57363 | 1.063 | 1.0518 | 1.0402 | 1.0283 | 1.017 | 1.001 | 0.98434 | 0.96774 | 0.95039 | 0.8582 | 0.7491 | 0.61959 | 0.53062 | 0.51971 | 1.0091 | 0.99585 | 0.97718 | 0.9585 | 0.94072 | 0.92284 | 0.90502 | 0.8873 | 0.86886 | 0.77137 | 0.65701 | 0.52268 | 0.54402 | 0.53311 | 1.0225 | 1.0106 | 0.99248 | 0.97428 | 0.95698 | 0.93928 | 0.92163 | 0.90409 | 0.88581 | 0.86757 | 0.8489 | 0.82933
|  | TRESSADY | CT |  |  |  | 0 | 0.58453 | 0.57363 | 1.063 | 1.0518 | 1.0402 | 1.0283 | 1.017 | 1.001 | 0.98434 | 0.96774 | 0.95039 | 0.8582 | 0.7491 | 0.61959 | 0.53062 | 0.51971 | 1.0091 | 0.99585 | 0.97718 | 0.9585 | 0.94072 | 0.92284 | 0.90502 | 0.8873 | 0.86886 | 0.77137 | 0.65701 | 0.52268 | 0.54402 | 0.53311 | 1.0225 | 1.0106 | 0.99248 | 0.97428 | 0.95698 | 0.93928 | 0.92163 | 0.90409 | 0.88581 | 0.86757 | 0.8489 | 0.82933
|  | TRESSADY | LW |  |  |  | 0 | 0.60053 | 0.59305 | 1.0875 | 1.0811 | 1.0734 | 1.0634 | 1.0473 | 1.0311 | 1.0149 | 0.99801 | 0.98132 | 0.89344 | 0.78156 | 0.63519 | 0.54662 | 0.53914 | 1.0336 | 1.0197 | 1.0026 | 0.98579 | 0.96829 | 0.95036 | 0.93256 | 0.91405 | 0.89577 | 0.80085 | 0.68194 | 0.52907 | 0.56002 | 0.55254 | 1.047 | 1.0348 | 1.0185 | 1.0021 | 0.98487 | 0.96719 | 0.94964 | 0.93137 | 0.91334 | 0.8955 | 0.87708 | 0.85855
|  | TRESSADY | ST |  |  |  | 0 | 0.6039 | 0.60078 | 1.098 | 1.0947 | 1.0912 | 1.0876 | 1.0838 | 1.0808 | 1.0779 | 1.0749 | 1.0719 | 1.0489 | 1.0126 | 0.97827 | 0.54999 | 0.54687 | 1.0441 | 1.0408 | 1.0373 | 1.0337 | 1.0299 | 1.0241 | 1.0169 | 1.0099 | 1.003 | 0.9699 | 0.93068 | 0.89355 | 0.56339 | 0.56026 | 1.0575 | 1.0542 | 1.0507 | 1.0471 | 1.0433 | 1.0389 | 1.0321 | 1.0253 | 1.0187 | 0.98646 | 0.94769 | 0.91099
|  | TRESSADY | FS |  |  |  | 0 | 0.60643 | 0.60506 | 1.1034 | 1.1016 | 1.0999 | 1.0982 | 1.0964 | 1.0945 | 1.0926 | 1.0906 | 1.0886 | 1.0794 | 1.0575 | 1.028 | 0.55252 | 0.55115 | 1.0494 | 1.0477 | 1.046 | 1.0443 | 1.0425 | 1.0406 | 1.0387 | 1.0367 | 1.0323 | 1.0064 | 0.97833 | 0.94636 | 0.56592 | 0.56455 | 1.0628 | 1.0611 | 1.0594 | 1.0577 | 1.0559 | 1.054 | 1.0521 | 1.0501 | 1.0471 | 1.0224 | 0.99492 | 0.96333
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0 | 6.654 | 6.6344 | 6.6151 | 6.5839 | 6.5519 | 6.5197 | 6.4877 | 6.4561 | 6.4248 | 6.3935 | 6.3602 | 6.1611 | 5.9154 | 5.5709 | 6.5445 | 6.5328 | 6.5221 | 6.4849 | 6.4416 | 6.3989 | 6.3567 | 6.3142 | 6.2719 | 6.23 | 6.1888 | 5.9693 | 5.7028 | 5.3378 | 6.5151 | 6.5035 | 6.4927 | 6.4802 | 6.4671 | 6.4526 | 6.4318 | 6.3916 | 6.3516 | 6.312 | 6.2729 | 6.2345 | 6.1925 | 6.1501
|  | TUMBLIN | CT |  |  |  | 0 | 6.654 | 6.6361 | 6.6183 | 6.593 | 6.5673 | 6.541 | 6.5146 | 6.4896 | 6.4645 | 6.4397 | 6.415 | 6.2734 | 6.0802 | 5.8446 | 6.5445 | 6.5328 | 6.5221 | 6.5023 | 6.4688 | 6.4352 | 6.4016 | 6.3688 | 6.3361 | 6.3037 | 6.2716 | 6.0998 | 5.892 | 5.6421 | 6.5151 | 6.5035 | 6.4927 | 6.4802 | 6.4671 | 6.4526 | 6.4375 | 6.425 | 6.4107 | 6.3799 | 6.3493 | 6.3188 | 6.2864 | 6.2529
|  | TUMBLIN | LW |  |  |  | 0 | 6.6613 | 6.6344 | 6.6151 | 6.5839 | 6.5519 | 6.5197 | 6.4877 | 6.4561 | 6.4248 | 6.3935 | 6.3602 | 6.1611 | 5.9154 | 5.5709 | 6.5537 | 6.5356 | 6.5266 | 6.4849 | 6.4416 | 6.3989 | 6.3567 | 6.3142 | 6.2719 | 6.23 | 6.1888 | 5.9693 | 5.7028 | 5.3378 | 6.5243 | 6.5062 | 6.4972 | 6.4845 | 6.4704 | 6.4552 | 6.4318 | 6.3916 | 6.3516 | 6.312 | 6.2729 | 6.2345 | 6.1925 | 6.1501
|  | TUMBLIN | ST |  |  |  | 0 | 6.6759 | 6.6717 | 6.6686 | 6.6554 | 6.6417 | 6.6279 | 6.6139 | 6.6021 | 6.5904 | 6.5791 | 6.568 | 6.5154 | 6.437 | 6.3729 | 6.5562 | 6.5524 | 6.5497 | 6.5452 | 6.5401 | 6.5344 | 6.5246 | 6.5075 | 6.4906 | 6.4742 | 6.4582 | 6.3824 | 6.282 | 6.2006 | 6.5269 | 6.523 | 6.5203 | 6.5158 | 6.5107 | 6.5051 | 6.4989 | 6.4956 | 6.4922 | 6.4889 | 6.4857 | 6.4579 | 6.3622 | 6.2852
|  | TUMBLIN | FS |  |  |  | 0 | 6.6774 | 6.6743 | 6.673 | 6.6713 | 6.6675 | 6.6609 | 6.6544 | 6.6465 | 6.6385 | 6.6304 | 6.6222 | 6.5849 | 6.5365 | 6.4706 | 6.5571 | 6.5542 | 6.5533 | 6.5523 | 6.5513 | 6.5503 | 6.5492 | 6.5475 | 6.5457 | 6.5418 | 6.5297 | 6.4737 | 6.4078 | 6.3253 | 6.5277 | 6.5249 | 6.5239 | 6.523 | 6.522 | 6.5209 | 6.5198 | 6.5181 | 6.5163 | 6.5144 | 6.5124 | 6.5051 | 6.4824 | 6.4034
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0 | 1.1454 | 1.1294 | 1.1137 | 1.0974 | 1.0816 | 1.0653 | 1.0489 | 1.0327 | 1.0155 | 0.98905 | 0.96269 | 0.82114 | 0.65646 | 0.46612 | 1.0651 | 1.0491 | 1.0333 | 1.0171 | 1.0012 | 0.985 | 0.96858 | 0.95234 | 0.93604 | 0.9189 | 0.90175 | 0.7642 | 0.59025 | 0.39083 | 1.0808 | 1.0648 | 1.049 | 1.0328 | 1.0169 | 1.0007 | 0.98425 | 0.96801 | 0.95172 | 0.93457 | 0.91742 | 0.90019 | 0.88163 | 0.86214
|  | TUMMEL BRIDGE | CT |  |  |  | 0 | 1.1454 | 1.1294 | 1.1137 | 1.0974 | 1.0816 | 1.0653 | 1.0489 | 1.0327 | 1.0155 | 0.98905 | 0.96269 | 0.82114 | 0.65646 | 0.46612 | 1.0651 | 1.0491 | 1.0333 | 1.0171 | 1.0012 | 0.985 | 0.96858 | 0.95234 | 0.93604 | 0.9189 | 0.90175 | 0.7642 | 0.59025 | 0.39083 | 1.0808 | 1.0648 | 1.049 | 1.0328 | 1.0169 | 1.0007 | 0.98425 | 0.96801 | 0.95172 | 0.93457 | 0.91742 | 0.90019 | 0.88163 | 0.86214
|  | TUMMEL BRIDGE | LW |  |  |  | 0 | 1.1707 | 1.1614 | 1.1541 | 1.1451 | 1.1356 | 1.125 | 1.1108 | 1.0865 | 1.0614 | 1.0364 | 1.0108 | 0.87447 | 0.71059 | 0.50575 | 1.0904 | 1.0811 | 1.0738 | 1.0648 | 1.0553 | 1.0447 | 1.0331 | 1.0223 | 1.0107 | 0.98398 | 0.95568 | 0.80603 | 0.62886 | 0.41095 | 1.106 | 1.0968 | 1.0894 | 1.0804 | 1.071 | 1.0604 | 1.0487 | 1.038 | 1.0264 | 1.0147 | 0.99598 | 0.9681 | 0.93872 | 0.90922
|  | TUMMEL BRIDGE | ST |  |  |  | 0 | 1.1757 | 1.1717 | 1.1681 | 1.1639 | 1.1587 | 1.1534 | 1.1479 | 1.1432 | 1.1385 | 1.1339 | 1.1301 | 1.0967 | 1.0371 | 0.97864 | 1.0954 | 1.0914 | 1.0878 | 1.0836 | 1.0784 | 1.0731 | 1.0676 | 1.0629 | 1.0582 | 1.0536 | 1.0498 | 1.0284 | 0.9848 | 0.92039 | 1.1111 | 1.1071 | 1.1034 | 1.0993 | 1.0941 | 1.0887 | 1.0833 | 1.0786 | 1.0739 | 1.0692 | 1.0654 | 1.0441 | 1.0143 | 0.96094
|  | TUMMEL BRIDGE | FS |  |  |  | 0 | 1.1782 | 1.176 | 1.1735 | 1.1709 | 1.1683 | 1.1657 | 1.1632 | 1.1604 | 1.1576 | 1.1548 | 1.1519 | 1.1368 | 1.118 | 1.0759 | 1.0979 | 1.0957 | 1.0931 | 1.0906 | 1.088 | 1.0854 | 1.0828 | 1.0801 | 1.0773 | 1.0745 | 1.0716 | 1.0565 | 1.0395 | 1.0175 | 1.1136 | 1.1114 | 1.1088 | 1.1063 | 1.1037 | 1.1011 | 1.0985 | 1.0958 | 1.093 | 1.0901 | 1.0873 | 1.0721 | 1.0552 | 1.0331
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 0.32421 | 10.2376 | 10.1066 | 9.9755 | 9.8089 | 9.6412 | 9.4742 | 9.3135 | 9.1586 | 9.0071 | 8.8582 | 8.718 | 7.9816 | 7.0748 | 5.7375 | 9.8754 | 9.7381 | 9.3589 | 8.8831 | 8.4252 | 7.9886 | 7.5901 | 7.1822 | 6.7919 | 6.4165 | 6.0747 | 4.4527 | 2.7647 | 0.69995 | 10.4647 | 10.4005 | 10.34 | 10.273 | 10.0552 | 9.7535 | 9.4741 | 9.1927 | 8.9219 | 8.6599 | 8.419 | 8.1931 | 7.9567 | 7.7195
|  | TURRIFF | CT |  |  |  | 0.32421 | 10.2376 | 10.1257 | 10.0114 | 9.8763 | 9.7329 | 9.5843 | 9.4452 | 9.3169 | 9.1888 | 9.0646 | 8.9445 | 8.2975 | 7.5252 | 6.5575 | 9.8754 | 9.8112 | 9.6837 | 9.351 | 9.0043 | 8.6513 | 8.3419 | 8.0381 | 7.7402 | 7.4608 | 7.1978 | 5.8979 | 4.5712 | 3.083 | 10.4647 | 10.4005 | 10.34 | 10.273 | 10.1996 | 10.0611 | 9.8982 | 9.6995 | 9.4866 | 9.2849 | 9.0934 | 8.9009 | 8.7033 | 8.5098
|  | TURRIFF | LW |  |  |  | 0.32421 | 10.2702 | 10.1066 | 9.9755 | 9.8089 | 9.6412 | 9.4742 | 9.3135 | 9.1586 | 9.0071 | 8.8582 | 8.718 | 7.9816 | 7.0748 | 5.7375 | 9.9444 | 9.7381 | 9.3589 | 8.8831 | 8.4252 | 7.9886 | 7.5901 | 7.1822 | 6.7919 | 6.4165 | 6.0747 | 4.4527 | 2.7647 | 0.69995 | 10.5338 | 10.4493 | 10.4036 | 10.2867 | 10.0552 | 9.7535 | 9.4741 | 9.1927 | 8.9219 | 8.6599 | 8.419 | 8.1931 | 7.9567 | 7.7195
|  | TURRIFF | ST |  |  |  | 0.32421 | 10.3571 | 10.3226 | 10.2911 | 10.2336 | 10.1695 | 10.1031 | 10.0381 | 9.9813 | 9.9236 | 9.8688 | 9.8161 | 9.5679 | 9.2325 | 8.969 | 9.9579 | 9.9386 | 9.9249 | 9.9037 | 9.8774 | 9.7552 | 9.5879 | 9.4184 | 9.2458 | 9.0811 | 8.9236 | 8.1967 | 7.4795 | 6.8606 | 10.5472 | 10.5279 | 10.5142 | 10.493 | 10.4667 | 10.4388 | 10.4089 | 10.3909 | 10.3728 | 10.3559 | 10.2986 | 9.9043 | 9.3782 | 8.9372
|  | TURRIFF | FS |  |  |  | 0.32421 | 10.3707 | 10.3446 | 10.3232 | 10.2992 | 10.2708 | 10.2364 | 10.2025 | 10.1624 | 10.1203 | 10.0784 | 10.037 | 9.8468 | 9.6322 | 9.3478 | 9.9647 | 9.951 | 9.9431 | 9.935 | 9.9276 | 9.9199 | 9.9123 | 9.8344 | 9.7015 | 9.5709 | 9.4428 | 8.8509 | 8.3208 | 7.7398 | 10.554 | 10.5404 | 10.5324 | 10.5244 | 10.517 | 10.5093 | 10.5016 | 10.4912 | 10.4803 | 10.469 | 10.4573 | 10.3148 | 9.9985 | 9.5659
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0.0052632 | 1.9454 | 1.9403 | 1.9352 | 1.9284 | 1.9214 | 1.9142 | 1.907 | 1.9003 | 1.8926 | 1.8847 | 1.8769 | 1.836 | 1.779 | 1.7014 | 1.7598 | 1.7561 | 1.7525 | 1.7485 | 1.7442 | 1.7397 | 1.7351 | 1.731 | 1.727 | 1.7229 | 1.7189 | 1.6958 | 1.6644 | 1.6196 | 1.8656 | 1.8596 | 1.8536 | 1.8451 | 1.8356 | 1.8258 | 1.8161 | 1.8058 | 1.7955 | 1.7853 | 1.7752 | 1.7652 | 1.7547 | 1.7441
|  | TYNDRUM | CT |  |  |  | 0.0052632 | 1.9454 | 1.9403 | 1.9352 | 1.9284 | 1.9214 | 1.9142 | 1.907 | 1.9003 | 1.8936 | 1.887 | 1.8803 | 1.8446 | 1.8003 | 1.7459 | 1.7598 | 1.7561 | 1.7525 | 1.7485 | 1.7442 | 1.7397 | 1.7351 | 1.731 | 1.727 | 1.7229 | 1.7189 | 1.6958 | 1.6644 | 1.6241 | 1.8656 | 1.8596 | 1.8536 | 1.8451 | 1.8363 | 1.8275 | 1.8187 | 1.8104 | 1.8021 | 1.7938 | 1.7855 | 1.7773 | 1.7687 | 1.7601
|  | TYNDRUM | LW |  |  |  | 0.0052632 | 1.9484 | 1.9427 | 1.9378 | 1.9306 | 1.9232 | 1.9158 | 1.9084 | 1.9005 | 1.8926 | 1.8847 | 1.8769 | 1.836 | 1.779 | 1.7014 | 1.7631 | 1.7591 | 1.7566 | 1.7535 | 1.7501 | 1.7465 | 1.7428 | 1.7388 | 1.7348 | 1.7307 | 1.7267 | 1.7042 | 1.6714 | 1.6196 | 1.8684 | 1.8617 | 1.8553 | 1.8455 | 1.8356 | 1.8258 | 1.8161 | 1.8058 | 1.7955 | 1.7853 | 1.7752 | 1.7652 | 1.7547 | 1.7441
|  | TYNDRUM | ST |  |  |  | 0.0052632 | 1.9522 | 1.9509 | 1.9498 | 1.9466 | 1.9433 | 1.94 | 1.9367 | 1.9332 | 1.9297 | 1.9263 | 1.9229 | 1.9071 | 1.8887 | 1.8736 | 1.7642 | 1.763 | 1.762 | 1.7604 | 1.7588 | 1.7571 | 1.7552 | 1.7539 | 1.7525 | 1.7512 | 1.7498 | 1.7434 | 1.7321 | 1.7239 | 1.8739 | 1.8726 | 1.8714 | 1.8672 | 1.8629 | 1.8586 | 1.8542 | 1.8494 | 1.8447 | 1.84 | 1.8353 | 1.8137 | 1.7909 | 1.7715
|  | TYNDRUM | FS |  |  |  | 0.0052632 | 1.9532 | 1.9528 | 1.9519 | 1.9509 | 1.9499 | 1.9485 | 1.9471 | 1.9454 | 1.9437 | 1.942 | 1.9402 | 1.9289 | 1.9146 | 1.8997 | 1.7651 | 1.7647 | 1.7639 | 1.763 | 1.7629 | 1.7627 | 1.7625 | 1.7622 | 1.7619 | 1.7616 | 1.7612 | 1.7566 | 1.7487 | 1.7399 | 1.8749 | 1.8745 | 1.8735 | 1.8725 | 1.871 | 1.8688 | 1.8666 | 1.864 | 1.8615 | 1.8589 | 1.8564 | 1.8409 | 1.8226 | 1.8038
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 0 | 2.9125 | 2.8947 | 2.8855 | 2.8721 | 2.8573 | 2.8416 | 2.8112 | 2.7685 | 2.7261 | 2.684 | 2.6427 | 2.4288 | 2.1791 | 1.8442 | 2.7959 | 2.7798 | 2.7723 | 2.7618 | 2.7499 | 2.737 | 2.7234 | 2.7128 | 2.6806 | 2.633 | 2.5863 | 2.3461 | 2.07 | 1.7093 | 2.8363 | 2.8202 | 2.8127 | 2.8022 | 2.7899 | 2.7429 | 2.6964 | 2.6508 | 2.6056 | 2.5608 | 2.5167 | 2.4734 | 2.4278 | 2.3819
|  | UIG | CT |  |  |  | 0 | 2.9125 | 2.9058 | 2.8999 | 2.8914 | 2.8814 | 2.8703 | 2.8586 | 2.8503 | 2.8337 | 2.8057 | 2.778 | 2.6324 | 2.4635 | 2.2598 | 2.7959 | 2.7903 | 2.7856 | 2.7791 | 2.7712 | 2.762 | 2.7522 | 2.7458 | 2.7392 | 2.7326 | 2.726 | 2.5737 | 2.3867 | 2.1655 | 2.8363 | 2.8307 | 2.826 | 2.8195 | 2.8116 | 2.8024 | 2.7803 | 2.7498 | 2.7195 | 2.6896 | 2.66 | 2.6305 | 2.5995 | 2.5684
|  | UIG | LW |  |  |  | 0 | 2.913 | 2.8947 | 2.8855 | 2.8721 | 2.8573 | 2.8416 | 2.8112 | 2.7685 | 2.7261 | 2.684 | 2.6427 | 2.4288 | 2.1791 | 1.8442 | 2.7968 | 2.7798 | 2.7723 | 2.7618 | 2.7499 | 2.737 | 2.7234 | 2.7128 | 2.6806 | 2.633 | 2.5863 | 2.3461 | 2.07 | 1.7093 | 2.8372 | 2.8202 | 2.8127 | 2.8022 | 2.7899 | 2.7429 | 2.6964 | 2.6508 | 2.6056 | 2.5608 | 2.5167 | 2.4734 | 2.4278 | 2.3819
|  | UIG | ST |  |  |  | 0 | 2.9148 | 2.9127 | 2.9116 | 2.9076 | 2.903 | 2.8979 | 2.8925 | 2.8895 | 2.8867 | 2.8839 | 2.8811 | 2.8478 | 2.7517 | 2.6739 | 2.7968 | 2.7947 | 2.7938 | 2.7911 | 2.7879 | 2.7842 | 2.78 | 2.7784 | 2.7768 | 2.7753 | 2.7739 | 2.7674 | 2.7048 | 2.6161 | 2.8372 | 2.8351 | 2.8342 | 2.8315 | 2.8283 | 2.8246 | 2.8204 | 2.8188 | 2.8172 | 2.8157 | 2.8127 | 2.7323 | 2.6306 | 2.5472
|  | UIG | FS |  |  |  | 0 | 2.9149 | 2.913 | 2.9128 | 2.9126 | 2.912 | 2.9109 | 2.9098 | 2.9081 | 2.9062 | 2.9043 | 2.9022 | 2.8946 | 2.865 | 2.7855 | 2.7968 | 2.795 | 2.7949 | 2.7948 | 2.7947 | 2.7945 | 2.7943 | 2.7935 | 2.7926 | 2.7917 | 2.7906 | 2.7878 | 2.7736 | 2.7428 | 2.8372 | 2.8354 | 2.8353 | 2.8352 | 2.8351 | 2.8349 | 2.8347 | 2.8339 | 2.833 | 2.8321 | 2.831 | 2.8206 | 2.7504 | 2.6667
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | YES | 0 | 3.1406 | 3.1261 | 3.1196 | 4.6106 | 4.6004 | 4.5893 | 4.5775 | 4.5683 | 4.5589 | 4.5494 | 4.54 | 4.4819 | 4.3351 | 4.0264 | 2.9891 | 2.9738 | 2.9664 | 4.4556 | 4.4437 | 4.4309 | 4.4176 | 4.4066 | 4.3956 | 4.3844 | 4.3426 | 4.1175 | 3.8536 | 3.5072 | 3.0054 | 2.9909 | 2.9844 | 4.4755 | 4.4653 | 4.4541 | 4.4423 | 4.4331 | 4.4237 | 4.4142 | 4.4049 | 4.3956 | 4.3629 | 4.319
|  | ULLAPOOL | CT |  |  |  | 0 | 3.1406 | 3.1356 | 3.1313 | 4.6256 | 4.6185 | 4.6103 | 4.6014 | 4.5956 | 4.5896 | 4.5836 | 4.5775 | 4.5376 | 4.4738 | 4.3753 | 2.9893 | 2.9837 | 2.9788 | 4.4718 | 4.4635 | 4.4541 | 4.4441 | 4.4372 | 4.43 | 4.4228 | 4.4156 | 4.3237 | 4.1421 | 3.9275 | 3.0054 | 3.0004 | 2.9961 | 4.4904 | 4.4833 | 4.4751 | 4.4662 | 4.4604 | 4.4544 | 4.4484 | 4.4423 | 4.436 | 4.428 | 4.4198
|  | ULLAPOOL | LW |  |  |  | 0 | 3.1406 | 3.1261 | 3.1196 | 4.6106 | 4.6004 | 4.5893 | 4.5775 | 4.5683 | 4.5589 | 4.5494 | 4.54 | 4.4819 | 4.3351 | 4.0264 | 2.9891 | 2.9738 | 2.9664 | 4.4556 | 4.4437 | 4.4309 | 4.4176 | 4.4066 | 4.3956 | 4.3844 | 4.3426 | 4.1175 | 3.8536 | 3.5072 | 3.0054 | 2.9909 | 2.9844 | 4.4755 | 4.4653 | 4.4541 | 4.4423 | 4.4331 | 4.4237 | 4.4142 | 4.4049 | 4.3956 | 4.3629 | 4.319
|  | ULLAPOOL | ST |  |  |  | 0 | 3.1406 | 3.1387 | 3.1378 | 4.6353 | 4.6323 | 4.6288 | 4.6249 | 4.6235 | 4.622 | 4.6206 | 4.6192 | 4.6131 | 4.5826 | 4.5668 | 2.9902 | 2.9882 | 2.9872 | 4.4839 | 4.4801 | 4.4759 | 4.4712 | 4.4689 | 4.4667 | 4.4645 | 4.4624 | 4.4526 | 4.4185 | 4.3503 | 3.0054 | 3.0035 | 3.0026 | 4.5001 | 4.4972 | 4.4937 | 4.4897 | 4.4883 | 4.4868 | 4.4854 | 4.4841 | 4.4779 | 4.4474 | 4.4317
|  | ULLAPOOL | FS |  |  |  | 0 | 3.1406 | 3.1388 | 3.1387 | 4.6386 | 4.6385 | 4.6383 | 4.6381 | 4.6373 | 4.6364 | 4.6355 | 4.6345 | 4.6317 | 4.6174 | 4.5861 | 2.9902 | 2.9883 | 2.9882 | 4.488 | 4.4876 | 4.4869 | 4.4862 | 4.4848 | 4.4834 | 4.4818 | 4.4802 | 4.4745 | 4.4574 | 4.4234 | 3.0054 | 3.0036 | 3.0035 | 4.5034 | 4.5033 | 4.5031 | 4.5029 | 4.5021 | 4.5013 | 4.5003 | 4.4993 | 4.4965 | 4.4822 | 4.451
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0 | 1.4471 | 1.439 | 1.4355 | 1.4305 | 1.4248 | 1.4187 | 1.4122 | 1.4071 | 1.4019 | 1.3966 | 1.3914 | 1.3333 | 1.2293 | 1.0795 | 1.3167 | 1.3087 | 1.3051 | 1.3001 | 1.2945 | 1.2857 | 1.2664 | 1.2479 | 1.2294 | 1.2112 | 1.1932 | 1.0983 | 0.98356 | 0.82062 | 1.3009 | 1.2928 | 1.2893 | 1.2843 | 1.2786 | 1.2725 | 1.266 | 1.2609 | 1.2557 | 1.2504 | 1.2367 | 1.2189 | 1.1997 | 1.1804
|  | UNST | CT |  |  |  | 0 | 1.4471 | 1.4443 | 1.4419 | 1.4386 | 1.4347 | 1.4301 | 1.4251 | 1.4219 | 1.4185 | 1.4151 | 1.4117 | 1.3894 | 1.3439 | 1.2539 | 1.3167 | 1.3139 | 1.3115 | 1.3083 | 1.3043 | 1.2997 | 1.2947 | 1.2915 | 1.2793 | 1.2672 | 1.2552 | 1.1906 | 1.1121 | 1.0151 | 1.3009 | 1.2981 | 1.2957 | 1.2924 | 1.2885 | 1.2839 | 1.2789 | 1.2757 | 1.2723 | 1.2689 | 1.2655 | 1.262 | 1.2575 | 1.2529
|  | UNST | LW |  |  |  | 0 | 1.4471 | 1.439 | 1.4355 | 1.4305 | 1.4248 | 1.4187 | 1.4122 | 1.4071 | 1.4019 | 1.3966 | 1.3914 | 1.3333 | 1.2293 | 1.0795 | 1.3167 | 1.3087 | 1.3051 | 1.3001 | 1.2945 | 1.2857 | 1.2664 | 1.2479 | 1.2294 | 1.2112 | 1.1932 | 1.0983 | 0.98356 | 0.82062 | 1.3009 | 1.2928 | 1.2893 | 1.2843 | 1.2786 | 1.2725 | 1.266 | 1.2609 | 1.2557 | 1.2504 | 1.2367 | 1.2189 | 1.1997 | 1.1804
|  | UNST | ST |  |  |  | 0 | 1.4471 | 1.446 | 1.4455 | 1.4441 | 1.4424 | 1.4405 | 1.4383 | 1.4375 | 1.4367 | 1.4359 | 1.4351 | 1.4317 | 1.4147 | 1.4059 | 1.3167 | 1.3156 | 1.3151 | 1.3137 | 1.3121 | 1.3101 | 1.3079 | 1.3071 | 1.3063 | 1.3055 | 1.3047 | 1.286 | 1.2419 | 1.2071 | 1.3009 | 1.2998 | 1.2993 | 1.2979 | 1.2962 | 1.2943 | 1.2921 | 1.2913 | 1.2905 | 1.2897 | 1.2889 | 1.2855 | 1.2685 | 1.2507
|  | UNST | FS |  |  |  | 0 | 1.4471 | 1.4461 | 1.446 | 1.446 | 1.4459 | 1.4458 | 1.4457 | 1.4452 | 1.4447 | 1.4442 | 1.4436 | 1.4421 | 1.434 | 1.4164 | 1.3167 | 1.3157 | 1.3156 | 1.3156 | 1.3155 | 1.3154 | 1.3153 | 1.3149 | 1.3144 | 1.3138 | 1.3133 | 1.3117 | 1.2854 | 1.2451 | 1.3009 | 1.2999 | 1.2998 | 1.2998 | 1.2997 | 1.2996 | 1.2995 | 1.299 | 1.2985 | 1.298 | 1.2974 | 1.2959 | 1.2878 | 1.2702
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0.0042105 | 9.1299 | 9.1076 | 9.0865 | 9.0638 | 9.0391 | 9.0125 | 8.9848 | 8.9613 | 8.9374 | 8.9135 | 8.8886 | 8.7435 | 8.4584 | 7.9667 | 8.7146 | 8.6923 | 8.6712 | 8.6485 | 8.6238 | 8.5972 | 8.5696 | 8.546 | 8.5221 | 8.4982 | 8.4602 | 8.1427 | 7.7519 | 7.2097 | 8.7499 | 8.7276 | 8.7065 | 8.6838 | 8.6591 | 8.6324 | 8.6048 | 8.5813 | 8.5574 | 8.5334 | 8.5086 | 8.4833 | 8.4547 | 8.4256
|  | VOE | CT |  |  |  | 0.0042105 | 9.1299 | 9.1076 | 9.0865 | 9.0638 | 9.0391 | 9.0125 | 8.9848 | 8.9613 | 8.9374 | 8.9135 | 8.8886 | 8.7435 | 8.5435 | 8.2322 | 8.7146 | 8.6923 | 8.6712 | 8.6485 | 8.6238 | 8.5972 | 8.5696 | 8.546 | 8.5221 | 8.4982 | 8.4733 | 8.261 | 7.9386 | 7.5497 | 8.7499 | 8.7276 | 8.7065 | 8.6838 | 8.6591 | 8.6324 | 8.6048 | 8.5813 | 8.5574 | 8.5334 | 8.5086 | 8.4833 | 8.4547 | 8.4256
|  | VOE | LW |  |  |  | 0.0042105 | 9.1544 | 9.1272 | 9.112 | 9.0919 | 9.0698 | 9.0455 | 9.0193 | 8.9972 | 8.974 | 8.9505 | 8.9273 | 8.7842 | 8.4584 | 7.9667 | 8.7391 | 8.7119 | 8.6967 | 8.6766 | 8.6546 | 8.6302 | 8.6041 | 8.5819 | 8.5587 | 8.5192 | 8.4602 | 8.1427 | 7.7519 | 7.2097 | 8.7743 | 8.7472 | 8.7319 | 8.7118 | 8.6898 | 8.6655 | 8.6393 | 8.6172 | 8.5939 | 8.5705 | 8.5473 | 8.5234 | 8.4936 | 8.429
|  | VOE | ST |  |  |  | 0.0042105 | 9.1594 | 9.153 | 9.1482 | 9.1409 | 9.1319 | 9.1222 | 9.1117 | 9.1052 | 9.0995 | 9.0939 | 9.0883 | 9.0592 | 8.9906 | 8.9413 | 8.7441 | 8.7377 | 8.7329 | 8.7256 | 8.7166 | 8.7069 | 8.6964 | 8.6899 | 8.6842 | 8.6786 | 8.6731 | 8.6439 | 8.5753 | 8.4772 | 8.7794 | 8.773 | 8.7681 | 8.7609 | 8.7519 | 8.7421 | 8.7317 | 8.7252 | 8.7194 | 8.7138 | 8.7083 | 8.6792 | 8.6106 | 8.5613
|  | VOE | FS |  |  |  | 0.0042105 | 9.1619 | 9.1574 | 9.1548 | 9.1521 | 9.1494 | 9.1465 | 9.1437 | 9.14 | 9.1361 | 9.132 | 9.1279 | 9.1101 | 9.0749 | 9.0131 | 8.7466 | 8.7421 | 8.7395 | 8.7368 | 8.7341 | 8.7312 | 8.7284 | 8.7247 | 8.7208 | 8.7167 | 8.7126 | 8.6948 | 8.6596 | 8.5978 | 8.7819 | 8.7774 | 8.7747 | 8.7721 | 8.7693 | 8.7665 | 8.7636 | 8.7599 | 8.756 | 8.752 | 8.7479 | 8.7301 | 8.6949 | 8.633
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 0 | 24.7408 | 24.6973 | 24.6752 | 24.6427 | 24.6069 | 24.5672 | 24.5253 | 24.4897 | 24.4527 | 24.4146 | 24.3765 | 24.1334 | 23.6747 | 22.429 | 23.1319 | 23.0766 | 23.0399 | 22.9808 | 22.9183 | 22.8525 | 22.7847 | 22.721 | 22.6558 | 22.5895 | 22.4843 | 21.6761 | 20.6648 | 19.2571 | 23.7738 | 23.731 | 23.7097 | 23.6785 | 23.6439 | 23.6055 | 23.5649 | 23.5306 | 23.495 | 23.4583 | 23.4216 | 23.3847 | 23.3372 | 23.2883
|  | WALTON | CT |  |  |  | 0 | 24.7408 | 24.7259 | 24.7126 | 24.693 | 24.6703 | 24.6437 | 24.6149 | 24.5936 | 24.5707 | 24.5474 | 24.5234 | 24.3637 | 24.093 | 23.6699 | 23.135 | 23.1112 | 23.0877 | 23.0496 | 23.0083 | 22.9634 | 22.9165 | 22.8755 | 22.8329 | 22.7898 | 22.7459 | 22.3668 | 21.6638 | 20.7828 | 23.7738 | 23.7594 | 23.7465 | 23.7279 | 23.7061 | 23.6803 | 23.6525 | 23.632 | 23.6102 | 23.5878 | 23.5648 | 23.5407 | 23.5094 | 23.4773
|  | WALTON | LW |  |  |  | 0 | 24.7408 | 24.6973 | 24.6752 | 24.6427 | 24.6069 | 24.5672 | 24.5253 | 24.4897 | 24.4527 | 24.4146 | 24.3765 | 24.1334 | 23.6747 | 22.429 | 23.1319 | 23.0766 | 23.0399 | 22.9808 | 22.9183 | 22.8525 | 22.7847 | 22.721 | 22.6558 | 22.5895 | 22.4843 | 21.6761 | 20.6648 | 19.2571 | 23.774 | 23.731 | 23.7097 | 23.6785 | 23.6439 | 23.6055 | 23.5649 | 23.5306 | 23.495 | 23.4583 | 23.4216 | 23.3847 | 23.3372 | 23.2883
|  | WALTON | ST |  |  |  | 0 | 24.7454 | 24.7389 | 24.7356 | 24.7241 | 24.711 | 24.6962 | 24.6802 | 24.6717 | 24.6631 | 24.6547 | 24.6465 | 24.6058 | 24.4627 | 24.3753 | 23.1526 | 23.1449 | 23.1401 | 23.1164 | 23.091 | 23.0642 | 23.0361 | 23.0141 | 22.9921 | 22.9703 | 22.9487 | 22.8402 | 22.6267 | 22.2668 | 23.7778 | 23.7713 | 23.7681 | 23.7572 | 23.7447 | 23.7305 | 23.7151 | 23.7072 | 23.6992 | 23.6915 | 23.684 | 23.6466 | 23.5069 | 23.4231
|  | WALTON | FS |  |  |  | 0 | 24.7451 | 24.7373 | 24.7365 | 24.7356 | 24.7336 | 24.7301 | 24.7265 | 24.7201 | 24.7133 | 24.7061 | 24.6986 | 24.6715 | 24.592 | 24.4323 | 23.1514 | 23.1425 | 23.1405 | 23.1375 | 23.131 | 23.118 | 23.105 | 23.0876 | 23.0698 | 23.0516 | 23.0331 | 22.9522 | 22.8168 | 22.6 | 23.7776 | 23.7697 | 23.7691 | 23.7682 | 23.7665 | 23.7634 | 23.7603 | 23.7545 | 23.7482 | 23.7415 | 23.7345 | 23.71 | 23.6332 | 23.4764
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 1.3084 | 26.5109 | 26.5126 | 26.5128 | 26.5129 | 26.5131 | 26.5133 | 26.5135 | 26.5143 | 26.5152 | 26.5162 | 26.5173 | 26.5201 | 26.5355 | 26.5699 | 24.5379 | 24.5267 | 24.5218 | 24.5148 | 24.507 | 24.4982 | 24.4888 | 24.4813 | 24.4736 | 24.4656 | 24.4577 | 24.4063 | 24.3205 | 24.1505 | 25.1997 | 25.2014 | 25.2017 | 25.2018 | 25.2019 | 25.2021 | 25.2023 | 25.2031 | 25.204 | 25.205 | 25.2061 | 25.209 | 25.2244 | 25.2587
|  | WATERLOO PLACE | CT |  |  |  | 1.3084 | 26.5109 | 26.5147 | 26.518 | 26.5224 | 26.5279 | 26.5344 | 26.5415 | 26.5462 | 26.5512 | 26.5563 | 26.5615 | 26.5972 | 26.6589 | 26.7573 | 24.5379 | 24.5418 | 24.5451 | 24.5495 | 24.5549 | 24.5614 | 24.5685 | 24.5732 | 24.5782 | 24.5833 | 24.5885 | 24.6243 | 24.686 | 24.5876 | 25.1997 | 25.2036 | 25.2069 | 25.2113 | 25.2167 | 25.2233 | 25.2303 | 25.235 | 25.24 | 25.2451 | 25.2503 | 25.2558 | 25.263 | 25.2704
|  | WATERLOO PLACE | LW |  |  |  | 1.3084 | 26.5109 | 26.5221 | 26.527 | 26.534 | 26.5418 | 26.5507 | 26.56 | 26.5675 | 26.5752 | 26.5832 | 26.5911 | 26.6425 | 26.7283 | 26.8983 | 24.5379 | 24.5267 | 24.5218 | 24.5148 | 24.507 | 24.4982 | 24.4888 | 24.4813 | 24.4736 | 24.4656 | 24.4577 | 24.4063 | 24.3205 | 24.1505 | 25.1997 | 25.2109 | 25.2159 | 25.2228 | 25.2307 | 25.2395 | 25.2489 | 25.2564 | 25.2641 | 25.272 | 25.2799 | 25.2878 | 25.2981 | 25.3088
|  | WATERLOO PLACE | ST |  |  |  | 1.3084 | 26.5109 | 26.5126 | 26.5134 | 26.5156 | 26.5182 | 26.5213 | 26.5248 | 26.5261 | 26.5274 | 26.5287 | 26.5299 | 26.5356 | 26.5664 | 26.5827 | 24.5379 | 24.5396 | 24.5404 | 24.5426 | 24.5453 | 24.5484 | 24.5519 | 24.5532 | 24.5545 | 24.5557 | 24.5569 | 24.5626 | 24.5934 | 24.6097 | 25.1997 | 25.2014 | 25.2022 | 25.2044 | 25.2071 | 25.2102 | 25.2137 | 25.215 | 25.2163 | 25.2175 | 25.2187 | 25.2244 | 25.2552 | 25.2716
|  | WATERLOO PLACE | FS |  |  |  | 1.3084 | 26.5109 | 26.5127 | 26.5128 | 26.5129 | 26.5131 | 26.5133 | 26.5135 | 26.5143 | 26.5152 | 26.5162 | 26.5173 | 26.5201 | 26.5355 | 26.5699 | 24.5379 | 24.5398 | 24.5399 | 24.54 | 24.5401 | 24.5403 | 24.5405 | 24.5413 | 24.5422 | 24.5432 | 24.5443 | 24.5472 | 24.5626 | 24.5969 | 25.1997 | 25.2016 | 25.2017 | 25.2018 | 25.2019 | 25.2021 | 25.2023 | 25.2031 | 25.204 | 25.205 | 25.2061 | 25.209 | 25.2244 | 25.2587
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 0.50526 | 25.2466 | 25.156 | 25.1142 | 25.056 | 24.9891 | 24.9157 | 24.8383 | 24.764 | 24.6855 | 24.6065 | 24.5287 | 23.7299 | 22.3334 | 20.3811 | 23.5893 | 23.4874 | 23.4368 | 23.3659 | 23.2869 | 23.2022 | 22.9771 | 22.692 | 22.4142 | 22.1429 | 21.8854 | 20.5824 | 19.0515 | 16.9675 | 24.2478 | 24.1443 | 24.0921 | 24.0188 | 23.9376 | 23.8508 | 23.7611 | 23.6869 | 23.5636 | 23.2913 | 23.033 | 22.7863 | 22.5223 | 22.2579
|  | WEST KIRKTON | CT |  |  |  | 0.50526 | 25.2466 | 25.2127 | 25.1838 | 25.1451 | 25.0982 | 25.0432 | 24.9842 | 24.945 | 24.9042 | 24.8631 | 24.8166 | 24.4949 | 23.971 | 22.7651 | 23.5893 | 23.5503 | 23.5155 | 23.4685 | 23.4131 | 23.3499 | 23.2836 | 23.2367 | 23.1885 | 23.0244 | 22.8469 | 21.9248 | 20.8692 | 19.5833 | 24.2483 | 24.2083 | 24.1725 | 24.1239 | 24.0669 | 24.0022 | 23.9346 | 23.8863 | 23.8367 | 23.7872 | 23.7377 | 23.6865 | 23.6244 | 23.4449
|  | WEST KIRKTON | LW |  |  |  | 0.50526 | 25.25 | 25.156 | 25.1142 | 25.056 | 24.9891 | 24.9157 | 24.8383 | 24.764 | 24.6855 | 24.6065 | 24.5287 | 23.7299 | 22.3334 | 20.3811 | 23.5894 | 23.4874 | 23.4368 | 23.3659 | 23.2869 | 23.2022 | 22.9771 | 22.692 | 22.4142 | 22.1429 | 21.8854 | 20.5824 | 19.0515 | 16.9675 | 24.2478 | 24.1443 | 24.0921 | 24.0188 | 23.9376 | 23.8508 | 23.7611 | 23.6869 | 23.5636 | 23.2913 | 23.033 | 22.7863 | 22.5223 | 22.2579
|  | WEST KIRKTON | ST |  |  |  | 0.50526 | 25.2508 | 25.2382 | 25.2322 | 25.216 | 25.1963 | 25.1731 | 25.1474 | 25.1377 | 25.128 | 25.1187 | 25.1098 | 25.0689 | 24.8487 | 24.7129 | 23.5989 | 23.5851 | 23.5777 | 23.5566 | 23.532 | 23.5039 | 23.4735 | 23.4588 | 23.444 | 23.4299 | 23.4162 | 23.3535 | 22.7836 | 22.3025 | 24.2588 | 24.2449 | 24.2373 | 24.2153 | 24.1896 | 24.1607 | 24.1295 | 24.1138 | 24.0981 | 24.083 | 24.0685 | 24.0018 | 23.7714 | 23.4512
|  | WEST KIRKTON | FS |  |  |  | 0.50526 | 25.2517 | 25.2393 | 25.2388 | 25.2381 | 25.2372 | 25.2358 | 25.2345 | 25.2292 | 25.2232 | 25.2167 | 25.2095 | 25.1906 | 25.0914 | 24.8667 | 23.6002 | 23.5869 | 23.5853 | 23.5833 | 23.5801 | 23.5752 | 23.5703 | 23.5611 | 23.551 | 23.5405 | 23.5294 | 23.4915 | 23.376 | 22.8734 | 24.2603 | 24.2468 | 24.245 | 24.2427 | 24.2391 | 24.2336 | 24.2281 | 24.2181 | 24.2073 | 24.196 | 24.1841 | 24.1428 | 24.0243 | 23.7882
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.10908 | 0.10815 | 0.10723 | 0.10629 | 0.10532 | 0.10434 | 0.10335 | 0.10241 | 0.10146 | 0.10052 | 0.099573 | 0.092178 | 0.082177 | 0.071525 | 0.10866 | 0.10772 | 0.1068 | 0.10584 | 0.10486 | 0.10386 | 0.10285 | 0.1019 | 0.10094 | 0.09998 | 0.099022 | 0.091562 | 0.082051 | 0.071129 | 0.10848 | 0.10755 | 0.10664 | 0.1057 | 0.10473 | 0.10375 | 0.10275 | 0.10181 | 0.10087 | 0.099925 | 0.09898 | 0.098032 | 0.097059 | 0.09524
|  | WESTER DRUMMOND | CT |  |  |  | 0 | 0.10908 | 0.10815 | 0.10723 | 0.10629 | 0.10532 | 0.10434 | 0.10335 | 0.10241 | 0.10146 | 0.10052 | 0.099573 | 0.092178 | 0.082177 | 0.071525 | 0.10866 | 0.10772 | 0.1068 | 0.10584 | 0.10486 | 0.10386 | 0.10285 | 0.1019 | 0.10094 | 0.09998 | 0.099022 | 0.091562 | 0.082051 | 0.071129 | 0.10848 | 0.10755 | 0.10664 | 0.1057 | 0.10473 | 0.10375 | 0.10275 | 0.10181 | 0.10087 | 0.099925 | 0.09898 | 0.098032 | 0.097059 | 0.09524
|  | WESTER DRUMMOND | LW |  |  |  | 0 | 0.11076 | 0.1105 | 0.11038 | 0.10938 | 0.10835 | 0.10731 | 0.10626 | 0.10525 | 0.10424 | 0.10323 | 0.10222 | 0.09621 | 0.089437 | 0.078811 | 0.11034 | 0.11007 | 0.10994 | 0.10891 | 0.10786 | 0.1068 | 0.10573 | 0.1047 | 0.10367 | 0.10264 | 0.10161 | 0.095989 | 0.088792 | 0.077736 | 0.11017 | 0.1099 | 0.10979 | 0.10878 | 0.10776 | 0.10671 | 0.10566 | 0.10466 | 0.10365 | 0.10264 | 0.10163 | 0.10063 | 0.099587 | 0.098539
|  | WESTER DRUMMOND | ST |  |  |  | 0 | 0.11076 | 0.11073 | 0.11071 | 0.11067 | 0.11062 | 0.11056 | 0.1105 | 0.11048 | 0.11045 | 0.11043 | 0.11041 | 0.11031 | 0.10982 | 0.10957 | 0.11035 | 0.11032 | 0.11031 | 0.11026 | 0.1102 | 0.11013 | 0.11005 | 0.11002 | 0.10999 | 0.10995 | 0.10992 | 0.10978 | 0.10926 | 0.10897 | 0.11017 | 0.11013 | 0.11012 | 0.11008 | 0.11003 | 0.10997 | 0.10991 | 0.10988 | 0.10986 | 0.10983 | 0.10981 | 0.10971 | 0.10923 | 0.10898
|  | WESTER DRUMMOND | FS |  |  |  | 0 | 0.1116 | 0.11157 | 0.11157 | 0.11157 | 0.11157 | 0.11156 | 0.11156 | 0.11155 | 0.11154 | 0.11152 | 0.1115 | 0.11146 | 0.11124 | 0.11076 | 0.1112 | 0.11117 | 0.11117 | 0.11116 | 0.11116 | 0.11115 | 0.11114 | 0.11112 | 0.1111 | 0.11108 | 0.11105 | 0.11097 | 0.11071 | 0.1102 | 0.11101 | 0.11098 | 0.11098 | 0.11098 | 0.11097 | 0.11097 | 0.11097 | 0.11096 | 0.11094 | 0.11093 | 0.11091 | 0.11087 | 0.11064 | 0.11016
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.0010526 | 1.2843 | 1.2785 | 1.2759 | 1.2723 | 1.2682 | 1.2592 | 1.2414 | 1.2235 | 1.2057 | 1.188 | 1.1705 | 1.0806 | 0.97493 | 0.83616 | 1.218 | 1.2049 | 1.1934 | 1.1745 | 1.1553 | 1.1363 | 1.1175 | 1.0983 | 1.0792 | 1.0603 | 1.0415 | 0.94572 | 0.83396 | 0.68912 | 1.21 | 1.2041 | 1.2016 | 1.198 | 1.1881 | 1.1687 | 1.1495 | 1.1299 | 1.1105 | 1.0911 | 1.0719 | 1.053 | 1.0331 | 1.013
|  | WESTRAY | CT |  |  |  | 0.0010526 | 1.2843 | 1.2823 | 1.2806 | 1.2782 | 1.2754 | 1.272 | 1.2684 | 1.2608 | 1.2487 | 1.2368 | 1.2249 | 1.1622 | 1.0893 | 1.0031 | 1.2206 | 1.2132 | 1.2056 | 1.1922 | 1.1785 | 1.1646 | 1.1508 | 1.1379 | 1.125 | 1.1122 | 1.0994 | 1.0326 | 0.95562 | 0.86528 | 1.21 | 1.2079 | 1.2062 | 1.2039 | 1.201 | 1.1976 | 1.1835 | 1.1703 | 1.1571 | 1.144 | 1.131 | 1.118 | 1.1044 | 1.0906
|  | WESTRAY | LW |  |  |  | 0.0010526 | 1.2843 | 1.2785 | 1.2759 | 1.2723 | 1.2682 | 1.2592 | 1.2414 | 1.2235 | 1.2057 | 1.188 | 1.1705 | 1.0806 | 0.97493 | 0.83616 | 1.218 | 1.2049 | 1.1934 | 1.1745 | 1.1553 | 1.1363 | 1.1175 | 1.0983 | 1.0792 | 1.0603 | 1.0415 | 0.94572 | 0.83396 | 0.68912 | 1.21 | 1.2041 | 1.2016 | 1.198 | 1.1881 | 1.1687 | 1.1495 | 1.1299 | 1.1105 | 1.0911 | 1.0719 | 1.053 | 1.0331 | 1.013
|  | WESTRAY | ST |  |  |  | 0.0010526 | 1.2843 | 1.2836 | 1.2832 | 1.2822 | 1.281 | 1.2796 | 1.278 | 1.2774 | 1.2768 | 1.2762 | 1.2757 | 1.2508 | 1.2091 | 1.1739 | 1.2286 | 1.2268 | 1.2254 | 1.2172 | 1.2088 | 1.2004 | 1.1921 | 1.1843 | 1.1767 | 1.1692 | 1.1619 | 1.1264 | 1.0821 | 1.0444 | 1.21 | 1.2092 | 1.2088 | 1.2078 | 1.2066 | 1.2052 | 1.2036 | 1.203 | 1.2024 | 1.2019 | 1.1946 | 1.1583 | 1.1131 | 1.0746
|  | WESTRAY | FS |  |  |  | 0.0010526 | 1.2843 | 1.2836 | 1.2836 | 1.2835 | 1.2835 | 1.2834 | 1.2833 | 1.283 | 1.2826 | 1.2823 | 1.2818 | 1.2807 | 1.2546 | 1.219 | 1.2289 | 1.228 | 1.227 | 1.2257 | 1.2236 | 1.2185 | 1.2133 | 1.2075 | 1.2017 | 1.1958 | 1.19 | 1.162 | 1.1304 | 1.0927 | 1.21 | 1.2092 | 1.2092 | 1.2092 | 1.2091 | 1.209 | 1.2089 | 1.2086 | 1.2083 | 1.2079 | 1.2075 | 1.1946 | 1.1623 | 1.124
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.5768 | 11.5897 | 11.5581 | 11.5229 | 11.3565 | 11.1918 | 11.0313 | 10.8788 | 10.7267 | 10.5787 | 10.4338 | 10.2955 | 9.6034 | 8.8162 | 7.7723 | 10.3526 | 10.2057 | 10.073 | 9.8837 | 9.6972 | 9.5162 | 9.345 | 9.1729 | 9.0056 | 8.8422 | 8.6864 | 7.9143 | 7.0509 | 5.9339 | 10.7601 | 10.6202 | 10.4953 | 10.3172 | 10.1414 | 9.9705 | 9.8085 | 9.6463 | 9.4885 | 9.3342 | 9.187 | 9.0467 | 8.8988 | 8.7514
|  | WHITEHOUSE | CT |  |  |  | 2.5768 | 11.5897 | 11.5616 | 11.5361 | 11.5018 | 11.3793 | 11.2558 | 11.1396 | 11.0294 | 10.921 | 10.8157 | 10.7136 | 10.1895 | 9.6046 | 8.9171 | 10.3715 | 10.2817 | 10.1864 | 10.0529 | 9.9151 | 9.7767 | 9.6471 | 9.523 | 9.4011 | 9.2831 | 9.1687 | 8.5873 | 7.9493 | 7.2113 | 10.7762 | 10.6909 | 10.6007 | 10.4747 | 10.3444 | 10.2134 | 10.0904 | 9.9731 | 9.8578 | 9.746 | 9.6377 | 9.5305 | 9.4184 | 9.3075
|  | WHITEHOUSE | LW |  |  |  | 2.5768 | 11.6099 | 11.5581 | 11.5229 | 11.3565 | 11.1918 | 11.0313 | 10.8788 | 10.7267 | 10.5787 | 10.4338 | 10.2955 | 9.6034 | 8.8162 | 7.7723 | 10.3526 | 10.2057 | 10.073 | 9.8837 | 9.6972 | 9.5162 | 9.345 | 9.1729 | 9.0056 | 8.8422 | 8.6864 | 7.9143 | 7.0509 | 5.9339 | 10.7601 | 10.6202 | 10.4953 | 10.3172 | 10.1414 | 9.9705 | 9.8085 | 9.6463 | 9.4885 | 9.3342 | 9.187 | 9.0467 | 8.8988 | 8.7514
|  | WHITEHOUSE | ST |  |  |  | 2.5768 | 11.6141 | 11.6056 | 11.6002 | 11.5899 | 11.5771 | 11.5627 | 11.547 | 11.5095 | 11.4489 | 11.3902 | 11.3334 | 11.0701 | 10.7627 | 10.5085 | 10.4613 | 10.4382 | 10.4165 | 10.3459 | 10.2724 | 10.1977 | 10.1258 | 10.0561 | 9.9864 | 9.9189 | 9.8534 | 9.5506 | 9.2088 | 8.9223 | 10.8612 | 10.8391 | 10.8187 | 10.7524 | 10.6834 | 10.6131 | 10.5453 | 10.4801 | 10.4149 | 10.3517 | 10.2905 | 10.0071 | 9.6822 | 9.4116
|  | WHITEHOUSE | FS |  |  |  | 2.5768 | 11.6166 | 11.6095 | 11.6067 | 11.6039 | 11.6009 | 11.5986 | 11.5964 | 11.5923 | 11.588 | 11.5834 | 11.5462 | 11.3344 | 11.1166 | 10.8595 | 10.4717 | 10.4532 | 10.437 | 10.4181 | 10.3884 | 10.3446 | 10.3011 | 10.2503 | 10.1975 | 10.1446 | 10.0924 | 9.8472 | 9.6012 | 9.3179 | 10.871 | 10.8534 | 10.8381 | 10.8204 | 10.7927 | 10.7519 | 10.7114 | 10.664 | 10.6148 | 10.5653 | 10.5166 | 10.2878 | 10.0557 | 9.7853
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | YES | 0.66316 | 17.0776 | 15.5242 | 13.7307 | 11.7666 | 9.9529 | 8.2868 | 6.8854 | 5.4128 | 4.0611 | 2.8132 | 1.7849 | -2.3745 | -5.6841 | -9.045 | 15.0806 | 13.0098 | 10.89 | 8.5936 | 6.4751 | 4.5308 | 2.898 | 1.1791 | -0.39781 | -1.8527 | -3.0499 | -7.8715 | -11.6605 | -15.4236 | 15.8969 | 13.8123 | 11.6917 | 9.3946 | 7.2755 | 5.3305 | 3.6972 | 1.9778 | 0.40038 | -1.055 | -2.2525 | -3.262 | -4.2614 | -5.2274
|  | WHITESTRIPES | CT |  |  |  | 0.66316 | 17.0983 | 17.0342 | 16.0431 | 14.9019 | 13.6305 | 12.3138 | 11.2889 | 10.2785 | 9.3111 | 8.4739 | 7.7395 | 4.5215 | 2.1312 | -0.22554 | 15.9735 | 14.948 | 13.6585 | 12.2604 | 10.7755 | 9.2385 | 8.0448 | 6.8651 | 5.7359 | 4.7596 | 3.9042 | 0.16958 | -2.5685 | -5.2316 | 16.4237 | 15.7631 | 14.4611 | 13.0626 | 11.5772 | 10.0398 | 8.8457 | 7.6656 | 6.5361 | 5.5595 | 4.7038 | 3.8503 | 3.0471 | 2.3187
|  | WHITESTRIPES | LW |  |  |  | 0.66316 | 17.0776 | 15.5242 | 13.7307 | 11.7666 | 9.9529 | 8.2868 | 6.8854 | 5.4128 | 4.0611 | 2.8132 | 1.7849 | -2.3745 | -5.6841 | -9.045 | 15.0806 | 13.0098 | 10.89 | 8.5936 | 6.4751 | 4.5308 | 2.898 | 1.1791 | -0.39781 | -1.8527 | -3.0499 | -7.8715 | -11.6605 | -15.4236 | 15.8969 | 13.8123 | 11.6917 | 9.3946 | 7.2755 | 5.3305 | 3.6972 | 1.9778 | 0.40038 | -1.055 | -2.2525 | -3.262 | -4.2614 | -5.2274
|  | WHITESTRIPES | ST |  |  |  | 0.66316 | 17.1034 | 17.0913 | 17.0851 | 17.0481 | 16.6429 | 16.052 | 15.5277 | 14.9359 | 14.2972 | 13.6998 | 13.1393 | 10.6758 | 8.8721 | 7.3378 | 16.0047 | 15.9734 | 15.7223 | 15.0944 | 14.4059 | 13.6718 | 13.0165 | 12.3012 | 11.5529 | 10.8532 | 10.1966 | 7.3114 | 5.2255 | 3.4409 | 16.4287 | 16.4166 | 16.4104 | 15.9112 | 15.2148 | 14.4745 | 13.819 | 13.1034 | 12.3549 | 11.6549 | 10.9981 | 8.112 | 6.0255 | 4.2403
|  | WHITESTRIPES | FS |  |  |  | 0.66316 | 17.1042 | 17.0936 | 17.0923 | 17.0909 | 17.0714 | 16.8565 | 16.4658 | 16.0287 | 15.5551 | 15.0799 | 14.6032 | 12.5013 | 11.0422 | 9.5717 | 16.0133 | 15.9866 | 15.9681 | 15.6626 | 15.1678 | 14.6635 | 14.1766 | 13.6294 | 13.0333 | 12.4579 | 11.8994 | 9.4352 | 7.7376 | 6.0438 | 16.4296 | 16.419 | 16.4176 | 16.4162 | 15.9853 | 15.475 | 14.9823 | 14.432 | 13.8358 | 13.2601 | 12.7015 | 10.2365 | 8.5383 | 6.8441
| CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0 | 8.5113 | 8.4913 | 8.4825 | 8.4701 | 8.454 | 8.4068 | 8.36 | 8.3145 | 8.2695 | 8.2248 | 8.181 | 7.9517 | 7.6795 | 7.3043 | 8.3596 | 8.3388 | 8.3289 | 8.3148 | 8.299 | 8.2821 | 8.2645 | 8.2418 | 8.1947 | 8.1479 | 8.102 | 7.8482 | 7.5493 | 7.148 | 8.3276 | 8.3077 | 8.2988 | 8.2522 | 8.1984 | 8.1453 | 8.093 | 8.0416 | 7.9908 | 7.9404 | 7.8909 | 7.8422 | 7.7909 | 7.7391
|  | WHITING BAY | CT |  |  |  | 0 | 8.5113 | 8.5046 | 8.4989 | 8.4912 | 8.4818 | 8.4709 | 8.4481 | 8.4172 | 8.3864 | 8.356 | 8.326 | 8.1677 | 7.9797 | 7.7528 | 8.3598 | 8.3525 | 8.3461 | 8.3372 | 8.3265 | 8.3144 | 8.3016 | 8.2927 | 8.2837 | 8.2746 | 8.253 | 8.0877 | 7.8813 | 7.6362 | 8.3276 | 8.3209 | 8.3153 | 8.3026 | 8.2654 | 8.228 | 8.1908 | 8.1557 | 8.1208 | 8.0864 | 8.0524 | 8.0185 | 7.9827 | 7.9467
|  | WHITING BAY | LW |  |  |  | 0 | 8.5113 | 8.4913 | 8.4825 | 8.4701 | 8.454 | 8.4068 | 8.36 | 8.3145 | 8.2695 | 8.2248 | 8.181 | 7.9517 | 7.6795 | 7.3043 | 8.3596 | 8.3388 | 8.3289 | 8.3148 | 8.299 | 8.2821 | 8.2645 | 8.2418 | 8.1947 | 8.1479 | 8.102 | 7.8482 | 7.5493 | 7.148 | 8.3276 | 8.3077 | 8.2988 | 8.2522 | 8.1984 | 8.1453 | 8.093 | 8.0416 | 7.9908 | 7.9404 | 7.8909 | 7.8422 | 7.7909 | 7.7391
|  | WHITING BAY | ST |  |  |  | 0 | 8.5113 | 8.5088 | 8.5077 | 8.5045 | 8.5006 | 8.4961 | 8.4911 | 8.4892 | 8.4873 | 8.4855 | 8.4836 | 8.4076 | 8.3051 | 8.2242 | 8.3608 | 8.3582 | 8.357 | 8.353 | 8.3483 | 8.343 | 8.3372 | 8.3345 | 8.3318 | 8.3292 | 8.3267 | 8.3154 | 8.2301 | 8.1452 | 8.3276 | 8.3252 | 8.324 | 8.3208 | 8.317 | 8.3125 | 8.3064 | 8.2862 | 8.2664 | 8.2471 | 8.2283 | 8.1401 | 8.0259 | 7.934
|  | WHITING BAY | FS |  |  |  | 0 | 8.5113 | 8.5091 | 8.509 | 8.5089 | 8.5087 | 8.5085 | 8.5082 | 8.5073 | 8.5062 | 8.505 | 8.5038 | 8.4923 | 8.4209 | 8.3322 | 8.3609 | 8.3587 | 8.3585 | 8.3583 | 8.3578 | 8.3571 | 8.3563 | 8.3547 | 8.3531 | 8.3513 | 8.3494 | 8.343 | 8.3227 | 8.2586 | 8.3276 | 8.3254 | 8.3253 | 8.3252 | 8.325 | 8.3248 | 8.3246 | 8.3236 | 8.3226 | 8.3214 | 8.3073 | 8.2356 | 8.1544 | 8.0566
| MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 0.012632 | 17.7824 | 17.7285 | 17.6794 | 17.6225 | 17.5588 | 17.4896 | 17.4172 | 17.3591 | 17.2998 | 17.2395 | 17.1739 | 16.3688 | 15.0773 | 13.3109 | 16.8394 | 16.7854 | 16.7364 | 16.6794 | 16.6157 | 16.5465 | 16.4741 | 16.4161 | 16.3568 | 16.2964 | 16.2309 | 15.0993 | 13.6992 | 11.8244 | 17.1762 | 17.1222 | 17.0732 | 17.0162 | 16.9525 | 16.8833 | 16.8109 | 16.7529 | 16.6936 | 16.6332 | 16.5677 | 16.5013 | 16.4221 | 16.2963
|  | WICK | CT |  |  |  | 0.012632 | 17.7824 | 17.7285 | 17.6794 | 17.6225 | 17.5588 | 17.4896 | 17.4172 | 17.3591 | 17.2998 | 17.2395 | 17.1788 | 16.8098 | 15.9929 | 14.7824 | 16.8394 | 16.7854 | 16.7364 | 16.6794 | 16.6157 | 16.5465 | 16.4741 | 16.4161 | 16.3568 | 16.2964 | 16.2357 | 15.8166 | 14.7414 | 13.4565 | 17.1762 | 17.1222 | 17.0732 | 17.0162 | 16.9525 | 16.8833 | 16.8109 | 16.7529 | 16.6936 | 16.6332 | 16.5725 | 16.5105 | 16.4382 | 16.3627
|  | WICK | LW |  |  |  | 0.012632 | 17.8304 | 17.7465 | 17.7037 | 17.646 | 17.5812 | 17.5105 | 17.4349 | 17.3715 | 17.3065 | 17.2398 | 17.1739 | 16.3688 | 15.0773 | 13.3109 | 16.8874 | 16.8035 | 16.7607 | 16.703 | 16.6382 | 16.5675 | 16.4918 | 16.4285 | 16.3635 | 16.2967 | 16.2309 | 15.0993 | 13.6992 | 11.8244 | 17.2242 | 17.1403 | 17.0975 | 17.0398 | 16.975 | 16.9043 | 16.8286 | 16.7653 | 16.7003 | 16.6335 | 16.5677 | 16.5013 | 16.4221 | 16.2963
|  | WICK | ST |  |  |  | 0.012632 | 17.8397 | 17.8229 | 17.8113 | 17.7916 | 17.7683 | 17.7422 | 17.714 | 17.6987 | 17.6834 | 17.6683 | 17.6545 | 17.585 | 17.3846 | 17.2547 | 16.8966 | 16.8798 | 16.8683 | 16.8486 | 16.8252 | 16.7992 | 16.771 | 16.7557 | 16.7403 | 16.7253 | 16.7115 | 16.6419 | 16.4416 | 16.2766 | 17.2334 | 17.2166 | 17.2051 | 17.1854 | 17.162 | 17.136 | 17.1078 | 17.0925 | 17.0771 | 17.0621 | 17.0483 | 16.9787 | 16.7784 | 16.6485
|  | WICK | FS |  |  |  | 0.012632 | 17.8447 | 17.8317 | 17.8263 | 17.8207 | 17.8149 | 17.8088 | 17.8027 | 17.7935 | 17.7846 | 17.7753 | 17.7655 | 17.723 | 17.6206 | 17.4263 | 16.9017 | 16.8887 | 16.8832 | 16.8777 | 16.8718 | 16.8657 | 16.8596 | 16.8504 | 16.8416 | 16.8323 | 16.8225 | 16.7799 | 16.6775 | 16.4832 | 17.2385 | 17.2255 | 17.22 | 17.2145 | 17.2086 | 17.2025 | 17.1964 | 17.1872 | 17.1784 | 17.1691 | 17.1593 | 17.1167 | 17.0143 | 16.82
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 0.10211 | 26.0928 | 25.9855 | 25.9371 | 25.8696 | 25.7922 | 25.7061 | 25.6148 | 25.5423 | 25.4676 | 25.391 | 25.3153 | 24.8286 | 24.032 | 22.1819 | 24.5706 | 24.4633 | 24.4149 | 24.3474 | 24.27 | 24.1839 | 24.0926 | 24.0201 | 23.9454 | 23.8688 | 23.7931 | 23.3064 | 21.4938 | 18.6381 | 25.2385 | 25.1311 | 25.0827 | 25.0152 | 24.9378 | 24.8517 | 24.7604 | 24.5239 | 24.1532 | 23.7921 | 23.454 | 21.745 | 19.7603 | 17.0118
|  | WOODHILL | CT |  |  |  | 0.10211 | 26.0928 | 26.0546 | 26.022 | 25.9782 | 25.9248 | 25.8612 | 25.7923 | 25.7466 | 25.6984 | 25.6494 | 25.5995 | 25.2626 | 24.6902 | 23.7895 | 24.5706 | 24.5324 | 24.4998 | 24.456 | 24.4026 | 24.339 | 24.2701 | 24.2244 | 24.1762 | 24.1272 | 24.0773 | 23.7404 | 23.168 | 22.2305 | 25.2385 | 25.2002 | 25.1677 | 25.1239 | 25.0704 | 25.0068 | 24.9379 | 24.8923 | 24.844 | 24.795 | 24.7451 | 23.5507 | 22.1464 | 20.4158
|  | WOODHILL | LW |  |  |  | 0.10211 | 26.0945 | 25.9855 | 25.9371 | 25.8696 | 25.7922 | 25.7061 | 25.6148 | 25.5423 | 25.4676 | 25.391 | 25.3153 | 24.8286 | 24.032 | 22.1819 | 24.5723 | 24.4633 | 24.4149 | 24.3474 | 24.27 | 24.1839 | 24.0926 | 24.0201 | 23.9454 | 23.8688 | 23.7931 | 23.3064 | 21.4938 | 18.6381 | 25.2402 | 25.1311 | 25.0827 | 25.0152 | 24.9378 | 24.8517 | 24.7604 | 24.5239 | 24.1532 | 23.7921 | 23.454 | 21.745 | 19.7603 | 17.0118
|  | WOODHILL | ST |  |  |  | 0.10211 | 26.0945 | 26.0787 | 26.0711 | 26.0508 | 26.026 | 25.9969 | 25.9645 | 25.9524 | 25.9402 | 25.9285 | 25.9173 | 25.8649 | 25.5858 | 25.439 | 24.5723 | 24.5565 | 24.5489 | 24.5286 | 24.5038 | 24.4747 | 24.4423 | 24.4302 | 24.418 | 24.4063 | 24.3951 | 24.3427 | 24.0636 | 23.9168 | 25.2402 | 25.2243 | 25.2168 | 25.1964 | 25.1716 | 25.1426 | 25.1102 | 25.098 | 25.0858 | 25.0741 | 25.0629 | 25.0105 | 24.6233 | 23.9449
|  | WOODHILL | FS |  |  |  | 0.10211 | 26.0954 | 26.0784 | 26.0777 | 26.0768 | 26.0754 | 26.0735 | 26.0717 | 26.0644 | 26.0562 | 26.0472 | 26.0374 | 26.0114 | 25.8728 | 25.5651 | 24.5732 | 24.5562 | 24.5555 | 24.5546 | 24.5532 | 24.5513 | 24.5495 | 24.5422 | 24.534 | 24.525 | 24.5152 | 24.4892 | 24.3506 | 24.0429 | 25.241 | 25.224 | 25.2233 | 25.2224 | 25.221 | 25.2192 | 25.2173 | 25.2101 | 25.2019 | 25.1928 | 25.183 | 25.157 | 25.0184 | 24.6775

## Local Authority Reference
Local Authority | Grid Supply Point | Primary Substation
Aberdeen City | CLAYHILLS | BALNAGASK
Aberdeen City | CLAYHILLS | CLAYHILLS
Aberdeen City | CLAYHILLS | COMMERCE STREET
Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
Aberdeen City | CRAIGIEBUCKLER | CULTER
Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeen City | DYCE | DYCE NORTH
Aberdeen City | DYCE | HARVEST AVENUE
Aberdeen City | KINTORE | PARK
Aberdeen City | KINTORE | SKENE
Aberdeen City | KINTORE | TORRYBURN
Aberdeen City | PERSLEY | BRIDGE OF DON
Aberdeen City | PERSLEY | HAUDAGAIN
Aberdeen City | PERSLEY | NORTHFIELD
Aberdeen City | PERSLEY | ST MACHAR
Aberdeen City | PERSLEY | STONEYWOOD T1&T2
Aberdeen City | PERSLEY | STONEYWOOD T3
Aberdeen City | PERSLEY | WHITESTRIPES
Aberdeen City | REDMOSS | KINCORTH
Aberdeen City | REDMOSS | REDMOSS
Aberdeen City | WILLOWDALE | DENBURN
Aberdeen City | WILLOWDALE | GREYFRIARS
Aberdeen City | WILLOWDALE | HAYTON
Aberdeen City | WILLOWDALE | ST NICHOLAS
Aberdeen City | WOODHILL | QUEENS LANE NORTH
Aberdeen City | WOODHILL | SPRINGHILL
Aberdeen City | WOODHILL | WOODHILL
Aberdeenshire | BOAT OF GARTEN | AVIEMORE
Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
Aberdeenshire | BRIDGE OF DUN | INCHBARE
Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
Aberdeenshire | BRIDGE OF DUN | ST CYRUS
Aberdeenshire | COUPAR ANGUS | DALRULZION
Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
Aberdeenshire | CRAIGIEBUCKLER | CULTER
Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeenshire | DYCE | BALMEDIE
Aberdeenshire | DYCE | DYCE NORTH
Aberdeenshire | DYCE | ELLON 11 kV
Aberdeenshire | DYCE | KINGSEAT
Aberdeenshire | FIDDES | EDZELL
Aberdeenshire | FIDDES | INVERBERVIE
Aberdeenshire | FIDDES | LAURENCEKIRK
Aberdeenshire | FIDDES | STONEHAVEN
Aberdeenshire | FRASERBURGH | FRASERBURGH
Aberdeenshire | KEITH | CULLEN
Aberdeenshire | KEITH | DUFFTOWN
Aberdeenshire | KEITH | HUNTLY
Aberdeenshire | KEITH | INSCH
Aberdeenshire | KEITH | KEITH
Aberdeenshire | KEITH | LIMEHILLOCKS
Aberdeenshire | KEITH | MARNOCH
Aberdeenshire | KINTORE | BANCHORY
Aberdeenshire | KINTORE | FYVIE
Aberdeenshire | KINTORE | INVERURIE
Aberdeenshire | KINTORE | KEMNAY
Aberdeenshire | KINTORE | METHLICK
Aberdeenshire | KINTORE | MIDMAR
Aberdeenshire | KINTORE | OLDMELDRUM
Aberdeenshire | KINTORE | PARK
Aberdeenshire | KINTORE | SKENE
Aberdeenshire | KINTORE | TORRYBURN
Aberdeenshire | LUNANHEAD | MARYTON
Aberdeenshire | MACDUFF | MACDUFF
Aberdeenshire | MACDUFF | PORTSOY
Aberdeenshire | MACDUFF | TURRIFF
Aberdeenshire | PERSLEY | BRIDGE OF DON
Aberdeenshire | PERSLEY | WHITESTRIPES
Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE 11kV
Aberdeenshire | PETERHEAD GRANGE | PHEAD NORTH ST
Aberdeenshire | PETERHEAD SHELL | BODDAM
Aberdeen City | REDMOSS | CRAIGINCHES
Aberdeenshire | REDMOSS | KINCORTH
Aberdeenshire | REDMOSS | NEWTONHILL
Aberdeenshire | REDMOSS | REDMOSS
Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
Aberdeenshire | STRICHEN | HATTON
Aberdeenshire | STRICHEN | MAUD
Aberdeenshire | STRICHEN | MINTLAW
Aberdeenshire | STRICHEN | NEW PITSLIGO
Aberdeenshire | STRICHEN | STONEYHILL
Aberdeenshire | STRICHEN | STRICHEN
Aberdeenshire | TARLAND | ABOYNE
Aberdeenshire | TARLAND | BALLATER
Aberdeenshire | TARLAND | MOSSAT
Aberdeenshire | TARLAND | STRATHDON
Aberdeenshire | TARLAND | WHITEHOUSE
Aberdeenshire | TUMMEL BRIDGE | BONSKEID
Aberdeenshire | WOODHILL | SPRINGHILL
Angus | ABERNETHY | BALBEGGIE
Angus | ARBROATH | CARNOUSTIE
Angus | ARBROATH | CHARLES AVENUE
Angus | ARBROATH | ELLIOT DEPOT
Angus | ARBROATH | HUME STREET
Angus | ARBROATH | REDFORD
Angus | BRIDGE OF DUN | BRECHIN
Angus | BRIDGE OF DUN | BRIDGE OF DUN 11kV
Angus | BRIDGE OF DUN | INCHBARE
Angus | BRIDGE OF DUN | LOGIE PERT
Angus | BRIDGE OF DUN | MILL RD MONTROSE
Angus | BRIDGE OF DUN | MONTROSE NORTH
Angus | BRIDGE OF DUN | ST CYRUS
Angus | CHARLESTON | GOURDIE
Angus | COUPAR ANGUS | ALYTH
Angus | COUPAR ANGUS | COUPAR ANGUS
Angus | COUPAR ANGUS | DALRULZION
Angus | COUPAR ANGUS | LEOCH
Angus | FIDDES | EDZELL
Angus | FIDDES | LAURENCEKIRK
Angus | KINTORE | BANCHORY
Angus | LUNANHEAD | FRIOCKHEIM
Angus | LUNANHEAD | INVERARITY
Angus | LUNANHEAD | LOCHSIDE
Angus | LUNANHEAD | LUNANHEAD
Angus | LUNANHEAD | MARYTON
Angus | LYNDHURST | MACALPINE ROAD
Angus | LYNDHURST | WEST KIRKTON
Angus | MILTON OF CRAIGIE | ASHLUDIE
Angus | MILTON OF CRAIGIE | BALDOVIE
Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
Angus | MILTON OF CRAIGIE | EDZELL STREET
Angus | MILTON OF CRAIGIE | LONGHAUGH
Angus | TARLAND | BALLATER
Argyll and Bute | CARRADALE | BALLURE
Argyll and Bute | CARRADALE | CAMPBELTOWN
Argyll and Bute | CARRADALE | CLAONAIG
Argyll and Bute | CARRADALE | DIPPEN
Argyll and Bute | CARRADALE | WESTPARK FERGUS
Argyll and Bute | CLACHAN | BUTTERBRIDGE
Argyll and Bute | CLACHAN | DOUGLAS PIER
Argyll and Bute | CLACHAN | INVERARAY
Argyll and Bute | CLACHAN | LOCHGOILHEAD
Argyll and Bute | CLACHAN | STRACHUR
Argyll and Bute | DUNOON | BRUCHAG
Argyll and Bute | DUNOON | COLINTRAIVE
Argyll and Bute | DUNOON | DUNOON
Argyll and Bute | DUNOON | GLENDARUEL
Argyll and Bute | DUNOON | INNELLAN
Argyll and Bute | DUNOON | KAMES
Argyll and Bute | DUNOON | NEWTON
Argyll and Bute | DUNOON | OTTER FERRY
Argyll and Bute | DUNOON | ROTHESAY
Argyll and Bute | DUNOON | SANDBANK
Argyll and Bute | FORT WILLIAM | SALEN 2
Argyll and Bute | KILLIN | CASHLIE
Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
Argyll and Bute | PORT ANN | BOWMORE
Argyll and Bute | PORT ANN | CRINAN
Argyll and Bute | PORT ANN | CROMALT
Argyll and Bute | PORT ANN | INVERNEIL
Argyll and Bute | PORT ANN | LOCHGILPHEAD
Argyll and Bute | PORT ANN | LUSSAGIVEN
Argyll and Bute | PORT ANN | PORT ASKAIG
Argyll and Bute | PORT ANN | PORT ELLEN
Argyll and Bute | PORT ANN | STONEFIELD
Argyll and Bute | PORT ANN | TARBERT JURA
Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
Argyll and Bute | RANNOCH | BLACKMOUNT
Argyll and Bute | RANNOCH | GLENETIVE
Argyll and Bute | RANNOCH | TYNDRUM
Argyll and Bute | STRATHLEVEN | DRYMEN
Argyll and Bute | TAYNUILT | BARCALDINE
Argyll and Bute | TAYNUILT | CONNEL
Argyll and Bute | TAYNUILT | DALMALLY
Argyll and Bute | TAYNUILT | DERVAIG
Argyll and Bute | TAYNUILT | EREDINE
Argyll and Bute | TAYNUILT | KENMORE
Argyll and Bute | TAYNUILT | KERRERA
Argyll and Bute | TAYNUILT | KILCHRENAN
Argyll and Bute | TAYNUILT | KILMELFORD PS
Argyll and Bute | TAYNUILT | KILNINVER
Argyll and Bute | TAYNUILT | KINLOCH
Argyll and Bute | TAYNUILT | LOCHDONHEAD
Argyll and Bute | TAYNUILT | OBAN
Argyll and Bute | TAYNUILT | SCAMMADALE
Argyll and Bute | TAYNUILT | TAYNUILT
Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
Clackmannanshire | ABERNETHY | GLENDEVON
Clackmannanshire | ABERNETHY | MILNATHORT
Clackmannanshire | BRACO | GLENEAGLES
Dundee City | CHARLESTON | CHARLESTON
Dundee City | CHARLESTON | GOURDIE
Dundee City | CHARLESTON | MENZIESHILL
Dundee City | CHARLESTON | NINEWELLS
Dundee City | COUPAR ANGUS | LEOCH
Dundee City | DUDHOPE | CONSTABLE STREET
Dundee City | DUDHOPE | ROSEBANK STREET
Dundee City | GLENAGNES | OVERGATE
Dundee City | GLENAGNES | WALTON
Dundee City | LYNDHURST | LOCHEE
Dundee City | LYNDHURST | LYNDHURST
Dundee City | LYNDHURST | MACALPINE ROAD
Dundee City | LYNDHURST | WEST KIRKTON
Dundee City | MILTON OF CRAIGIE | ASHLUDIE
Dundee City | MILTON OF CRAIGIE | BALDOVIE
Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
Dundee City | MILTON OF CRAIGIE | EDZELL STREET
Dundee City | MILTON OF CRAIGIE | LONGHAUGH
Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
East Dunbartonshire | BRACO | KIPPEN
East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
East Dunbartonshire | STRATHLEVEN | KILLEARN
Eilean Siar | ARDMORE | AIRD
Eilean Siar | ARDMORE | CLACHAN
Eilean Siar | ARDMORE | DRIMORE
Eilean Siar | ARDMORE | HARRIS GRID
Eilean Siar | ARDMORE | LOCH CARNAN
Eilean Siar | ARDMORE | POLLACHAR
Eilean Siar | ARDMORE / HARRIS GRID | STOCKINISH
Eilean Siar | ARDMORE / HARRIS GRID | TARBERT
Eilean Siar | STORNOWAY | ARNISH
Eilean Siar | STORNOWAY | BARVAS
Eilean Siar | STORNOWAY | BATTERY POINT
Eilean Siar | STORNOWAY | CALLANISH
Eilean Siar | STORNOWAY | COLL
Eilean Siar | STORNOWAY | GISLA
Eilean Siar | STORNOWAY | LAXAY
Eilean Siar | STORNOWAY | MAARUIG
Fife | ABERNETHY | ABERNETHY
Fife | ABERNETHY | BRIDGE OF EARN
Fife | ABERNETHY | GLENDEVON
Fife | ABERNETHY | MILNATHORT
Highland | ALNESS | BALALDIE
Highland | ALNESS | CONTULLICH
Highland | ALNESS | CROSSHILLS
Highland | ALNESS | GLASTULLICH
Highland | ALNESS | INVERGORDON
Highland | ALNESS | NIGG
Highland | ALNESS | PEDDIESTON
Highland | ALNESS | TAIN
Highland | BEAULY | AIGAS
Highland | BEAULY | BLACKSTAND
Highland | BEAULY | CONON BRIDGE
Highland | BEAULY | DINGWALL
Highland | BEAULY | KILTARLITY
Highland | BEAULY | MARYBANK
Highland | BEAULY | MUIR OF ORD
Highland | BEAULY | MUIREND
Highland | BOAT OF GARTEN | AVIEMORE
Highland | BOAT OF GARTEN | BALLINDALLOCH
Highland | BOAT OF GARTEN | BOAT OF GARTEN 11 kV
Highland | BOAT OF GARTEN | DALWHINNIE
Highland | BOAT OF GARTEN | GRANTOWN
Highland | BOAT OF GARTEN | KINGUSSIE
Highland | BOAT OF GARTEN | TOMATIN
Highland | BROADFORD | ACHINTEE
Highland | BROADFORD | BROADFORD
Highland | BROADFORD | KALNAKIL
Highland | BROADFORD | KISHORNHILL
Highland | BROADFORD | KYLE
Highland | BROADFORD | LOWER OLLACH
Highland | BROADFORD | NOSTIE BRIDGE
Highland | BROADFORD | SHIELDAIG
Highland | BROADFORD | SKULAMUS
Highland | BRORA | DORNOCH
Highland | BRORA | GOLSPIE
Highland | BRORA | HELMSDALE
Highland | CASSLEY | OVERSCAIG
Highland | CASSLEY | RHICONICH
Highland | CEANNACROC | DRUMNADROCHIT
Highland | DOUNREAY | BETTYHILL
Highland | DOUNREAY | COLDBACKIE
Highland | DOUNREAY | DOUNREAY
Highland | DOUNREAY | FORSS
Highland | DUNOON | DUNOON
Highland | DUNVEGAN | DRYNOCH
Highland | DUNVEGAN | DUNVEGAN GRID
Highland | DUNVEGAN | PORTREE
Highland | DUNVEGAN | UIG
Highland | FORT AUGUSTUS | ABERCHALDER
Highland | FORT AUGUSTUS | ARDOCHY
Highland | FORT AUGUSTUS | BUNOICH
Highland | FORT AUGUSTUS | GLEN LAOGH
Highland | FORT AUGUSTUS | GLENDOE PRIMARY
Highland | FORT AUGUSTUS | INVERGARRY
Highland | FORT WILLIAM | ANNAT
Highland | FORT WILLIAM | ARISAIG
Highland | FORT WILLIAM | CORRAN
Highland | FORT WILLIAM | FISHNISH
Highland | FORT WILLIAM | GLENUIG
Highland | FORT WILLIAM | INVERLOCHY
Highland | FORT WILLIAM | KINGAIRLOCH
Highland | FORT WILLIAM | KINLOCHMOIDART
Highland | FORT WILLIAM | LIDDESDALE
Highland | FORT WILLIAM | LOCHALINE
Highland | FORT WILLIAM | MALLAIG
Highland | FORT WILLIAM | PINEGROVE
Highland | FORT WILLIAM | POOR HOUSE
Highland | FORT WILLIAM | RAHOY
Highland | FORT WILLIAM | SHONA BEAG
Highland | FORT WILLIAM | STRONTIAN
Highland | GRUDIE BRIDGE | ACHILTIBUIE
Highland | GRUDIE BRIDGE | AULTBEA
Highland | GRUDIE BRIDGE | BIDEN CLAN RAONAILD
Highland | BEAULY | CONON FALLS
Highland | GRUDIE BRIDGE | DRUMRUNIE
Highland | GRUDIE BRIDGE | GARBAT FOREST
Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
Highland | GRUDIE BRIDGE | INVERBROOM
Highland | GRUDIE BRIDGE | KERRY FALLS
Highland | GRUDIE BRIDGE | KINLOCHEWE
Highland | GRUDIE BRIDGE | LETTEREWE
Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
Highland | GRUDIE BRIDGE | LOCHINVER
Highland | GRUDIE BRIDGE | ULLAPOOL
Highland | INVERNESS | CULLODEN
Highland | INVERNESS | DALNEIGH
Highland | INVERNESS | ERROGIE
Highland | INVERNESS | FOYERS
Highland | INVERNESS | HILTON
Highland | INVERNESS | INVERARNIE
Highland | INVERNESS | INVERNESS 11 kV
Highland | INVERNESS | RAIGMORE
Highland | INVERNESS | WATERLOO PLACE
Highland | KEITH | ABERLOUR
Argyll and Bute | KILLIN | CHAORACH
Highland | KILLIN | WESTER DRUMMOND
Highland | KINLOCHLEVEN | GLENCOE
Highland | KINLOCHLEVEN | KINLOCHLEVEN
Highland | LAIRG | LAIRG GRID
Highland | LAIRG | TORBOLL
Highland | LAIRG | TRESSADY
Highland | MYBSTER | LATHERON
Highland | MYBSTER | MELVICH
Highland | MYBSTER | WICK
Highland | NAIRN | ARDERSIER
Highland | NAIRN | DALCROSS
Highland | NAIRN | FORRES
Highland | NAIRN | LETHEN
Highland | NAIRN | NAIRN CENTRAL
Highland | QUOICH | QUOICH PRIMARY
Highland | RANNOCH | BLACKMOUNT
Highland | RANNOCH | BRIDGE OF GAUR
Highland | RANNOCH | GLENETIVE
Highland | SHIN | GLEDFIELD
Highland | SHIN | SHIN
Highland | ST FILLANS | COMRIE
Highland | TAYNUILT | BARCALDINE
Highland | TAYNUILT | SALEN
Highland | THURSO | HALKIRK
Highland | THURSO | HASTIGROW
Highland | THURSO | MOUNT PLEASANT
Highland | THURSO | ORMLIE
Highland | TUMMEL BRIDGE | BONSKEID
Highland | TUMMEL BRIDGE | CALVINE
Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
Moray | BOAT OF GARTEN | AVIEMORE
Moray | BOAT OF GARTEN | BALLINDALLOCH
Moray | BOAT OF GARTEN | GRANTOWN
Moray | ELGIN | ASHGROVE
Moray | ELGIN | BILBOHALL
Moray | ELGIN | BURGHEAD
Moray | ELGIN | CUMMING STREET
Moray | ELGIN | ELGIN
Moray | ELGIN | FOCHABERS
Moray | ELGIN | KINLOSS
Moray | ELGIN | LHANBRYDE
Moray | ELGIN | LOSSIEMOUTH
Moray | KEITH | ABERLOUR
Moray | KEITH | BUCKIE
Moray | KEITH | CULLEN
Moray | KEITH | DUFFTOWN
Moray | KEITH | HUNTLY
Moray | KEITH | KEITH
Moray | KEITH | LIMEHILLOCKS
Moray | KEITH | MARNOCH
Moray | KEITH | ROTHES
Moray | MACDUFF | PORTSOY
Moray | NAIRN | FORRES
Moray | NAIRN | LETHEN
Moray | NAIRN | NAIRN CENTRAL
Moray | TARLAND | BALLATER
Moray | TARLAND | MOSSAT
Moray | TARLAND | STRATHDON
North Ayrshire | CARRADALE | BALLIEKINE
North Ayrshire | CARRADALE | BRODICK
North Ayrshire | CARRADALE | MACHRIE
North Ayrshire | CARRADALE | WHITING BAY
North Ayrshire | DUNOON | BRUCHAG
North Lanarkshire | BRACO | KIPPEN
Orkney Islands | THURSO | BURGARHILL
Orkney Islands | THURSO | EDAY
Orkney Islands | THURSO | EDAY TIDAL
Orkney Islands | THURSO | FLOTTA
Orkney Islands | THURSO | KIRKWALL
Orkney Islands | THURSO | LYNESS
Orkney Islands | THURSO | NORTH HOY
Orkney Islands | THURSO | RACKWICK
Orkney Islands | THURSO | ROUSAY
Orkney Islands | THURSO | SANDAY
Orkney Islands | THURSO | SHAPINSAY
Orkney Islands | THURSO | ST MARYS
Orkney Islands | THURSO | STROMNESS
Orkney Islands | THURSO | STRONSAY
Orkney Islands | THURSO | WESTRAY
Perth and Kinross | ABERNETHY | ABERNETHY
Perth and Kinross | ABERNETHY | BALBEGGIE
Perth and Kinross | ABERNETHY | BRIDGE OF EARN
Perth and Kinross | ABERNETHY | ERROL
Perth and Kinross | ABERNETHY | GLENDEVON
Perth and Kinross | ABERNETHY | HARBOUR
Perth and Kinross | ABERNETHY | MILNATHORT
Perth and Kinross | ABERNETHY | SCONE
Perth and Kinross | BOAT OF GARTEN | AVIEMORE
Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
Perth and Kinross | BRACO | CALLANDER
Perth and Kinross | BRACO | CRIEFF
Perth and Kinross | BRACO | DUNBLANE
Perth and Kinross | BRACO | FORTEVIOT
Perth and Kinross | BRACO | GLENEAGLES
Perth and Kinross | BURGHMUIR | BURGHMUIR
Perth and Kinross | BURGHMUIR | GOODLYBURN
Perth and Kinross | BURGHMUIR | INVERALMOND
Perth and Kinross | BURGHMUIR | REDGORTON
Perth and Kinross | BURGHMUIR | THIMBLEROW
Perth and Kinross | CHARLESTON | GOURDIE
Perth and Kinross | CHARLESTON | NINEWELLS
Perth and Kinross | COUPAR ANGUS | ALYTH
Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
Perth and Kinross | COUPAR ANGUS | CAPUTH
Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
Perth and Kinross | COUPAR ANGUS | DALRULZION
Perth and Kinross | COUPAR ANGUS | LEOCH
Perth and Kinross | FORT WILLIAM | INVERLOCHY
Perth and Kinross | KILLIN | CASHLIE
Perth and Kinross | KILLIN | CHAORACH
Perth and Kinross | KILLIN | COSHIEVILLE
Perth and Kinross | KILLIN | KILLIN TOWN
Perth and Kinross | KILLIN | LOCHEARNHEAD
Perth and Kinross | LUNANHEAD | MARYTON
Perth and Kinross | RANNOCH | BLACKMOUNT
Perth and Kinross | RANNOCH | BRIDGE OF GAUR
Perth and Kinross | RANNOCH | GLENETIVE
Perth and Kinross | RANNOCH | TYNDRUM
Perth and Kinross | ST FILLANS | DALCHONZIE
Perth and Kinross | ST FILLANS | ST FILLANS P S
Perth and Kinross | TARLAND | BALLATER
Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
Perth and Kinross | TUMMEL BRIDGE | BONSKEID
Perth and Kinross | TUMMEL BRIDGE | CALVINE
Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
Shetland Islands | SHETLAND | FIRTH
Shetland Islands | SHETLAND | GUTCHER
Shetland Islands | SHETLAND | MID YELL
Shetland Islands | SHETLAND | SANDWICK
Shetland Islands | SHETLAND | SCALLOWAY
Shetland Islands | SHETLAND | SUMBURGH
Shetland Islands | SHETLAND | TUMBLIN
Shetland Islands | SHETLAND | UNST
Shetland Islands | SHETLAND | VOE
Shetland Islands | WOODHILL | BRAE
Stirling | BRACO | CALLANDER
Stirling | BRACO | DUNBLANE
Stirling | BRACO | GLENEAGLES
Stirling | BRACO | KIPPEN
Stirling | KILLIN | ARCHYLE
Stirling | KILLIN | CASHLIE
Stirling | KILLIN | CHAORACH
Stirling | KILLIN | COSHIEVILLE
Stirling | KILLIN | KILLIN TOWN
Stirling | KILLIN | LOCHEARNHEAD
Stirling | KILLIN | LUBNAIG
Stirling | RANNOCH | TYNDRUM
Stirling | ST FILLANS | DALCHONZIE
Stirling | ST FILLANS | ST FILLANS P S
Stirling | STRATHLEVEN | ABERFOYLE
Stirling | STRATHLEVEN | DRYMEN
Stirling | STRATHLEVEN | KEPCULLOCH
Stirling | STRATHLEVEN | KILLEARN
Stirling | TAYNUILT | DALMALLY
West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
West Dunbartonshire | STRATHLEVEN | DRYMEN
West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
| GSPs in November 2023 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2024 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2028 | Under active review
| Killin | 2024 | Under active review | 2030 | Under active review
| Rannoch | 2024 | Under active review | 2025 | Under active review
| St Fillans | 2024 | Under active review | 2028 | Under active review
| Tummel Bridge | 2024 | Under active review | 2025 | Under active review
| Redmoss | NA |  | NA
| Woodhill | NA |  | NA
| Ardkinglas | 2024 | Under active review | 2030 | Under active review
| Ardmore | NA | Under active review | 2026 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2030 | Under active review
| Lyndhurst | 2032 | Under active review | 2030 | Under active review
| Peterhead Grange | 2033 | Under active review | 2026 | Under active review
| Dunbeath | NA |  | 2028 | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2026 | Under active review | 2026 | Under active review
| Brora | NA |  | 2030 | Under active review
| Dunvegan | NA |  | 2026 | Under active review
| Fasnakyle | 2024 | Under active review | 2027 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2030 | Under active review
| Shin | NA |  | 2027 | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2027 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2024 | Under active review | NA
| Kinlochleven | 2024 | Under active review | NA
| Glenfarclas | 2024 | Under active review | NA
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2028 | Under active review
| Craigiebuckler | NA |  | NA
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | NA
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2030 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2029 | Under active review | 2029 | Under active review
| Quoich | NA |  | NA
| Boat of Garten | 2024 | Under active review | 2028 | Under active review
| Inverness | NA |  | 2024 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2024 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2028 | Under active review
| Carradale 1 | 2024 | Under active review | 2034 | Under active review
| Carradale 2 | 2024 | Under active review | 2034 | Under active review
| Clachan | 2024 | Under active review | 2030 | Under active review
| Dunoon | 2024 | Under active review | 2028 | Under active review
| Fort William | 2024 | Under active review | 2024 | Under active review
| Port Ann | 2027 | Under active review | 2034 | Under active review
| Taynuilt | 2024 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | NA
| Mybster 2 | NA |  | NA
| Thurso | NA |  | NA
| Sloy | 2024 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2023-03-01 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 For storage, both the demand and generation EISDs may be relevant.
3 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.